## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6810-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6810-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6810-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6810-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6810-4_0_2_node_49 | 0.4 | n |  | TRUE
5 | bus_LV_6810-4_0_2_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_6810-4_0_2_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_6810-4_0_2_node_46 | 0.4 | n |  | TRUE
8 | bus_LV_6810-4_0_2_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_6810-4_0_2_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_6810-4_0_2_node_117 | 0.4 | n |  | TRUE
11 | bus_LV_6810-4_0_2_node_68 | 0.4 | n |  | TRUE
12 | bus_LV_6810-4_0_2_node_50 | 0.4 | n |  | TRUE
13 | bus_LV_6810-4_0_2_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_6810-4_0_2_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_6810-4_0_2_node_53 | 0.4 | n |  | TRUE
16 | bus_LV_6810-4_0_2_node_54 | 0.4 | n |  | TRUE
17 | bus_LV_6810-4_0_2_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_6810-4_0_2_node_74 | 0.4 | n |  | TRUE
19 | bus_LV_6810-4_0_2_node_73 | 0.4 | n |  | TRUE
20 | bus_LV_6810-4_0_2_node_77 | 0.4 | n |  | TRUE
21 | bus_LV_6810-4_0_2_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_6810-4_0_2_node_65 | 0.4 | n |  | TRUE
23 | bus_LV_6810-4_0_2_node_66 | 0.4 | n |  | TRUE
24 | bus_LV_6810-4_0_2_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_6810-4_0_2_node_80 | 0.4 | n |  | TRUE
26 | bus_LV_6810-4_0_2_node_114 | 0.4 | n |  | TRUE
27 | bus_LV_6810-4_0_2_node_115 | 0.4 | n |  | TRUE
28 | bus_LV_6810-4_0_2_node_116 | 0.4 | n |  | TRUE
29 | bus_LV_6810-4_0_2_node_118 | 0.4 | n |  | TRUE
30 | bus_MV_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6810-4_0_2_load_0 | 0 | 0.00054328 | 0.00013616 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6810-4_0_2_load_1 | 1 | 0.0030448 | 0.00076311 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6810-4_0_2_load_3 | 3 | 0.013648 | 0.0034206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6810-4_0_2_load_44 | 5 | 0.00071797 | 0.00017994 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6810-4_0_2_load_45 | 6 | 0.0020135 | 0.00050462 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6810-4_0_2_load_47 | 8 | 0.00043701 | 0.00010953 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6810-4_0_2_load_48 | 9 | 0.00039914 | 0.00010003 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6810-4_0_2_load_50 | 12 | 0.0048027 | 0.0012037 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6810-4_0_2_load_54 | 16 | 0.0013563 | 0.00033991 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6810-4_0_2_load_74 | 18 | 0.0015856 | 0.00039739 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6810-4_0_2_load_73 | 19 | 0.00072658 | 0.0001821 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6810-4_0_2_load_77 | 20 | 0.001452 | 0.00036391 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6810-4_0_2_load_64 | 21 | 0.00069185 | 0.00017339 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6810-4_0_2_load_65 | 22 | 0.00073224 | 0.00018352 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6810-4_0_2_load_66 | 23 | 0.0015005 | 0.00037607 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6810-4_0_2_load_67 | 24 | 0.0004009 | 0.00010047 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6810-4_0_2_load_80 | 25 | 0.0010873 | 0.0002725 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6810-4_0_2_load_114 | 26 | 0.00016447 | 4.1221e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6810-4_0_2_load_115 | 27 | 0.0013634 | 0.00034171 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6810-4_0_2_load_118 | 29 | 0.00063305 | 0.00015866 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6810-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6810-4_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.13992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6810-4_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.20955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6810-4_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.98349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6810-4_0_2_line_4 | NAYY 4x150 SE | 4 | 8 | 0.089719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6810-4_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.07783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6810-4_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.067177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6810-4_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.004193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6810-4_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.014422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6810-4_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.26024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6810-4_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.02726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6810-4_0_2_line_11 | NAYY 4x150 SE | 10 | 27 | 0.0093287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6810-4_0_2_line_12 | NAYY 4x150 SE | 11 | 25 | 0.10003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6810-4_0_2_line_13 | NAYY 4x150 SE | 11 | 23 | 0.0069502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6810-4_0_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.043738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6810-4_0_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.014748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6810-4_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.009309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6810-4_0_2_line_17 | NAYY 4x150 SE | 13 | 16 | 0.060941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6810-4_0_2_line_18 | NAYY 4x150 SE | 14 | 17 | 0.013789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6810-4_0_2_line_19 | NAYY 4x150 SE | 15 | 18 | 0.01337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6810-4_0_2_line_20 | NAYY 4x150 SE | 15 | 19 | 0.048541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6810-4_0_2_line_21 | NAYY 4x150 SE | 17 | 20 | 0.071213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6810-4_0_2_line_22 | NAYY 4x150 SE | 19 | 24 | 0.0080947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6810-4_0_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.0093864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6810-4_0_2_line_24 | NAYY 4x150 SE | 21 | 23 | 0.021162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6810-4_0_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.0061339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6810-4_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.013362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6810-4_0_2_line_27 | NAYY 4x150 SE | 26 | 28 | 0.011307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6810-4_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.028361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6810-4_0_2_trafo_49 | 0.25 MVA 20/0.4 kV | 30 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2584361.0974 | 1253504.408 | 2584360.071 | 1253506.3793 | 2584354.0505 | 1253515.2072
1 | 2584285.6474 | 1253637.1302 | 2584288.7437 | 1253629.8616 | 2584303.761 | 1253603.1262 | 2584343.1921 | 1253531.1293 | 2584354.0505 | 1253515.2072
2 | 2584285.6474 | 1253637.1302 | 2584282.5325 | 1253643.1091 | 2584276.7241 | 1253648.9952 | 2584269.2768 | 1253651.4167 | 2584260.5198 | 1253652.0961 | 2584248.6801 | 1253651.0381 | 2584238.3759 | 1253648.6641 | 2584227.8452 | 1253643.4444 | 2584217.9703 | 1253635.1765 | 2584207.6508 | 1253627.1211 | 2584202.3825 | 1253623.4216 | 2584197.9783 | 1253615.5727 | 2584192.8936 | 1253598.7642 | 2584188.0282 | 1253582.1774 | 2584184.7025 | 1253568.644 | 2584183.1435 | 1253558.3859 | 2584176.3208 | 1253546.174 | 2584166.2151 | 1253536.3724 | 2584160.7198 | 1253529.6161 | 2584158.7261 | 1253523.2839
3 | 2583887.484 | 1252577.9416 | 2584158.7261 | 1253523.2839
4 | 2583887.484 | 1252577.9416 | 2583887.0468 | 1252567.0579 | 2583884.2054 | 1252557.2259 | 2583879.3512 | 1252550.8683 | 2583867.1917 | 1252535.8028 | 2583854.2511 | 1252524.8755 | 2583848.1706 | 1252517.0982 | 2583847.5242 | 1252512.4969 | 2583849.4228 | 1252508.6781 | 2583853.2375 | 1252504.6984 | 2583853.2375 | 1252504.6984
5 | 2583775.5294 | 1252479.4464 | 2583789.7374 | 1252484.3705 | 2583847.3259 | 1252500.7342 | 2583849.755 | 1252502.3631
6 | 2583712.3521 | 1252458.3557 | 2583721.7545 | 1252458.4853 | 2583743.7778 | 1252468.4422 | 2583775.5294 | 1252479.4464
7 | 2583849.755 | 1252502.3631 | 2583853.2375 | 1252504.6984
8 | 2583712.3521 | 1252458.3557 | 2583704.6616 | 1252468.7726 | 2583703.811 | 1252469.9757
9 | 2583853.2375 | 1252504.6984 | 2584011.4604 | 1252298.0758
10 | 2583688.0732 | 1252492.2339 | 2583703.811 | 1252469.9757
11 | 2584011.4604 | 1252298.0758 | 2584017.2709 | 1252290.7776
12 | 2583688.0732 | 1252492.2339 | 2583690.1588 | 1252479.6977 | 2583692.1088 | 1252461.7806 | 2583692.888 | 1252448.8588 | 2583681.2279 | 1252412.7785 | 2583677.1957 | 1252394.793
13 | 2583688.0732 | 1252492.2339 | 2583683.4727 | 1252497.4436
14 | 2583639.6003 | 1252576.7127 | 2583652.8746 | 1252585.4149 | 2583669.7947 | 1252589.1927 | 2583680.1191 | 1252591.2574
15 | 2583694.5806 | 1252594.1495 | 2583680.1191 | 1252591.2574
16 | 2583630.9739 | 1252573.3455 | 2583637.5215 | 1252575.3509 | 2583639.6003 | 1252576.7127
17 | 2583687.5008 | 1252538.944 | 2583646.554 | 1252570.0779 | 2583639.6003 | 1252576.7127
18 | 2583694.5806 | 1252594.1495 | 2583708.1783 | 1252591.6325
19 | 2583630.9739 | 1252573.3455 | 2583620.4602 | 1252581.6046
20 | 2583630.9739 | 1252573.3455 | 2583635.4883 | 1252563.2375 | 2583645.7015 | 1252540.2162 | 2583653.8337 | 1252531.0071
21 | 2583708.1783 | 1252591.6325 | 2583737.5306 | 1252586.1923 | 2583778.0586 | 1252577.9362
22 | 2583653.8337 | 1252531.0071 | 2583659.1918 | 1252524.9396
23 | 2583669.465 | 1252513.3061 | 2583663.2519 | 1252520.3419
24 | 2583669.465 | 1252513.3061 | 2583683.4727 | 1252497.4436
25 | 2583659.1918 | 1252524.9396 | 2583663.2519 | 1252520.3419
26 | 2584022.1001 | 1252278.5699 | 2584021.7885 | 1252280.5252 | 2584019.5598 | 1252287.9027 | 2584017.2709 | 1252290.7776
27 | 2584022.0773 | 1252267.3936 | 2584022.9459 | 1252273.2617 | 2584022.1001 | 1252278.5699
28 | 2584022.0773 | 1252267.3936 | 2584015.3201 | 1252263.2981 | 2584013.2785 | 1252258.9897 | 2584011.769 | 1252253.3234 | 2584008.3789 | 1252249.8303 | 2584003.7257 | 1252248.1128

## bus_geodata
| x | y | coords
0 | 2584361.0974 | 1253504.408
1 | 2584354.0505 | 1253515.2072
2 | 2584285.6474 | 1253637.1302
3 | 2584158.7261 | 1253523.2839
4 | 2583887.484 | 1252577.9416
5 | 2583775.5294 | 1252479.4464
6 | 2583849.755 | 1252502.3631
7 | 2583712.3521 | 1252458.3557
8 | 2583853.2375 | 1252504.6984
9 | 2583703.811 | 1252469.9757
10 | 2584011.4604 | 1252298.0758
11 | 2583688.0732 | 1252492.2339
12 | 2583680.1191 | 1252591.2574
13 | 2583639.6003 | 1252576.7127
14 | 2583694.5806 | 1252594.1495
15 | 2583630.9739 | 1252573.3455
16 | 2583687.5008 | 1252538.944
17 | 2583708.1783 | 1252591.6325
18 | 2583620.4602 | 1252581.6046
19 | 2583653.8337 | 1252531.0071
20 | 2583778.0586 | 1252577.9362
21 | 2583669.465 | 1252513.3061
22 | 2583663.2519 | 1252520.3419
23 | 2583683.4727 | 1252497.4436
24 | 2583659.1918 | 1252524.9396
25 | 2583677.1957 | 1252394.793
26 | 2584022.1001 | 1252278.5699
27 | 2584017.2709 | 1252290.7776
28 | 2584022.0773 | 1252267.3936
29 | 2584003.7257 | 1252248.1128
30 | 2583887.484 | 1252577.9416

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1