## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6810-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6810-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6810-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6810-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6810-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6810-5_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6810-5_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6810-5_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_6810-5_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_6810-5_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_6810-5_0_3_node_162 | 0.4 | n |  | TRUE
11 | bus_LV_6810-5_0_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_6810-5_0_3_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_6810-5_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_6810-5_0_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_6810-5_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_6810-5_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_6810-5_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_6810-5_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_6810-5_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_6810-5_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_6810-5_0_3_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_6810-5_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_6810-5_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_6810-5_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_6810-5_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_6810-5_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_6810-5_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_6810-5_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_6810-5_0_3_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_6810-5_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_6810-5_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_6810-5_0_3_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_6810-5_0_3_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_6810-5_0_3_node_80 | 0.4 | n |  | TRUE
35 | bus_LV_6810-5_0_3_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_6810-5_0_3_node_47 | 0.4 | n |  | TRUE
37 | bus_LV_6810-5_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_6810-5_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_6810-5_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_6810-5_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_6810-5_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_6810-5_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_6810-5_0_3_node_62 | 0.4 | n |  | TRUE
44 | bus_LV_6810-5_0_3_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_6810-5_0_3_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_6810-5_0_3_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_6810-5_0_3_node_68 | 0.4 | n |  | TRUE
48 | bus_LV_6810-5_0_3_node_82 | 0.4 | n |  | TRUE
49 | bus_LV_6810-5_0_3_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_6810-5_0_3_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_6810-5_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_6810-5_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_6810-5_0_3_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_6810-5_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_6810-5_0_3_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_6810-5_0_3_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_6810-5_0_3_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_6810-5_0_3_node_160 | 0.4 | n |  | TRUE
59 | bus_LV_6810-5_0_3_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_6810-5_0_3_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_6810-5_0_3_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_6810-5_0_3_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_6810-5_0_3_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_6810-5_0_3_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_6810-5_0_3_node_83 | 0.4 | n |  | TRUE
66 | bus_LV_6810-5_0_3_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_6810-5_0_3_node_96 | 0.4 | n |  | TRUE
68 | bus_LV_6810-5_0_3_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_6810-5_0_3_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_6810-5_0_3_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_6810-5_0_3_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_6810-5_0_3_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_6810-5_0_3_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_6810-5_0_3_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_6810-5_0_3_node_79 | 0.4 | n |  | TRUE
76 | bus_LV_6810-5_0_3_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_6810-5_0_3_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_6810-5_0_3_node_87 | 0.4 | n |  | TRUE
79 | bus_LV_6810-5_0_3_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_6810-5_0_3_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_6810-5_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_6810-5_0_3_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_6810-5_0_3_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_6810-5_0_3_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_6810-5_0_3_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_6810-5_0_3_node_75 | 0.4 | n |  | TRUE
87 | bus_LV_6810-5_0_3_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_6810-5_0_3_node_92 | 0.4 | n |  | TRUE
89 | bus_LV_6810-5_0_3_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_6810-5_0_3_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_6810-5_0_3_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_6810-5_0_3_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_6810-5_0_3_node_88 | 0.4 | n |  | TRUE
94 | bus_LV_6810-5_0_3_node_95 | 0.4 | n |  | TRUE
95 | bus_LV_6810-5_0_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_6810-5_0_3_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_6810-5_0_3_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_6810-5_0_3_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_6810-5_0_3_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_6810-5_0_3_node_155 | 0.4 | n |  | TRUE
101 | bus_LV_6810-5_0_3_node_153 | 0.4 | n |  | TRUE
102 | bus_LV_6810-5_0_3_node_154 | 0.4 | n |  | TRUE
103 | bus_LV_6810-5_0_3_node_156 | 0.4 | n |  | TRUE
104 | bus_LV_6810-5_0_3_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_6810-5_0_3_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_6810-5_0_3_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_6810-5_0_3_node_108 | 0.4 | n |  | TRUE
108 | bus_LV_6810-5_0_3_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_6810-5_0_3_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_6810-5_0_3_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_6810-5_0_3_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_6810-5_0_3_node_157 | 0.4 | n |  | TRUE
113 | bus_LV_6810-5_0_3_node_158 | 0.4 | n |  | TRUE
114 | bus_LV_6810-5_0_3_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_6810-5_0_3_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_6810-5_0_3_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_6810-5_0_3_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_6810-5_0_3_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_6810-5_0_3_node_119 | 0.4 | n |  | TRUE
120 | bus_LV_6810-5_0_3_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_6810-5_0_3_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_6810-5_0_3_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_6810-5_0_3_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_6810-5_0_3_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_6810-5_0_3_node_133 | 0.4 | n |  | TRUE
126 | bus_LV_6810-5_0_3_node_120 | 0.4 | n |  | TRUE
127 | bus_LV_6810-5_0_3_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_6810-5_0_3_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_6810-5_0_3_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_6810-5_0_3_node_134 | 0.4 | n |  | TRUE
131 | bus_LV_6810-5_0_3_node_136 | 0.4 | n |  | TRUE
132 | bus_LV_6810-5_0_3_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_6810-5_0_3_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_6810-5_0_3_node_126 | 0.4 | n |  | TRUE
135 | bus_LV_6810-5_0_3_node_127 | 0.4 | n |  | TRUE
136 | bus_LV_6810-5_0_3_node_128 | 0.4 | n |  | TRUE
137 | bus_LV_6810-5_0_3_node_129 | 0.4 | n |  | TRUE
138 | bus_LV_6810-5_0_3_node_130 | 0.4 | n |  | TRUE
139 | bus_LV_6810-5_0_3_node_131 | 0.4 | n |  | TRUE
140 | bus_LV_6810-5_0_3_node_132 | 0.4 | n |  | TRUE
141 | bus_LV_6810-5_0_3_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_6810-5_0_3_node_135 | 0.4 | n |  | TRUE
143 | bus_LV_6810-5_0_3_node_138 | 0.4 | n |  | TRUE
144 | bus_LV_6810-5_0_3_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_6810-5_0_3_node_141 | 0.4 | n |  | TRUE
146 | bus_LV_6810-5_0_3_node_142 | 0.4 | n |  | TRUE
147 | bus_LV_6810-5_0_3_node_140 | 0.4 | n |  | TRUE
148 | bus_LV_6810-5_0_3_node_152 | 0.4 | n |  | TRUE
149 | bus_LV_6810-5_0_3_node_151 | 0.4 | n |  | TRUE
150 | bus_LV_6810-5_0_3_node_159 | 0.4 | n |  | TRUE
151 | bus_LV_6810-5_0_3_node_149 | 0.4 | n |  | TRUE
152 | bus_LV_6810-5_0_3_node_143 | 0.4 | n |  | TRUE
153 | bus_LV_6810-5_0_3_node_144 | 0.4 | n |  | TRUE
154 | bus_LV_6810-5_0_3_node_145 | 0.4 | n |  | TRUE
155 | bus_LV_6810-5_0_3_node_146 | 0.4 | n |  | TRUE
156 | bus_LV_6810-5_0_3_node_147 | 0.4 | n |  | TRUE
157 | bus_LV_6810-5_0_3_node_148 | 0.4 | n |  | TRUE
158 | bus_LV_6810-5_0_3_node_150 | 0.4 | n |  | TRUE
159 | bus_MV_342_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6810-5_0_3_load_0 | 0 | 0.0055669 | 0.0013952 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6810-5_0_3_load_1 | 1 | 0.0043112 | 0.0010805 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6810-5_0_3_load_2 | 2 | 0.0011182 | 0.00028024 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6810-5_0_3_load_3 | 3 | 0.0025803 | 0.00064669 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6810-5_0_3_load_5 | 5 | 0.0017051 | 0.00042733 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6810-5_0_3_load_6 | 6 | 0.0010386 | 0.00026029 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6810-5_0_3_load_7 | 7 | 0.00239 | 0.000599 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6810-5_0_3_load_9 | 8 | 0.0043892 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6810-5_0_3_load_162 | 10 | 0.0013642 | 0.0003419 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6810-5_0_3_load_13 | 13 | 0.0007018 | 0.00017589 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6810-5_0_3_load_27 | 14 | 0.00069834 | 0.00017502 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6810-5_0_3_load_12 | 15 | 0.00039865 | 9.9911e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6810-5_0_3_load_24 | 16 | 0.0020567 | 0.00051545 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6810-5_0_3_load_10 | 17 | 0.00084737 | 0.00021237 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6810-5_0_3_load_11 | 18 | 0.00040578 | 0.0001017 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6810-5_0_3_load_14 | 19 | 0.0023049 | 0.00057767 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6810-5_0_3_load_15 | 20 | 0.00060992 | 0.00015286 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6810-5_0_3_load_16 | 21 | 0.004377 | 0.001097 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6810-5_0_3_load_19 | 23 | 0.00042304 | 0.00010602 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6810-5_0_3_load_20 | 24 | 0.0016209 | 0.00040624 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6810-5_0_3_load_28 | 25 | 0.0016467 | 0.00041269 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6810-5_0_3_load_29 | 26 | 0.0039695 | 0.00099484 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6810-5_0_3_load_22 | 28 | 0.00054343 | 0.0001362 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6810-5_0_3_load_36 | 29 | 0.00079277 | 0.00019869 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6810-5_0_3_load_25 | 30 | 0.001246 | 0.00031227 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6810-5_0_3_load_69 | 33 | 0.00060044 | 0.00015048 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6810-5_0_3_load_49 | 35 | 0.0012928 | 0.00032399 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6810-5_0_3_load_30 | 37 | 0.00061524 | 0.00015419 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6810-5_0_3_load_31 | 38 | 0.0010057 | 0.00025204 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6810-5_0_3_load_32 | 39 | 0.007555 | 0.0018935 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6810-5_0_3_load_34 | 41 | 0.00066676 | 0.00016711 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6810-5_0_3_load_35 | 42 | 0.00056059 | 0.0001405 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6810-5_0_3_load_62 | 43 | 0.0040108 | 0.0010052 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6810-5_0_3_load_104 | 44 | 0.0016242 | 0.00040706 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6810-5_0_3_load_61 | 45 | 0.0030911 | 0.0007747 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6810-5_0_3_load_64 | 46 | 0.0010921 | 0.0002737 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6810-5_0_3_load_82 | 48 | 0.0019891 | 0.00049852 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6810-5_0_3_load_38 | 50 | 0.0027761 | 0.00069575 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6810-5_0_3_load_39 | 51 | 0.00043366 | 0.00010869 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6810-5_0_3_load_40 | 52 | 0.00032208 | 8.0721e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6810-5_0_3_load_42 | 54 | 0.00032997 | 8.2699e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6810-5_0_3_load_43 | 55 | 0.00057912 | 0.00014514 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6810-5_0_3_load_52 | 56 | 0.00047424 | 0.00011886 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6810-5_0_3_load_53 | 57 | 0.00027767 | 6.9591e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6810-5_0_3_load_160 | 58 | 0.00051726 | 0.00012964 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6810-5_0_3_load_44 | 59 | 0.001083 | 0.00027142 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6810-5_0_3_load_48 | 61 | 0.0010783 | 0.00027025 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6810-5_0_3_load_46 | 62 | 0.00064225 | 0.00016096 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6810-5_0_3_load_50 | 63 | 0.0023803 | 0.00059655 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6810-5_0_3_load_51 | 64 | 0.00067912 | 0.0001702 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6810-5_0_3_load_83 | 65 | 0.0014576 | 0.00036532 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6810-5_0_3_load_59 | 66 | 0.0013024 | 0.00032642 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6810-5_0_3_load_96 | 67 | 0.00037561 | 9.4136e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6810-5_0_3_load_54 | 68 | 0.0037203 | 0.00093239 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6810-5_0_3_load_55 | 69 | 0.00020489 | 5.1349e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6810-5_0_3_load_56 | 70 | 0.00082395 | 0.0002065 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6810-5_0_3_load_57 | 71 | 0.00046041 | 0.00011539 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6810-5_0_3_load_58 | 72 | 0.0011296 | 0.0002831 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6810-5_0_3_load_81 | 73 | 0.0011794 | 0.00029558 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6810-5_0_3_load_76 | 74 | 0.0015836 | 0.00039688 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6810-5_0_3_load_65 | 76 | 0.0047438 | 0.0011889 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6810-5_0_3_load_86 | 77 | 0.0011535 | 0.0002891 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6810-5_0_3_load_87 | 78 | 0.0029704 | 0.00074444 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6810-5_0_3_load_66 | 79 | 0.0022893 | 0.00057376 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6810-5_0_3_load_67 | 80 | 0.004034 | 0.001011 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6810-5_0_3_load_70 | 81 | 0.0015206 | 0.0003811 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6810-5_0_3_load_71 | 82 | 0.00099935 | 0.00025046 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6810-5_0_3_load_72 | 83 | 0.00065597 | 0.0001644 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6810-5_0_3_load_92 | 88 | 0.00070956 | 0.00017783 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6810-5_0_3_load_89 | 89 | 0.0010401 | 0.00026066 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6810-5_0_3_load_78 | 90 | 0.00081042 | 0.00020311 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6810-5_0_3_load_84 | 92 | 0.0047696 | 0.0011954 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6810-5_0_3_load_88 | 93 | 0.00035706 | 8.9487e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6810-5_0_3_load_95 | 94 | 0.00053971 | 0.00013526 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6810-5_0_3_load_91 | 95 | 0.00066876 | 0.00016761 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6810-5_0_3_load_94 | 97 | 0.0017683 | 0.00044318 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6810-5_0_3_load_97 | 98 | 0.0021761 | 0.00054538 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6810-5_0_3_load_90 | 99 | 0.00029819 | 7.4733e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6810-5_0_3_load_155 | 100 | 0.00057416 | 0.0001439 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6810-5_0_3_load_153 | 101 | 0.00049483 | 0.00012402 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6810-5_0_3_load_154 | 102 | 0.00019405 | 4.8634e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6810-5_0_3_load_156 | 103 | 0.00060432 | 0.00015146 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6810-5_0_3_load_99 | 105 | 0.00070558 | 0.00017684 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6810-5_0_3_load_108 | 107 | 0.0010905 | 0.0002733 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6810-5_0_3_load_106 | 108 | 0.0016392 | 0.00041082 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6810-5_0_3_load_101 | 109 | 0.00058602 | 0.00014687 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6810-5_0_3_load_102 | 110 | 0.00074574 | 0.0001869 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6810-5_0_3_load_103 | 111 | 0.0071975 | 0.0018039 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6810-5_0_3_load_157 | 112 | 0.00066421 | 0.00016647 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6810-5_0_3_load_158 | 113 | 0.00049559 | 0.00012421 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6810-5_0_3_load_107 | 114 | 0.00060549 | 0.00015175 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6810-5_0_3_load_110 | 116 | 0.00080314 | 0.00020129 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6810-5_0_3_load_112 | 118 | 0.0065442 | 0.0016401 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6810-5_0_3_load_119 | 119 | 0.0014082 | 0.00035294 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6810-5_0_3_load_116 | 120 | 0.0036075 | 0.00090413 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6810-5_0_3_load_113 | 121 | 0.0010435 | 0.00026153 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6810-5_0_3_load_121 | 122 | 0.0029595 | 0.00074173 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6810-5_0_3_load_114 | 123 | 0.0047701 | 0.0011955 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6810-5_0_3_load_133 | 125 | 0.0026409 | 0.00066187 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6810-5_0_3_load_123 | 127 | 0.0015488 | 0.00038817 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6810-5_0_3_load_118 | 128 | 0.00056879 | 0.00014255 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_6810-5_0_3_load_117 | 129 | 0.0050922 | 0.0012762 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_6810-5_0_3_load_134 | 130 | 0.0012608 | 0.000316 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_6810-5_0_3_load_136 | 131 | 0.0018397 | 0.00046107 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_6810-5_0_3_load_124 | 132 | 0.00036555 | 9.1615e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_6810-5_0_3_load_125 | 133 | 0.00024939 | 6.2503e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_6810-5_0_3_load_126 | 134 | 0.0008378 | 0.00020997 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_6810-5_0_3_load_129 | 137 | 0.0012526 | 0.00031392 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_6810-5_0_3_load_130 | 138 | 0.0022507 | 0.00056408 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_6810-5_0_3_load_131 | 139 | 0.0011212 | 0.00028099 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_6810-5_0_3_load_132 | 140 | 0.0018384 | 0.00046074 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_6810-5_0_3_load_135 | 142 | 0.0035423 | 0.00088778 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_6810-5_0_3_load_139 | 144 | 0.00055843 | 0.00013996 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_6810-5_0_3_load_141 | 145 | 0.00039267 | 9.8412e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_6810-5_0_3_load_142 | 146 | 0.00048033 | 0.00012038 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_6810-5_0_3_load_140 | 147 | 0.00019297 | 4.8363e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_6810-5_0_3_load_152 | 148 | 0.0015723 | 0.00039405 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_6810-5_0_3_load_151 | 149 | 0.00077899 | 0.00019523 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_6810-5_0_3_load_159 | 150 | 0.0006324 | 0.00015849 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_6810-5_0_3_load_149 | 151 | 0.00027448 | 6.8792e-05 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_6810-5_0_3_load_143 | 152 | 0.00017026 | 4.2671e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_6810-5_0_3_load_146 | 155 | 0.00024572 | 6.1582e-05 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_6810-5_0_3_load_147 | 156 | 0.00023899 | 5.9897e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_6810-5_0_3_load_148 | 157 | 0.00047031 | 0.00011787 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_6810-5_0_3_load_150 | 158 | 0.0019542 | 0.00048977 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 78 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6810-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0055522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6810-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6810-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.014315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6810-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6810-5_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.020877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6810-5_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.037336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6810-5_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.033737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6810-5_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.020193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6810-5_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.020842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6810-5_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.063913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6810-5_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.015502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6810-5_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.02738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6810-5_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.024452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6810-5_0_3_line_13 | NAYY 4x150 SE | 11 | 16 | 0.012316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6810-5_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.041199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6810-5_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.015721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6810-5_0_3_line_16 | NAYY 4x150 SE | 14 | 28 | 0.027912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6810-5_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.04124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6810-5_0_3_line_18 | NAYY 4x150 SE | 16 | 29 | 0.0188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6810-5_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.018183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6810-5_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.011203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6810-5_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.038211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6810-5_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.036198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6810-5_0_3_line_23 | NAYY 4x150 SE | 22 | 25 | 0.085387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6810-5_0_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.091953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6810-5_0_3_line_25 | NAYY 4x150 SE | 24 | 27 | 0.056173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6810-5_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.03392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6810-5_0_3_line_27 | NAYY 4x150 SE | 26 | 35 | 0.013777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6810-5_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.010417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6810-5_0_3_line_29 | NAYY 4x150 SE | 29 | 32 | 0.015247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6810-5_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.029259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6810-5_0_3_line_31 | NAYY 4x150 SE | 31 | 33 | 0.032644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6810-5_0_3_line_32 | NAYY 4x150 SE | 31 | 34 | 0.019704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6810-5_0_3_line_33 | NAYY 4x150 SE | 32 | 46 | 0.014197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6810-5_0_3_line_34 | NAYY 4x150 SE | 32 | 45 | 0.0051384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6810-5_0_3_line_35 | NAYY 4x150 SE | 33 | 47 | 0.010175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6810-5_0_3_line_36 | NAYY 4x150 SE | 34 | 48 | 0.022238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6810-5_0_3_line_37 | NAYY 4x150 SE | 34 | 49 | 0.017839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6810-5_0_3_line_38 | NAYY 4x150 SE | 35 | 36 | 0.018692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6810-5_0_3_line_39 | NAYY 4x150 SE | 36 | 63 | 0.034493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6810-5_0_3_line_40 | NAYY 4x150 SE | 36 | 62 | 0.029713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6810-5_0_3_line_41 | NAYY 4x150 SE | 37 | 38 | 0.017103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6810-5_0_3_line_42 | NAYY 4x150 SE | 37 | 39 | 0.01792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6810-5_0_3_line_43 | NAYY 4x150 SE | 38 | 40 | 0.019099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6810-5_0_3_line_44 | NAYY 4x150 SE | 40 | 41 | 0.039391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_6810-5_0_3_line_45 | NAYY 4x150 SE | 40 | 42 | 0.0084463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6810-5_0_3_line_46 | NAYY 4x150 SE | 41 | 43 | 0.017012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6810-5_0_3_line_47 | NAYY 4x150 SE | 42 | 44 | 0.025653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_6810-5_0_3_line_48 | NAYY 4x150 SE | 43 | 45 | 0.030205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_6810-5_0_3_line_49 | NAYY 4x150 SE | 46 | 76 | 0.0055474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_6810-5_0_3_line_50 | NAYY 4x150 SE | 47 | 81 | 0.015451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6810-5_0_3_line_51 | NAYY 4x150 SE | 47 | 79 | 0.018254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6810-5_0_3_line_52 | NAYY 4x150 SE | 49 | 73 | 0.021561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6810-5_0_3_line_53 | NAYY 4x150 SE | 49 | 74 | 0.010221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6810-5_0_3_line_54 | NAYY 4x150 SE | 49 | 72 | 0.058207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6810-5_0_3_line_55 | NAYY 4x150 SE | 50 | 51 | 0.032776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_6810-5_0_3_line_56 | NAYY 4x150 SE | 50 | 52 | 0.02162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_6810-5_0_3_line_57 | NAYY 4x150 SE | 51 | 53 | 0.011592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_6810-5_0_3_line_58 | NAYY 4x150 SE | 53 | 54 | 0.047914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_6810-5_0_3_line_59 | NAYY 4x150 SE | 53 | 55 | 0.035397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_6810-5_0_3_line_60 | NAYY 4x150 SE | 54 | 56 | 0.070354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_6810-5_0_3_line_61 | NAYY 4x150 SE | 55 | 57 | 0.02539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_6810-5_0_3_line_62 | NAYY 4x150 SE | 56 | 58 | 0.021009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_6810-5_0_3_line_63 | NAYY 4x150 SE | 58 | 67 | 0.0092508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_6810-5_0_3_line_64 | NAYY 4x150 SE | 59 | 60 | 0.061482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_6810-5_0_3_line_65 | NAYY 4x150 SE | 59 | 61 | 0.10348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_6810-5_0_3_line_66 | NAYY 4x150 SE | 60 | 62 | 0.017043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_6810-5_0_3_line_67 | NAYY 4x150 SE | 63 | 64 | 0.0033657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_6810-5_0_3_line_68 | NAYY 4x150 SE | 64 | 65 | 0.0035545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_6810-5_0_3_line_69 | NAYY 4x150 SE | 65 | 66 | 0.026028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_6810-5_0_3_line_70 | NAYY 4x150 SE | 66 | 71 | 0.028099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_6810-5_0_3_line_71 | NAYY 4x150 SE | 67 | 94 | 0.006908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_6810-5_0_3_line_72 | NAYY 4x150 SE | 68 | 69 | 0.0088812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_6810-5_0_3_line_73 | NAYY 4x150 SE | 68 | 70 | 0.00327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_6810-5_0_3_line_74 | NAYY 4x150 SE | 69 | 71 | 0.011148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_6810-5_0_3_line_75 | NAYY 4x150 SE | 70 | 72 | 0.015322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_6810-5_0_3_line_76 | NAYY 4x150 SE | 73 | 75 | 0.032076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_6810-5_0_3_line_77 | NAYY 4x150 SE | 75 | 92 | 0.0060323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_6810-5_0_3_line_78 | NAYY 4x150 SE | 75 | 86 | 0.01556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_6810-5_0_3_line_79 | NAYY 4x150 SE | 76 | 77 | 0.021031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_6810-5_0_3_line_80 | NAYY 4x150 SE | 77 | 78 | 0.0054354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_6810-5_0_3_line_81 | NAYY 4x150 SE | 78 | 96 | 0.026452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_6810-5_0_3_line_82 | NAYY 4x150 SE | 79 | 80 | 0.018643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_6810-5_0_3_line_83 | NAYY 4x150 SE | 82 | 83 | 0.037692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_6810-5_0_3_line_84 | NAYY 4x150 SE | 82 | 84 | 0.022646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_6810-5_0_3_line_85 | NAYY 4x150 SE | 83 | 85 | 0.0065197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_6810-5_0_3_line_86 | NAYY 4x150 SE | 84 | 86 | 0.00679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_6810-5_0_3_line_87 | NAYY 4x150 SE | 85 | 87 | 0.02 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_6810-5_0_3_line_88 | NAYY 4x150 SE | 87 | 88 | 0.012402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_6810-5_0_3_line_89 | NAYY 4x150 SE | 87 | 89 | 0.017856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_6810-5_0_3_line_90 | NAYY 4x150 SE | 89 | 93 | 0.0011618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_6810-5_0_3_line_91 | NAYY 4x150 SE | 90 | 91 | 0.035259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_6810-5_0_3_line_92 | NAYY 4x150 SE | 91 | 94 | 0.0099856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_6810-5_0_3_line_93 | NAYY 4x150 SE | 91 | 95 | 0.020769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_6810-5_0_3_line_94 | NAYY 4x150 SE | 92 | 96 | 0.016719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_6810-5_0_3_line_95 | NAYY 4x150 SE | 93 | 99 | 0.018268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_6810-5_0_3_line_96 | NAYY 4x150 SE | 95 | 100 | 0.039381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_6810-5_0_3_line_97 | NAYY 4x150 SE | 95 | 99 | 0.027776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_6810-5_0_3_line_98 | NAYY 4x150 SE | 96 | 97 | 0.029996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_6810-5_0_3_line_99 | NAYY 4x150 SE | 97 | 98 | 0.012666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_6810-5_0_3_line_100 | NAYY 4x150 SE | 98 | 107 | 0.0078268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_6810-5_0_3_line_101 | NAYY 4x150 SE | 100 | 103 | 0.017849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_6810-5_0_3_line_102 | NAYY 4x150 SE | 100 | 102 | 0.024886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_6810-5_0_3_line_103 | NAYY 4x150 SE | 101 | 102 | 0.012338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_6810-5_0_3_line_104 | NAYY 4x150 SE | 104 | 105 | 0.016239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_6810-5_0_3_line_105 | NAYY 4x150 SE | 104 | 106 | 0.006605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_6810-5_0_3_line_106 | NAYY 4x150 SE | 105 | 109 | 0.02334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_6810-5_0_3_line_107 | NAYY 4x150 SE | 106 | 110 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_6810-5_0_3_line_108 | NAYY 4x150 SE | 107 | 108 | 0.014135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_6810-5_0_3_line_109 | NAYY 4x150 SE | 108 | 114 | 0.0039478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_6810-5_0_3_line_110 | NAYY 4x150 SE | 109 | 111 | 0.023144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_6810-5_0_3_line_111 | NAYY 4x150 SE | 110 | 112 | 0.02692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_6810-5_0_3_line_112 | NAYY 4x150 SE | 112 | 113 | 0.010726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_6810-5_0_3_line_113 | NAYY 4x150 SE | 113 | 142 | 0.0019371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_6810-5_0_3_line_114 | NAYY 4x150 SE | 114 | 115 | 0.0020208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_6810-5_0_3_line_115 | NAYY 4x150 SE | 115 | 116 | 0.0042747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_6810-5_0_3_line_116 | NAYY 4x150 SE | 115 | 117 | 0.015068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_6810-5_0_3_line_117 | NAYY 4x150 SE | 116 | 118 | 0.01854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_6810-5_0_3_line_118 | NAYY 4x150 SE | 117 | 119 | 0.0034124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_6810-5_0_3_line_119 | NAYY 4x150 SE | 117 | 120 | 0.023989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_6810-5_0_3_line_120 | NAYY 4x150 SE | 118 | 121 | 0.017549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_6810-5_0_3_line_121 | NAYY 4x150 SE | 119 | 122 | 0.016837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_6810-5_0_3_line_122 | NAYY 4x150 SE | 121 | 123 | 0.018572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_6810-5_0_3_line_123 | NAYY 4x150 SE | 123 | 124 | 0.021908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_6810-5_0_3_line_124 | NAYY 4x150 SE | 124 | 125 | 0.015794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_6810-5_0_3_line_125 | NAYY 4x150 SE | 124 | 126 | 0.017336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_6810-5_0_3_line_126 | NAYY 4x150 SE | 126 | 127 | 0.035939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_6810-5_0_3_line_127 | NAYY 4x150 SE | 126 | 128 | 0.013876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_6810-5_0_3_line_128 | NAYY 4x150 SE | 127 | 130 | 0.0074418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_6810-5_0_3_line_129 | NAYY 4x150 SE | 128 | 129 | 0.0081951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_6810-5_0_3_line_130 | NAYY 4x150 SE | 130 | 131 | 0.0013375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_6810-5_0_3_line_131 | NAYY 4x150 SE | 131 | 137 | 0.01555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_6810-5_0_3_line_132 | NAYY 4x150 SE | 132 | 133 | 0.010492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_6810-5_0_3_line_133 | NAYY 4x150 SE | 132 | 134 | 0.00085416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_6810-5_0_3_line_134 | NAYY 4x150 SE | 133 | 135 | 0.012791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_6810-5_0_3_line_135 | NAYY 4x150 SE | 134 | 136 | 0.038717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_6810-5_0_3_line_136 | NAYY 4x150 SE | 135 | 137 | 0.021659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_6810-5_0_3_line_137 | NAYY 4x150 SE | 135 | 138 | 0.0081133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_6810-5_0_3_line_138 | NAYY 4x150 SE | 136 | 139 | 0.0029103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_6810-5_0_3_line_139 | NAYY 4x150 SE | 136 | 140 | 0.013817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_6810-5_0_3_line_140 | NAYY 4x150 SE | 138 | 141 | 0.015782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_6810-5_0_3_line_141 | NAYY 4x150 SE | 139 | 142 | 0.014911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_6810-5_0_3_line_142 | NAYY 4x150 SE | 141 | 143 | 0.016223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_6810-5_0_3_line_143 | NAYY 4x150 SE | 141 | 144 | 0.024353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_6810-5_0_3_line_144 | NAYY 4x150 SE | 143 | 145 | 0.0056404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_6810-5_0_3_line_145 | NAYY 4x150 SE | 144 | 146 | 0.052231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_6810-5_0_3_line_146 | NAYY 4x150 SE | 145 | 149 | 0.017117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_6810-5_0_3_line_147 | NAYY 4x150 SE | 147 | 148 | 0.0049279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_6810-5_0_3_line_148 | NAYY 4x150 SE | 148 | 150 | 0.010237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_6810-5_0_3_line_149 | NAYY 4x150 SE | 149 | 151 | 0.020236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_6810-5_0_3_line_150 | NAYY 4x150 SE | 150 | 158 | 0.029355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_6810-5_0_3_line_151 | NAYY 4x150 SE | 151 | 156 | 0.013926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_6810-5_0_3_line_152 | NAYY 4x150 SE | 152 | 153 | 0.030638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_6810-5_0_3_line_153 | NAYY 4x150 SE | 152 | 154 | 0.0098829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_6810-5_0_3_line_154 | NAYY 4x150 SE | 153 | 155 | 0.0079919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_6810-5_0_3_line_155 | NAYY 4x150 SE | 154 | 156 | 0.0016941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_6810-5_0_3_line_156 | NAYY 4x150 SE | 154 | 157 | 0.016529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_6810-5_0_3_line_157 | NAYY 4x150 SE | 157 | 158 | 0.014045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6810-5_0_3_trafo_87 | 0.25 MVA 20/0.4 kV | 159 | 78 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2580242.711 | 1253123.7893 | 2580242.711 | 1253123.7893 | 2580241.4516 | 1253118.3818
1 | 2580242.711 | 1253123.7893 | 2580242.2531 | 1253137.9891 | 2580239.4466 | 1253152.0221
2 | 2580238.6472 | 1253104.3878 | 2580238.6538 | 1253106.3691 | 2580241.4516 | 1253118.3818
3 | 2580234.8803 | 1253175.8054 | 2580239.0623 | 1253153.9436 | 2580239.4466 | 1253152.0221
4 | 2580238.6472 | 1253104.3878 | 2580238.6087 | 1253092.9271 | 2580242.7455 | 1253084.4677
5 | 2580234.8803 | 1253175.8054 | 2580233.9411 | 1253213.1299
6 | 2580234.8803 | 1253175.8054 | 2580201.496 | 1253180.6727
7 | 2580252.2439 | 1253066.6627 | 2580252.1553 | 1253066.9201 | 2580246.2222 | 1253077.358 | 2580242.7455 | 1253084.4677
8 | 2580233.7928 | 1253233.9697 | 2580233.7818 | 1253219.4601 | 2580233.9411 | 1253213.1299
9 | 2580201.496 | 1253180.6727 | 2580141.3431 | 1253159.0753
10 | 2580257.2888 | 1253052.0042 | 2580252.2439 | 1253066.6627
11 | 2580233.7928 | 1253233.9697 | 2580234.7131 | 1253254.1911 | 2580233.7032 | 1253261.2547
12 | 2580233.7928 | 1253233.9697 | 2580257.3069 | 1253227.2628
13 | 2580257.2888 | 1253052.0042 | 2580246.4127 | 1253046.2254
14 | 2580233.7032 | 1253261.2547 | 2580251.7701 | 1253271.6788 | 2580263.9266 | 1253276.7637 | 2580270.7368 | 1253278.9841
15 | 2580257.3069 | 1253227.2628 | 2580272.4247 | 1253222.9507
16 | 2580270.7368 | 1253278.9841 | 2580272.6352 | 1253279.6031 | 2580282.2263 | 1253282.384 | 2580294.6054 | 1253284.1215 | 2580298.0234 | 1253284.3909
17 | 2580312.0831 | 1253211.639 | 2580272.4247 | 1253222.9507
18 | 2580246.4127 | 1253046.2254 | 2580243.9178 | 1253044.8998 | 2580235.1453 | 1253043.3393 | 2580228.0818 | 1253043.4263
19 | 2580312.0831 | 1253211.639 | 2580329.5687 | 1253206.6516
20 | 2580456.7001 | 1253139.2336 | 2580456.1948 | 1253139.7662 | 2580454.6122 | 1253142.5956 | 2580453.9493 | 1253147.4565 | 2580454.2136 | 1253149.7628
21 | 2580478.2991 | 1253167.0383 | 2580468.4174 | 1253169.323 | 2580464.4493 | 1253169.4585 | 2580461.1646 | 1253168.6688 | 2580459.1148 | 1253167.0968 | 2580457.6342 | 1253164.2776 | 2580456.1472 | 1253159.535 | 2580454.6486 | 1253153.5582 | 2580454.2136 | 1253149.7628
22 | 2580486.2311 | 1253119.2532 | 2580482.3113 | 1253122.624 | 2580479.4869 | 1253124.1009 | 2580474.7317 | 1253125.8178 | 2580470.0904 | 1253127.7456 | 2580466.2425 | 1253130.0154 | 2580462.7435 | 1253132.8622 | 2580456.7001 | 1253139.2336
23 | 2580473.9642 | 1253034.7521 | 2580486.2311 | 1253119.2532
24 | 2580363.7967 | 1253277.3323 | 2580454.0027 | 1253259.4928
25 | 2580308.4084 | 1253285.2095 | 2580325.5497 | 1253285.1189 | 2580363.7967 | 1253277.3323
26 | 2580473.3802 | 1253000.8482 | 2580473.307 | 1253021.4648 | 2580473.9642 | 1253034.7521
27 | 2580473.3802 | 1253000.8482 | 2580473.4085 | 1252992.89 | 2580473.3485 | 1252987.0714
28 | 2580308.4084 | 1253285.2095 | 2580298.0234 | 1253284.3909
29 | 2580212.8356 | 1253043.6143 | 2580228.0818 | 1253043.4263
30 | 2580286.174 | 1252998.7502 | 2580281.5232 | 1253000.0888 | 2580277.3413 | 1253024.1477
31 | 2580286.174 | 1252998.7502 | 2580307.6079 | 1253000.4908 | 2580311.4543 | 1253002.268 | 2580315.1589 | 1253008.0917
32 | 2580286.174 | 1252998.7502 | 2580287.0438 | 1252979.0676
33 | 2580212.8356 | 1253043.6143 | 2580212.718 | 1253029.4177
34 | 2580212.8356 | 1253043.6143 | 2580207.7017 | 1253043.8294
35 | 2580322.0687 | 1253015.3746 | 2580317.4464 | 1253011.6876 | 2580315.1589 | 1253008.0917
36 | 2580304.5359 | 1252984.346 | 2580302.9061 | 1252984.3181 | 2580297.2546 | 1252984.2591 | 2580297.284 | 1252979.5003 | 2580287.0438 | 1252979.0676
37 | 2580284.3666 | 1252961.4316 | 2580287.0438 | 1252979.0676
38 | 2580469.686 | 1252969.2757 | 2580472.2175 | 1252972.7362 | 2580473.2862 | 1252981.0271 | 2580473.3485 | 1252987.0714
39 | 2580469.686 | 1252969.2757 | 2580461.1423 | 1252963.9449 | 2580439.2696 | 1252953.0798
40 | 2580469.686 | 1252969.2757 | 2580472.0478 | 1252969.3457 | 2580499.0384 | 1252973.7657
41 | 2580122.8752 | 1253083.5765 | 2580122.069 | 1253066.4922
42 | 2580140.6512 | 1253085.8403 | 2580122.8752 | 1253083.5765
43 | 2580121.1687 | 1253047.4139 | 2580122.069 | 1253066.4922
44 | 2580121.1687 | 1253047.4139 | 2580141.349 | 1253046.6232 | 2580160.5267 | 1253045.8125
45 | 2580121.1687 | 1253047.4139 | 2580112.7255 | 1253047.6402
46 | 2580177.5231 | 1253045.0942 | 2580176.7829 | 1253045.1252 | 2580160.5267 | 1253045.8125
47 | 2580087.0813 | 1253048.3273 | 2580112.7255 | 1253047.6402
48 | 2580207.7017 | 1253043.8294 | 2580177.5231 | 1253045.0942
49 | 2580212.718 | 1253029.4177 | 2580212.6721 | 1253023.8705
50 | 2580321.1846 | 1253030.7988 | 2580322.0687 | 1253015.3746
51 | 2580322.0687 | 1253015.3746 | 2580329.4057 | 1253016.3396 | 2580340.2577 | 1253016.148
52 | 2580284.3666 | 1252961.4316 | 2580278.5663 | 1252961.9958 | 2580271.4767 | 1252962.82 | 2580262.9132 | 1252963.5644
53 | 2580284.3666 | 1252961.4316 | 2580282.3035 | 1252951.4208
54 | 2580284.3666 | 1252961.4316 | 2580320.8294 | 1252956.0507 | 2580342.0523 | 1252953.733
55 | 2580503.6386 | 1252773.633 | 2580490.9725 | 1252773.7985 | 2580475.0035 | 1252775.1523 | 2580470.9565 | 1252775.6928
56 | 2580525.2296 | 1252772.9027 | 2580520.5944 | 1252773.4115 | 2580503.6386 | 1252773.633
57 | 2580459.4669 | 1252777.2273 | 2580470.9565 | 1252775.6928
58 | 2580459.4669 | 1252777.2273 | 2580412.6042 | 1252787.2073
59 | 2580459.4669 | 1252777.2273 | 2580461.0688 | 1252768.7942 | 2580475.5927 | 1252746.2553
60 | 2580412.6042 | 1252787.2073 | 2580370.5249 | 1252796.1685 | 2580343.9223 | 1252802.4369
61 | 2580475.5927 | 1252746.2553 | 2580489.346 | 1252724.9124
62 | 2580343.9223 | 1252802.4369 | 2580327.1129 | 1252806.3977 | 2580323.5907 | 1252807.6534
63 | 2580314.8771 | 1252810.7598 | 2580323.5907 | 1252807.6534
64 | 2580515.9002 | 1252976.2385 | 2580531.8676 | 1252992.8189 | 2580556.2873 | 1253019.1224 | 2580558.288 | 1253020.739
65 | 2580558.288 | 1253020.739 | 2580621.0219 | 1252938.4469
66 | 2580515.9002 | 1252976.2385 | 2580503.3921 | 1252974.4787 | 2580499.0384 | 1252973.7657
67 | 2580439.2696 | 1252953.0798 | 2580436.2552 | 1252951.5825
68 | 2580436.2552 | 1252951.5825 | 2580435.0837 | 1252951.0005 | 2580433.0082 | 1252950.1412
69 | 2580408.0353 | 1252944.3865 | 2580415.7984 | 1252944.2045 | 2580422.2695 | 1252945.6951 | 2580433.0082 | 1252950.1412
70 | 2580408.0353 | 1252944.3865 | 2580403.0858 | 1252944.5025 | 2580389.1491 | 1252946.5168 | 2580380.2494 | 1252948.2507
71 | 2580308.5643 | 1252813.4687 | 2580310.0808 | 1252812.4696 | 2580314.8771 | 1252810.7598
72 | 2580360.5339 | 1252951.7147 | 2580364.9373 | 1252951.2338 | 2580369.3068 | 1252950.3825
73 | 2580360.5339 | 1252951.7147 | 2580357.2832 | 1252952.0697
74 | 2580380.2494 | 1252948.2507 | 2580369.3068 | 1252950.3825
75 | 2580342.0523 | 1252953.733 | 2580357.2832 | 1252952.0697
76 | 2580230.9502 | 1252964.5903 | 2580241.7349 | 1252965.4213 | 2580257.9069 | 1252963.9996 | 2580262.9132 | 1252963.5644
77 | 2580230.9502 | 1252964.5903 | 2580228.0193 | 1252965.8454 | 2580225.3512 | 1252966.8301
78 | 2580230.9502 | 1252964.5903 | 2580233.0833 | 1252961.7145 | 2580233.6292 | 1252960.2451 | 2580234.451 | 1252957.8074 | 2580235.1308 | 1252955.7815 | 2580236.8555 | 1252950.3388
79 | 2580212.2823 | 1253002.8513 | 2580212.5183 | 1253005.29 | 2580212.6721 | 1253023.8705
80 | 2580212.2823 | 1253002.8513 | 2580211.759 | 1252997.4411
81 | 2580209.2119 | 1252971.1119 | 2580211.759 | 1252997.4411
82 | 2580358.8976 | 1253015.8188 | 2580340.2577 | 1253016.148
83 | 2580242.9232 | 1252921.5433 | 2580243.6726 | 1252917.7389 | 2580247.5918 | 1252896.1671 | 2580251.155 | 1252884.8238
84 | 2580238.5462 | 1252943.7622 | 2580242.9232 | 1252921.5433
85 | 2580253.1088 | 1252878.6037 | 2580251.155 | 1252884.8238
86 | 2580238.5462 | 1252943.7622 | 2580236.8555 | 1252950.3388
87 | 2580236.1566 | 1252867.9201 | 2580240.2478 | 1252870.686 | 2580253.1088 | 1252878.6037
88 | 2580236.1566 | 1252867.9201 | 2580223.9766 | 1252865.5835
89 | 2580236.1566 | 1252867.9201 | 2580247.5905 | 1252854.2047
90 | 2580248.3344 | 1252853.3124 | 2580247.5905 | 1252854.2047
91 | 2580300.2256 | 1252818.9624 | 2580284.3449 | 1252833.1248 | 2580275.5711 | 1252844.0093
92 | 2580300.2256 | 1252818.9624 | 2580308.5643 | 1252813.4687
93 | 2580300.2256 | 1252818.9624 | 2580296.1149 | 1252817.1305 | 2580291.3912 | 1252817.0462 | 2580280.3715 | 1252820.4853
94 | 2580209.2119 | 1252971.1119 | 2580221.8475 | 1252968.1231 | 2580225.3512 | 1252966.8301
95 | 2580260.251 | 1252839.4708 | 2580255.2298 | 1252845.0412 | 2580248.3344 | 1252853.3124
96 | 2580280.3715 | 1252820.4853 | 2580245.5036 | 1252802.1788
97 | 2580280.3715 | 1252820.4853 | 2580270.5502 | 1252828.0454 | 2580260.251 | 1252839.4708
98 | 2580209.2119 | 1252971.1119 | 2580184.9457 | 1252975.285 | 2580179.5899 | 1252975.7259
99 | 2580179.5899 | 1252975.7259 | 2580166.9667 | 1252976.7649
100 | 2580159.1549 | 1252977.0592 | 2580162.6938 | 1252977.1166 | 2580166.9667 | 1252976.7649
101 | 2580245.5036 | 1252802.1788 | 2580249.8109 | 1252799.6071 | 2580252.6349 | 1252795.6951 | 2580256.3451 | 1252788.5989
102 | 2580245.5036 | 1252802.1788 | 2580245.5036 | 1252802.1788 | 2580233.2719 | 1252799.7293 | 2580220.9711 | 1252798.0746
103 | 2580220.9711 | 1252798.0746 | 2580215.2078 | 1252797.2994 | 2580208.7521 | 1252798.2327 | 2580208.7521 | 1252798.2327
104 | 2580185.2854 | 1252863.1099 | 2580185.6752 | 1252879.3442
105 | 2580178.6608 | 1252863.1544 | 2580185.2854 | 1252863.1099
106 | 2580185.6752 | 1252879.3442 | 2580186.2355 | 1252902.6772
107 | 2580178.6608 | 1252863.1544 | 2580164.343 | 1252863.3689
108 | 2580145.0216 | 1252976.83 | 2580159.1549 | 1252977.0592
109 | 2580145.0216 | 1252976.83 | 2580142.8265 | 1252976.7944 | 2580141.0743 | 1252976.7693
110 | 2580196.4449 | 1252921.522 | 2580186.4611 | 1252912.0716 | 2580186.2355 | 1252902.6772
111 | 2580137.4269 | 1252863.2628 | 2580153.7703 | 1252863.5272 | 2580164.343 | 1252863.3689
112 | 2580137.4269 | 1252863.2628 | 2580128.1754 | 1252863.1132 | 2580126.7035 | 1252863.1729
113 | 2580124.7679 | 1252863.2514 | 2580126.7035 | 1252863.1729
114 | 2580139.0537 | 1252976.7404 | 2580141.0743 | 1252976.7693
115 | 2580139.0537 | 1252976.7404 | 2580134.783 | 1252976.5563
116 | 2580138.0752 | 1252961.7782 | 2580139.0018 | 1252965.8 | 2580139.0333 | 1252972.9157 | 2580139.0537 | 1252976.7404
117 | 2580116.2605 | 1252975.7581 | 2580134.783 | 1252976.5563
118 | 2580138.0752 | 1252961.7782 | 2580141.4875 | 1252961.8158
119 | 2580138.0752 | 1252961.7782 | 2580114.0878 | 1252961.5137
120 | 2580116.2605 | 1252975.7581 | 2580114.4078 | 1252975.6783 | 2580098.7331 | 1252974.8797
121 | 2580141.4875 | 1252961.8158 | 2580158.3236 | 1252962.001
122 | 2580098.7331 | 1252974.8797 | 2580095.7832 | 1252974.7294 | 2580085.4522 | 1252974.1972 | 2580080.1788 | 1252974.1489
123 | 2580058.563 | 1252976.8899 | 2580061.2914 | 1252976.0356 | 2580073.0476 | 1252974.0835 | 2580080.1788 | 1252974.1489
124 | 2580058.563 | 1252976.8899 | 2580050.122 | 1252979.7203 | 2580044.143 | 1252983.146
125 | 2580053.678 | 1252960.3177 | 2580054.4949 | 1252965.3738 | 2580056.919 | 1252972.6926 | 2580058.563 | 1252976.8899
126 | 2580053.678 | 1252960.3177 | 2580048.0463 | 1252941.6021 | 2580044.6827 | 1252930.9065 | 2580044.1683 | 1252925.7497
127 | 2580053.678 | 1252960.3177 | 2580067.4882 | 1252958.9722
128 | 2580043.7051 | 1252918.3362 | 2580043.6283 | 1252920.3364 | 2580044.1683 | 1252925.7497
129 | 2580075.6524 | 1252959.2623 | 2580069.6382 | 1252958.7627 | 2580067.4882 | 1252958.9722
130 | 2580043.7051 | 1252918.3362 | 2580043.7564 | 1252916.9996
131 | 2580044.9587 | 1252901.5044 | 2580044.0027 | 1252910.5842 | 2580043.7564 | 1252916.9996
132 | 2580069.6077 | 1252874.2341 | 2580060.7257 | 1252877.9728 | 2580059.8801 | 1252878.0976
133 | 2580069.6077 | 1252874.2341 | 2580070.3949 | 1252873.9027
134 | 2580047.2265 | 1252879.9642 | 2580059.8801 | 1252878.0976
135 | 2580106.961 | 1252863.9741 | 2580095.4485 | 1252864.4355 | 2580085.8706 | 1252865.7909 | 2580077.5277 | 1252870.9003 | 2580070.3949 | 1252873.9027
136 | 2580047.2265 | 1252879.9642 | 2580044.9587 | 1252901.5044
137 | 2580047.2265 | 1252879.9642 | 2580045.4905 | 1252872.0389
138 | 2580106.961 | 1252863.9741 | 2580109.8689 | 1252863.8561
139 | 2580106.961 | 1252863.9741 | 2580104.7013 | 1252877.6048
140 | 2580041.0599 | 1252857.0589 | 2580042.8045 | 1252859.777 | 2580045.4905 | 1252872.0389
141 | 2580124.7679 | 1252863.2514 | 2580109.8689 | 1252863.8561
142 | 2580041.0599 | 1252857.0589 | 2580028.59 | 1252846.6387
143 | 2580041.0599 | 1252857.0589 | 2580042.9302 | 1252854.5509 | 2580046.6515 | 1252843.8312 | 2580049.2221 | 1252834.2945
144 | 2580028.59 | 1252846.6387 | 2580022.9499 | 1252846.6969
145 | 2580067.8475 | 1252786.2216 | 2580064.0362 | 1252799.3431 | 2580059.564 | 1252804.4505 | 2580055.1017 | 1252812.482 | 2580049.2221 | 1252834.2945
146 | 2580022.9499 | 1252846.6969 | 2580005.8343 | 1252846.8737
147 | 2580013.9443 | 1252817.044 | 2580013.2904 | 1252816.1482 | 2580009.4743 | 1252816.2925
148 | 2579999.245 | 1252816.6794 | 2580009.4743 | 1252816.2925
149 | 2579985.6141 | 1252846.4555 | 2579994.9393 | 1252846.9863 | 2580005.8343 | 1252846.8737
150 | 2579999.245 | 1252816.6794 | 2579993.9165 | 1252816.881 | 2579980.9919 | 1252814.8124 | 2579970.0585 | 1252814.7272
151 | 2579971.7461 | 1252845.3223 | 2579975.4007 | 1252845.8741 | 2579985.6141 | 1252846.4555
152 | 2579930.4905 | 1252836.8096 | 2579946.8045 | 1252841.5573 | 2579960.2989 | 1252843.5943
153 | 2579970.071 | 1252845.0694 | 2579960.2989 | 1252843.5943
154 | 2579930.4905 | 1252836.8096 | 2579922.9948 | 1252834.0376
155 | 2579970.071 | 1252845.0694 | 2579971.7461 | 1252845.3223
156 | 2579970.071 | 1252845.0694 | 2579970.1468 | 1252840.733 | 2579969.8578 | 1252833.3847 | 2579969.0162 | 1252828.62
157 | 2579970.0585 | 1252814.7272 | 2579970.0585 | 1252814.7272 | 2579968.5115 | 1252825.762 | 2579969.0162 | 1252828.62

## bus_geodata
| x | y | coords
0 | 2580242.711 | 1253123.7893
1 | 2580241.4516 | 1253118.3818
2 | 2580239.4466 | 1253152.0221
3 | 2580238.6472 | 1253104.3878
4 | 2580234.8803 | 1253175.8054
5 | 2580242.7455 | 1253084.4677
6 | 2580233.9411 | 1253213.1299
7 | 2580201.496 | 1253180.6727
8 | 2580252.2439 | 1253066.6627
9 | 2580233.7928 | 1253233.9697
10 | 2580141.3431 | 1253159.0753
11 | 2580257.2888 | 1253052.0042
12 | 2580233.7032 | 1253261.2547
13 | 2580257.3069 | 1253227.2628
14 | 2580270.7368 | 1253278.9841
15 | 2580272.4247 | 1253222.9507
16 | 2580246.4127 | 1253046.2254
17 | 2580312.0831 | 1253211.639
18 | 2580329.5687 | 1253206.6516
19 | 2580454.2136 | 1253149.7628
20 | 2580456.7001 | 1253139.2336
21 | 2580478.2991 | 1253167.0383
22 | 2580486.2311 | 1253119.2532
23 | 2580454.0027 | 1253259.4928
24 | 2580363.7967 | 1253277.3323
25 | 2580473.9642 | 1253034.7521
26 | 2580473.3802 | 1253000.8482
27 | 2580308.4084 | 1253285.2095
28 | 2580298.0234 | 1253284.3909
29 | 2580228.0818 | 1253043.4263
30 | 2580277.3413 | 1253024.1477
31 | 2580286.174 | 1252998.7502
32 | 2580212.8356 | 1253043.6143
33 | 2580315.1589 | 1253008.0917
34 | 2580287.0438 | 1252979.0676
35 | 2580473.3485 | 1252987.0714
36 | 2580469.686 | 1252969.2757
37 | 2580122.8752 | 1253083.5765
38 | 2580122.069 | 1253066.4922
39 | 2580140.6512 | 1253085.8403
40 | 2580121.1687 | 1253047.4139
41 | 2580160.5267 | 1253045.8125
42 | 2580112.7255 | 1253047.6402
43 | 2580177.5231 | 1253045.0942
44 | 2580087.0813 | 1253048.3273
45 | 2580207.7017 | 1253043.8294
46 | 2580212.718 | 1253029.4177
47 | 2580322.0687 | 1253015.3746
48 | 2580304.5359 | 1252984.346
49 | 2580284.3666 | 1252961.4316
50 | 2580503.6386 | 1252773.633
51 | 2580470.9565 | 1252775.6928
52 | 2580525.2296 | 1252772.9027
53 | 2580459.4669 | 1252777.2273
54 | 2580412.6042 | 1252787.2073
55 | 2580475.5927 | 1252746.2553
56 | 2580343.9223 | 1252802.4369
57 | 2580489.346 | 1252724.9124
58 | 2580323.5907 | 1252807.6534
59 | 2580558.288 | 1253020.739
60 | 2580515.9002 | 1252976.2385
61 | 2580621.0219 | 1252938.4469
62 | 2580499.0384 | 1252973.7657
63 | 2580439.2696 | 1252953.0798
64 | 2580436.2552 | 1252951.5825
65 | 2580433.0082 | 1252950.1412
66 | 2580408.0353 | 1252944.3865
67 | 2580314.8771 | 1252810.7598
68 | 2580360.5339 | 1252951.7147
69 | 2580369.3068 | 1252950.3825
70 | 2580357.2832 | 1252952.0697
71 | 2580380.2494 | 1252948.2507
72 | 2580342.0523 | 1252953.733
73 | 2580262.9132 | 1252963.5644
74 | 2580282.3035 | 1252951.4208
75 | 2580230.9502 | 1252964.5903
76 | 2580212.6721 | 1253023.8705
77 | 2580212.2823 | 1253002.8513
78 | 2580211.759 | 1252997.4411
79 | 2580340.2577 | 1253016.148
80 | 2580358.8976 | 1253015.8188
81 | 2580321.1846 | 1253030.7988
82 | 2580242.9232 | 1252921.5433
83 | 2580251.155 | 1252884.8238
84 | 2580238.5462 | 1252943.7622
85 | 2580253.1088 | 1252878.6037
86 | 2580236.8555 | 1252950.3388
87 | 2580236.1566 | 1252867.9201
88 | 2580223.9766 | 1252865.5835
89 | 2580247.5905 | 1252854.2047
90 | 2580275.5711 | 1252844.0093
91 | 2580300.2257 | 1252818.9624
92 | 2580225.3512 | 1252966.8301
93 | 2580248.3344 | 1252853.3124
94 | 2580308.5643 | 1252813.4687
95 | 2580280.3715 | 1252820.4853
96 | 2580209.2119 | 1252971.1119
97 | 2580179.5899 | 1252975.7259
98 | 2580166.9667 | 1252976.7649
99 | 2580260.251 | 1252839.4708
100 | 2580245.5036 | 1252802.1788
101 | 2580208.7521 | 1252798.2328
102 | 2580220.9711 | 1252798.0746
103 | 2580256.3451 | 1252788.5989
104 | 2580185.2854 | 1252863.1099
105 | 2580185.6752 | 1252879.3442
106 | 2580178.6608 | 1252863.1544
107 | 2580159.1549 | 1252977.0592
108 | 2580145.0216 | 1252976.83
109 | 2580186.2355 | 1252902.6772
110 | 2580164.343 | 1252863.3689
111 | 2580196.4449 | 1252921.522
112 | 2580137.4269 | 1252863.2628
113 | 2580126.7035 | 1252863.1729
114 | 2580141.0743 | 1252976.7693
115 | 2580139.0537 | 1252976.7404
116 | 2580134.783 | 1252976.5563
117 | 2580138.0752 | 1252961.7782
118 | 2580116.2605 | 1252975.7581
119 | 2580141.4875 | 1252961.8158
120 | 2580114.0878 | 1252961.5137
121 | 2580098.7331 | 1252974.8797
122 | 2580158.3236 | 1252962.001
123 | 2580080.1788 | 1252974.1489
124 | 2580058.563 | 1252976.8899
125 | 2580044.143 | 1252983.146
126 | 2580053.678 | 1252960.3177
127 | 2580044.1683 | 1252925.7497
128 | 2580067.4882 | 1252958.9722
129 | 2580075.6524 | 1252959.2623
130 | 2580043.7051 | 1252918.3362
131 | 2580043.7564 | 1252916.9996
132 | 2580069.6077 | 1252874.2341
133 | 2580059.8801 | 1252878.0976
134 | 2580070.3949 | 1252873.9027
135 | 2580047.2265 | 1252879.9642
136 | 2580106.961 | 1252863.9741
137 | 2580044.9587 | 1252901.5044
138 | 2580045.4905 | 1252872.0389
139 | 2580109.8689 | 1252863.8561
140 | 2580104.7013 | 1252877.6048
141 | 2580041.0599 | 1252857.0589
142 | 2580124.7679 | 1252863.2514
143 | 2580028.59 | 1252846.6387
144 | 2580049.2221 | 1252834.2945
145 | 2580022.9499 | 1252846.6969
146 | 2580067.8475 | 1252786.2216
147 | 2580013.9443 | 1252817.044
148 | 2580009.4743 | 1252816.2925
149 | 2580005.8343 | 1252846.8737
150 | 2579999.245 | 1252816.6794
151 | 2579985.6141 | 1252846.4555
152 | 2579960.2989 | 1252843.5943
153 | 2579930.4905 | 1252836.8096
154 | 2579970.071 | 1252845.0694
155 | 2579922.9948 | 1252834.0376
156 | 2579971.7461 | 1252845.3223
157 | 2579969.0163 | 1252828.62
158 | 2579970.0585 | 1252814.7272
159 | 2580209.2119 | 1252971.1119

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1