## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2824-2_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2824-2_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2824-2_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2824-2_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2824-2_0_7_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_2824-2_0_7_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2824-2_0_7_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_2824-2_0_7_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2824-2_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2824-2_0_7_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2824-2_0_7_node_68 | 0.4 | n |  | TRUE
11 | bus_LV_2824-2_0_7_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_2824-2_0_7_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_2824-2_0_7_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_2824-2_0_7_node_66 | 0.4 | n |  | TRUE
15 | bus_LV_2824-2_0_7_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_2824-2_0_7_node_69 | 0.4 | n |  | TRUE
17 | bus_LV_2824-2_0_7_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_2824-2_0_7_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_2824-2_0_7_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2824-2_0_7_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2824-2_0_7_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2824-2_0_7_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2824-2_0_7_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2824-2_0_7_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_2824-2_0_7_node_70 | 0.4 | n |  | TRUE
26 | bus_LV_2824-2_0_7_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2824-2_0_7_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2824-2_0_7_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2824-2_0_7_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_2824-2_0_7_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_2824-2_0_7_node_60 | 0.4 | n |  | TRUE
32 | bus_LV_2824-2_0_7_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2824-2_0_7_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2824-2_0_7_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_2824-2_0_7_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_2824-2_0_7_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_2824-2_0_7_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_2824-2_0_7_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2824-2_0_7_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_2824-2_0_7_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_2824-2_0_7_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_2824-2_0_7_node_64 | 0.4 | n |  | TRUE
43 | bus_LV_2824-2_0_7_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2824-2_0_7_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2824-2_0_7_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2824-2_0_7_node_51 | 0.4 | n |  | TRUE
47 | bus_LV_2824-2_0_7_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_2824-2_0_7_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_2824-2_0_7_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_2824-2_0_7_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_2824-2_0_7_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_2824-2_0_7_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_2824-2_0_7_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2824-2_0_7_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_2824-2_0_7_node_58 | 0.4 | n |  | TRUE
56 | bus_LV_2824-2_0_7_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2824-2_0_7_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2824-2_0_7_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_2824-2_0_7_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_2824-2_0_7_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_2824-2_0_7_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_2824-2_0_7_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_2824-2_0_7_node_63 | 0.4 | n |  | TRUE
64 | bus_MV_295_0_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2824-2_0_7_load_0 | 0 | 0.014226 | 0.0035654 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2824-2_0_7_load_1 | 1 | 0.0080513 | 0.0020178 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2824-2_0_7_load_10 | 4 | 0.035681 | 0.0089425 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2824-2_0_7_load_9 | 5 | 0.029909 | 0.0074959 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2824-2_0_7_load_23 | 6 | 0.01774 | 0.004446 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2824-2_0_7_load_5 | 7 | 0.054303 | 0.01361 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2824-2_0_7_load_6 | 8 | 0.0077079 | 0.0019318 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2824-2_0_7_load_68 | 10 | 0.00072535 | 0.00018179 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2824-2_0_7_load_19 | 12 | 0.02783 | 0.0069747 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2824-2_0_7_load_65 | 13 | 0.0030645 | 0.00076804 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2824-2_0_7_load_69 | 16 | 0.001363 | 0.0003416 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2824-2_0_7_load_62 | 18 | 0.0021807 | 0.00054654 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2824-2_0_7_load_11 | 20 | 0.0016719 | 0.00041902 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2824-2_0_7_load_12 | 21 | 0.0041647 | 0.0010438 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2824-2_0_7_load_70 | 25 | 0.0025426 | 0.00063724 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2824-2_0_7_load_16 | 28 | 0.0023093 | 0.00057877 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2824-2_0_7_load_60 | 31 | 0.0031479 | 0.00078894 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2824-2_0_7_load_31 | 33 | 0.087044 | 0.021815 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2824-2_0_7_load_61 | 35 | 0.0033377 | 0.0008365 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2824-2_0_7_load_72 | 37 | 0.004388 | 0.0010997 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2824-2_0_7_load_52 | 39 | 0.0030854 | 0.00077327 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2824-2_0_7_load_54 | 40 | 0.0097213 | 0.0024364 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2824-2_0_7_load_24 | 43 | 0.015035 | 0.003768 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2824-2_0_7_load_30 | 45 | 0.024509 | 0.0061425 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2824-2_0_7_load_57 | 47 | 0.041628 | 0.010433 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2824-2_0_7_load_36 | 50 | 0.074316 | 0.018625 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2824-2_0_7_load_37 | 51 | 0.027932 | 0.0070004 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2824-2_0_7_load_58 | 55 | 0.038826 | 0.0097308 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2824-2_0_7_load_42 | 56 | 0.02559 | 0.0064136 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2824-2_0_7_load_45 | 58 | 0.018614 | 0.0046652 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2824-2_0_7_load_59 | 60 | 0.0080007 | 0.0020052 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2824-2_0_7_load_63 | 63 | 0.00028983 | 7.2638e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2824-2_0_7_line_0 |  | 0 | 1 | 0.019465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2824-2_0_7_line_1 |  | 0 | 2 | 0.067024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2824-2_0_7_line_2 |  | 2 | 3 | 0.013599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2824-2_0_7_line_3 |  | 3 | 4 | 0.047637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2824-2_0_7_line_4 |  | 3 | 5 | 0.037605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2824-2_0_7_line_5 |  | 4 | 6 | 0.0054665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2824-2_0_7_line_6 |  | 6 | 19 | 0.054866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2824-2_0_7_line_7 |  | 7 | 8 | 0.076724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2824-2_0_7_line_8 |  | 8 | 9 | 0.12829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2824-2_0_7_line_9 |  | 8 | 10 | 0.063359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2824-2_0_7_line_10 |  | 9 | 11 | 0.014915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2824-2_0_7_line_11 |  | 9 | 12 | 0.069809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2824-2_0_7_line_12 |  | 10 | 16 | 0.022421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2824-2_0_7_line_13 |  | 11 | 17 | 0.025557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2824-2_0_7_line_14 |  | 11 | 18 | 0.01553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2824-2_0_7_line_15 |  | 12 | 19 | 0.030167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2824-2_0_7_line_16 |  | 13 | 14 | 0.020757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2824-2_0_7_line_17 |  | 14 | 15 | 0.024735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2824-2_0_7_line_18 |  | 15 | 16 | 0.04454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2824-2_0_7_line_19 |  | 17 | 40 | 0.025067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2824-2_0_7_line_20 |  | 19 | 38 | 0.059791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2824-2_0_7_line_21 |  | 20 | 21 | 0.030374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2824-2_0_7_line_22 |  | 20 | 22 | 0.025669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2824-2_0_7_line_23 |  | 22 | 23 | 0.031771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2824-2_0_7_line_24 |  | 23 | 24 | 0.064977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2824-2_0_7_line_25 |  | 23 | 25 | 0.015685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2824-2_0_7_line_26 |  | 24 | 35 | 0.0074942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2824-2_0_7_line_27 |  | 24 | 34 | 0.027317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2824-2_0_7_line_28 |  | 25 | 36 | 0.019908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2824-2_0_7_line_29 |  | 26 | 27 | 0.054964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2824-2_0_7_line_30 |  | 26 | 28 | 0.030061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2824-2_0_7_line_31 |  | 27 | 37 | 0.00892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2824-2_0_7_line_32 |  | 27 | 36 | 0.028674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2824-2_0_7_line_33 |  | 29 | 30 | 0.020032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2824-2_0_7_line_34 |  | 29 | 31 | 0.037752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2824-2_0_7_line_35 |  | 29 | 32 | 0.024165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2824-2_0_7_line_36 |  | 30 | 33 | 0.023241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2824-2_0_7_line_37 |  | 31 | 34 | 0.0026486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2824-2_0_7_line_38 |  | 32 | 43 | 0.034265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2824-2_0_7_line_39 |  | 33 | 49 | 0.02104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2824-2_0_7_line_40 |  | 38 | 39 | 0.063441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2824-2_0_7_line_41 |  | 39 | 41 | 0.051258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2824-2_0_7_line_42 |  | 40 | 62 | 0.024367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2824-2_0_7_line_43 |  | 41 | 42 | 0.085374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2824-2_0_7_line_44 |  | 42 | 63 | 0.061404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2824-2_0_7_line_45 |  | 43 | 44 | 0.0057612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2824-2_0_7_line_46 |  | 44 | 45 | 0.034225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2824-2_0_7_line_47 |  | 46 | 47 | 0.043777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2824-2_0_7_line_48 |  | 46 | 48 | 0.030859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2824-2_0_7_line_49 |  | 47 | 53 | 0.04033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2824-2_0_7_line_50 |  | 48 | 56 | 0.0055079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2824-2_0_7_line_51 |  | 49 | 50 | 0.02934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2824-2_0_7_line_52 |  | 49 | 51 | 0.002831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2824-2_0_7_line_53 |  | 50 | 52 | 0.048002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2824-2_0_7_line_54 |  | 52 | 53 | 0.041359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2824-2_0_7_line_55 |  | 53 | 54 | 0.042856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2824-2_0_7_line_56 |  | 54 | 55 | 0.037537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2824-2_0_7_line_57 |  | 56 | 57 | 0.018167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2824-2_0_7_line_58 |  | 57 | 58 | 0.021944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2824-2_0_7_line_59 |  | 57 | 59 | 0.047148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2824-2_0_7_line_60 |  | 59 | 60 | 0.010507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2824-2_0_7_line_61 |  | 60 | 61 | 0.021552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2824-2_0_7_line_62 |  | 61 | 62 | 0.022218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2824-2_0_7_trafo_43 | 0.63 MVA 20/0.4 kV | 64 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2621056.3199 | 1260968.7277 | 2621075.2308 | 1260973.341
1 | 2620991.2052 | 1260952.8428 | 2621056.3199 | 1260968.7277
2 | 2620977.9551 | 1260949.616 | 2620991.2052 | 1260952.8428
3 | 2620977.9551 | 1260949.616 | 2620967.7035 | 1260996.1369
4 | 2620977.9551 | 1260949.616 | 2620979.0822 | 1260944.1273 | 2620984.2273 | 1260923.1979 | 2620988.326 | 1260913.5864
5 | 2620967.7035 | 1260996.1369 | 2620966.5271 | 1261001.4753
6 | 2620960.9131 | 1261055.5949 | 2620960.0941 | 1261042.1495 | 2620959.7743 | 1261036.7113 | 2620960.0435 | 1261030.8972 | 2620966.5271 | 1261001.4753
7 | 2620873.6234 | 1260899.4799 | 2620873.0477 | 1260949.1233 | 2620873.5258 | 1260976.1964
8 | 2620876.0946 | 1261100.2708 | 2620871.1745 | 1261098.0854 | 2620868.4473 | 1261091.5713 | 2620868.2119 | 1261074.9591 | 2620871.8356 | 1261053.7017 | 2620874.4801 | 1261030.2394 | 2620873.5258 | 1260976.1964
9 | 2620873.5258 | 1260976.1964 | 2620811.6557 | 1260989.8498
10 | 2620876.0946 | 1261100.2708 | 2620884.615 | 1261107.0833 | 2620886.0484 | 1261110.8464
11 | 2620876.0946 | 1261100.2708 | 2620884.1358 | 1261089.1026 | 2620894.5091 | 1261079.0211 | 2620910.2412 | 1261068.4916 | 2620919.1101 | 1261064.0754 | 2620920.5216 | 1261063.3688 | 2620929.7097 | 1261060.3547 | 2620931.1586 | 1261059.9857
12 | 2620811.6557 | 1260989.8498 | 2620810.5647 | 1260995.1131 | 2620803.8507 | 1261001.6829 | 2620801.5688 | 1261008.9866
13 | 2620886.0484 | 1261110.8464 | 2620894.6031 | 1261114.3234 | 2620905.9711 | 1261114.8749 | 2620906.3878 | 1261109.9508
14 | 2620886.0484 | 1261110.8464 | 2620881.3623 | 1261123.5275 | 2620880.609 | 1261125.3919
15 | 2620960.9131 | 1261055.5949 | 2620944.8595 | 1261056.8502 | 2620940.4338 | 1261057.624 | 2620931.1586 | 1261059.9857
16 | 2620767.8177 | 1260980.5088 | 2620787.3089 | 1260987.646
17 | 2620763.2344 | 1261004.7649 | 2620765.3394 | 1260997.5229 | 2620767.8177 | 1260980.5088
18 | 2620763.2344 | 1261004.7649 | 2620799.5756 | 1261015.3661 | 2620801.5688 | 1261008.9866
19 | 2620906.3878 | 1261109.9508 | 2620931.1674 | 1261113.7369
20 | 2621020.3393 | 1261062.232 | 2620997.5316 | 1261057.926 | 2620978.793 | 1261055.6582 | 2620960.9131 | 1261055.5949
21 | 2621173.6255 | 1261310.7602 | 2621203.2868 | 1261317.3018
22 | 2621148.5586 | 1261305.2319 | 2621173.6255 | 1261310.7602
23 | 2621148.5586 | 1261305.2319 | 2621129.0521 | 1261303.0387 | 2621130.0222 | 1261290.8783
24 | 2621083.5842 | 1261291.6358 | 2621083.9925 | 1261289.1355 | 2621077.5769 | 1261288.0564 | 2621077.8978 | 1261284.6774 | 2621108.2073 | 1261289.444 | 2621115.4689 | 1261289.9258 | 2621130.0222 | 1261290.8783
25 | 2621130.0222 | 1261290.8783 | 2621131.3263 | 1261275.2478
26 | 2621083.5842 | 1261291.6358 | 2621090.3022 | 1261294.9573
27 | 2621056.6434 | 1261286.6589 | 2621083.5842 | 1261291.6358
28 | 2621132.9816 | 1261255.4089 | 2621131.3263 | 1261275.2478
29 | 2621165.6612 | 1261229.4632 | 2621161.902 | 1261225.1024 | 2621159.3273 | 1261220.2788 | 2621157.5187 | 1261214.0125 | 2621152.8833 | 1261214.4852 | 2621154.2128 | 1261221.9617 | 2621156.32 | 1261226.8726 | 2621156.1511 | 1261229.874 | 2621155.813 | 1261246.4842
30 | 2621165.6612 | 1261229.4632 | 2621169.3682 | 1261231.589 | 2621174.3442 | 1261232.8188 | 2621194.5977 | 1261236.9052
31 | 2621146.9414 | 1261245.3296 | 2621155.813 | 1261246.4842
32 | 2621132.9816 | 1261255.4089 | 2621136.8798 | 1261252.4986 | 2621153.2717 | 1261253.4244 | 2621155.813 | 1261246.4842
33 | 2621016.925 | 1261279.2685 | 2621018.4442 | 1261271.5464 | 2621021.0105 | 1261259.6584
34 | 2621016.925 | 1261279.2685 | 2621043.5194 | 1261284.2329 | 2621054.039 | 1261286.1774
35 | 2621016.925 | 1261279.2685 | 2621010.6304 | 1261278.0787 | 2620993.1999 | 1261274.6813
36 | 2621021.0105 | 1261259.6584 | 2621025.4493 | 1261236.8448
37 | 2621056.6434 | 1261286.6589 | 2621054.039 | 1261286.1774
38 | 2620993.1999 | 1261274.6813 | 2620979.4035 | 1261255.7195 | 2620979.2774 | 1261248.781 | 2620977.8538 | 1261245.1764
39 | 2621029.4677 | 1261216.192 | 2621025.4493 | 1261236.8448
40 | 2621020.3393 | 1261062.232 | 2621022.4259 | 1261049.6196 | 2621023.784 | 1261044.8545 | 2621026.3809 | 1261041.3391 | 2621031.4657 | 1261037.4433 | 2621034.9235 | 1261035.5098 | 2621058.0781 | 1261029.1543 | 2621064.5476 | 1261026.6062
41 | 2621110.5783 | 1261004.4907 | 2621102.0198 | 1261010.531 | 2621085.7122 | 1261017.4778 | 2621073.2142 | 1261023.1928 | 2621064.5476 | 1261026.6062
42 | 2620955.2544 | 1261117.4172 | 2620931.1674 | 1261113.7369
43 | 2621110.5783 | 1261004.4907 | 2621172.9193 | 1260946.1618
44 | 2621172.9193 | 1260946.1618 | 2621186.2305 | 1260913.298 | 2621196.0912 | 1260895.0652 | 2621198.5727 | 1260890.4745
45 | 2620975.7377 | 1261239.8179 | 2620977.8538 | 1261245.1764
46 | 2620975.7377 | 1261239.8179 | 2620977.3942 | 1261237.9892 | 2620978.0081 | 1261230.6085 | 2620975.3607 | 1261224.9842 | 2620963.021 | 1261211.6537
47 | 2621004.3435 | 1261176.876 | 2621046.5065 | 1261188.6538
48 | 2621013.4971 | 1261147.3994 | 2621004.3435 | 1261176.876
49 | 2621085.5118 | 1261198.8012 | 2621077.7185 | 1261197.3726 | 2621046.5065 | 1261188.6538
50 | 2621013.4971 | 1261147.3994 | 2621015.1285 | 1261142.1386
51 | 2621029.4677 | 1261216.192 | 2621047.3582 | 1261219.5021 | 2621048.1858 | 1261215.6135 | 2621055.2635 | 1261216.7629
52 | 2621026.7049 | 1261215.5373 | 2621029.4677 | 1261216.192
53 | 2621102.6446 | 1261224.4575 | 2621055.2635 | 1261216.7629
54 | 2621102.6446 | 1261224.4575 | 2621104.2609 | 1261202.2147 | 2621085.5118 | 1261198.8012
55 | 2621085.5118 | 1261198.8012 | 2621090.1612 | 1261177.4587 | 2621101.131 | 1261179.7771 | 2621105.814 | 1261180.7611 | 2621106.1784 | 1261175.7589
56 | 2621106.1784 | 1261175.7589 | 2621108.8893 | 1261138.3198
57 | 2621020.5092 | 1261124.7865 | 2621015.1285 | 1261142.1386
58 | 2621020.5092 | 1261124.7865 | 2621037.2957 | 1261120.7988 | 2621041.938 | 1261121.4661
59 | 2621020.5092 | 1261124.7865 | 2621020.3761 | 1261107.085 | 2620991.4394 | 1261101.6344
60 | 2620991.4394 | 1261101.6344 | 2620981.1139 | 1261099.6883
61 | 2620959.9349 | 1261095.6967 | 2620981.1139 | 1261099.6883
62 | 2620955.2544 | 1261117.4172 | 2620959.9349 | 1261095.6967

## bus_geodata
| x | y | coords
0 | 2621056.3199 | 1260968.7276
1 | 2621075.2308 | 1260973.341
2 | 2620991.2052 | 1260952.8428
3 | 2620977.9551 | 1260949.616
4 | 2620967.7035 | 1260996.1369
5 | 2620988.326 | 1260913.5864
6 | 2620966.5271 | 1261001.4753
7 | 2620873.6234 | 1260899.4799
8 | 2620873.5258 | 1260976.1964
9 | 2620876.0946 | 1261100.2708
10 | 2620811.6557 | 1260989.8498
11 | 2620886.0484 | 1261110.8464
12 | 2620931.1586 | 1261059.9857
13 | 2620787.3089 | 1260987.646
14 | 2620767.8177 | 1260980.5088
15 | 2620763.2344 | 1261004.7649
16 | 2620801.5688 | 1261008.9866
17 | 2620906.3878 | 1261109.9508
18 | 2620880.609 | 1261125.3919
19 | 2620960.9131 | 1261055.5949
20 | 2621173.6255 | 1261310.7602
21 | 2621203.2868 | 1261317.3018
22 | 2621148.5586 | 1261305.2319
23 | 2621130.0222 | 1261290.8783
24 | 2621083.5842 | 1261291.6358
25 | 2621131.3263 | 1261275.2478
26 | 2621165.6612 | 1261229.4632
27 | 2621155.813 | 1261246.4842
28 | 2621194.5977 | 1261236.9052
29 | 2621016.925 | 1261279.2685
30 | 2621021.0105 | 1261259.6584
31 | 2621054.039 | 1261286.1774
32 | 2620993.1999 | 1261274.6813
33 | 2621025.4493 | 1261236.8448
34 | 2621056.6434 | 1261286.6589
35 | 2621090.3022 | 1261294.9573
36 | 2621132.9816 | 1261255.4089
37 | 2621146.9414 | 1261245.3296
38 | 2621020.3393 | 1261062.232
39 | 2621064.5476 | 1261026.6062
40 | 2620931.1674 | 1261113.7369
41 | 2621110.5783 | 1261004.4907
42 | 2621172.9193 | 1260946.1618
43 | 2620977.8538 | 1261245.1764
44 | 2620975.7377 | 1261239.8179
45 | 2620963.021 | 1261211.6537
46 | 2621004.3435 | 1261176.876
47 | 2621046.5065 | 1261188.6538
48 | 2621013.4971 | 1261147.3994
49 | 2621029.4677 | 1261216.192
50 | 2621055.2635 | 1261216.7629
51 | 2621026.7049 | 1261215.5373
52 | 2621102.6446 | 1261224.4575
53 | 2621085.5118 | 1261198.8012
54 | 2621106.1784 | 1261175.7589
55 | 2621108.8893 | 1261138.3198
56 | 2621015.1285 | 1261142.1386
57 | 2621020.5092 | 1261124.7865
58 | 2621041.938 | 1261121.4661
59 | 2620991.4394 | 1261101.6344
60 | 2620981.1139 | 1261099.6883
61 | 2620959.9349 | 1261095.6967
62 | 2620955.2544 | 1261117.4172
63 | 2621198.5727 | 1260890.4745
64 | 2621020.3761 | 1261107.085

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1