## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6421-103_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6421-103_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6421-103_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6421-103_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6421-103_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6421-103_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6421-103_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_6421-103_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_6421-103_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_6421-103_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6421-103_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_6421-103_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_6421-103_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_6421-103_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_6421-103_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6421-103_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_6421-103_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6421-103_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_6421-103_0_4_node_46 | 0.4 | n |  | TRUE
19 | bus_LV_6421-103_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_6421-103_0_4_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_6421-103_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_6421-103_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_6421-103_0_4_node_54 | 0.4 | n |  | TRUE
24 | bus_LV_6421-103_0_4_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_6421-103_0_4_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_6421-103_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_6421-103_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_6421-103_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_6421-103_0_4_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_6421-103_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_6421-103_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_6421-103_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_6421-103_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_6421-103_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_6421-103_0_4_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_6421-103_0_4_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_6421-103_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6421-103_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6421-103_0_4_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_6421-103_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_6421-103_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_6421-103_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_6421-103_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_6421-103_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_6421-103_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_6421-103_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_6421-103_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_6421-103_0_4_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_6421-103_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_6421-103_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_6421-103_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_6421-103_0_4_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_6421-103_0_4_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_6421-103_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_MV_335_0_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6421-103_0_4_load_0 | 0 | 0.0006963 | 0.00017451 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6421-103_0_4_load_3 | 3 | 0.00073705 | 0.00018472 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6421-103_0_4_load_4 | 4 | 0.0028493 | 0.0007141 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6421-103_0_4_load_5 | 5 | 0.0003797 | 9.5161e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6421-103_0_4_load_15 | 7 | 0.033873 | 0.0084894 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6421-103_0_4_load_7 | 9 | 0.0051515 | 0.0012911 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6421-103_0_4_load_18 | 10 | 0.00037837 | 9.4828e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6421-103_0_4_load_14 | 11 | 0.033873 | 0.0084893 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6421-103_0_4_load_8 | 12 | 0.015277 | 0.0038289 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6421-103_0_4_load_9 | 13 | 0.01502 | 0.0037643 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6421-103_0_4_load_12 | 16 | 0.00096011 | 0.00024063 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6421-103_0_4_load_16 | 17 | 0.019466 | 0.0048786 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6421-103_0_4_load_46 | 18 | 0.0068342 | 0.0017128 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6421-103_0_4_load_20 | 21 | 0.0019713 | 0.00049406 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6421-103_0_4_load_21 | 22 | 0.003655 | 0.00091602 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6421-103_0_4_load_54 | 23 | 0.0037366 | 0.00093649 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6421-103_0_4_load_55 | 25 | 0.0013656 | 0.00034224 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6421-103_0_4_load_22 | 26 | 0.00063019 | 0.00015794 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6421-103_0_4_load_23 | 27 | 0.0025748 | 0.0006453 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6421-103_0_4_load_31 | 29 | 0.0033363 | 0.00083615 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6421-103_0_4_load_25 | 30 | 0.00092893 | 0.00023281 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6421-103_0_4_load_30 | 32 | 0.0045406 | 0.001138 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6421-103_0_4_load_29 | 33 | 0.002484 | 0.00062256 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6421-103_0_4_load_28 | 34 | 0.000675 | 0.00016917 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6421-103_0_4_load_43 | 35 | 0.0017933 | 0.00044945 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6421-103_0_4_load_27 | 37 | 0.0019547 | 0.0004899 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6421-103_0_4_load_37 | 40 | 0.00078401 | 0.00019649 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6421-103_0_4_load_35 | 42 | 0.0025262 | 0.00063313 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6421-103_0_4_load_39 | 43 | 0.001516 | 0.00037994 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6421-103_0_4_load_36 | 44 | 0.0020943 | 0.00052488 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6421-103_0_4_load_38 | 45 | 0.00056203 | 0.00014086 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6421-103_0_4_load_41 | 46 | 0.0013773 | 0.00034518 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6421-103_0_4_load_45 | 48 | 0.0003713 | 9.3057e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6421-103_0_4_load_47 | 49 | 0.00023402 | 5.8651e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6421-103_0_4_load_50 | 51 | 0.0019626 | 0.00049186 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6421-103_0_4_load_51 | 52 | 0.0048323 | 0.0012111 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6421-103_0_4_load_53 | 53 | 0.00053319 | 0.00013363 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6421-103_0_4_load_52 | 54 | 0.00030117 | 7.548e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6421-103_0_4_line_0 |  | 0 | 1 | 0.0061273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6421-103_0_4_line_1 |  | 0 | 2 | 0.031617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6421-103_0_4_line_2 |  | 1 | 3 | 0.027734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6421-103_0_4_line_3 |  | 1 | 4 | 0.07112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6421-103_0_4_line_4 |  | 2 | 5 | 0.048439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6421-103_0_4_line_5 |  | 3 | 6 | 0.031171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6421-103_0_4_line_6 |  | 4 | 7 | 0.1678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6421-103_0_4_line_7 |  | 5 | 8 | 0.038933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6421-103_0_4_line_8 |  | 6 | 10 | 0.028889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6421-103_0_4_line_9 |  | 7 | 11 | 0.023526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6421-103_0_4_line_10 |  | 8 | 9 | 0.073447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6421-103_0_4_line_11 |  | 10 | 23 | 0.011825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6421-103_0_4_line_12 |  | 11 | 15 | 0.0072732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6421-103_0_4_line_13 |  | 12 | 13 | 0.00017374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6421-103_0_4_line_14 |  | 12 | 14 | 0.046482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6421-103_0_4_line_15 |  | 14 | 15 | 0.015282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6421-103_0_4_line_16 |  | 14 | 16 | 0.17259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6421-103_0_4_line_17 |  | 15 | 17 | 0.030952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_6421-103_0_4_line_18 |  | 16 | 18 | 0.019784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6421-103_0_4_line_19 |  | 17 | 19 | 0.08086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6421-103_0_4_line_20 |  | 18 | 20 | 0.096086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6421-103_0_4_line_21 |  | 19 | 21 | 0.079471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6421-103_0_4_line_22 |  | 19 | 22 | 0.085833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6421-103_0_4_line_23 |  | 20 | 38 | 0.08556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6421-103_0_4_line_24 |  | 22 | 25 | 0.02005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6421-103_0_4_line_25 |  | 23 | 24 | 0.26429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6421-103_0_4_line_26 |  | 24 | 52 | 0.055697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6421-103_0_4_line_27 |  | 24 | 49 | 0.066759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6421-103_0_4_line_28 |  | 26 | 27 | 0.031028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6421-103_0_4_line_29 |  | 26 | 28 | 0.097016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6421-103_0_4_line_30 |  | 27 | 29 | 0.5235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6421-103_0_4_line_31 |  | 28 | 30 | 0.14619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6421-103_0_4_line_32 |  | 28 | 31 | 0.13655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6421-103_0_4_line_33 |  | 29 | 32 | 0.019061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6421-103_0_4_line_34 |  | 30 | 33 | 0.027815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6421-103_0_4_line_35 |  | 31 | 34 | 0.17652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6421-103_0_4_line_36 |  | 32 | 38 | 0.13449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6421-103_0_4_line_37 |  | 34 | 37 | 0.015562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6421-103_0_4_line_38 |  | 35 | 36 | 0.28705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6421-103_0_4_line_39 |  | 36 | 47 | 0.17305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6421-103_0_4_line_40 |  | 36 | 41 | 0.24563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6421-103_0_4_line_41 |  | 38 | 39 | 0.051977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6421-103_0_4_line_42 |  | 39 | 40 | 0.23858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6421-103_0_4_line_43 |  | 39 | 41 | 0.084645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6421-103_0_4_line_44 |  | 40 | 42 | 0.056133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6421-103_0_4_line_45 |  | 41 | 43 | 0.11164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6421-103_0_4_line_46 |  | 42 | 44 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6421-103_0_4_line_47 |  | 43 | 46 | 0.012085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6421-103_0_4_line_48 |  | 44 | 45 | 0.0015478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6421-103_0_4_line_49 |  | 47 | 48 | 0.29005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6421-103_0_4_line_50 |  | 49 | 50 | 0.17366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6421-103_0_4_line_51 |  | 50 | 51 | 0.12163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6421-103_0_4_line_52 |  | 51 | 53 | 0.022775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6421-103_0_4_line_53 |  | 53 | 54 | 0.0091385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6421-103_0_4_trafo_19 | 0.63 MVA 20/0.4 kV | 55 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2554859.3373 | 1218386.9187 | 2554854.8348 | 1218383.6732 | 2554854.3673 | 1218383.335
1 | 2554828.7501 | 1218364.8045 | 2554854.3673 | 1218383.335
2 | 2554859.3373 | 1218386.9187 | 2554881.9798 | 1218402.9337
3 | 2554859.3373 | 1218386.9187 | 2554900.8875 | 1218335.5615 | 2554904.0769 | 1218331.6339
4 | 2554828.7501 | 1218364.8045 | 2554807.9833 | 1218351.6212 | 2554787.1296 | 1218340.0672
5 | 2554906.6663 | 1218421.9582 | 2554885.4797 | 1218405.4091 | 2554881.9798 | 1218402.9337
6 | 2554904.0769 | 1218331.6339 | 2554928.6491 | 1218301.3749 | 2554950.9016 | 1218264.2841 | 2554959.589 | 1218232.8661 | 2554961.7757 | 1218222.977 | 2554968.644 | 1218191.873 | 2554970.5394 | 1218181.0529
7 | 2554750.8145 | 1218326.2298 | 2554781.894 | 1218337.1665 | 2554787.1296 | 1218340.0672
8 | 2554906.6663 | 1218421.9582 | 2554892.7386 | 1218447.2682
9 | 2554974.5987 | 1218157.8801 | 2554970.5394 | 1218181.0529
10 | 2554750.8145 | 1218326.2298 | 2554746.5953 | 1218324.3163 | 2554682.0035 | 1218300.5813
11 | 2554887.0374 | 1218457.6285 | 2554892.7386 | 1218447.2682
12 | 2554975.8536 | 1218150.716 | 2554974.5987 | 1218157.8801
13 | 2554941.4318 | 1218106.8189 | 2554941.2953 | 1218106.7114
14 | 2554977.9476 | 1218135.58 | 2554964.0128 | 1218124.6012 | 2554941.4318 | 1218106.8189
15 | 2554975.8536 | 1218150.716 | 2554977.9476 | 1218135.58
16 | 2554977.9476 | 1218135.58 | 2555031.1203 | 1218177.4136 | 2555113.8559 | 1218241.9515
17 | 2554975.8536 | 1218150.716 | 2554997.8334 | 1218172.5084
18 | 2555113.8559 | 1218241.9515 | 2555129.4551 | 1218254.1197
19 | 2555034.995 | 1218241.1002 | 2555033.2174 | 1218223.8478 | 2555029.6763 | 1218210.2442 | 2555020.426 | 1218198.4405 | 2555008.3929 | 1218182.9778 | 2554997.8334 | 1218172.5084
20 | 2555207.154 | 1218310.5975 | 2555155.8196 | 1218274.6853 | 2555129.4551 | 1218254.1197
21 | 2555034.995 | 1218241.1002 | 2555038.4501 | 1218263.3874 | 2555043.4556 | 1218320.0723
22 | 2555034.995 | 1218241.1002 | 2555032.0629 | 1218255.8089 | 2555029.1445 | 1218264.325 | 2555012.4214 | 1218311.035 | 2555011.7936 | 1218323.2382
23 | 2555207.154 | 1218310.5975 | 2555277.3569 | 1218359.7871
24 | 2555011.7936 | 1218323.2382 | 2555010.7634 | 1218343.262
25 | 2554887.0374 | 1218457.6285 | 2555043.7243 | 1218670.4687
26 | 2555043.7243 | 1218670.4687 | 2555060.3968 | 1218672.3327 | 2555092.5642 | 1218694.2432
27 | 2555043.7243 | 1218670.4687 | 2555040.6207 | 1218698.598 | 2555027.4462 | 1218734.7304
28 | 2555589.6628 | 1217824.8779 | 2555581.8723 | 1217827.5306 | 2555564.0237 | 1217813.346
29 | 2555667.846 | 1217770.377 | 2555636.9918 | 1217801.9704 | 2555628.6294 | 1217807.336 | 2555609.6807 | 1217818.0617 | 2555589.6628 | 1217824.8779
30 | 2555257.0753 | 1218237.4217 | 2555564.0237 | 1217813.346
31 | 2555667.846 | 1217770.377 | 2555692.3676 | 1217822.9144 | 2555713.5943 | 1217859.1222 | 2555748.917 | 1217888.96
32 | 2555625.6212 | 1217642.3713 | 2555630.2644 | 1217689.8427 | 2555667.846 | 1217770.377
33 | 2555248.2162 | 1218253.3763 | 2555254.3153 | 1218247.9937 | 2555257.0753 | 1218237.4217
34 | 2555748.917 | 1217888.96 | 2555770.1653 | 1217906.9089
35 | 2555625.6212 | 1217642.3713 | 2555524.6093 | 1217744.1424 | 2555506.0523 | 1217747.3721 | 2555494.1505 | 1217755.282
36 | 2555277.3569 | 1218359.7871 | 2555286.4007 | 1218346.2777 | 2555287.1772 | 1218340.5351 | 2555286.111 | 1218335.0176 | 2555284.0831 | 1218329.7741 | 2555278.8895 | 1218325.444 | 2555271.9794 | 1218321.9494 | 2555263.2396 | 1218317.368 | 2555256.5382 | 1218312.371 | 2555250.0631 | 1218305.171 | 2555245.4648 | 1218298.2571 | 2555241.503 | 1218288.1809 | 2555238.9939 | 1218280.5396 | 2555237.4006 | 1218273.5586 | 2555237.1614 | 1218265.9892 | 2555241.1469 | 1218260.0668 | 2555247.2506 | 1218254.2284 | 2555248.2162 | 1218253.3763
37 | 2555479.5044 | 1217753.2757 | 2555485.8522 | 1217755.2057 | 2555491.9588 | 1217756.7387 | 2555494.1505 | 1217755.282
38 | 2555611.7948 | 1218543.8569 | 2555621.379 | 1218537.6149 | 2555633.9119 | 1218541.0456 | 2555699.5634 | 1218558.7999 | 2555737.9052 | 1218560.8933 | 2555757.7511 | 1218553.7301 | 2555770.7272 | 1218544.3279 | 2555775.5024 | 1218528.2161 | 2555773.5662 | 1218504.6387 | 2555759.3918 | 1218465.254 | 2555759.8365 | 1218460.7702 | 2555764.1673 | 1218451.2211 | 2555764.1682 | 1218444.2058 | 2555761.0327 | 1218437.9477 | 2555753.9975 | 1218434.6731
39 | 2555774.355 | 1218604.4702 | 2555611.7948 | 1218543.8569
40 | 2555390.8271 | 1218436.3247 | 2555402.7074 | 1218443.7622 | 2555436.8129 | 1218463.7628 | 2555465.079 | 1218479.3269 | 2555488.4599 | 1218491.1922 | 2555524.8508 | 1218508.3634 | 2555567.1665 | 1218526.2465 | 2555611.7948 | 1218543.8569
41 | 2555277.3569 | 1218359.7871 | 2555320.1202 | 1218389.5055
42 | 2555320.1202 | 1218389.5055 | 2555316.7788 | 1218397.3131 | 2555343.7565 | 1218418.0894 | 2555360.9398 | 1218434.3256 | 2555412.9874 | 1218473.5918 | 2555491.0496 | 1218521.8133 | 2555483.531 | 1218535.2999
43 | 2555390.8271 | 1218436.3247 | 2555375.1875 | 1218426.5362 | 2555320.1202 | 1218389.5055
44 | 2555428.1776 | 1218537.8518 | 2555435.3095 | 1218540.5533 | 2555483.531 | 1218535.2999
45 | 2555390.8271 | 1218436.3247 | 2555399.0903 | 1218426.9904 | 2555406.9945 | 1218423.4067 | 2555416.5438 | 1218425.6476 | 2555428.3349 | 1218431.3181 | 2555476.2912 | 1218428.0345 | 2555482.82 | 1218432.3215 | 2555492.6219 | 1218438.7516
46 | 2555428.1776 | 1218537.8518 | 2555415.0274 | 1218532.8707
47 | 2555502.7264 | 1218445.3802 | 2555492.6219 | 1218438.7516
48 | 2555413.58 | 1218532.3224 | 2555415.0274 | 1218532.8707
49 | 2555774.355 | 1218604.4702 | 2555676.72 | 1218877.5896
50 | 2554952.164 | 1218891.1052 | 2554962.5774 | 1218864.2658 | 2555027.4462 | 1218734.7304
51 | 2554952.164 | 1218891.1052 | 2554934.0917 | 1218882.7039 | 2554894.1216 | 1218866.8309 | 2554837.7477 | 1218850.4942
52 | 2554837.7477 | 1218850.4942 | 2554836.7363 | 1218850.2011 | 2554815.4606 | 1218847.7058 | 2554815.1741 | 1218847.795
53 | 2554806.4487 | 1218850.5115 | 2554815.1741 | 1218847.795

## bus_geodata
| x | y | coords
0 | 2554854.3673 | 1218383.335
1 | 2554859.3373 | 1218386.9187
2 | 2554828.7501 | 1218364.8045
3 | 2554881.9798 | 1218402.9337
4 | 2554904.0769 | 1218331.6339
5 | 2554787.1296 | 1218340.0672
6 | 2554906.6663 | 1218421.9582
7 | 2554970.5394 | 1218181.0529
8 | 2554750.8145 | 1218326.2298
9 | 2554682.0035 | 1218300.5813
10 | 2554892.7386 | 1218447.2682
11 | 2554974.5987 | 1218157.8801
12 | 2554941.4318 | 1218106.8189
13 | 2554941.2953 | 1218106.7114
14 | 2554977.9476 | 1218135.58
15 | 2554975.8536 | 1218150.716
16 | 2555113.8559 | 1218241.9515
17 | 2554997.8334 | 1218172.5084
18 | 2555129.4551 | 1218254.1197
19 | 2555034.995 | 1218241.1002
20 | 2555207.154 | 1218310.5975
21 | 2555043.4556 | 1218320.0723
22 | 2555011.7936 | 1218323.2382
23 | 2554887.0374 | 1218457.6285
24 | 2555043.7243 | 1218670.4687
25 | 2555010.7634 | 1218343.262
26 | 2555589.6628 | 1217824.8779
27 | 2555564.0237 | 1217813.346
28 | 2555667.846 | 1217770.377
29 | 2555257.0753 | 1218237.4217
30 | 2555748.917 | 1217888.96
31 | 2555625.6212 | 1217642.3713
32 | 2555248.2162 | 1218253.3763
33 | 2555770.1653 | 1217906.9089
34 | 2555494.1505 | 1217755.282
35 | 2555753.9975 | 1218434.6731
36 | 2555611.7948 | 1218543.8569
37 | 2555479.5044 | 1217753.2757
38 | 2555277.3569 | 1218359.7871
39 | 2555320.1202 | 1218389.5055
40 | 2555483.531 | 1218535.2999
41 | 2555390.8271 | 1218436.3247
42 | 2555428.1776 | 1218537.8518
43 | 2555492.6219 | 1218438.7516
44 | 2555415.0274 | 1218532.8707
45 | 2555413.58 | 1218532.3224
46 | 2555502.7264 | 1218445.3802
47 | 2555774.355 | 1218604.4702
48 | 2555676.72 | 1218877.5896
49 | 2555027.4462 | 1218734.7304
50 | 2554952.164 | 1218891.1052
51 | 2554837.7477 | 1218850.4942
52 | 2555092.5642 | 1218694.2432
53 | 2554815.1741 | 1218847.795
54 | 2554806.4487 | 1218850.5115
55 | 2555043.4556 | 1218320.0723

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1