## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6421-27_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6421-27_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6421-27_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6421-27_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6421-27_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6421-27_0_5_node_77 | 0.4 | n |  | TRUE
6 | bus_LV_6421-27_0_5_node_70 | 0.4 | n |  | TRUE
7 | bus_LV_6421-27_0_5_node_61 | 0.4 | n |  | TRUE
8 | bus_LV_6421-27_0_5_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_6421-27_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6421-27_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_6421-27_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_6421-27_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_6421-27_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_6421-27_0_5_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_6421-27_0_5_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_6421-27_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6421-27_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_6421-27_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6421-27_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_6421-27_0_5_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_6421-27_0_5_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_6421-27_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_6421-27_0_5_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_6421-27_0_5_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_6421-27_0_5_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_6421-27_0_5_node_88 | 0.4 | n |  | TRUE
27 | bus_LV_6421-27_0_5_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_6421-27_0_5_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_6421-27_0_5_node_52 | 0.4 | n |  | TRUE
30 | bus_LV_6421-27_0_5_node_83 | 0.4 | n |  | TRUE
31 | bus_LV_6421-27_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_6421-27_0_5_node_78 | 0.4 | n |  | TRUE
33 | bus_LV_6421-27_0_5_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_6421-27_0_5_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_6421-27_0_5_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_6421-27_0_5_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_6421-27_0_5_node_87 | 0.4 | n |  | TRUE
38 | bus_LV_6421-27_0_5_node_86 | 0.4 | n |  | TRUE
39 | bus_LV_6421-27_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_6421-27_0_5_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_6421-27_0_5_node_81 | 0.4 | n |  | TRUE
42 | bus_LV_6421-27_0_5_node_82 | 0.4 | n |  | TRUE
43 | bus_LV_6421-27_0_5_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_6421-27_0_5_node_72 | 0.4 | n |  | TRUE
45 | bus_LV_6421-27_0_5_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_6421-27_0_5_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_6421-27_0_5_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_6421-27_0_5_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_6421-27_0_5_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_6421-27_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_6421-27_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_6421-27_0_5_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_6421-27_0_5_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_6421-27_0_5_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_6421-27_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_6421-27_0_5_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_6421-27_0_5_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_6421-27_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_6421-27_0_5_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_6421-27_0_5_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_6421-27_0_5_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_6421-27_0_5_node_85 | 0.4 | n |  | TRUE
63 | bus_LV_6421-27_0_5_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_6421-27_0_5_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_6421-27_0_5_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_6421-27_0_5_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_6421-27_0_5_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_6421-27_0_5_node_79 | 0.4 | n |  | TRUE
69 | bus_LV_6421-27_0_5_node_80 | 0.4 | n |  | TRUE
70 | bus_LV_6421-27_0_5_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_6421-27_0_5_node_74 | 0.4 | n |  | TRUE
72 | bus_LV_6421-27_0_5_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_6421-27_0_5_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_6421-27_0_5_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_6421-27_0_5_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_6421-27_0_5_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_6421-27_0_5_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_6421-27_0_5_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_6421-27_0_5_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_6421-27_0_5_node_67 | 0.4 | n |  | TRUE
81 | bus_MV_335_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6421-27_0_5_load_0 | 0 | 0.011288 | 0.0028291 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6421-27_0_5_load_1 | 1 | 0.0091702 | 0.0022983 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6421-27_0_5_load_2 | 2 | 0.010878 | 0.0027264 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6421-27_0_5_load_3 | 3 | 0.0095158 | 0.0023849 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6421-27_0_5_load_70 | 6 | 0.0063249 | 0.0015852 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6421-27_0_5_load_61 | 7 | 0.0083698 | 0.0020977 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6421-27_0_5_load_59 | 8 | 0.011592 | 0.0029052 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6421-27_0_5_load_7 | 9 | 0.0041273 | 0.0010344 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6421-27_0_5_load_8 | 10 | 0.0074907 | 0.0018773 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6421-27_0_5_load_9 | 11 | 0.012134 | 0.0030411 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6421-27_0_5_load_10 | 12 | 0.0010727 | 0.00026884 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6421-27_0_5_load_11 | 13 | 0.005873 | 0.0014719 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6421-27_0_5_load_19 | 14 | 0.00088346 | 0.00022142 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6421-27_0_5_load_20 | 15 | 0.0012991 | 0.00032559 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6421-27_0_5_load_12 | 16 | 0.017313 | 0.0043392 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6421-27_0_5_load_13 | 17 | 0.0081932 | 0.0020534 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6421-27_0_5_load_14 | 18 | 0.00088536 | 0.00022189 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6421-27_0_5_load_18 | 22 | 0.003223 | 0.00080775 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6421-27_0_5_load_88 | 26 | 0.0060671 | 0.0015205 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6421-27_0_5_load_39 | 27 | 0.0045485 | 0.00114 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6421-27_0_5_load_83 | 30 | 0.0022446 | 0.00056254 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6421-27_0_5_load_78 | 32 | 0.0045483 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6421-27_0_5_load_73 | 33 | 0.0059133 | 0.001482 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6421-27_0_5_load_30 | 34 | 0.030496 | 0.007643 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6421-27_0_5_load_31 | 35 | 0.0059582 | 0.0014933 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6421-27_0_5_load_26 | 36 | 0.0076297 | 0.0019122 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6421-27_0_5_load_86 | 38 | 0.020814 | 0.0052166 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6421-27_0_5_load_38 | 39 | 0.0093551 | 0.0023446 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6421-27_0_5_load_81 | 41 | 0.004062 | 0.001018 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6421-27_0_5_load_82 | 42 | 0.00081758 | 0.0002049 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6421-27_0_5_load_72 | 44 | 0.0010116 | 0.00025354 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6421-27_0_5_load_27 | 45 | 0.065499 | 0.016416 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6421-27_0_5_load_29 | 46 | 0.0021258 | 0.00053278 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6421-27_0_5_load_32 | 47 | 0.00024306 | 6.0918e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6421-27_0_5_load_34 | 48 | 0.0048836 | 0.0012239 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6421-27_0_5_load_49 | 49 | 0.0052697 | 0.0013207 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6421-27_0_5_load_33 | 50 | 0.0014367 | 0.00036006 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6421-27_0_5_load_48 | 52 | 0.007132 | 0.0017874 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6421-27_0_5_load_43 | 53 | 0.00022357 | 5.6033e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6421-27_0_5_load_36 | 54 | 0.0051902 | 0.0013008 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6421-27_0_5_load_37 | 55 | 0.0058599 | 0.0014686 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6421-27_0_5_load_45 | 56 | 0.0041974 | 0.001052 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6421-27_0_5_load_46 | 57 | 0.0033585 | 0.00084171 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6421-27_0_5_load_40 | 58 | 0.014814 | 0.0037127 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6421-27_0_5_load_41 | 59 | 0.00036226 | 9.0791e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6421-27_0_5_load_42 | 60 | 0.012047 | 0.0030192 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6421-27_0_5_load_71 | 61 | 0.012269 | 0.003075 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6421-27_0_5_load_85 | 62 | 0.015313 | 0.0038378 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6421-27_0_5_load_53 | 63 | 0.0043206 | 0.0010829 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6421-27_0_5_load_54 | 64 | 0.013807 | 0.0034605 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6421-27_0_5_load_55 | 65 | 0.013491 | 0.0033812 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6421-27_0_5_load_57 | 67 | 0.0094537 | 0.0023693 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6421-27_0_5_load_79 | 68 | 0.0033681 | 0.00084413 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6421-27_0_5_load_80 | 69 | 0.0099816 | 0.0025016 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6421-27_0_5_load_76 | 72 | 0.0067528 | 0.0016924 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6421-27_0_5_load_58 | 75 | 0.013987 | 0.0035054 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6421-27_0_5_load_75 | 76 | 0.011264 | 0.0028231 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6421-27_0_5_load_69 | 77 | 0.0063281 | 0.001586 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6421-27_0_5_load_65 | 78 | 0.017501 | 0.0043861 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6421-27_0_5_load_66 | 79 | 0.021898 | 0.0054881 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6421-27_0_5_line_0 |  | 0 | 1 | 0.039812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6421-27_0_5_line_1 |  | 0 | 2 | 0.01609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6421-27_0_5_line_2 |  | 1 | 3 | 0.014559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6421-27_0_5_line_3 |  | 2 | 4 | 0.033682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_6421-27_0_5_line_4 |  | 4 | 5 | 0.001987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_6421-27_0_5_line_5 |  | 5 | 6 | 0.015041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_6421-27_0_5_line_6 |  | 6 | 80 | 0.03036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_6421-27_0_5_line_7 |  | 7 | 8 | 0.023093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6421-27_0_5_line_8 |  | 8 | 75 | 0.0013547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6421-27_0_5_line_9 |  | 9 | 10 | 0.0057927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6421-27_0_5_line_10 |  | 9 | 11 | 0.012715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6421-27_0_5_line_11 |  | 10 | 12 | 0.053895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6421-27_0_5_line_12 |  | 11 | 13 | 0.016658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6421-27_0_5_line_13 |  | 13 | 14 | 0.020344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6421-27_0_5_line_14 |  | 14 | 15 | 0.01245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6421-27_0_5_line_15 |  | 15 | 23 | 0.031673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6421-27_0_5_line_16 |  | 16 | 17 | 0.02849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_6421-27_0_5_line_17 |  | 16 | 18 | 0.024145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_6421-27_0_5_line_18 |  | 17 | 19 | 0.016627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_6421-27_0_5_line_19 |  | 18 | 20 | 0.0439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6421-27_0_5_line_20 |  | 19 | 21 | 0.011865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_6421-27_0_5_line_21 |  | 19 | 22 | 0.023993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6421-27_0_5_line_22 |  | 20 | 23 | 0.036625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6421-27_0_5_line_23 |  | 20 | 24 | 0.1134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_6421-27_0_5_line_24 |  | 21 | 25 | 0.054576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_6421-27_0_5_line_25 |  | 21 | 26 | 0.041578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6421-27_0_5_line_26 |  | 22 | 27 | 0.019154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6421-27_0_5_line_27 |  | 24 | 31 | 0.05929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6421-27_0_5_line_28 |  | 24 | 32 | 0.034871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_6421-27_0_5_line_29 |  | 25 | 34 | 0.025228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6421-27_0_5_line_30 |  | 25 | 35 | 0.04174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6421-27_0_5_line_31 |  | 25 | 36 | 0.014427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6421-27_0_5_line_32 |  | 26 | 37 | 0.0065005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6421-27_0_5_line_33 |  | 27 | 39 | 0.013704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6421-27_0_5_line_34 |  | 28 | 29 | 0.051734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6421-27_0_5_line_35 |  | 28 | 30 | 0.028207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6421-27_0_5_line_36 |  | 29 | 40 | 0.079048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6421-27_0_5_line_37 |  | 29 | 41 | 0.030754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6421-27_0_5_line_38 |  | 30 | 42 | 0.010357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6421-27_0_5_line_39 |  | 31 | 33 | 0.01156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6421-27_0_5_line_40 |  | 32 | 43 | 0.020124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_6421-27_0_5_line_41 |  | 33 | 44 | 0.00017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6421-27_0_5_line_42 |  | 34 | 48 | 0.0026911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6421-27_0_5_line_43 |  | 35 | 49 | 0.013504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6421-27_0_5_line_44 |  | 36 | 45 | 0.018174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6421-27_0_5_line_45 |  | 37 | 38 | 0.010296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6421-27_0_5_line_46 |  | 38 | 40 | 0.025248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6421-27_0_5_line_47 |  | 39 | 58 | 0.0075413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6421-27_0_5_line_48 |  | 40 | 62 | 0.0036245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6421-27_0_5_line_49 |  | 43 | 66 | 0.024687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6421-27_0_5_line_50 |  | 43 | 73 | 0.043959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_6421-27_0_5_line_51 |  | 44 | 61 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6421-27_0_5_line_52 |  | 45 | 46 | 0.0058126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6421-27_0_5_line_53 |  | 46 | 47 | 0.041827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6421-27_0_5_line_54 |  | 47 | 50 | 0.00077742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6421-27_0_5_line_55 |  | 48 | 51 | 0.030314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6421-27_0_5_line_56 |  | 49 | 52 | 0.023189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6421-27_0_5_line_57 |  | 50 | 53 | 0.015748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6421-27_0_5_line_58 |  | 51 | 54 | 0.041397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6421-27_0_5_line_59 |  | 51 | 55 | 0.020678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6421-27_0_5_line_60 |  | 54 | 56 | 0.015139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6421-27_0_5_line_61 |  | 56 | 57 | 0.017026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6421-27_0_5_line_62 |  | 58 | 59 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6421-27_0_5_line_63 |  | 59 | 60 | 0.0023033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6421-27_0_5_line_64 |  | 63 | 64 | 0.005082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6421-27_0_5_line_65 |  | 63 | 65 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6421-27_0_5_line_66 |  | 64 | 66 | 0.015754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6421-27_0_5_line_67 |  | 65 | 67 | 0.022234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6421-27_0_5_line_68 |  | 66 | 68 | 0.007267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6421-27_0_5_line_69 |  | 67 | 69 | 0.00025881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6421-27_0_5_line_70 |  | 70 | 71 | 0.02405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_6421-27_0_5_line_71 |  | 70 | 72 | 0.015532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_6421-27_0_5_line_72 |  | 71 | 77 | 0.01966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_6421-27_0_5_line_73 |  | 72 | 76 | 0.035643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_6421-27_0_5_line_74 |  | 73 | 74 | 0.033613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_6421-27_0_5_line_75 |  | 73 | 75 | 0.0088102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6421-27_0_5_line_76 |  | 74 | 76 | 0.0056716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_6421-27_0_5_line_77 |  | 77 | 80 | 0.010402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_6421-27_0_5_line_78 |  | 78 | 79 | 0.026238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6421-27_0_5_line_79 |  | 78 | 80 | 0.0061771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6421-27_0_5_trafo_16 | 0.63 MVA 20/0.4 kV | 81 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2554417.1006 | 1217310.6296 | 2554411.2565 | 1217291.0278 | 2554398.7195 | 1217276.278
1 | 2554417.1006 | 1217310.6296 | 2554421.6979 | 1217326.049
2 | 2554389.2906 | 1217265.185 | 2554398.7195 | 1217276.278
3 | 2554440.8319 | 1217330.747 | 2554439.7205 | 1217329.3436 | 2554438.9188 | 1217328.7383 | 2554438.1744 | 1217328.6773 | 2554437.0795 | 1217329.4306 | 2554434.3875 | 1217331.7748 | 2554432.8598 | 1217333.5098 | 2554427.347 | 1217336.2425 | 2554425.8791 | 1217336.8653 | 2554424.3392 | 1217336.9994 | 2554423.0469 | 1217336.7647 | 2554422.1841 | 1217336.1043 | 2554421.5392 | 1217335.1531 | 2554421.4556 | 1217334.1531 | 2554423.4267 | 1217331.8478 | 2554421.6979 | 1217326.049
4 | 2554439.4079 | 1217332.1365 | 2554440.8319 | 1217330.747
5 | 2554439.4079 | 1217332.1365 | 2554441.678 | 1217332.197 | 2554444.9729 | 1217333.239 | 2554449.0116 | 1217336.2543 | 2554452.1841 | 1217339.1188
6 | 2554474.4242 | 1217359.7848 | 2554455.3484 | 1217341.9758 | 2554452.1841 | 1217339.1188
7 | 2554355.6357 | 1217378.1829 | 2554341.9625 | 1217362.6912 | 2554340.3516 | 1217360.872
8 | 2554356.5322 | 1217379.1986 | 2554355.6357 | 1217378.1829
9 | 2554292.398 | 1217635.6772 | 2554296.8503 | 1217639.3829
10 | 2554292.398 | 1217635.6772 | 2554282.6251 | 1217627.5431
11 | 2554335.4572 | 1217642.5477 | 2554321.1613 | 1217659.6172 | 2554296.8503 | 1217639.3829
12 | 2554269.8213 | 1217616.8864 | 2554282.6251 | 1217627.5431
13 | 2554269.8213 | 1217616.8864 | 2554261.0463 | 1217609.5828 | 2554266.7776 | 1217602.738
14 | 2554274.7701 | 1217593.1924 | 2554266.7776 | 1217602.738
15 | 2554295.1036 | 1217568.9077 | 2554274.7701 | 1217593.1924
16 | 2554222.6824 | 1217596.9798 | 2554204.1283 | 1217618.5999
17 | 2554238.4068 | 1217578.657 | 2554222.6824 | 1217596.9798
18 | 2554193.3001 | 1217631.2174 | 2554204.1283 | 1217618.5999
19 | 2554266.9963 | 1217545.3431 | 2554238.4068 | 1217578.657
20 | 2554193.3001 | 1217631.2174 | 2554185.5971 | 1217640.2599
21 | 2554193.3001 | 1217631.2174 | 2554211.8024 | 1217646.4929
22 | 2554266.9963 | 1217545.3431 | 2554274.4119 | 1217551.2007 | 2554295.1036 | 1217568.9077
23 | 2554266.9963 | 1217545.3431 | 2554271.4242 | 1217540.7397 | 2554273.38 | 1217538.4344 | 2554278.7131 | 1217532.1118 | 2554301.8136 | 1217504.74 | 2554309.1779 | 1217496.0227 | 2554312.1251 | 1217493.3206 | 2554336.7063 | 1217465.9821 | 2554341.77 | 1217460.1398
24 | 2554150.9458 | 1217682.4967 | 2554157.1897 | 1217675.2109 | 2554176.7789 | 1217651.3456 | 2554185.5971 | 1217640.2599
25 | 2554185.5971 | 1217640.2599 | 2554178.1021 | 1217638.8613 | 2554152.2955 | 1217616.796
26 | 2554211.8024 | 1217646.4929 | 2554226.5731 | 1217658.6876
27 | 2554341.77 | 1217460.1398 | 2554336.7063 | 1217465.9821 | 2554352.9314 | 1217480.2772 | 2554375.2571 | 1217500.2177
28 | 2554341.77 | 1217460.1398 | 2554366.4206 | 1217435.4747
29 | 2554150.9458 | 1217682.4967 | 2554134.8018 | 1217701.8822
30 | 2554150.9458 | 1217682.4967 | 2554119.0781 | 1217655.5401
31 | 2554150.9458 | 1217682.4967 | 2554161.6411 | 1217692.1784
32 | 2554147.3548 | 1217612.5715 | 2554152.2955 | 1217616.796
33 | 2554237.1406 | 1217667.4122 | 2554226.5731 | 1217658.6876
34 | 2554208.2649 | 1217530.264 | 2554188.9485 | 1217513.7696 | 2554171.3685 | 1217533.4724
35 | 2554208.2649 | 1217530.264 | 2554229.7041 | 1217548.5943
36 | 2554120.3361 | 1217589.4773 | 2554129.2335 | 1217578.8134 | 2554168.8015 | 1217531.3243 | 2554171.3685 | 1217533.4724
37 | 2554171.3685 | 1217533.4724 | 2554194.7505 | 1217553.4493
38 | 2554229.7041 | 1217548.5943 | 2554234.7869 | 1217552.94 | 2554232.4483 | 1217555.7676
39 | 2554375.2571 | 1217500.2177 | 2554383.8775 | 1217507.9193
40 | 2554380.6015 | 1217421.1962 | 2554373.1445 | 1217428.7468 | 2554366.4206 | 1217435.4747
41 | 2554384.0063 | 1217508.0344 | 2554383.8775 | 1217507.9193
42 | 2554133.0796 | 1217703.9501 | 2554134.8018 | 1217701.8822
43 | 2554119.0781 | 1217655.5401 | 2554108.7682 | 1217646.819
44 | 2554161.6411 | 1217692.1784 | 2554175.1146 | 1217704.3748
45 | 2554147.3548 | 1217612.5715 | 2554139.5285 | 1217605.882
46 | 2554120.3361 | 1217589.4773 | 2554139.5285 | 1217605.882
47 | 2554237.1406 | 1217667.4122 | 2554242.956 | 1217672.2134
48 | 2554120.3361 | 1217589.4773 | 2554117.5813 | 1217587.122
49 | 2554380.6015 | 1217421.1962 | 2554382.8244 | 1217423.0136 | 2554385.4969 | 1217424.0826 | 2554388.3603 | 1217424.2941 | 2554391.1562 | 1217423.6278 | 2554393.6271 | 1217422.1524 | 2554400.8418 | 1217429.5237
50 | 2554380.6015 | 1217421.1962 | 2554379.0035 | 1217418.707 | 2554378.2604 | 1217415.8443 | 2554378.4427 | 1217412.8967 | 2554379.5375 | 1217410.1533 | 2554381.433 | 1217407.893 | 2554374.4071 | 1217399.4196 | 2554362.3621 | 1217385.8039
51 | 2554400.7752 | 1217523.0161 | 2554384.0063 | 1217508.0344
52 | 2554179.4239 | 1217708.2757 | 2554175.1146 | 1217704.3748
53 | 2554179.4239 | 1217708.2757 | 2554210.4328 | 1217736.3456
54 | 2554211.0091 | 1217736.8673 | 2554210.4328 | 1217736.3456
55 | 2554113.6805 | 1217727.2443 | 2554133.0796 | 1217703.9501
56 | 2554091.0637 | 1217631.8429 | 2554108.7682 | 1217646.819
57 | 2554222.684 | 1217747.4356 | 2554211.0091 | 1217736.8673
58 | 2554113.6805 | 1217727.2443 | 2554082.2407 | 1217700.314
59 | 2554113.6805 | 1217727.2443 | 2554129.6123 | 1217740.4267
60 | 2554070.7431 | 1217690.4655 | 2554082.2407 | 1217700.314
61 | 2554070.7431 | 1217690.4655 | 2554057.8127 | 1217679.3897
62 | 2554242.956 | 1217672.2134 | 2554254.4703 | 1217681.7195
63 | 2554256.2465 | 1217683.186 | 2554254.4703 | 1217681.7195
64 | 2554415.3382 | 1217444.4905 | 2554411.8025 | 1217440.8401
65 | 2554415.3382 | 1217444.4905 | 2554429.6153 | 1217459.231
66 | 2554400.8418 | 1217429.5237 | 2554411.8025 | 1217440.8401
67 | 2554429.6153 | 1217459.231 | 2554445.0841 | 1217475.2018
68 | 2554400.8418 | 1217429.5237 | 2554395.5208 | 1217434.4897
69 | 2554445.2642 | 1217475.3878 | 2554445.0841 | 1217475.2018
70 | 2554437.5806 | 1217384.882 | 2554441.5515 | 1217381.0382 | 2554446.8415 | 1217375.9724 | 2554448.2507 | 1217374.6275 | 2554454.7006 | 1217381.2598
71 | 2554437.5806 | 1217384.882 | 2554426.7613 | 1217373.7384
72 | 2554454.7006 | 1217381.2598 | 2554458.3115 | 1217376.9851 | 2554460.0493 | 1217374.9373 | 2554465.4051 | 1217372.517 | 2554466.4083 | 1217369.7077 | 2554467.2783 | 1217367.344
73 | 2554396.3073 | 1217368.8333 | 2554400.2914 | 1217365.7231 | 2554405.5025 | 1217363.2372 | 2554411.8168 | 1217363.0665 | 2554418.9204 | 1217366.8365 | 2554424.9483 | 1217371.8711 | 2554426.7613 | 1217373.7384
74 | 2554393.9177 | 1217373.977 | 2554362.3621 | 1217385.8039
75 | 2554362.3621 | 1217385.8039 | 2554356.5322 | 1217379.1986
76 | 2554393.9177 | 1217373.977 | 2554396.3073 | 1217368.8333
77 | 2554474.4242 | 1217359.7848 | 2554467.2783 | 1217367.344
78 | 2554479.0007 | 1217363.9336 | 2554498.4396 | 1217381.5556
79 | 2554474.4242 | 1217359.7848 | 2554479.0007 | 1217363.9336

## bus_geodata
| x | y | coords
0 | 2554417.1006 | 1217310.6296
1 | 2554398.7195 | 1217276.278
2 | 2554421.6979 | 1217326.049
3 | 2554389.2906 | 1217265.185
4 | 2554440.8319 | 1217330.747
5 | 2554439.4079 | 1217332.1365
6 | 2554452.1841 | 1217339.1188
7 | 2554340.3516 | 1217360.872
8 | 2554355.6357 | 1217378.1829
9 | 2554292.398 | 1217635.6772
10 | 2554296.8503 | 1217639.3829
11 | 2554282.6251 | 1217627.5431
12 | 2554335.4572 | 1217642.5477
13 | 2554269.8213 | 1217616.8864
14 | 2554266.7776 | 1217602.738
15 | 2554274.7701 | 1217593.1924
16 | 2554222.6824 | 1217596.9798
17 | 2554204.1283 | 1217618.5999
18 | 2554238.4068 | 1217578.657
19 | 2554193.3001 | 1217631.2174
20 | 2554266.9963 | 1217545.3431
21 | 2554185.5971 | 1217640.2599
22 | 2554211.8024 | 1217646.4929
23 | 2554295.1036 | 1217568.9077
24 | 2554341.77 | 1217460.1398
25 | 2554150.9458 | 1217682.4967
26 | 2554152.2955 | 1217616.796
27 | 2554226.5731 | 1217658.6876
28 | 2554208.2649 | 1217530.264
29 | 2554171.3685 | 1217533.4724
30 | 2554229.7041 | 1217548.5943
31 | 2554375.2571 | 1217500.2177
32 | 2554366.4206 | 1217435.4747
33 | 2554383.8775 | 1217507.9193
34 | 2554134.8018 | 1217701.8822
35 | 2554119.0781 | 1217655.5401
36 | 2554161.6411 | 1217692.1784
37 | 2554147.3548 | 1217612.5715
38 | 2554139.5285 | 1217605.882
39 | 2554237.1406 | 1217667.4122
40 | 2554120.3361 | 1217589.4773
41 | 2554194.7505 | 1217553.4493
42 | 2554232.4483 | 1217555.7676
43 | 2554380.6015 | 1217421.1962
44 | 2554384.0063 | 1217508.0344
45 | 2554175.1146 | 1217704.3748
46 | 2554179.4239 | 1217708.2757
47 | 2554210.4328 | 1217736.3456
48 | 2554133.0796 | 1217703.9501
49 | 2554108.7682 | 1217646.819
50 | 2554211.0091 | 1217736.8673
51 | 2554113.6805 | 1217727.2443
52 | 2554091.0637 | 1217631.8429
53 | 2554222.684 | 1217747.4356
54 | 2554082.2407 | 1217700.314
55 | 2554129.6123 | 1217740.4267
56 | 2554070.7431 | 1217690.4655
57 | 2554057.8127 | 1217679.3897
58 | 2554242.956 | 1217672.2134
59 | 2554254.4703 | 1217681.7195
60 | 2554256.2465 | 1217683.186
61 | 2554400.7752 | 1217523.0161
62 | 2554117.5813 | 1217587.122
63 | 2554415.3382 | 1217444.4905
64 | 2554411.8025 | 1217440.8401
65 | 2554429.6153 | 1217459.231
66 | 2554400.8418 | 1217429.5237
67 | 2554445.0841 | 1217475.2018
68 | 2554395.5208 | 1217434.4897
69 | 2554445.2642 | 1217475.3878
70 | 2554437.5806 | 1217384.882
71 | 2554454.7006 | 1217381.2598
72 | 2554426.7613 | 1217373.7384
73 | 2554362.3621 | 1217385.8039
74 | 2554393.9177 | 1217373.977
75 | 2554356.5322 | 1217379.1986
76 | 2554396.3073 | 1217368.8333
77 | 2554467.2783 | 1217367.344
78 | 2554479.0007 | 1217363.9336
79 | 2554498.4396 | 1217381.5556
80 | 2554474.4242 | 1217359.7848
81 | 2554278.7131 | 1217532.1118

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1