## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6711-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6711-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6711-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6711-9_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_6711-9_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6711-9_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_6711-9_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6711-9_0_4_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_6711-9_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_6711-9_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_6711-9_0_4_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_6711-9_0_4_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_6711-9_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_6711-9_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6711-9_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_6711-9_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_6711-9_0_4_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_6711-9_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_6711-9_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_6711-9_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_6711-9_0_4_node_69 | 0.4 | n |  | TRUE
21 | bus_LV_6711-9_0_4_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_6711-9_0_4_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_6711-9_0_4_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_6711-9_0_4_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_6711-9_0_4_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_6711-9_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6711-9_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_6711-9_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_6711-9_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_6711-9_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_6711-9_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6711-9_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_6711-9_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_6711-9_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_6711-9_0_4_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_6711-9_0_4_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_6711-9_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_6711-9_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_6711-9_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_6711-9_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_6711-9_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_6711-9_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_6711-9_0_4_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_6711-9_0_4_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_6711-9_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_6711-9_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_6711-9_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_6711-9_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_6711-9_0_4_node_64 | 0.4 | n |  | TRUE
50 | bus_LV_6711-9_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_6711-9_0_4_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_6711-9_0_4_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_6711-9_0_4_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_6711-9_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_6711-9_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_6711-9_0_4_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_6711-9_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_6711-9_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_6711-9_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_6711-9_0_4_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_6711-9_0_4_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_6711-9_0_4_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_6711-9_0_4_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_6711-9_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_6711-9_0_4_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_6711-9_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_6711-9_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_6711-9_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_6711-9_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_6711-9_0_4_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_6711-9_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_6711-9_0_4_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_6711-9_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_6711-9_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_6711-9_0_4_node_75 | 0.4 | n |  | TRUE
76 | bus_MV_332_1_node_141 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6711-9_0_4_load_0 | 0 | 0.031579 | 0.0079144 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6711-9_0_4_load_1 | 1 | 0.047144 | 0.011815 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6711-9_0_4_load_2 | 2 | 0.00059509 | 0.00014914 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6711-9_0_4_load_4 | 3 | 0.0017051 | 0.00042734 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6711-9_0_4_load_10 | 5 | 0.016978 | 0.0042552 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6711-9_0_4_load_6 | 6 | 0.0053318 | 0.0013363 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6711-9_0_4_load_5 | 9 | 0.0012266 | 0.00030741 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6711-9_0_4_load_29 | 11 | 0.0058232 | 0.0014594 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6711-9_0_4_load_7 | 12 | 0.0086012 | 0.0021557 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6711-9_0_4_load_9 | 14 | 0.0055594 | 0.0013933 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6711-9_0_4_load_23 | 17 | 0.0037382 | 0.00093687 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6711-9_0_4_load_13 | 19 | 0.005239 | 0.001313 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6711-9_0_4_load_69 | 20 | 0.018033 | 0.0045194 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6711-9_0_4_load_66 | 21 | 0.0034866 | 0.00087382 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6711-9_0_4_load_70 | 22 | 0.0048227 | 0.0012087 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6711-9_0_4_load_74 | 23 | 0.0074814 | 0.001875 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6711-9_0_4_load_67 | 24 | 0.012499 | 0.0031324 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6711-9_0_4_load_71 | 25 | 0.00075252 | 0.0001886 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6711-9_0_4_load_14 | 26 | 0.0034278 | 0.0008591 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6711-9_0_4_load_15 | 27 | 0.0050038 | 0.0012541 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6711-9_0_4_load_19 | 31 | 0.011289 | 0.0028292 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6711-9_0_4_load_20 | 32 | 0.0049408 | 0.0012383 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6711-9_0_4_load_27 | 33 | 0.011752 | 0.0029452 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6711-9_0_4_load_21 | 34 | 0.0058806 | 0.0014738 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6711-9_0_4_load_45 | 35 | 0.0038201 | 0.00095741 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6711-9_0_4_load_46 | 36 | 0.016306 | 0.0040867 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6711-9_0_4_load_24 | 37 | 0.0028774 | 0.00072114 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6711-9_0_4_load_26 | 38 | 0.0050445 | 0.0012643 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6711-9_0_4_load_28 | 39 | 0.01748 | 0.0043809 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6711-9_0_4_load_30 | 40 | 0.00054997 | 0.00013784 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6711-9_0_4_load_32 | 41 | 0.0061646 | 0.001545 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6711-9_0_4_load_72 | 43 | 0.0014917 | 0.00037386 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6711-9_0_4_load_76 | 44 | 0.0064278 | 0.001611 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6711-9_0_4_load_34 | 46 | 0.022802 | 0.0057147 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6711-9_0_4_load_35 | 47 | 0.0017728 | 0.00044432 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6711-9_0_4_load_37 | 48 | 0.001453 | 0.00036415 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6711-9_0_4_load_64 | 49 | 0.0020612 | 0.00051659 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6711-9_0_4_load_40 | 54 | 0.0018286 | 0.00045829 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6711-9_0_4_load_42 | 56 | 0.00055987 | 0.00014032 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6711-9_0_4_load_48 | 57 | 0.0047127 | 0.0011811 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6711-9_0_4_load_47 | 59 | 0.0014988 | 0.00037564 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6711-9_0_4_load_44 | 60 | 0.0051856 | 0.0012996 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6711-9_0_4_load_63 | 62 | 0.0018181 | 0.00045567 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6711-9_0_4_load_49 | 64 | 0.0059894 | 0.0015011 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6711-9_0_4_load_50 | 65 | 0.0027096 | 0.00067908 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6711-9_0_4_load_52 | 67 | 0.010978 | 0.0027513 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6711-9_0_4_load_53 | 68 | 0.017213 | 0.004314 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6711-9_0_4_load_58 | 69 | 0.00095913 | 0.00024038 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6711-9_0_4_load_65 | 70 | 0.0066618 | 0.0016696 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6711-9_0_4_load_55 | 71 | 0.0072186 | 0.0018091 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6711-9_0_4_load_59 | 72 | 0.0023546 | 0.00059013 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6711-9_0_4_load_62 | 73 | 0.003345 | 0.00083833 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6711-9_0_4_load_68 | 74 | 0.0044277 | 0.0011097 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6711-9_0_4_load_75 | 75 | 0.001678 | 0.00042055 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6711-9_0_4_line_0 |  | 0 | 1 | 0.008584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6711-9_0_4_line_1 |  | 0 | 2 | 0.0085942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6711-9_0_4_line_2 |  | 2 | 3 | 0.0213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6711-9_0_4_line_3 |  | 3 | 7 | 0.029306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6711-9_0_4_line_4 |  | 4 | 5 | 0.031596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6711-9_0_4_line_5 |  | 4 | 6 | 0.025548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_6711-9_0_4_line_6 |  | 5 | 8 | 0.012167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_6711-9_0_4_line_7 |  | 6 | 9 | 0.012582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_6711-9_0_4_line_8 |  | 7 | 10 | 0.050659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_6711-9_0_4_line_9 |  | 7 | 11 | 0.014292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6711-9_0_4_line_10 |  | 8 | 18 | 0.048406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6711-9_0_4_line_11 |  | 8 | 19 | 0.023592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_6711-9_0_4_line_12 |  | 9 | 12 | 0.010958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6711-9_0_4_line_13 |  | 10 | 43 | 0.028399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6711-9_0_4_line_14 |  | 10 | 44 | 0.11448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6711-9_0_4_line_15 |  | 11 | 40 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_6711-9_0_4_line_16 |  | 12 | 13 | 0.027252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6711-9_0_4_line_17 |  | 13 | 14 | 0.018191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6711-9_0_4_line_18 |  | 14 | 15 | 0.04394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6711-9_0_4_line_19 |  | 15 | 16 | 0.077174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6711-9_0_4_line_20 |  | 15 | 17 | 0.017056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6711-9_0_4_line_21 |  | 16 | 35 | 0.03832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6711-9_0_4_line_22 |  | 16 | 28 | 0.013018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6711-9_0_4_line_23 |  | 17 | 37 | 0.01384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6711-9_0_4_line_24 |  | 18 | 20 | 0.029843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6711-9_0_4_line_25 |  | 18 | 21 | 0.022995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6711-9_0_4_line_26 |  | 19 | 22 | 0.029925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_6711-9_0_4_line_27 |  | 20 | 23 | 0.035109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6711-9_0_4_line_28 |  | 21 | 24 | 0.010217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6711-9_0_4_line_29 |  | 22 | 25 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_6711-9_0_4_line_30 |  | 23 | 75 | 0.020454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6711-9_0_4_line_31 |  | 24 | 74 | 0.00044116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6711-9_0_4_line_32 |  | 25 | 43 | 0.023532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_6711-9_0_4_line_33 |  | 26 | 27 | 0.01956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6711-9_0_4_line_34 |  | 27 | 28 | 0.019997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6711-9_0_4_line_35 |  | 28 | 32 | 0.058967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6711-9_0_4_line_36 |  | 29 | 30 | 0.047852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6711-9_0_4_line_37 |  | 29 | 31 | 0.025166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6711-9_0_4_line_38 |  | 30 | 33 | 0.026235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6711-9_0_4_line_39 |  | 30 | 34 | 0.027305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6711-9_0_4_line_40 |  | 32 | 34 | 0.028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6711-9_0_4_line_41 |  | 35 | 36 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6711-9_0_4_line_42 |  | 36 | 58 | 0.075037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6711-9_0_4_line_43 |  | 37 | 38 | 0.01531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6711-9_0_4_line_44 |  | 38 | 39 | 0.018977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6711-9_0_4_line_45 |  | 40 | 41 | 0.019458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_6711-9_0_4_line_46 |  | 41 | 42 | 0.017695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_6711-9_0_4_line_47 |  | 42 | 45 | 0.019203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_6711-9_0_4_line_48 |  | 45 | 46 | 0.046046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_6711-9_0_4_line_49 |  | 46 | 47 | 0.003333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_6711-9_0_4_line_50 |  | 47 | 48 | 0.034122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_6711-9_0_4_line_51 |  | 48 | 49 | 0.045453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_6711-9_0_4_line_52 |  | 49 | 50 | 0.0052283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_6711-9_0_4_line_53 |  | 50 | 51 | 0.087458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_6711-9_0_4_line_54 |  | 51 | 52 | 0.094545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_6711-9_0_4_line_55 |  | 51 | 53 | 0.013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6711-9_0_4_line_56 |  | 52 | 70 | 0.045866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6711-9_0_4_line_57 |  | 52 | 66 | 0.015821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_6711-9_0_4_line_58 |  | 53 | 73 | 0.037742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6711-9_0_4_line_59 |  | 53 | 72 | 0.024007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6711-9_0_4_line_60 |  | 54 | 55 | 0.041172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6711-9_0_4_line_61 |  | 55 | 56 | 0.041206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6711-9_0_4_line_62 |  | 56 | 57 | 0.01448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6711-9_0_4_line_63 |  | 57 | 59 | 0.025292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6711-9_0_4_line_64 |  | 58 | 59 | 0.036915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6711-9_0_4_line_65 |  | 60 | 61 | 0.22431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_6711-9_0_4_line_66 |  | 61 | 62 | 0.020065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_6711-9_0_4_line_67 |  | 61 | 63 | 0.10842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_6711-9_0_4_line_68 |  | 62 | 69 | 0.0021122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_6711-9_0_4_line_69 |  | 63 | 71 | 0.040042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6711-9_0_4_line_70 |  | 64 | 65 | 0.005356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_6711-9_0_4_line_71 |  | 64 | 66 | 0.055285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_6711-9_0_4_line_72 |  | 65 | 67 | 0.01626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_6711-9_0_4_line_73 |  | 66 | 68 | 0.055608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6711-9_0_4_line_74 |  | 67 | 69 | 0.030456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6711-9_0_4_trafo_5 | 0.63 MVA 20/0.4 kV | 76 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2594182.9773 | 1245627.8907 | 2594191.4989 | 1245626.8574
1 | 2594182.9773 | 1245627.8907 | 2594174.4456 | 1245628.9252
2 | 2594174.4456 | 1245628.9252 | 2594153.3004 | 1245631.4892
3 | 2594124.4223 | 1245635.5774 | 2594133.3741 | 1245635.4128 | 2594144.4158 | 1245632.5666 | 2594153.3004 | 1245631.4892
4 | 2594260.5283 | 1245618.4871 | 2594262.2645 | 1245586.9384
5 | 2594260.5283 | 1245618.4871 | 2594259.3774 | 1245644.009
6 | 2594262.933 | 1245574.7903 | 2594262.2645 | 1245586.9384
7 | 2594258.8107 | 1245656.5787 | 2594259.3774 | 1245644.009
8 | 2594139.3315 | 1245587.154 | 2594124.4223 | 1245635.5774
9 | 2594124.4223 | 1245635.5774 | 2594120.5472 | 1245649.3343
10 | 2594268.0078 | 1245526.6548 | 2594262.933 | 1245574.7903
11 | 2594262.933 | 1245574.7903 | 2594239.4738 | 1245577.2909
12 | 2594258.8107 | 1245656.5787 | 2594258.317 | 1245667.5255
13 | 2594139.3315 | 1245587.154 | 2594154.3822 | 1245589.3069 | 2594166.3895 | 1245585.0812 | 2594166.8526 | 1245585.0318
14 | 2594139.3315 | 1245587.154 | 2594032.1155 | 1245547.0257
15 | 2594120.5472 | 1245649.3343 | 2594116.6379 | 1245663.2126
16 | 2594257.74 | 1245694.7604 | 2594257.6079 | 1245683.2532 | 2594258.317 | 1245667.5255
17 | 2594257.74 | 1245694.7604 | 2594275.8449 | 1245692.9905
18 | 2594319.6197 | 1245689.2298 | 2594300.5916 | 1245690.5714 | 2594275.8449 | 1245692.9905
19 | 2594319.6197 | 1245689.2298 | 2594339.8945 | 1245688.2429 | 2594366.7735 | 1245688.973 | 2594396.9098 | 1245691.1454
20 | 2594319.6197 | 1245689.2298 | 2594320.4215 | 1245672.193
21 | 2594396.9098 | 1245691.1454 | 2594402.6367 | 1245691.8181 | 2594434.9362 | 1245695.8817
22 | 2594396.9098 | 1245691.1454 | 2594399.4585 | 1245678.3793
23 | 2594321.0721 | 1245658.368 | 2594320.4215 | 1245672.193
24 | 2594268.0078 | 1245526.6548 | 2594238.3136 | 1245529.6289
25 | 2594268.0078 | 1245526.6548 | 2594290.9895 | 1245527.4452
26 | 2594239.4738 | 1245577.2909 | 2594209.717 | 1245580.4628
27 | 2594238.3136 | 1245529.6289 | 2594203.3796 | 1245533.1279
28 | 2594290.9895 | 1245527.4452 | 2594301.2008 | 1245527.7964
29 | 2594209.717 | 1245580.4628 | 2594190.2516 | 1245582.5376
30 | 2594203.3796 | 1245533.1279 | 2594183.0277 | 1245535.1663 | 2594183.0277 | 1245535.1663
31 | 2594301.2008 | 1245527.7964 | 2594301.6417 | 1245527.8116
32 | 2594190.2516 | 1245582.5376 | 2594166.8526 | 1245585.0318
33 | 2594379.6818 | 1245675.4169 | 2594366.7133 | 1245673.4743 | 2594367.0433 | 1245667.0357
34 | 2594399.4585 | 1245678.3793 | 2594379.6818 | 1245675.4169
35 | 2594399.4585 | 1245678.3793 | 2594404.0773 | 1245642.0852 | 2594403.8463 | 1245621.7614 | 2594403.8595 | 1245619.7062
36 | 2594356.2275 | 1245563.5925 | 2594404.2144 | 1245564.4025
37 | 2594356.2275 | 1245563.5925 | 2594357.6858 | 1245538.4689
38 | 2594404.2144 | 1245564.4025 | 2594405.5127 | 1245538.1999
39 | 2594404.2144 | 1245564.4025 | 2594404.0392 | 1245591.7072
40 | 2594404.0392 | 1245591.7072 | 2594403.8595 | 1245619.7062
41 | 2594434.9362 | 1245695.8817 | 2594450.0943 | 1245697.7887
42 | 2594524.7341 | 1245704.6218 | 2594503.0756 | 1245704.2641 | 2594464.1211 | 1245699.5534 | 2594450.0943 | 1245697.7887
43 | 2594321.7918 | 1245643.0751 | 2594321.0721 | 1245658.368
44 | 2594322.6839 | 1245624.1189 | 2594321.7918 | 1245643.0751
45 | 2594116.6379 | 1245663.2126 | 2594111.3621 | 1245681.9422
46 | 2594107.8744 | 1245699.2789 | 2594109.4739 | 1245689.7824 | 2594111.3621 | 1245681.9422
47 | 2594107.8744 | 1245699.2789 | 2594104.1131 | 1245700.1054 | 2594100.8215 | 1245702.0989 | 2594098.3542 | 1245705.0477 | 2594096.9829 | 1245708.6402 | 2594096.8508 | 1245712.4761
48 | 2594096.8508 | 1245712.4761 | 2594089.6916 | 1245714.7292 | 2594087.2901 | 1245715.4766 | 2594062.5749 | 1245725.3745 | 2594055.3948 | 1245729.3288 | 2594054.4657 | 1245730.0968
49 | 2594054.4657 | 1245730.0968 | 2594051.8967 | 1245732.2202
50 | 2594051.8967 | 1245732.2202 | 2594050.5868 | 1245733.3029 | 2594045.0701 | 1245738.723 | 2594040.513 | 1245744.2979 | 2594036.9529 | 1245749.7049 | 2594034.2854 | 1245756.2674 | 2594033.4053 | 1245759.9595 | 2594033.3963 | 1245760.0941
51 | 2594072.6378 | 1245761.97 | 2594071.7981 | 1245762.0551 | 2594069.5025 | 1245762.9247 | 2594055.6616 | 1245768.8536 | 2594052.7768 | 1245769.7015 | 2594050.0197 | 1245769.9267 | 2594047.315 | 1245769.6515 | 2594037.5365 | 1245766.326 | 2594035.1405 | 1245765.0721 | 2594033.7791 | 1245763.5058 | 2594033.2714 | 1245761.9609 | 2594033.3963 | 1245760.0941
52 | 2594077.8266 | 1245762.2381 | 2594074.4569 | 1245761.7856 | 2594072.6378 | 1245761.97
53 | 2594077.8266 | 1245762.2381 | 2594085.625 | 1245764.6095 | 2594081.5588 | 1245777.5773 | 2594077.8659 | 1245786.1532 | 2594081.2979 | 1245788.4957 | 2594083.7186 | 1245791.8731 | 2594084.8105 | 1245795.8857 | 2594084.4445 | 1245800.0109 | 2594091.7955 | 1245800.7373 | 2594097.5374 | 1245801.4764 | 2594116.6369 | 1245803.9476 | 2594118.8734 | 1245796.9632
54 | 2594118.8734 | 1245796.9632 | 2594116.6369 | 1245803.9476 | 2594139.2796 | 1245806.7934 | 2594203.2257 | 1245814.3456
55 | 2594123.0981 | 1245783.8061 | 2594118.8734 | 1245796.9632
56 | 2594203.2257 | 1245814.3456 | 2594209.9805 | 1245768.9793
57 | 2594203.2257 | 1245814.3456 | 2594218.9705 | 1245816.3091
58 | 2594123.0981 | 1245783.8061 | 2594134.6188 | 1245747.8659
59 | 2594123.0981 | 1245783.8061 | 2594118.4423 | 1245781.3314 | 2594116.6427 | 1245779.71 | 2594116.3077 | 1245777.0976 | 2594120.1572 | 1245763.9724
60 | 2594572.1825 | 1245753.1195 | 2594575.7859 | 1245761.288 | 2594582.4482 | 1245777.0807 | 2594582.4574 | 1245787.0203 | 2594581.0991 | 1245792.0021
61 | 2594572.1825 | 1245753.1195 | 2594558.309 | 1245765.1845 | 2594542.6975 | 1245768.4789 | 2594535.8562 | 1245767.9097
62 | 2594522.5519 | 1245762.6763 | 2594532.5211 | 1245767.6323 | 2594535.8562 | 1245767.9097
63 | 2594522.5519 | 1245762.6763 | 2594517.6097 | 1245760.2193 | 2594515.8851 | 1245749.7921 | 2594517.1208 | 1245740.672
64 | 2594524.7341 | 1245704.6218 | 2594519.1561 | 1245725.6515 | 2594517.1208 | 1245740.672
65 | 2594222.1759 | 1245925.8088 | 2594440.2502 | 1245978.3308
66 | 2594222.1759 | 1245925.8088 | 2594225.8166 | 1245906.0772
67 | 2594116.7043 | 1245901.0425 | 2594148.8455 | 1245907.2921 | 2594198.938 | 1245916.4369 | 2594222.1759 | 1245925.8088
68 | 2594225.8166 | 1245906.0772 | 2594226.1999 | 1245904.0001
69 | 2594116.7043 | 1245901.0425 | 2594112.1629 | 1245929.6208 | 2594111.3522 | 1245934.7137 | 2594110.4178 | 1245940.5878
70 | 2594235.4914 | 1245852.7656 | 2594234.6657 | 1245858.0575
71 | 2594218.9705 | 1245816.3091 | 2594240.6318 | 1245819.8233 | 2594235.4914 | 1245852.7656
72 | 2594234.6657 | 1245858.0575 | 2594234.6039 | 1245858.4537 | 2594231.7262 | 1245874.0494
73 | 2594218.9705 | 1245816.3091 | 2594227.9468 | 1245761.4299
74 | 2594231.7262 | 1245874.0494 | 2594226.1999 | 1245904.0001

## bus_geodata
| x | y | coords
0 | 2594182.9773 | 1245627.8907
1 | 2594191.4989 | 1245626.8574
2 | 2594174.4456 | 1245628.9252
3 | 2594153.3004 | 1245631.4892
4 | 2594260.5283 | 1245618.4871
5 | 2594262.2645 | 1245586.9384
6 | 2594259.3774 | 1245644.009
7 | 2594124.4223 | 1245635.5774
8 | 2594262.933 | 1245574.7903
9 | 2594258.8107 | 1245656.5787
10 | 2594139.3315 | 1245587.154
11 | 2594120.5472 | 1245649.3343
12 | 2594258.317 | 1245667.5255
13 | 2594257.74 | 1245694.7604
14 | 2594275.8449 | 1245692.9905
15 | 2594319.6197 | 1245689.2298
16 | 2594396.9098 | 1245691.1454
17 | 2594320.4215 | 1245672.193
18 | 2594268.0078 | 1245526.6548
19 | 2594239.4738 | 1245577.2909
20 | 2594238.3136 | 1245529.6289
21 | 2594290.9895 | 1245527.4452
22 | 2594209.717 | 1245580.4628
23 | 2594203.3796 | 1245533.1279
24 | 2594301.2008 | 1245527.7964
25 | 2594190.2516 | 1245582.5376
26 | 2594367.0433 | 1245667.0357
27 | 2594379.6818 | 1245675.4169
28 | 2594399.4585 | 1245678.3793
29 | 2594356.2275 | 1245563.5925
30 | 2594404.2144 | 1245564.4025
31 | 2594357.6858 | 1245538.4689
32 | 2594403.8595 | 1245619.7062
33 | 2594405.5127 | 1245538.1999
34 | 2594404.0392 | 1245591.7072
35 | 2594434.9362 | 1245695.8817
36 | 2594450.0943 | 1245697.7887
37 | 2594321.0721 | 1245658.368
38 | 2594321.7918 | 1245643.0751
39 | 2594322.6839 | 1245624.1189
40 | 2594116.6379 | 1245663.2126
41 | 2594111.3621 | 1245681.9422
42 | 2594107.8744 | 1245699.2789
43 | 2594166.8526 | 1245585.0318
44 | 2594032.1155 | 1245547.0257
45 | 2594096.8508 | 1245712.4761
46 | 2594054.4657 | 1245730.0968
47 | 2594051.8967 | 1245732.2202
48 | 2594033.3963 | 1245760.0941
49 | 2594072.6378 | 1245761.97
50 | 2594077.8266 | 1245762.2381
51 | 2594118.8734 | 1245796.9632
52 | 2594203.2257 | 1245814.3456
53 | 2594123.0981 | 1245783.8061
54 | 2594581.0991 | 1245792.0021
55 | 2594572.1825 | 1245753.1195
56 | 2594535.8562 | 1245767.9097
57 | 2594522.5519 | 1245762.6763
58 | 2594524.7341 | 1245704.6218
59 | 2594517.1208 | 1245740.672
60 | 2594440.2502 | 1245978.3308
61 | 2594222.1759 | 1245925.8087
62 | 2594225.8166 | 1245906.0772
63 | 2594116.7043 | 1245901.0425
64 | 2594235.4914 | 1245852.7656
65 | 2594234.6657 | 1245858.0575
66 | 2594218.9705 | 1245816.3091
67 | 2594231.7262 | 1245874.0494
68 | 2594227.9468 | 1245761.4299
69 | 2594226.1999 | 1245904.0001
70 | 2594209.9805 | 1245768.9793
71 | 2594110.4178 | 1245940.5878
72 | 2594120.1572 | 1245763.9724
73 | 2594134.6188 | 1245747.8659
74 | 2594301.6417 | 1245527.8116
75 | 2594183.0277 | 1245535.1663
76 | 2594260.5283 | 1245618.4871

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1