## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1-2_0_3_node_34 | 0.4 | n |  | TRUE
3 | bus_LV_1-2_0_3_node_277 | 0.4 | n |  | TRUE
4 | bus_LV_1-2_0_3_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_1-2_0_3_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_1-2_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1-2_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1-2_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1-2_0_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1-2_0_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1-2_0_3_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_1-2_0_3_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_1-2_0_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1-2_0_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1-2_0_3_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1-2_0_3_node_51 | 0.4 | n |  | TRUE
17 | bus_LV_1-2_0_3_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1-2_0_3_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1-2_0_3_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_1-2_0_3_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_1-2_0_3_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1-2_0_3_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_1-2_0_3_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1-2_0_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1-2_0_3_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_1-2_0_3_node_262 | 0.4 | n |  | TRUE
27 | bus_LV_1-2_0_3_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_1-2_0_3_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_1-2_0_3_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_1-2_0_3_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_1-2_0_3_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_1-2_0_3_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_1-2_0_3_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_1-2_0_3_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_1-2_0_3_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_1-2_0_3_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_1-2_0_3_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_1-2_0_3_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_1-2_0_3_node_55 | 0.4 | n |  | TRUE
40 | bus_LV_1-2_0_3_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_1-2_0_3_node_57 | 0.4 | n |  | TRUE
42 | bus_LV_1-2_0_3_node_58 | 0.4 | n |  | TRUE
43 | bus_LV_1-2_0_3_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_1-2_0_3_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_1-2_0_3_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_1-2_0_3_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1-2_0_3_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_1-2_0_3_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_1-2_0_3_node_67 | 0.4 | n |  | TRUE
50 | bus_LV_1-2_0_3_node_201 | 0.4 | n |  | TRUE
51 | bus_LV_1-2_0_3_node_200 | 0.4 | n |  | TRUE
52 | bus_LV_1-2_0_3_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_1-2_0_3_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_1-2_0_3_node_71 | 0.4 | n |  | TRUE
55 | bus_LV_1-2_0_3_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_1-2_0_3_node_74 | 0.4 | n |  | TRUE
57 | bus_LV_1-2_0_3_node_230 | 0.4 | n |  | TRUE
58 | bus_LV_1-2_0_3_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_1-2_0_3_node_76 | 0.4 | n |  | TRUE
60 | bus_LV_1-2_0_3_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_1-2_0_3_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_1-2_0_3_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_1-2_0_3_node_205 | 0.4 | n |  | TRUE
64 | bus_LV_1-2_0_3_node_179 | 0.4 | n |  | TRUE
65 | bus_LV_1-2_0_3_node_181 | 0.4 | n |  | TRUE
66 | bus_LV_1-2_0_3_node_196 | 0.4 | n |  | TRUE
67 | bus_LV_1-2_0_3_node_183 | 0.4 | n |  | TRUE
68 | bus_LV_1-2_0_3_node_184 | 0.4 | n |  | TRUE
69 | bus_LV_1-2_0_3_node_185 | 0.4 | n |  | TRUE
70 | bus_LV_1-2_0_3_node_186 | 0.4 | n |  | TRUE
71 | bus_LV_1-2_0_3_node_199 | 0.4 | n |  | TRUE
72 | bus_LV_1-2_0_3_node_187 | 0.4 | n |  | TRUE
73 | bus_LV_1-2_0_3_node_188 | 0.4 | n |  | TRUE
74 | bus_LV_1-2_0_3_node_189 | 0.4 | n |  | TRUE
75 | bus_LV_1-2_0_3_node_190 | 0.4 | n |  | TRUE
76 | bus_LV_1-2_0_3_node_191 | 0.4 | n |  | TRUE
77 | bus_LV_1-2_0_3_node_192 | 0.4 | n |  | TRUE
78 | bus_LV_1-2_0_3_node_193 | 0.4 | n |  | TRUE
79 | bus_LV_1-2_0_3_node_194 | 0.4 | n |  | TRUE
80 | bus_LV_1-2_0_3_node_195 | 0.4 | n |  | TRUE
81 | bus_LV_1-2_0_3_node_227 | 0.4 | n |  | TRUE
82 | bus_LV_1-2_0_3_node_197 | 0.4 | n |  | TRUE
83 | bus_LV_1-2_0_3_node_198 | 0.4 | n |  | TRUE
84 | bus_LV_1-2_0_3_node_208 | 0.4 | n |  | TRUE
85 | bus_LV_1-2_0_3_node_202 | 0.4 | n |  | TRUE
86 | bus_LV_1-2_0_3_node_203 | 0.4 | n |  | TRUE
87 | bus_LV_1-2_0_3_node_204 | 0.4 | n |  | TRUE
88 | bus_LV_1-2_0_3_node_206 | 0.4 | n |  | TRUE
89 | bus_LV_1-2_0_3_node_207 | 0.4 | n |  | TRUE
90 | bus_LV_1-2_0_3_node_210 | 0.4 | n |  | TRUE
91 | bus_LV_1-2_0_3_node_287 | 0.4 | n |  | TRUE
92 | bus_LV_1-2_0_3_node_209 | 0.4 | n |  | TRUE
93 | bus_LV_1-2_0_3_node_211 | 0.4 | n |  | TRUE
94 | bus_LV_1-2_0_3_node_214 | 0.4 | n |  | TRUE
95 | bus_LV_1-2_0_3_node_215 | 0.4 | n |  | TRUE
96 | bus_LV_1-2_0_3_node_216 | 0.4 | n |  | TRUE
97 | bus_LV_1-2_0_3_node_217 | 0.4 | n |  | TRUE
98 | bus_LV_1-2_0_3_node_223 | 0.4 | n |  | TRUE
99 | bus_LV_1-2_0_3_node_225 | 0.4 | n |  | TRUE
100 | bus_LV_1-2_0_3_node_226 | 0.4 | n |  | TRUE
101 | bus_LV_1-2_0_3_node_218 | 0.4 | n |  | TRUE
102 | bus_LV_1-2_0_3_node_219 | 0.4 | n |  | TRUE
103 | bus_LV_1-2_0_3_node_220 | 0.4 | n |  | TRUE
104 | bus_LV_1-2_0_3_node_221 | 0.4 | n |  | TRUE
105 | bus_LV_1-2_0_3_node_222 | 0.4 | n |  | TRUE
106 | bus_LV_1-2_0_3_node_224 | 0.4 | n |  | TRUE
107 | bus_LV_1-2_0_3_node_228 | 0.4 | n |  | TRUE
108 | bus_LV_1-2_0_3_node_231 | 0.4 | n |  | TRUE
109 | bus_LV_1-2_0_3_node_229 | 0.4 | n |  | TRUE
110 | bus_LV_1-2_0_3_node_240 | 0.4 | n |  | TRUE
111 | bus_LV_1-2_0_3_node_241 | 0.4 | n |  | TRUE
112 | bus_LV_1-2_0_3_node_242 | 0.4 | n |  | TRUE
113 | bus_LV_1-2_0_3_node_252 | 0.4 | n |  | TRUE
114 | bus_LV_1-2_0_3_node_249 | 0.4 | n |  | TRUE
115 | bus_LV_1-2_0_3_node_250 | 0.4 | n |  | TRUE
116 | bus_LV_1-2_0_3_node_251 | 0.4 | n |  | TRUE
117 | bus_LV_1-2_0_3_node_253 | 0.4 | n |  | TRUE
118 | bus_LV_1-2_0_3_node_254 | 0.4 | n |  | TRUE
119 | bus_LV_1-2_0_3_node_255 | 0.4 | n |  | TRUE
120 | bus_LV_1-2_0_3_node_257 | 0.4 | n |  | TRUE
121 | bus_LV_1-2_0_3_node_260 | 0.4 | n |  | TRUE
122 | bus_LV_1-2_0_3_node_258 | 0.4 | n |  | TRUE
123 | bus_LV_1-2_0_3_node_259 | 0.4 | n |  | TRUE
124 | bus_LV_1-2_0_3_node_292 | 0.4 | n |  | TRUE
125 | bus_LV_1-2_0_3_node_275 | 0.4 | n |  | TRUE
126 | bus_LV_1-2_0_3_node_276 | 0.4 | n |  | TRUE
127 | bus_LV_1-2_0_3_node_278 | 0.4 | n |  | TRUE
128 | bus_LV_1-2_0_3_node_290 | 0.4 | n |  | TRUE
129 | bus_LV_1-2_0_3_node_279 | 0.4 | n |  | TRUE
130 | bus_LV_1-2_0_3_node_280 | 0.4 | n |  | TRUE
131 | bus_LV_1-2_0_3_node_281 | 0.4 | n |  | TRUE
132 | bus_LV_1-2_0_3_node_282 | 0.4 | n |  | TRUE
133 | bus_LV_1-2_0_3_node_283 | 0.4 | n |  | TRUE
134 | bus_LV_1-2_0_3_node_284 | 0.4 | n |  | TRUE
135 | bus_LV_1-2_0_3_node_285 | 0.4 | n |  | TRUE
136 | bus_LV_1-2_0_3_node_291 | 0.4 | n |  | TRUE
137 | bus_MV_349_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1-2_0_3_load_0 | 0 | 0.0025182 | 0.00063111 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1-2_0_3_load_1 | 1 | 0.00053583 | 0.00013429 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1-2_0_3_load_34 | 2 | 0.00035293 | 8.8454e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1-2_0_3_load_21 | 4 | 0.0010424 | 0.00026126 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1-2_0_3_load_22 | 5 | 0.00070124 | 0.00017575 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1-2_0_3_load_24 | 7 | 0.0007614 | 0.00019082 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1-2_0_3_load_25 | 8 | 0.00025502 | 6.3914e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1-2_0_3_load_26 | 9 | 0.00047247 | 0.00011841 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1-2_0_3_load_27 | 10 | 0.00017983 | 4.5069e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1-2_0_3_load_28 | 11 | 0.0017276 | 0.00043298 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1-2_0_3_load_32 | 12 | 0.0014631 | 0.00036669 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1-2_0_3_load_30 | 14 | 0.0024782 | 0.00062109 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1-2_0_3_load_31 | 15 | 0.0034583 | 0.00086673 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1-2_0_3_load_33 | 17 | 0.00032917 | 8.2498e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1-2_0_3_load_36 | 18 | 0.00076129 | 0.0001908 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1-2_0_3_load_37 | 19 | 0.0011811 | 0.00029602 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1-2_0_3_load_38 | 20 | 0.00011825 | 2.9635e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1-2_0_3_load_39 | 21 | 0.00085257 | 0.00021367 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1-2_0_3_load_40 | 22 | 0.00012909 | 3.2354e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1-2_0_3_load_42 | 24 | 0.00088259 | 0.0002212 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1-2_0_3_load_262 | 26 | 0.00012146 | 3.0442e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1-2_0_3_load_48 | 27 | 0.0023149 | 0.00058016 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1-2_0_3_load_44 | 29 | 0.0018402 | 0.00046119 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1-2_0_3_load_46 | 30 | 0.0018127 | 0.0004543 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1-2_0_3_load_47 | 31 | 0.001192 | 0.00029875 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1-2_0_3_load_49 | 32 | 0.0025806 | 0.00064676 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1-2_0_3_load_72 | 33 | 0.0012426 | 0.00031142 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1-2_0_3_load_52 | 35 | 0.0030048 | 0.00075307 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1-2_0_3_load_54 | 36 | 0.0015311 | 0.00038374 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1-2_0_3_load_69 | 37 | 0.002248 | 0.0005634 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1-2_0_3_load_53 | 38 | 0.0011053 | 0.00027702 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1-2_0_3_load_55 | 39 | 0.0015037 | 0.00037686 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1-2_0_3_load_56 | 40 | 0.0014608 | 0.0003661 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1-2_0_3_load_57 | 41 | 0.0012617 | 0.00031622 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1-2_0_3_load_59 | 43 | 0.00127 | 0.0003183 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1-2_0_3_load_60 | 44 | 0.0012686 | 0.00031794 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1-2_0_3_load_61 | 45 | 0.0016975 | 0.00042543 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1-2_0_3_load_64 | 46 | 0.0020381 | 0.00051079 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1-2_0_3_load_65 | 47 | 0.0011399 | 0.00028569 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1-2_0_3_load_66 | 48 | 0.0011282 | 0.00028276 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1-2_0_3_load_67 | 49 | 0.0027407 | 0.00068689 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1-2_0_3_load_201 | 50 | 0.0012691 | 0.00031807 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1-2_0_3_load_200 | 51 | 0.0011301 | 0.00028323 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1-2_0_3_load_68 | 52 | 0.0034341 | 0.00086067 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1-2_0_3_load_70 | 53 | 0.0015937 | 0.00039943 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1-2_0_3_load_71 | 54 | 0.0015514 | 0.00038881 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1-2_0_3_load_73 | 55 | 0.0021186 | 0.00053098 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1-2_0_3_load_74 | 56 | 0.0023741 | 0.00059501 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1-2_0_3_load_230 | 57 | 0.0012239 | 0.00030673 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1-2_0_3_load_75 | 58 | 0.0027971 | 0.00070103 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1-2_0_3_load_76 | 59 | 0.0022481 | 0.00056342 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1-2_0_3_load_77 | 60 | 0.0039177 | 0.00098186 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1-2_0_3_load_78 | 61 | 0.002292 | 0.00057444 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1-2_0_3_load_79 | 62 | 0.0028941 | 0.00072534 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1-2_0_3_load_205 | 63 | 0.0026861 | 0.00067321 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1-2_0_3_load_179 | 64 | 0.001969 | 0.00049348 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1-2_0_3_load_181 | 65 | 0.0015177 | 0.00038038 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1-2_0_3_load_196 | 66 | 0.0012988 | 0.0003255 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1-2_0_3_load_183 | 67 | 0.0023054 | 0.00057778 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1-2_0_3_load_184 | 68 | 0.0011441 | 0.00028674 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1-2_0_3_load_185 | 69 | 0.0011269 | 0.00028243 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1-2_0_3_load_186 | 70 | 0.0020484 | 0.00051339 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1-2_0_3_load_199 | 71 | 0.0011354 | 0.00028457 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1-2_0_3_load_187 | 72 | 0.0015074 | 0.00037779 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1-2_0_3_load_188 | 73 | 0.00075657 | 0.00018961 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1-2_0_3_load_190 | 75 | 0.00099621 | 0.00024967 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1-2_0_3_load_191 | 76 | 0.0020108 | 0.00050395 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1-2_0_3_load_192 | 77 | 0.0016823 | 0.00042162 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1-2_0_3_load_193 | 78 | 0.0021193 | 0.00053113 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1-2_0_3_load_195 | 80 | 0.0013142 | 0.00032938 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1-2_0_3_load_227 | 81 | 0.0011844 | 0.00029685 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1-2_0_3_load_197 | 82 | 0.0020115 | 0.00050414 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1-2_0_3_load_198 | 83 | 0.0015134 | 0.00037929 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1-2_0_3_load_208 | 84 | 0.0019847 | 0.00049742 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1-2_0_3_load_202 | 85 | 0.0025242 | 0.00063262 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1-2_0_3_load_206 | 88 | 0.001147 | 0.00028746 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1-2_0_3_load_207 | 89 | 0.0019079 | 0.00047816 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1-2_0_3_load_287 | 91 | 0.0039213 | 0.00098277 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1-2_0_3_load_209 | 92 | 0.0017264 | 0.00043269 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1-2_0_3_load_211 | 93 | 0.0020397 | 0.0005112 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1-2_0_3_load_214 | 94 | 0.0025326 | 0.00063474 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1-2_0_3_load_217 | 97 | 0.0035778 | 0.00089667 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1-2_0_3_load_223 | 98 | 0.0013971 | 0.00035015 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1-2_0_3_load_225 | 99 | 0.0013954 | 0.00034971 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1-2_0_3_load_226 | 100 | 0.0017853 | 0.00044745 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1-2_0_3_load_218 | 101 | 0.0013449 | 0.00033706 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1-2_0_3_load_219 | 102 | 0.0013542 | 0.0003394 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1-2_0_3_load_220 | 103 | 0.001873 | 0.00046942 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1-2_0_3_load_221 | 104 | 0.0016458 | 0.00041247 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1-2_0_3_load_222 | 105 | 0.0013787 | 0.00034553 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1-2_0_3_load_224 | 106 | 0.0016451 | 0.00041231 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1-2_0_3_load_228 | 107 | 0.0031393 | 0.00078678 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1-2_0_3_load_231 | 108 | 0.0013435 | 0.00033672 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1-2_0_3_load_229 | 109 | 0.0015667 | 0.00039266 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1-2_0_3_load_240 | 110 | 0.00044724 | 0.00011209 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1-2_0_3_load_241 | 111 | 0.001231 | 0.00030852 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1-2_0_3_load_242 | 112 | 0.0015861 | 0.00039751 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1-2_0_3_load_249 | 114 | 0.001173 | 0.00029398 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1-2_0_3_load_250 | 115 | 0.00093009 | 0.0002331 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1-2_0_3_load_251 | 116 | 0.0013962 | 0.00034993 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1-2_0_3_load_253 | 117 | 0.0010082 | 0.00025267 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1-2_0_3_load_254 | 118 | 0.0012735 | 0.00031918 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1-2_0_3_load_255 | 119 | 0.00084726 | 0.00021234 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1-2_0_3_load_258 | 122 | 0.0019391 | 0.00048599 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1-2_0_3_load_259 | 123 | 0.0019295 | 0.00048359 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1-2_0_3_load_292 | 124 | 0.00045041 | 0.00011288 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1-2_0_3_load_275 | 125 | 0.006987 | 0.0017511 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1-2_0_3_load_290 | 128 | 0.0018596 | 0.00046607 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1-2_0_3_load_279 | 129 | 0.0013331 | 0.0003341 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1-2_0_3_load_280 | 130 | 0.00059835 | 0.00014996 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1-2_0_3_load_281 | 131 | 0.00038558 | 9.6634e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1-2_0_3_load_282 | 132 | 0.0029672 | 0.00074366 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1-2_0_3_load_283 | 133 | 0.00097882 | 0.00024531 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1-2_0_3_load_284 | 134 | 0.00086421 | 0.00021659 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1-2_0_3_line_0 |  | 0 | 1 | 0.039599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1-2_0_3_line_1 |  | 1 | 2 | 0.18034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1-2_0_3_line_2 |  | 1 | 3 | 0.22296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1-2_0_3_line_3 |  | 2 | 17 | 0.032627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1-2_0_3_line_4 |  | 3 | 128 | 0.052869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1-2_0_3_line_5 |  | 3 | 125 | 0.084086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1-2_0_3_line_6 |  | 4 | 5 | 0.054393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1-2_0_3_line_7 |  | 4 | 6 | 0.02108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1-2_0_3_line_8 |  | 5 | 7 | 0.10965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1-2_0_3_line_9 |  | 6 | 8 | 0.0025129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1-2_0_3_line_10 |  | 6 | 9 | 0.061994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1-2_0_3_line_11 |  | 7 | 10 | 0.027718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1-2_0_3_line_12 |  | 8 | 11 | 0.027565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1-2_0_3_line_13 |  | 10 | 12 | 0.03375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1-2_0_3_line_14 |  | 11 | 13 | 0.077021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1-2_0_3_line_15 |  | 12 | 17 | 0.047864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1-2_0_3_line_16 |  | 13 | 14 | 0.033485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1-2_0_3_line_17 |  | 13 | 15 | 0.071236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1-2_0_3_line_18 |  | 14 | 16 | 0.015314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1-2_0_3_line_19 |  | 16 | 36 | 0.048736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1-2_0_3_line_20 |  | 16 | 34 | 0.002837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1-2_0_3_line_21 |  | 18 | 19 | 0.049943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1-2_0_3_line_22 |  | 18 | 20 | 0.021832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1-2_0_3_line_23 |  | 19 | 21 | 0.024332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1-2_0_3_line_24 |  | 20 | 22 | 0.063247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1-2_0_3_line_25 |  | 21 | 23 | 0.037006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1-2_0_3_line_26 |  | 22 | 24 | 0.04798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1-2_0_3_line_27 |  | 23 | 25 | 0.035023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1-2_0_3_line_28 |  | 24 | 26 | 0.039738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1-2_0_3_line_29 |  | 25 | 27 | 0.0093558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1-2_0_3_line_30 |  | 25 | 28 | 0.003442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1-2_0_3_line_31 |  | 27 | 33 | 0.038806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1-2_0_3_line_32 |  | 28 | 30 | 0.025786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1-2_0_3_line_33 |  | 28 | 29 | 0.022649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1-2_0_3_line_34 |  | 30 | 31 | 0.038749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1-2_0_3_line_35 |  | 31 | 32 | 0.0043806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1-2_0_3_line_36 |  | 32 | 34 | 0.043432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1-2_0_3_line_37 |  | 33 | 53 | 0.0056303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1-2_0_3_line_38 |  | 34 | 35 | 0.018175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1-2_0_3_line_39 |  | 35 | 37 | 0.031198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1-2_0_3_line_40 |  | 36 | 38 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1-2_0_3_line_41 |  | 38 | 39 | 0.0024886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1-2_0_3_line_42 |  | 40 | 41 | 0.009185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1-2_0_3_line_43 |  | 40 | 42 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1-2_0_3_line_44 |  | 41 | 43 | 0.00076234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1-2_0_3_line_45 |  | 42 | 44 | 0.024745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1-2_0_3_line_46 |  | 42 | 45 | 0.022616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1-2_0_3_line_47 |  | 43 | 46 | 0.025009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1-2_0_3_line_48 |  | 44 | 47 | 9.4796e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1-2_0_3_line_49 |  | 45 | 48 | 0.012087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1-2_0_3_line_50 |  | 46 | 49 | 0.0011397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1-2_0_3_line_51 |  | 47 | 50 | 0.0032829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1-2_0_3_line_52 |  | 48 | 51 | 0.0081921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1-2_0_3_line_53 |  | 49 | 52 | 0.010341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1-2_0_3_line_54 |  | 50 | 85 | 0.037778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1-2_0_3_line_55 |  | 51 | 71 | 0.0078651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1-2_0_3_line_56 |  | 53 | 54 | 0.027789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1-2_0_3_line_57 |  | 54 | 55 | 0.0063091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1-2_0_3_line_58 |  | 55 | 56 | 0.018194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1-2_0_3_line_59 |  | 56 | 57 | 0.0086559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1-2_0_3_line_60 |  | 57 | 109 | 0.017304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1-2_0_3_line_61 |  | 58 | 59 | 0.010127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1-2_0_3_line_62 |  | 58 | 60 | 0.020824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1-2_0_3_line_63 |  | 59 | 61 | 0.019462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_1-2_0_3_line_64 |  | 61 | 62 | 0.0095888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1-2_0_3_line_65 |  | 62 | 63 | 0.014476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_1-2_0_3_line_66 |  | 63 | 86 | 0.018746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_1-2_0_3_line_67 |  | 64 | 65 | 0.01271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1-2_0_3_line_68 |  | 65 | 66 | 0.026585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1-2_0_3_line_69 |  | 66 | 79 | 0.012883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1-2_0_3_line_70 |  | 67 | 68 | 0.019852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1-2_0_3_line_71 |  | 68 | 69 | 0.0079075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1-2_0_3_line_72 |  | 69 | 70 | 0.013128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1-2_0_3_line_73 |  | 70 | 71 | 0.006452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1-2_0_3_line_74 |  | 72 | 73 | 0.022962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1-2_0_3_line_75 |  | 72 | 74 | 0.0030287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1-2_0_3_line_76 |  | 73 | 75 | 0.019497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1-2_0_3_line_77 |  | 74 | 76 | 0.024672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1-2_0_3_line_78 |  | 74 | 77 | 0.020655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1-2_0_3_line_79 |  | 75 | 78 | 0.020062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1-2_0_3_line_80 |  | 76 | 79 | 0.024131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1-2_0_3_line_81 |  | 77 | 80 | 0.033121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1-2_0_3_line_82 |  | 78 | 81 | 0.0049386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1-2_0_3_line_83 |  | 79 | 82 | 0.015211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1-2_0_3_line_84 |  | 81 | 110 | 0.0090206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1-2_0_3_line_85 |  | 82 | 83 | 0.0075725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1-2_0_3_line_86 |  | 83 | 84 | 0.024809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1-2_0_3_line_87 |  | 84 | 92 | 0.0019043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1-2_0_3_line_88 |  | 85 | 86 | 0.024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1-2_0_3_line_89 |  | 86 | 87 | 0.003002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_1-2_0_3_line_90 |  | 87 | 88 | 0.024649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_1-2_0_3_line_91 |  | 87 | 89 | 0.064941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1-2_0_3_line_92 |  | 88 | 90 | 0.020315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_1-2_0_3_line_93 |  | 89 | 91 | 0.014115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1-2_0_3_line_94 |  | 90 | 93 | 0.0083723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_1-2_0_3_line_95 |  | 90 | 92 | 0.018293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1-2_0_3_line_96 |  | 93 | 94 | 0.020992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1-2_0_3_line_97 |  | 94 | 95 | 0.018248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_1-2_0_3_line_98 |  | 95 | 96 | 0.040233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1-2_0_3_line_99 |  | 95 | 97 | 0.025021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_1-2_0_3_line_100 |  | 96 | 98 | 0.0042419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1-2_0_3_line_101 |  | 96 | 99 | 0.017023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1-2_0_3_line_102 |  | 97 | 100 | 0.0059331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_1-2_0_3_line_103 |  | 98 | 104 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1-2_0_3_line_104 |  | 99 | 108 | 0.0015361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1-2_0_3_line_105 |  | 100 | 109 | 0.02048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_1-2_0_3_line_106 |  | 101 | 102 | 0.021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1-2_0_3_line_107 |  | 101 | 103 | 0.0078207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1-2_0_3_line_108 |  | 102 | 104 | 0.0087133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1-2_0_3_line_109 |  | 103 | 105 | 0.01527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1-2_0_3_line_110 |  | 105 | 106 | 0.010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1-2_0_3_line_111 |  | 106 | 107 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1-2_0_3_line_112 |  | 110 | 111 | 0.010906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1-2_0_3_line_113 |  | 111 | 112 | 0.0032664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1-2_0_3_line_114 |  | 112 | 113 | 0.023611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1-2_0_3_line_115 |  | 113 | 118 | 0.035681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1-2_0_3_line_116 |  | 113 | 119 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1-2_0_3_line_117 |  | 113 | 115 | 0.014455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1-2_0_3_line_118 |  | 114 | 115 | 0.01281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1-2_0_3_line_119 |  | 114 | 116 | 0.0065518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1-2_0_3_line_120 |  | 116 | 117 | 0.002695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1-2_0_3_line_121 |  | 119 | 120 | 0.011774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1-2_0_3_line_122 |  | 120 | 121 | 0.023996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1-2_0_3_line_123 |  | 121 | 122 | 0.017964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1-2_0_3_line_124 |  | 122 | 123 | 0.015317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1-2_0_3_line_125 |  | 123 | 124 | 0.13304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1-2_0_3_line_126 |  | 124 | 136 | 0.19601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1-2_0_3_line_127 |  | 125 | 126 | 0.076257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1-2_0_3_line_128 |  | 126 | 127 | 0.069124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1-2_0_3_line_129 |  | 127 | 129 | 0.020192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1-2_0_3_line_130 |  | 130 | 131 | 0.00064942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1-2_0_3_line_131 |  | 130 | 132 | 0.0083321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1-2_0_3_line_132 |  | 131 | 133 | 0.0094694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1-2_0_3_line_133 |  | 132 | 134 | 0.010391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1-2_0_3_line_134 |  | 133 | 135 | 0.0094677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1-2_0_3_line_135 |  | 135 | 136 | 0.36327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1-2_0_3_trafo_76 | 0.63 MVA 20/0.4 kV | 137 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2678452.8284 | 1236598.8828 | 2678453.8164 | 1236593.8409 | 2678460.2812 | 1236559.9915
1 | 2678639.461 | 1236580.4012 | 2678460.2812 | 1236559.9915
2 | 2678460.2812 | 1236559.9915 | 2678448.4499 | 1236337.347
3 | 2678640.8696 | 1236547.8313 | 2678639.6276 | 1236561.4747 | 2678639.461 | 1236580.4012
4 | 2678448.4499 | 1236337.347 | 2678399.4939 | 1236317.3869
5 | 2678448.4499 | 1236337.347 | 2678459.3945 | 1236317.1552 | 2678468.5788 | 1236296.1841 | 2678474.3405 | 1236298.2616 | 2678487.0337 | 1236268.7781
6 | 2678743.983 | 1236300.0868 | 2678713.4938 | 1236345.1316
7 | 2678755.7988 | 1236282.6302 | 2678743.983 | 1236300.0868
8 | 2678713.4938 | 1236345.1316 | 2678686.1986 | 1236385.4575 | 2678670.5571 | 1236410.5456 | 2678660.8428 | 1236440.3951
9 | 2678755.7988 | 1236282.6302 | 2678757.1216 | 1236280.4936
10 | 2678755.7988 | 1236282.6302 | 2678760.3449 | 1236287.9163 | 2678761.7279 | 1236293.1939 | 2678754.1901 | 1236313.1968 | 2678754.3189 | 1236317.1791 | 2678756.414 | 1236323.5446 | 2678769.9871 | 1236334.5977
11 | 2678654.8402 | 1236467.4428 | 2678660.1047 | 1236442.663 | 2678660.8428 | 1236440.3951
12 | 2678757.1216 | 1236280.4936 | 2678771.6318 | 1236257.0565
13 | 2678654.8402 | 1236467.4428 | 2678650.9203 | 1236485.8937 | 2678648.5132 | 1236500.5848
14 | 2678812.1756 | 1236191.5698 | 2678771.6318 | 1236257.0565
15 | 2678648.5132 | 1236500.5848 | 2678640.9914 | 1236546.4934 | 2678640.8696 | 1236547.8313
16 | 2678812.1756 | 1236191.5698 | 2678836.8165 | 1236201.8149 | 2678842.9996 | 1236204.6434
17 | 2678812.1756 | 1236191.5698 | 2678820.6319 | 1236172.5243 | 2678831.3544 | 1236132.7054 | 2678832.9415 | 1236123.6839
18 | 2678851.7339 | 1236217.1013 | 2678847.1336 | 1236209.0569 | 2678842.9996 | 1236204.6434
19 | 2678851.7339 | 1236217.1013 | 2678863.6134 | 1236233.1924 | 2678866.3375 | 1236236.6309 | 2678870.6796 | 1236238.4787 | 2678874.8184 | 1236238.5337 | 2678878.6266 | 1236236.127 | 2678885.2294 | 1236227.3484
20 | 2678851.7339 | 1236217.1013 | 2678850.8656 | 1236219.8028
21 | 2678828.3851 | 1236420.4916 | 2678832.4249 | 1236414.5938 | 2678860.657 | 1236382.4336
22 | 2678828.3851 | 1236420.4916 | 2678816.0475 | 1236438.5034
23 | 2678860.657 | 1236382.4336 | 2678876.7096 | 1236364.1474
24 | 2678795.3017 | 1236498.073 | 2678795.3272 | 1236497.9932 | 2678813.5259 | 1236442.1846 | 2678816.0475 | 1236438.5034
25 | 2678907.6438 | 1236344.6991 | 2678899.4978 | 1236347.7931 | 2678881.3706 | 1236358.8379 | 2678876.7096 | 1236364.1474
26 | 2678780.6597 | 1236543.764 | 2678795.3017 | 1236498.073
27 | 2678907.6438 | 1236344.6991 | 2678917.2195 | 1236316.0285 | 2678918.8837 | 1236311.5252
28 | 2678780.6597 | 1236543.764 | 2678775.6115 | 1236583.1801
29 | 2678918.8837 | 1236311.5252 | 2678920.6669 | 1236307.1792 | 2678922.7987 | 1236303.0376
30 | 2678918.8837 | 1236311.5252 | 2678915.8869 | 1236309.8176
31 | 2678941.8137 | 1236269.2495 | 2678932.8087 | 1236283.5907 | 2678922.7987 | 1236303.0376
32 | 2678915.8869 | 1236309.8176 | 2678915.4639 | 1236306.3429 | 2678908.8893 | 1236302.7975 | 2678899.887 | 1236291.0306
33 | 2678915.8869 | 1236309.8176 | 2678910.0402 | 1236308.4501 | 2678905.583 | 1236310.1476 | 2678896.376 | 1236317.6474
34 | 2678876.5967 | 1236260.0995 | 2678880.0143 | 1236265.5437 | 2678888.9171 | 1236276.6919 | 2678899.887 | 1236291.0306
35 | 2678874.2677 | 1236256.3893 | 2678876.5967 | 1236260.0995
36 | 2678850.8656 | 1236219.8028 | 2678866.2893 | 1236243.6796 | 2678874.2677 | 1236256.3893
37 | 2678941.8137 | 1236269.2495 | 2678944.8077 | 1236264.4813 | 2678944.8077 | 1236264.4813
38 | 2678850.8656 | 1236219.8028 | 2678844.7898 | 1236235.6776 | 2678844.3238 | 1236236.7583
39 | 2678828.5244 | 1236263.2144 | 2678837.0675 | 1236253.5877 | 2678844.3238 | 1236236.7583
40 | 2678891.9605 | 1236218.3991 | 2678885.2294 | 1236227.3484
41 | 2678893.4564 | 1236216.4102 | 2678891.9605 | 1236218.3991
42 | 2678918.4247 | 1236077.5339 | 2678912.9093 | 1236084.8786
43 | 2678924.6953 | 1236063.3073 | 2678922.5665 | 1236072.0184 | 2678918.4247 | 1236077.5339
44 | 2678912.4516 | 1236085.4882 | 2678912.9093 | 1236084.8786
45 | 2678924.6953 | 1236063.3073 | 2678936.4061 | 1236066.4873 | 2678946.2803 | 1236074.3311
46 | 2678924.6953 | 1236063.3073 | 2678938.5903 | 1236045.4627
47 | 2678897.434 | 1236105.4866 | 2678912.4516 | 1236085.4882
48 | 2678946.3545 | 1236074.3901 | 2678946.2803 | 1236074.3311
49 | 2678938.5903 | 1236045.4627 | 2678946.0161 | 1236035.9262
50 | 2678897.434 | 1236105.4866 | 2678896.7497 | 1236106.398
51 | 2678948.9251 | 1236076.4321 | 2678946.3545 | 1236074.3901
52 | 2678946.0161 | 1236035.9262 | 2678951.0491 | 1236029.4626
53 | 2678890.54 | 1236114.6672 | 2678896.7497 | 1236106.398
54 | 2678948.9251 | 1236076.4321 | 2678954.7837 | 1236081.086 | 2678955.1673 | 1236085.2496 | 2678974.3605 | 1236100.5375 | 2678975.5735 | 1236101.5455
55 | 2678955.8812 | 1236023.2569 | 2678951.0491 | 1236029.4626
56 | 2678961.9167 | 1236242.5834 | 2678944.8077 | 1236264.4813
57 | 2678965.801 | 1236237.6118 | 2678961.9167 | 1236242.5834
58 | 2678965.801 | 1236237.6118 | 2678977.0029 | 1236223.2745
59 | 2678982.3505 | 1236216.4682 | 2678980.9534 | 1236218.2183 | 2678977.0029 | 1236223.2745
60 | 2678982.3505 | 1236216.4682 | 2678993.1467 | 1236202.9448
61 | 2678952.717 | 1236161.4617 | 2678946.6145 | 1236169.5435
62 | 2678934.066 | 1236186.1618 | 2678946.6145 | 1236169.5435
63 | 2678952.717 | 1236161.4617 | 2678964.4447 | 1236145.9303
64 | 2678964.4447 | 1236145.9303 | 2678970.2229 | 1236138.2781
65 | 2678970.2229 | 1236138.2781 | 2678976.5506 | 1236129.8982 | 2678979.3071 | 1236127.0338
66 | 2678994.7852 | 1236117.1094 | 2678992.3853 | 1236117.7446 | 2678984.2629 | 1236121.884 | 2678979.3071 | 1236127.0338
67 | 2679092.5502 | 1236009.2302 | 2679086.0083 | 1236020.1276
68 | 2679086.0083 | 1236020.1276 | 2679082.5617 | 1236025.869 | 2679073.8954 | 1236043.7703
69 | 2679068.2817 | 1236055.3662 | 2679073.8954 | 1236043.7703
70 | 2678972.6135 | 1236001.4494 | 2678984.6509 | 1235985.6634
71 | 2678972.6135 | 1236001.4494 | 2678967.8187 | 1236007.7374
72 | 2678959.8378 | 1236018.1605 | 2678962.7543 | 1236014.3788 | 2678967.8187 | 1236007.7374
73 | 2678959.8378 | 1236018.1605 | 2678958.6036 | 1236019.7607 | 2678955.8812 | 1236023.2569
74 | 2679117.86 | 1236069.6057 | 2679140.8097 | 1236070.3557
75 | 2679114.833 | 1236069.5067 | 2679117.86 | 1236069.6057
76 | 2679160.296 | 1236070.9926 | 2679140.8097 | 1236070.3557
77 | 2679114.833 | 1236069.5067 | 2679093.9053 | 1236065.1362 | 2679090.829 | 1236063.9632
78 | 2679114.833 | 1236069.5067 | 2679124.1325 | 1236051.0636
79 | 2679180.3471 | 1236071.6479 | 2679160.296 | 1236070.9926
80 | 2679068.2817 | 1236055.3662 | 2679090.829 | 1236063.9632
81 | 2679147.7789 | 1236028.995 | 2679128.2654 | 1236042.867 | 2679124.1325 | 1236051.0636
82 | 2679185.2831 | 1236071.8092 | 2679180.3471 | 1236071.6479
83 | 2679068.2817 | 1236055.3662 | 2679062.5243 | 1236069.4458
84 | 2679185.2831 | 1236071.8092 | 2679194.2989 | 1236072.1039
85 | 2679059.6581 | 1236076.455 | 2679062.5243 | 1236069.4458
86 | 2679059.6581 | 1236076.455 | 2679050.268 | 1236099.4184
87 | 2679049.5473 | 1236101.1811 | 2679050.268 | 1236099.4184
88 | 2678994.7852 | 1236117.1094 | 2678982.3665 | 1236106.8594 | 2678977.4743 | 1236103.1251 | 2678975.5735 | 1236101.5455
89 | 2678994.7852 | 1236117.1094 | 2678997.694 | 1236116.3365
90 | 2678997.694 | 1236116.3365 | 2679022.3242 | 1236117.3103
91 | 2678997.694 | 1236116.3365 | 2678996.3779 | 1236110.0257 | 2678995.3893 | 1236091.6108 | 2678998.7263 | 1236083.683 | 2679017.7445 | 1236058.633
92 | 2679042.6235 | 1236118.113 | 2679022.3242 | 1236117.3103
93 | 2679026.2797 | 1236047.3908 | 2679017.7445 | 1236058.633
94 | 2679042.6235 | 1236118.113 | 2679039.6307 | 1236125.932
95 | 2679042.6235 | 1236118.113 | 2679049.5473 | 1236101.1811
96 | 2679039.6307 | 1236125.932 | 2679032.1267 | 1236145.5367
97 | 2679023.2633 | 1236161.4523 | 2679031.2078 | 1236147.9375 | 2679032.1267 | 1236145.5367
98 | 2679023.2633 | 1236161.4523 | 2679041.8701 | 1236173.0079 | 2679048.487 | 1236175.6533 | 2679056.0815 | 1236175.9212 | 2679059.6151 | 1236174.823
99 | 2679023.2633 | 1236161.4523 | 2679017.2632 | 1236172.736 | 2679009.6259 | 1236182.3026
100 | 2679059.6151 | 1236174.823 | 2679063.4287 | 1236172.9655
101 | 2679059.6151 | 1236174.823 | 2679067.0462 | 1236190.1388
102 | 2679009.6259 | 1236182.3026 | 2679005.9242 | 1236186.9394
103 | 2679089.295 | 1236160.3663 | 2679063.4287 | 1236172.9655
104 | 2679067.7168 | 1236191.5208 | 2679067.0462 | 1236190.1388
105 | 2679005.9242 | 1236186.9394 | 2678993.1467 | 1236202.9448
106 | 2679116.6479 | 1236147.043 | 2679097.1284 | 1236156.5507
107 | 2679123.679 | 1236143.6183 | 2679116.6479 | 1236147.043
108 | 2679089.295 | 1236160.3663 | 2679097.1284 | 1236156.5507
109 | 2679123.679 | 1236143.6183 | 2679137.4068 | 1236136.9316
110 | 2679147.1311 | 1236132.195 | 2679137.4068 | 1236136.9316
111 | 2679157.8474 | 1236126.9752 | 2679147.1311 | 1236132.195
112 | 2679205.1995 | 1236072.4601 | 2679194.2989 | 1236072.1039
113 | 2679208.4641 | 1236072.5668 | 2679205.1995 | 1236072.4601
114 | 2679232.0622 | 1236073.3381 | 2679208.4641 | 1236072.5668
115 | 2679232.0622 | 1236073.3381 | 2679231.7528 | 1236087.4549 | 2679232.8525 | 1236108.8289 | 2679232.8981 | 1236108.9805
116 | 2679232.0622 | 1236073.3381 | 2679246.3041 | 1236071.5614
117 | 2679232.0622 | 1236073.3381 | 2679233.4315 | 1236068.8421 | 2679238.8323 | 1236060.7178
118 | 2679245.9242 | 1236050.0498 | 2679238.8323 | 1236060.7178
119 | 2679245.9242 | 1236050.0498 | 2679249.5513 | 1236044.5936
120 | 2679251.0433 | 1236042.3493 | 2679249.5513 | 1236044.5936
121 | 2679257.9877 | 1236070.1038 | 2679246.3041 | 1236071.5614
122 | 2679270.8397 | 1236090.3894 | 2679257.9877 | 1236070.1038
123 | 2679270.8397 | 1236090.3894 | 2679287.4665 | 1236083.5879
124 | 2679287.4665 | 1236083.5879 | 2679301.6429 | 1236077.7887
125 | 2679301.6429 | 1236077.7887 | 2679409.1956 | 1236156.0937
126 | 2679409.1956 | 1236156.0937 | 2679430.3346 | 1236154.8087 | 2679499.4087 | 1236148.4169 | 2679528.6865 | 1236146.3183 | 2679542.4663 | 1236145.8469 | 2679561.1967 | 1236147.5432 | 2679581.7431 | 1236150.9541 | 2679597.8627 | 1236152.0819 | 2679604.939 | 1236151.4874
127 | 2678494.1521 | 1236212.9973 | 2678510.6528 | 1236213.9159 | 2678487.0337 | 1236268.7781
128 | 2678494.1521 | 1236212.9973 | 2678499.2564 | 1236199.5554 | 2678494.4637 | 1236191.7199 | 2678504.1615 | 1236182.2971 | 2678506.0674 | 1236173.227 | 2678502.1716 | 1236164.514 | 2678492.4905 | 1236155.502
129 | 2678492.4905 | 1236155.502 | 2678480.7537 | 1236166.8882 | 2678479.2418 | 1236170.4178
130 | 2679691.1912 | 1236510.3857 | 2679691.7399 | 1236510.0383
131 | 2679691.1912 | 1236510.3857 | 2679684.1513 | 1236514.8424
132 | 2679691.7399 | 1236510.0383 | 2679699.7408 | 1236504.9732
133 | 2679675.3719 | 1236520.4003 | 2679684.1513 | 1236514.8424
134 | 2679707.7403 | 1236499.909 | 2679699.7408 | 1236504.9732
135 | 2679604.939 | 1236151.4874 | 2679707.7403 | 1236499.909

## bus_geodata
| x | y | coords
0 | 2678452.8284 | 1236598.8828
1 | 2678460.2812 | 1236559.9915
2 | 2678639.461 | 1236580.4012
3 | 2678448.4499 | 1236337.347
4 | 2678743.983 | 1236300.0868
5 | 2678713.4938 | 1236345.1315
6 | 2678755.7988 | 1236282.6302
7 | 2678660.8428 | 1236440.3951
8 | 2678757.1216 | 1236280.4936
9 | 2678769.9871 | 1236334.5977
10 | 2678654.8402 | 1236467.4428
11 | 2678771.6318 | 1236257.0565
12 | 2678648.5132 | 1236500.5848
13 | 2678812.1756 | 1236191.5698
14 | 2678842.9996 | 1236204.6434
15 | 2678832.9415 | 1236123.6839
16 | 2678851.7339 | 1236217.1013
17 | 2678640.8696 | 1236547.8313
18 | 2678828.3851 | 1236420.4916
19 | 2678860.657 | 1236382.4336
20 | 2678816.0475 | 1236438.5034
21 | 2678876.7096 | 1236364.1474
22 | 2678795.3017 | 1236498.073
23 | 2678907.6438 | 1236344.6991
24 | 2678780.6597 | 1236543.764
25 | 2678918.8837 | 1236311.5252
26 | 2678775.6115 | 1236583.1801
27 | 2678922.7987 | 1236303.0376
28 | 2678915.8869 | 1236309.8176
29 | 2678896.376 | 1236317.6474
30 | 2678899.887 | 1236291.0306
31 | 2678876.5967 | 1236260.0995
32 | 2678874.2677 | 1236256.3893
33 | 2678941.8137 | 1236269.2495
34 | 2678850.8656 | 1236219.8028
35 | 2678844.3238 | 1236236.7583
36 | 2678885.2294 | 1236227.3484
37 | 2678828.5244 | 1236263.2144
38 | 2678891.9605 | 1236218.3991
39 | 2678893.4564 | 1236216.4102
40 | 2678918.4247 | 1236077.5339
41 | 2678912.9093 | 1236084.8786
42 | 2678924.6953 | 1236063.3073
43 | 2678912.4516 | 1236085.4882
44 | 2678946.2803 | 1236074.3311
45 | 2678938.5903 | 1236045.4627
46 | 2678897.434 | 1236105.4866
47 | 2678946.3545 | 1236074.3901
48 | 2678946.0161 | 1236035.9262
49 | 2678896.7497 | 1236106.398
50 | 2678948.9251 | 1236076.4321
51 | 2678951.0491 | 1236029.4626
52 | 2678890.54 | 1236114.6672
53 | 2678944.8077 | 1236264.4813
54 | 2678961.9167 | 1236242.5834
55 | 2678965.801 | 1236237.6118
56 | 2678977.0029 | 1236223.2745
57 | 2678982.3505 | 1236216.4682
58 | 2678946.6145 | 1236169.5435
59 | 2678952.717 | 1236161.4617
60 | 2678934.066 | 1236186.1618
61 | 2678964.4447 | 1236145.9303
62 | 2678970.2229 | 1236138.2781
63 | 2678979.3071 | 1236127.0338
64 | 2679092.5502 | 1236009.2302
65 | 2679086.0083 | 1236020.1276
66 | 2679073.8954 | 1236043.7703
67 | 2678984.6509 | 1235985.6634
68 | 2678972.6135 | 1236001.4494
69 | 2678967.8187 | 1236007.7374
70 | 2678959.8378 | 1236018.1605
71 | 2678955.8812 | 1236023.2569
72 | 2679117.86 | 1236069.6057
73 | 2679140.8097 | 1236070.3557
74 | 2679114.833 | 1236069.5067
75 | 2679160.296 | 1236070.9926
76 | 2679090.829 | 1236063.9632
77 | 2679124.1325 | 1236051.0636
78 | 2679180.3471 | 1236071.6479
79 | 2679068.2817 | 1236055.3662
80 | 2679147.7789 | 1236028.995
81 | 2679185.2831 | 1236071.8092
82 | 2679062.5243 | 1236069.4458
83 | 2679059.6581 | 1236076.455
84 | 2679050.268 | 1236099.4184
85 | 2678975.5735 | 1236101.5455
86 | 2678994.7852 | 1236117.1094
87 | 2678997.694 | 1236116.3365
88 | 2679022.3242 | 1236117.3103
89 | 2679017.7445 | 1236058.633
90 | 2679042.6235 | 1236118.113
91 | 2679026.2797 | 1236047.3908
92 | 2679049.5473 | 1236101.1811
93 | 2679039.6307 | 1236125.932
94 | 2679032.1267 | 1236145.5367
95 | 2679023.2633 | 1236161.4523
96 | 2679059.6151 | 1236174.823
97 | 2679009.6259 | 1236182.3026
98 | 2679063.4287 | 1236172.9655
99 | 2679067.0462 | 1236190.1388
100 | 2679005.9242 | 1236186.9394
101 | 2679116.6479 | 1236147.043
102 | 2679097.1284 | 1236156.5507
103 | 2679123.679 | 1236143.6183
104 | 2679089.295 | 1236160.3663
105 | 2679137.4068 | 1236136.9316
106 | 2679147.1311 | 1236132.195
107 | 2679157.8474 | 1236126.9752
108 | 2679067.7168 | 1236191.5208
109 | 2678993.1467 | 1236202.9448
110 | 2679194.2989 | 1236072.1039
111 | 2679205.1995 | 1236072.4601
112 | 2679208.4641 | 1236072.5668
113 | 2679232.0622 | 1236073.3381
114 | 2679245.9242 | 1236050.0498
115 | 2679238.8323 | 1236060.7178
116 | 2679249.5513 | 1236044.5936
117 | 2679251.0433 | 1236042.3493
118 | 2679232.8981 | 1236108.9805
119 | 2679246.3041 | 1236071.5614
120 | 2679257.9877 | 1236070.1038
121 | 2679270.8397 | 1236090.3894
122 | 2679287.4665 | 1236083.5879
123 | 2679301.6429 | 1236077.7887
124 | 2679409.1956 | 1236156.0937
125 | 2678487.0337 | 1236268.7781
126 | 2678494.1521 | 1236212.9973
127 | 2678492.4905 | 1236155.502
128 | 2678399.4939 | 1236317.3869
129 | 2678479.2418 | 1236170.4178
130 | 2679691.1912 | 1236510.3857
131 | 2679691.7399 | 1236510.0383
132 | 2679684.1513 | 1236514.8424
133 | 2679699.7408 | 1236504.9732
134 | 2679675.3719 | 1236520.4003
135 | 2679707.7403 | 1236499.909
136 | 2679604.939 | 1236151.4874
137 | 2678934.066 | 1236186.1618

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97309 | -0.52092 | 0.0025182 | 0.00063111
1 | 0.97318 | -0.51908 | 0.00053583 | 0.00013429
2 | 0.97541 | -0.47519 | 0.00035293 | 8.8454e-05
3 | 0.97106 | -0.561 | 0 | 0
4 | 0.97987 | -0.38796 | 0.0010424 | 0.00026126
5 | 0.979 | -0.40481 | 0.00070124 | 0.00017575
6 | 0.98022 | -0.38103 | 0 | 0
7 | 0.97733 | -0.43747 | 0.0007614 | 0.00019082
8 | 0.98026 | -0.38019 | 0.00025502 | 6.3914e-05
9 | 0.98019 | -0.38157 | 0.00047247 | 0.00011841
10 | 0.97693 | -0.44536 | 0.00017983 | 4.5069e-05
11 | 0.98075 | -0.37078 | 0.0017276 | 0.00043298
12 | 0.97645 | -0.45486 | 0.0014631 | 0.00036669
13 | 0.98222 | -0.34213 | 0 | 0
14 | 0.98297 | -0.32761 | 0.0024782 | 0.00062109
15 | 0.98199 | -0.34658 | 0.0034583 | 0.00086673
16 | 0.98334 | -0.32029 | 0 | 0
17 | 0.97582 | -0.46706 | 0.00032917 | 8.2498e-05
18 | 0.98507 | -0.28686 | 0.00076129 | 0.0001908
19 | 0.98516 | -0.28505 | 0.0011811 | 0.00029602
20 | 0.98504 | -0.28735 | 0.00011825 | 2.9635e-05
21 | 0.98523 | -0.28365 | 0.00085257 | 0.00021367
22 | 0.98498 | -0.28865 | 0.00012909 | 3.2354e-05
23 | 0.98537 | -0.28096 | 0 | 0
24 | 0.98493 | -0.28951 | 0.00088259 | 0.0002212
25 | 0.9855 | -0.27841 | 0 | 0
26 | 0.98493 | -0.2896 | 0.00012146 | 3.0442e-05
27 | 0.9857 | -0.27443 | 0.0023149 | 0.00058016
28 | 0.98543 | -0.27975 | 0 | 0
29 | 0.98539 | -0.28049 | 0.0018402 | 0.00046119
30 | 0.98494 | -0.28935 | 0.0018127 | 0.0004543
31 | 0.98422 | -0.30317 | 0.001192 | 0.00029875
32 | 0.98415 | -0.30469 | 0.0025806 | 0.00064676
33 | 0.9866 | -0.25715 | 0.0012426 | 0.00031142
34 | 0.98342 | -0.31873 | 0 | 0
35 | 0.98334 | -0.32045 | 0.0030048 | 0.00075307
36 | 0.98316 | -0.32393 | 0.0015311 | 0.00038374
37 | 0.98327 | -0.32171 | 0.002248 | 0.0005634
38 | 0.98313 | -0.32446 | 0.0011053 | 0.00027702
39 | 0.98313 | -0.32453 | 0.0015037 | 0.00037686
40 | 0.99263 | -0.14109 | 0.0014608 | 0.0003661
41 | 0.99254 | -0.14283 | 0.0012617 | 0.00031622
42 | 0.99281 | -0.13766 | 0 | 0
43 | 0.99254 | -0.14296 | 0.00127 | 0.0003183
44 | 0.99335 | -0.1272 | 0.0012686 | 0.00031794
45 | 0.99257 | -0.14235 | 0.0016975 | 0.00042543
46 | 0.99235 | -0.14659 | 0.0020381 | 0.00051079
47 | 0.99335 | -0.12715 | 0.0011399 | 0.00028569
48 | 0.99246 | -0.14449 | 0.0011282 | 0.00028276
49 | 0.99234 | -0.14672 | 0.0027407 | 0.00068689
50 | 0.99343 | -0.12563 | 0.0012691 | 0.00031807
51 | 0.99239 | -0.14578 | 0.0011301 | 0.00028323
52 | 0.99231 | -0.14735 | 0.0034341 | 0.00086067
53 | 0.98673 | -0.25458 | 0.0015937 | 0.00039943
54 | 0.9874 | -0.24152 | 0.0015514 | 0.00038881
55 | 0.98756 | -0.23847 | 0.0021186 | 0.00053098
56 | 0.98803 | -0.22933 | 0.0023741 | 0.00059501
57 | 0.98827 | -0.22481 | 0.0012239 | 0.00030673
58 | 0.99994 | -0.0011854 | 0.0027971 | 0.00070103
59 | 1 | 0 | -0.18681 | -0.047174
60 | 0.99986 | -0.0026078 | 0.0039177 | 0.00098186
61 | 0.99842 | -0.029978 | 0.002292 | 0.00057444
62 | 0.99765 | -0.04459 | 0.0028941 | 0.00072534
63 | 0.99652 | -0.066325 | 0.0026861 | 0.00067321
64 | 0.98948 | -0.20157 | 0.001969 | 0.00049348
65 | 0.98951 | -0.20112 | 0.0015177 | 0.00038038
66 | 0.98959 | -0.19947 | 0.0012988 | 0.0003255
67 | 0.99217 | -0.14997 | 0.0023054 | 0.00057778
68 | 0.99221 | -0.14916 | 0.0011441 | 0.00028674
69 | 0.99224 | -0.14868 | 0.0011269 | 0.00028243
70 | 0.99229 | -0.14762 | 0.0020484 | 0.00051339
71 | 0.99233 | -0.14686 | 0.0011354 | 0.00028457
72 | 0.9882 | -0.22642 | 0.0015074 | 0.00037779
73 | 0.98767 | -0.23671 | 0.00075657 | 0.00018961
74 | 0.98828 | -0.22498 | 0 | 0
75 | 0.98724 | -0.24519 | 0.00099621 | 0.00024967
76 | 0.98895 | -0.21196 | 0.0020108 | 0.00050395
77 | 0.98822 | -0.22609 | 0.0016823 | 0.00042162
78 | 0.9868 | -0.25357 | 0.0021193 | 0.00053113
79 | 0.98965 | -0.19837 | 0 | 0
80 | 0.98818 | -0.22686 | 0.0013142 | 0.00032938
81 | 0.98671 | -0.25544 | 0.0011844 | 0.00029685
82 | 0.99016 | -0.18852 | 0.0020115 | 0.00050414
83 | 0.99042 | -0.18335 | 0.0015134 | 0.00037929
84 | 0.99133 | -0.16577 | 0.0019847 | 0.00049742
85 | 0.99438 | -0.10723 | 0.0025242 | 0.00063262
86 | 0.99506 | -0.094102 | 0 | 0
87 | 0.99487 | -0.097761 | 0 | 0
88 | 0.99337 | -0.12659 | 0.001147 | 0.00028746
89 | 0.99453 | -0.10443 | 0.0019079 | 0.00047816
90 | 0.99214 | -0.15021 | 0 | 0
91 | 0.99448 | -0.10541 | 0.0039213 | 0.00098277
92 | 0.99141 | -0.16435 | 0.0017264 | 0.00043269
93 | 0.9918 | -0.15672 | 0.0020397 | 0.0005112
94 | 0.99097 | -0.17269 | 0.0025326 | 0.00063474
95 | 0.99027 | -0.18619 | 0 | 0
96 | 0.98966 | -0.19801 | 0 | 0
97 | 0.9895 | -0.20104 | 0.0035778 | 0.00089667
98 | 0.98961 | -0.19905 | 0.0013971 | 0.00035015
99 | 0.98962 | -0.19884 | 0.0013954 | 0.00034971
100 | 0.98933 | -0.20438 | 0.0017853 | 0.00044745
101 | 0.98901 | -0.21069 | 0.0013449 | 0.00033706
102 | 0.98919 | -0.20706 | 0.0013542 | 0.0003394
103 | 0.98895 | -0.21181 | 0.001873 | 0.00046942
104 | 0.98928 | -0.20539 | 0.0016458 | 0.00041247
105 | 0.98886 | -0.21349 | 0.0013787 | 0.00034553
106 | 0.98882 | -0.21441 | 0.0016451 | 0.00041231
107 | 0.98878 | -0.21508 | 0.0031393 | 0.00078678
108 | 0.98962 | -0.19888 | 0.0013435 | 0.00033672
109 | 0.98875 | -0.21558 | 0.0015667 | 0.00039266
110 | 0.98654 | -0.25868 | 0.00044724 | 0.00011209
111 | 0.98635 | -0.26251 | 0.001231 | 0.00030852
112 | 0.98629 | -0.26358 | 0.0015861 | 0.00039751
113 | 0.98593 | -0.27068 | 0 | 0
114 | 0.98582 | -0.27267 | 0.001173 | 0.00029398
115 | 0.98587 | -0.27185 | 0.00093009 | 0.0002331
116 | 0.98581 | -0.27295 | 0.0013962 | 0.00034993
117 | 0.98581 | -0.273 | 0.0010082 | 0.00025267
118 | 0.98588 | -0.27149 | 0.0012735 | 0.00031918
119 | 0.98578 | -0.27351 | 0.00084726 | 0.00021234
120 | 0.98567 | -0.27565 | 0 | 0
121 | 0.98545 | -0.28001 | 0 | 0
122 | 0.98528 | -0.28328 | 0.0019391 | 0.00048599
123 | 0.98516 | -0.28554 | 0.0019295 | 0.00048359
124 | 0.9844 | -0.30052 | 0.00045041 | 0.00011288
125 | 0.97041 | -0.57395 | 0.006987 | 0.0017511
126 | 0.97031 | -0.57583 | 0 | 0
127 | 0.97023 | -0.57754 | 0 | 0
128 | 0.97097 | -0.56281 | 0.0018596 | 0.00046607
129 | 0.9702 | -0.57804 | 0.0013331 | 0.0003341
130 | 0.98131 | -0.36096 | 0.00059835 | 0.00014996
131 | 0.98131 | -0.36091 | 0.00038558 | 9.6634e-05
132 | 0.98128 | -0.36154 | 0.0029672 | 0.00074366
133 | 0.98135 | -0.36008 | 0.00097882 | 0.00024531
134 | 0.98127 | -0.3617 | 0.00086421 | 0.00021659
135 | 0.9814 | -0.35909 | 0 | 0
136 | 0.98335 | -0.32103 | 0 | 0
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0025182 | -0.00063111 | 0.0025184 | 0.00063076 | 2.2018e-07 | -3.5106e-07 | 0.0038507 | 0.0038505 | 0.0038507 | 0.97309 | -0.52092 | 0.97318 | -0.51908 | 1.0579
1 | -0.01326 | -0.0033264 | 0.013288 | 0.003342 | 2.7801e-05 | 1.5547e-05 | 0.020276 | 0.020275 | 0.020276 | 0.97318 | -0.51908 | 0.97541 | -0.47519 | 5.5703
2 | 0.010206 | 0.0025614 | -0.010185 | -0.0025511 | 2.0364e-05 | 1.0269e-05 | 0.015606 | 0.015607 | 0.015607 | 0.97318 | -0.51908 | 0.97106 | -0.561 | 4.2876
3 | -0.013641 | -0.0034304 | 0.013646 | 0.0034334 | 5.3002e-06 | 2.9847e-06 | 0.020813 | 0.020813 | 0.020813 | 0.97541 | -0.47519 | 0.97582 | -0.46706 | 5.718
4 | 0.0018598 | 0.00046552 | -0.0018596 | -0.00046607 | 1.6101e-07 | -5.5093e-07 | 0.0028497 | 0.0028499 | 0.0028499 | 0.97106 | -0.561 | 0.97097 | -0.56281 | 0.78294
5 | 0.0083255 | 0.0020856 | -0.0083204 | -0.0020833 | 5.132e-06 | 2.2449e-06 | 0.012757 | 0.012758 | 0.012758 | 0.97106 | -0.561 | 0.97041 | -0.57395 | 3.5049
6 | 0.017141 | 0.0043295 | -0.017127 | -0.0043214 | 1.3834e-05 | 8.1692e-06 | 0.026043 | 0.026043 | 0.026043 | 0.97987 | -0.38796 | 0.979 | -0.40481 | 7.1546
7 | -0.018184 | -0.0045908 | 0.01819 | 0.0045944 | 6.0327e-06 | 3.5953e-06 | 0.027626 | 0.027625 | 0.027626 | 0.97987 | -0.38796 | 0.98022 | -0.38103 | 7.5894
8 | 0.016426 | 0.0041456 | -0.0164 | -0.0041306 | 2.5652e-05 | 1.5041e-05 | 0.024977 | 0.024977 | 0.024977 | 0.979 | -0.40481 | 0.97733 | -0.43747 | 6.8619
9 | -0.018662 | -0.004712 | 0.018663 | 0.0047125 | 7.5698e-07 | 4.5279e-07 | 0.028342 | 0.028342 | 0.028342 | 0.98022 | -0.38103 | 0.98026 | -0.38019 | 7.7864
10 | 0.00047249 | 0.00011764 | -0.00047247 | -0.00011841 | 1.1955e-08 | -7.7379e-07 | 0.00071698 | 0.00071725 | 0.00071725 | 0.98022 | -0.38103 | 0.98019 | -0.38157 | 0.19705
11 | 0.015639 | 0.0039398 | -0.015633 | -0.0039363 | 5.8967e-06 | 3.4267e-06 | 0.023818 | 0.023818 | 0.023818 | 0.97733 | -0.43747 | 0.97693 | -0.44536 | 6.5435
12 | -0.018918 | -0.0047764 | 0.018926 | 0.0047815 | 8.5319e-06 | 5.1128e-06 | 0.02873 | 0.028729 | 0.02873 | 0.98026 | -0.38019 | 0.98075 | -0.37078 | 7.8927
13 | 0.015453 | 0.0038913 | -0.015446 | -0.0038872 | 7.0158e-06 | 4.0678e-06 | 0.023544 | 0.023545 | 0.023545 | 0.97693 | -0.44536 | 0.97645 | -0.45486 | 6.4683
14 | -0.020654 | -0.0052145 | 0.020682 | 0.0052317 | 2.8388e-05 | 1.7195e-05 | 0.031351 | 0.03135 | 0.031351 | 0.98075 | -0.37078 | 0.98222 | -0.34213 | 8.6128
15 | 0.013983 | 0.0035205 | -0.013975 | -0.0035159 | 8.1548e-06 | 4.6207e-06 | 0.021315 | 0.021315 | 0.021315 | 0.97645 | -0.45486 | 0.97582 | -0.46706 | 5.8558
16 | -0.024141 | -0.006098 | 0.024158 | 0.0061083 | 1.6812e-05 | 1.0335e-05 | 0.03659 | 0.03659 | 0.03659 | 0.98222 | -0.34213 | 0.98297 | -0.32761 | 10.0523
17 | 0.003459 | 0.0008663 | -0.0034583 | -0.00086673 | 7.3354e-07 | -4.3195e-07 | 0.00524 | 0.0052404 | 0.0052404 | 0.98222 | -0.34213 | 0.98199 | -0.34658 | 1.4397
18 | -0.026636 | -0.0067294 | 0.026646 | 0.0067352 | 9.346e-06 | 5.7873e-06 | 0.040342 | 0.040342 | 0.040342 | 0.98297 | -0.32761 | 0.98334 | -0.32029 | 11.0828
19 | 0.0041409 | 0.0010373 | -0.0041402 | -0.0010375 | 7.1757e-07 | -1.5889e-07 | 0.0062659 | 0.0062662 | 0.0062662 | 0.98334 | -0.32029 | 0.98316 | -0.32393 | 1.7215
20 | -0.030787 | -0.0077725 | 0.030789 | 0.007774 | 2.311e-06 | 1.4431e-06 | 0.046607 | 0.046607 | 0.046607 | 0.98334 | -0.32029 | 0.98342 | -0.31873 | 12.8042
21 | -0.0020128 | -0.00050232 | 0.002013 | 0.00050179 | 1.7304e-07 | -5.251e-07 | 0.0030398 | 0.0030395 | 0.0030398 | 0.98507 | -0.28686 | 0.98516 | -0.28505 | 0.8351
22 | 0.0012515 | 0.00031152 | -0.0012515 | -0.00031178 | 2.924e-08 | -2.5921e-07 | 0.0018898 | 0.0018899 | 0.0018899 | 0.98507 | -0.28686 | 0.98504 | -0.28735 | 0.5192
23 | -0.0031941 | -0.00079781 | 0.0031944 | 0.00079764 | 2.123e-07 | -1.7397e-07 | 0.0048236 | 0.0048235 | 0.0048236 | 0.98516 | -0.28505 | 0.98523 | -0.28365 | 1.3252
24 | 0.0011333 | 0.00028214 | -0.0011332 | -0.00028291 | 6.9466e-08 | -7.606e-07 | 0.0017113 | 0.0017115 | 0.0017115 | 0.98504 | -0.28735 | 0.98498 | -0.28865 | 0.4702
25 | -0.0040469 | -0.0010113 | 0.0040474 | 0.0010112 | 5.1824e-07 | -1.3965e-07 | 0.0061111 | 0.0061109 | 0.0061111 | 0.98523 | -0.28365 | 0.98537 | -0.28096 | 1.6789
26 | 0.0010041 | 0.00025055 | -0.0010041 | -0.00025114 | 4.1385e-08 | -5.8417e-07 | 0.0015165 | 0.0015167 | 0.0015167 | 0.98498 | -0.28865 | 0.98493 | -0.28951 | 0.41668
27 | -0.0040474 | -0.0010112 | 0.0040479 | 0.001011 | 4.9044e-07 | -1.3231e-07 | 0.0061109 | 0.0061108 | 0.0061109 | 0.98537 | -0.28096 | 0.9855 | -0.27841 | 1.6788
28 | 0.00012147 | 2.9936e-05 | -0.00012146 | -3.0442e-05 | 5.0133e-10 | -5.0542e-07 | 0.00018333 | 0.00018351 | 0.00018351 | 0.98493 | -0.28951 | 0.98493 | -0.2896 | 0.050414
29 | -0.047591 | -0.012007 | 0.0476 | 0.012013 | 9.0653e-06 | 5.5633e-06 | 0.071887 | 0.071887 | 0.071887 | 0.9855 | -0.27841 | 0.9857 | -0.27443 | 9.8746
30 | 0.043543 | 0.010996 | -0.04354 | -0.010995 | 2.7922e-06 | 1.6993e-06 | 0.065776 | 0.065776 | 0.065776 | 0.9855 | -0.27841 | 0.98543 | -0.27975 | 9.0352
31 | -0.049915 | -0.012593 | 0.049957 | 0.012618 | 4.1345e-05 | 2.5471e-05 | 0.075381 | 0.075381 | 0.075381 | 0.9857 | -0.27443 | 0.9866 | -0.25715 | 10.3546
32 | 0.0417 | 0.010534 | -0.041681 | -0.010522 | 1.9188e-05 | 1.1624e-05 | 0.062998 | 0.062998 | 0.062998 | 0.98543 | -0.27975 | 0.98494 | -0.28935 | 8.6535
33 | 0.0018402 | 0.00046095 | -0.0018402 | -0.00046119 | 6.5581e-08 | -2.4656e-07 | 0.0027787 | 0.0027788 | 0.0027788 | 0.98543 | -0.27975 | 0.98539 | -0.28049 | 0.76341
34 | 0.039868 | 0.010068 | -0.039842 | -0.010052 | 2.6382e-05 | 1.5899e-05 | 0.060259 | 0.06026 | 0.06026 | 0.98494 | -0.28935 | 0.98422 | -0.30317 | 8.2774
35 | 0.03865 | 0.009753 | -0.038647 | -0.0097513 | 2.8068e-06 | 1.685e-06 | 0.058457 | 0.058457 | 0.058457 | 0.98422 | -0.30317 | 0.98415 | -0.30469 | 8.0299
36 | 0.036067 | 0.0091046 | -0.036042 | -0.0090902 | 2.4238e-05 | 1.4409e-05 | 0.054556 | 0.054556 | 0.054556 | 0.98415 | -0.30469 | 0.98342 | -0.31873 | 7.494
37 | -0.051199 | -0.01293 | 0.051205 | 0.012934 | 6.3007e-06 | 3.8886e-06 | 0.077255 | 0.077255 | 0.077255 | 0.9866 | -0.25715 | 0.98673 | -0.25458 | 10.612
38 | 0.0052533 | 0.0013162 | -0.0052529 | -0.0013162 | 4.3061e-07 | 4.5013e-08 | 0.0079486 | 0.0079487 | 0.0079487 | 0.98342 | -0.31873 | 0.98334 | -0.32045 | 2.1837
39 | 0.0022481 | 0.00056309 | -0.002248 | -0.0005634 | 1.3539e-07 | -3.0909e-07 | 0.0034018 | 0.0034019 | 0.0034019 | 0.98334 | -0.32045 | 0.98327 | -0.32171 | 0.9346
40 | 0.0026091 | 0.00065375 | -0.002609 | -0.00065385 | 6.5481e-08 | -1.0009e-07 | 0.0039488 | 0.0039488 | 0.0039488 | 0.98316 | -0.32393 | 0.98313 | -0.32446 | 1.0848
41 | 0.0015037 | 0.00037683 | -0.0015037 | -0.00037686 | 4.834e-09 | -2.8463e-08 | 0.0022759 | 0.0022759 | 0.0022759 | 0.98313 | -0.32446 | 0.98313 | -0.32453 | 0.62525
42 | 0.010747 | 0.0026939 | -0.010746 | -0.0026934 | 8.9403e-07 | 4.5346e-07 | 0.016111 | 0.016111 | 0.016111 | 0.99263 | -0.14109 | 0.99254 | -0.14283 | 4.4261
43 | -0.012208 | -0.00306 | 0.01221 | 0.0030611 | 1.9925e-06 | 1.0701e-06 | 0.018301 | 0.018301 | 0.018301 | 0.99263 | -0.14109 | 0.99281 | -0.13766 | 5.0277
44 | 0.0094846 | 0.0023772 | -0.0094845 | -0.0023772 | 5.7802e-08 | 2.7141e-08 | 0.014219 | 0.014219 | 0.014219 | 0.99254 | -0.14283 | 0.99254 | -0.14296 | 3.9064
45 | -0.023931 | -0.0059995 | 0.023943 | 0.0060068 | 1.1939e-05 | 7.3206e-06 | 0.035869 | 0.035869 | 0.035869 | 0.99281 | -0.13766 | 0.99335 | -0.1272 | 9.854
46 | 0.011721 | 0.0029384 | -0.011719 | -0.002937 | 2.6176e-06 | 1.3829e-06 | 0.017568 | 0.017568 | 0.017568 | 0.99281 | -0.13766 | 0.99257 | -0.14235 | 4.8264
47 | 0.0082145 | 0.0020589 | -0.0082131 | -0.0020583 | 1.4224e-06 | 5.8718e-07 | 0.012315 | 0.012315 | 0.012315 | 0.99254 | -0.14296 | 0.99235 | -0.14659 | 3.3834
48 | -0.025212 | -0.0063247 | 0.025212 | 0.0063248 | 5.0709e-08 | 3.1227e-08 | 0.037769 | 0.037769 | 0.037769 | 0.99335 | -0.1272 | 0.99335 | -0.12715 | 10.3761
49 | 0.010021 | 0.0025116 | -0.01002 | -0.0025111 | 1.023e-06 | 4.9851e-07 | 0.015023 | 0.015023 | 0.015023 | 0.99257 | -0.14235 | 0.99246 | -0.14449 | 4.1273
50 | 0.006175 | 0.0015475 | -0.006175 | -0.0015475 | 3.6642e-08 | 8.7268e-09 | 0.0092593 | 0.0092593 | 0.0092593 | 0.99235 | -0.14659 | 0.99234 | -0.14672 | 2.5438
51 | -0.026352 | -0.0066104 | 0.026354 | 0.0066116 | 1.9185e-06 | 1.1853e-06 | 0.039476 | 0.039476 | 0.039476 | 0.99335 | -0.12715 | 0.99343 | -0.12563 | 10.8452
52 | 0.0088919 | 0.0022283 | -0.0088914 | -0.0022281 | 5.4602e-07 | 2.436e-07 | 0.013332 | 0.013332 | 0.013332 | 0.99246 | -0.14449 | 0.99239 | -0.14578 | 3.6626
53 | 0.0034342 | 0.0008606 | -0.0034341 | -0.00086067 | 1.0284e-07 | -6.7779e-08 | 0.0051496 | 0.0051496 | 0.0051496 | 0.99234 | -0.14672 | 0.99231 | -0.14735 | 1.4147
54 | -0.027623 | -0.0069297 | 0.027647 | 0.0069447 | 2.4255e-05 | 1.5033e-05 | 0.041377 | 0.041377 | 0.041377 | 0.99343 | -0.12563 | 0.99438 | -0.10723 | 11.3674
55 | 0.0077613 | 0.0019449 | -0.0077609 | -0.0019447 | 3.9943e-07 | 1.5402e-07 | 0.011637 | 0.011637 | 0.011637 | 0.99239 | -0.14578 | 0.99233 | -0.14686 | 3.1971
56 | -0.052799 | -0.013333 | 0.052832 | 0.013354 | 3.3063e-05 | 2.045e-05 | 0.079659 | 0.079658 | 0.079659 | 0.98673 | -0.25458 | 0.9874 | -0.24152 | 10.9421
57 | -0.054384 | -0.013742 | 0.054392 | 0.013747 | 7.9535e-06 | 4.9288e-06 | 0.081996 | 0.081996 | 0.081996 | 0.9874 | -0.24152 | 0.98756 | -0.23847 | 11.2632
58 | -0.05651 | -0.014278 | 0.056535 | 0.014294 | 2.4757e-05 | 1.5379e-05 | 0.085188 | 0.085188 | 0.085188 | 0.98756 | -0.23847 | 0.98803 | -0.22933 | 11.7017
59 | -0.058909 | -0.014889 | 0.058922 | 0.014897 | 1.2788e-05 | 7.9622e-06 | 0.088764 | 0.088764 | 0.088764 | 0.98803 | -0.22933 | 0.98827 | -0.22481 | 12.1928
60 | -0.060146 | -0.015203 | 0.060172 | 0.01522 | 2.6636e-05 | 1.6604e-05 | 0.090606 | 0.090606 | 0.090606 | 0.98827 | -0.22481 | 0.98875 | -0.21558 | 12.4459
61 | -0.0067151 | -0.0016828 | 0.0067155 | 0.0016829 | 3.7921e-07 | 1.0984e-07 | 0.0099927 | 0.0099927 | 0.0099927 | 0.99994 | -0.0011854 | 1 | 0 | 2.7453
62 | 0.003918 | 0.00098176 | -0.0039177 | -0.00098186 | 2.6545e-07 | -1.0325e-07 | 0.0058303 | 0.0058304 | 0.0058304 | 0.99994 | -0.0011854 | 0.99986 | -0.0026078 | 1.6017
63 | 0.17845 | 0.045491 | -0.17819 | -0.045326 | 0.00025781 | 0.00016449 | 0.2658 | 0.2658 | 0.2658 | 1 | 0 | 0.99842 | -0.029978 | 36.5115
64 | 0.1759 | 0.044752 | -0.17577 | -0.044673 | 0.00012378 | 7.8969e-05 | 0.26239 | 0.26239 | 0.26239 | 0.99842 | -0.029978 | 0.99765 | -0.04459 | 36.0422
65 | 0.17288 | 0.043948 | -0.1727 | -0.043832 | 0.00018077 | 0.00011531 | 0.25807 | 0.25807 | 0.25807 | 0.99765 | -0.04459 | 0.99652 | -0.066325 | 35.4493
66 | 0.17001 | 0.043159 | -0.16979 | -0.043014 | 0.00022687 | 0.00014471 | 0.25406 | 0.25406 | 0.25406 | 0.99652 | -0.066325 | 0.99506 | -0.094102 | 34.8984
67 | -0.001969 | -0.00049348 | 0.001969 | 0.00049334 | 4.1789e-08 | -1.3652e-07 | 0.002961 | 0.002961 | 0.002961 | 0.98948 | -0.20157 | 0.98951 | -0.20112 | 0.81347
68 | -0.0034868 | -0.00087372 | 0.003487 | 0.00087356 | 2.7408e-07 | -1.6611e-07 | 0.0052434 | 0.0052432 | 0.0052434 | 0.98951 | -0.20112 | 0.98959 | -0.19947 | 1.4405
69 | -0.0047858 | -0.0011991 | 0.0047861 | 0.0011991 | 2.5018e-07 | -5.4127e-09 | 0.0071961 | 0.0071961 | 0.0071961 | 0.98959 | -0.19947 | 0.98965 | -0.19837 | 1.977
70 | -0.0023054 | -0.00057778 | 0.0023055 | 0.00057758 | 8.8991e-08 | -1.9944e-07 | 0.0034575 | 0.0034574 | 0.0034575 | 0.99217 | -0.14997 | 0.99221 | -0.14916 | 0.94986
71 | -0.0034496 | -0.00086432 | 0.0034496 | 0.00086427 | 7.9357e-08 | -5.1346e-08 | 0.0051732 | 0.0051732 | 0.0051732 | 0.99221 | -0.14916 | 0.99224 | -0.14868 | 1.4212
72 | -0.0045766 | -0.0011467 | 0.0045768 | 0.0011467 | 2.3188e-07 | -2.117e-08 | 0.0068631 | 0.0068631 | 0.0068631 | 0.99224 | -0.14868 | 0.99229 | -0.14762 | 1.8855
73 | -0.0066252 | -0.0016601 | 0.0066255 | 0.0016601 | 2.3881e-07 | 6.9487e-08 | 0.0099349 | 0.0099348 | 0.0099349 | 0.99229 | -0.14762 | 0.99233 | -0.14686 | 2.7294
74 | 0.025138 | 0.0063168 | -0.025126 | -0.0063092 | 1.2341e-05 | 7.6044e-06 | 0.037858 | 0.037858 | 0.037858 | 0.9882 | -0.22642 | 0.98767 | -0.23671 | 10.4006
75 | -0.026645 | -0.0066946 | 0.026647 | 0.0066958 | 1.8288e-06 | 1.1317e-06 | 0.040128 | 0.040128 | 0.040128 | 0.9882 | -0.22642 | 0.98828 | -0.22498 | 11.0242
76 | 0.024369 | 0.0061196 | -0.024359 | -0.0061136 | 9.8573e-06 | 6.0593e-06 | 0.036718 | 0.036718 | 0.036718 | 0.98767 | -0.23671 | 0.98724 | -0.24519 | 10.0875
77 | -0.029644 | -0.0074462 | 0.029662 | 0.0074577 | 1.8436e-05 | 1.1483e-05 | 0.04464 | 0.04464 | 0.04464 | 0.98828 | -0.22498 | 0.98895 | -0.21196 | 12.2637
78 | 0.0029967 | 0.00075044 | -0.0029966 | -0.00075061 | 1.5768e-07 | -1.6373e-07 | 0.0045119 | 0.004512 | 0.004512 | 0.98828 | -0.22498 | 0.98822 | -0.22609 | 1.2395
79 | 0.023363 | 0.0058639 | -0.023354 | -0.0058582 | 9.3305e-06 | 5.7151e-06 | 0.035217 | 0.035217 | 0.035217 | 0.98724 | -0.24519 | 0.9868 | -0.25357 | 9.675
80 | -0.031673 | -0.0079616 | 0.031694 | 0.0079745 | 2.0559e-05 | 1.2848e-05 | 0.047665 | 0.047665 | 0.047665 | 0.98895 | -0.21196 | 0.98965 | -0.19837 | 13.0948
81 | 0.0013143 | 0.00032899 | -0.0013142 | -0.00032938 | 4.864e-08 | -3.932e-07 | 0.0019788 | 0.001979 | 0.001979 | 0.98822 | -0.22609 | 0.98818 | -0.22686 | 0.54368
82 | 0.021234 | 0.005327 | -0.021232 | -0.0053259 | 1.899e-06 | 1.1523e-06 | 0.032021 | 0.032021 | 0.032021 | 0.9868 | -0.25357 | 0.98671 | -0.25544 | 8.7971
83 | -0.03648 | -0.0091735 | 0.036497 | 0.0091843 | 1.7168e-05 | 1.0792e-05 | 0.054861 | 0.054861 | 0.054861 | 0.98965 | -0.19837 | 0.99016 | -0.18852 | 15.0717
84 | 0.020048 | 0.005029 | -0.020045 | -0.0050272 | 3.0924e-06 | 1.8639e-06 | 0.030235 | 0.030235 | 0.030235 | 0.98671 | -0.25544 | 0.98654 | -0.25868 | 8.3064
85 | -0.038508 | -0.0096885 | 0.038518 | 0.0096945 | 9.5146e-06 | 5.9919e-06 | 0.057884 | 0.057884 | 0.057884 | 0.99016 | -0.18852 | 0.99042 | -0.18335 | 15.9022
86 | -0.040031 | -0.010074 | 0.040065 | 0.010095 | 3.3669e-05 | 2.1228e-05 | 0.060158 | 0.060158 | 0.060158 | 0.99042 | -0.18335 | 0.99133 | -0.16577 | 16.5268
87 | -0.04205 | -0.010592 | 0.042053 | 0.010594 | 2.8467e-06 | 1.7973e-06 | 0.063137 | 0.063137 | 0.063137 | 0.99133 | -0.16577 | 0.99141 | -0.16435 | 17.3453
88 | -0.030171 | -0.0075773 | 0.03019 | 0.0075891 | 1.8907e-05 | 1.178e-05 | 0.045154 | 0.045154 | 0.045154 | 0.99438 | -0.10723 | 0.99506 | -0.094102 | 12.4051
89 | 0.13959 | 0.035425 | -0.13957 | -0.03541 | 2.4565e-05 | 1.5644e-05 | 0.20891 | 0.20891 | 0.20891 | 0.99506 | -0.094102 | 0.99487 | -0.097761 | 28.6959
90 | 0.13374 | 0.033948 | -0.13355 | -0.033831 | 0.00018521 | 0.0001179 | 0.20018 | 0.20018 | 0.20018 | 0.99487 | -0.097761 | 0.99337 | -0.12659 | 27.4979
91 | 0.0058312 | 0.0014612 | -0.0058294 | -0.0014609 | 1.8525e-06 | 3.4263e-07 | 0.0087216 | 0.0087219 | 0.0087219 | 0.99487 | -0.097761 | 0.99453 | -0.10443 | 2.3961
92 | 0.13241 | 0.033543 | -0.13226 | -0.033448 | 0.00015004 | 9.5498e-05 | 0.19847 | 0.19847 | 0.19847 | 0.99337 | -0.12659 | 0.99214 | -0.15021 | 27.2619
93 | 0.0039215 | 0.0009827 | -0.0039213 | -0.00098277 | 1.8222e-07 | -6.6529e-08 | 0.0058673 | 0.0058674 | 0.0058674 | 0.99453 | -0.10443 | 0.99448 | -0.10541 | 1.6119
94 | 0.088448 | 0.022402 | -0.088421 | -0.022385 | 2.7659e-05 | 1.7486e-05 | 0.13274 | 0.13274 | 0.13274 | 0.99214 | -0.15021 | 0.9918 | -0.15672 | 18.2334
95 | 0.043809 | 0.011046 | -0.043779 | -0.011027 | 2.9635e-05 | 1.8731e-05 | 0.065728 | 0.065728 | 0.065728 | 0.99214 | -0.15021 | 0.99141 | -0.16435 | 18.0571
96 | 0.086381 | 0.021873 | -0.086315 | -0.021832 | 6.6189e-05 | 4.182e-05 | 0.12968 | 0.12968 | 0.12968 | 0.9918 | -0.15672 | 0.99097 | -0.17269 | 17.8131
97 | 0.083782 | 0.021197 | -0.083728 | -0.021163 | 5.4212e-05 | 3.4226e-05 | 0.12588 | 0.12588 | 0.12588 | 0.99097 | -0.17269 | 0.99027 | -0.18619 | 17.2907
98 | 0.016535 | 0.0041486 | -0.016525 | -0.0041432 | 9.3147e-06 | 5.4441e-06 | 0.024847 | 0.024847 | 0.024847 | 0.99027 | -0.18619 | 0.98966 | -0.19801 | 6.8262
99 | 0.067193 | 0.017014 | -0.067146 | -0.016984 | 4.7885e-05 | 3.0003e-05 | 0.10103 | 0.10103 | 0.10103 | 0.99027 | -0.18619 | 0.9895 | -0.20104 | 13.8777
100 | 0.013786 | 0.0034569 | -0.013786 | -0.0034565 | 6.8352e-07 | 3.8295e-07 | 0.020729 | 0.020729 | 0.020729 | 0.98966 | -0.19801 | 0.98961 | -0.19905 | 5.6948
101 | 0.002739 | 0.00068627 | -0.0027389 | -0.00068642 | 1.0827e-07 | -1.4944e-07 | 0.0041182 | 0.0041183 | 0.0041183 | 0.98966 | -0.19801 | 0.98962 | -0.19884 | 1.1314
102 | 0.063568 | 0.016087 | -0.063558 | -0.016081 | 1.0178e-05 | 6.3613e-06 | 0.095649 | 0.095649 | 0.095649 | 0.9895 | -0.20104 | 0.98933 | -0.20438 | 13.1386
103 | 0.012388 | 0.0031064 | -0.012385 | -0.0031044 | 3.7441e-06 | 2.0267e-06 | 0.018628 | 0.018628 | 0.018628 | 0.98961 | -0.19905 | 0.98928 | -0.20539 | 5.1177
104 | 0.0013435 | 0.00033671 | -0.0013435 | -0.00033672 | 2.351e-09 | -1.8232e-08 | 0.0020202 | 0.0020202 | 0.0020202 | 0.98962 | -0.19884 | 0.98962 | -0.19888 | 0.555
105 | 0.061772 | 0.015633 | -0.061739 | -0.015613 | 3.3187e-05 | 2.0714e-05 | 0.092964 | 0.092964 | 0.092964 | 0.98933 | -0.20438 | 0.98875 | -0.21558 | 12.7698
106 | -0.0093822 | -0.0023513 | 0.0093838 | 0.0023521 | 1.6224e-06 | 7.5965e-07 | 0.014116 | 0.014116 | 0.014116 | 0.98901 | -0.21069 | 0.98919 | -0.20706 | 3.878
107 | 0.0080373 | 0.0020142 | -0.0080369 | -0.0020141 | 4.2886e-07 | 1.7412e-07 | 0.012093 | 0.012093 | 0.012093 | 0.98901 | -0.21069 | 0.98895 | -0.21181 | 3.3221
108 | -0.010738 | -0.0026915 | 0.010739 | 0.0026919 | 8.5255e-07 | 4.3377e-07 | 0.016153 | 0.016153 | 0.016153 | 0.98919 | -0.20706 | 0.98928 | -0.20539 | 4.4376
109 | 0.0061639 | 0.0015446 | -0.0061634 | -0.0015445 | 4.9254e-07 | 1.1931e-07 | 0.0092744 | 0.0092745 | 0.0092745 | 0.98895 | -0.21181 | 0.98886 | -0.21349 | 2.5479
110 | 0.0047847 | 0.001199 | -0.0047845 | -0.001199 | 2.1027e-07 | -4.1853e-09 | 0.0071999 | 0.0071999 | 0.0071999 | 0.98886 | -0.21349 | 0.98882 | -0.21441 | 1.978
111 | 0.0031394 | 0.00078669 | -0.0031393 | -0.00078678 | 9.9764e-08 | -8.9048e-08 | 0.0047243 | 0.0047243 | 0.0047243 | 0.98882 | -0.21441 | 0.98878 | -0.21508 | 1.2979
112 | 0.019598 | 0.0049151 | -0.019594 | -0.0049129 | 3.5739e-06 | 2.148e-06 | 0.029561 | 0.029561 | 0.029561 | 0.98654 | -0.25868 | 0.98635 | -0.26251 | 8.1211
113 | 0.018363 | 0.0046044 | -0.018362 | -0.0046039 | 9.4009e-07 | 5.5997e-07 | 0.027704 | 0.027704 | 0.027704 | 0.98635 | -0.26251 | 0.98629 | -0.26358 | 7.6109
114 | 0.016776 | 0.0042063 | -0.01677 | -0.004203 | 5.6722e-06 | 3.329e-06 | 0.025311 | 0.025311 | 0.025311 | 0.98629 | -0.26358 | 0.98593 | -0.27068 | 6.9535
115 | 0.0012736 | 0.00031875 | -0.0012735 | -0.00031918 | 4.9433e-08 | -4.2337e-07 | 0.001922 | 0.0019222 | 0.0019222 | 0.98593 | -0.27068 | 0.98588 | -0.27149 | 0.52807
116 | 0.010989 | 0.0027548 | -0.010987 | -0.002754 | 1.4805e-06 | 7.645e-07 | 0.016585 | 0.016585 | 0.016585 | 0.98593 | -0.27068 | 0.98578 | -0.27351 | 4.5564
117 | 0.0045079 | 0.0011295 | -0.0045077 | -0.0011295 | 2.5092e-07 | -2.3746e-08 | 0.0068035 | 0.0068036 | 0.0068036 | 0.98593 | -0.27068 | 0.98587 | -0.27185 | 1.8691
118 | -0.0035774 | -0.00089649 | 0.0035776 | 0.00089641 | 1.4007e-07 | -7.3694e-08 | 0.0053998 | 0.0053997 | 0.0053998 | 0.98582 | -0.27267 | 0.98587 | -0.27185 | 1.4835
119 | 0.0024044 | 0.0006025 | -0.0024044 | -0.00060257 | 3.2361e-08 | -6.2823e-08 | 0.0036292 | 0.0036293 | 0.0036293 | 0.98582 | -0.27267 | 0.98581 | -0.27295 | 0.99705
120 | 0.0010082 | 0.00025264 | -0.0010082 | -0.00025267 | 2.3403e-09 | -3.2862e-08 | 0.0015217 | 0.0015218 | 0.0015218 | 0.98581 | -0.27295 | 0.98581 | -0.273 | 0.41807
121 | 0.01014 | 0.0025417 | -0.010139 | -0.0025411 | 1.0345e-06 | 5.1196e-07 | 0.015306 | 0.015306 | 0.015306 | 0.98578 | -0.27351 | 0.98567 | -0.27565 | 4.2051
122 | 0.010139 | 0.0025411 | -0.010137 | -0.0025401 | 2.1083e-06 | 1.0435e-06 | 0.015306 | 0.015307 | 0.015307 | 0.98567 | -0.27565 | 0.98545 | -0.28001 | 4.2051
123 | 0.010137 | 0.0025401 | -0.010135 | -0.0025393 | 1.5783e-06 | 7.8129e-07 | 0.015307 | 0.015307 | 0.015307 | 0.98545 | -0.28001 | 0.98528 | -0.28328 | 4.2051
124 | 0.0081963 | 0.0020533 | -0.0081954 | -0.002053 | 8.8004e-07 | 3.6818e-07 | 0.012378 | 0.012378 | 0.012378 | 0.98528 | -0.28328 | 0.98516 | -0.28554 | 3.4006
125 | 0.0062658 | 0.0015694 | -0.0062614 | -0.0015682 | 4.4685e-06 | 1.1672e-06 | 0.0094637 | 0.0094643 | 0.0094643 | 0.98516 | -0.28554 | 0.9844 | -0.30052 | 2.6001
126 | 0.0058109 | 0.0014553 | -0.0058053 | -0.0014542 | 5.6713e-06 | 1.1404e-06 | 0.0087835 | 0.0087843 | 0.0087843 | 0.9844 | -0.30052 | 0.98335 | -0.32103 | 2.4133
127 | 0.0013333 | 0.00033222 | -0.0013332 | -0.00033308 | 1.1947e-07 | -8.6555e-07 | 0.0020438 | 0.0020441 | 0.0020441 | 0.97041 | -0.57395 | 0.97031 | -0.57583 | 0.56158
128 | 0.0013332 | 0.00033308 | -0.0013331 | -0.00033387 | 1.0833e-07 | -7.8441e-07 | 0.0020441 | 0.0020444 | 0.0020444 | 0.97031 | -0.57583 | 0.97023 | -0.57754 | 0.56166
129 | 0.0013331 | 0.00033387 | -0.0013331 | -0.0003341 | 3.1651e-08 | -2.291e-07 | 0.0020444 | 0.0020445 | 0.0020445 | 0.97023 | -0.57754 | 0.9702 | -0.57804 | 0.56169
130 | -0.0044299 | -0.00111 | 0.0044299 | 0.00111 | 1.0989e-08 | -1.1718e-09 | 0.0067172 | 0.0067172 | 0.0067172 | 0.98131 | -0.36096 | 0.98131 | -0.36091 | 1.8454
131 | 0.0038315 | 0.00096008 | -0.0038314 | -0.00096012 | 1.0547e-07 | -3.7759e-08 | 0.0058099 | 0.00581 | 0.00581 | 0.98131 | -0.36096 | 0.98128 | -0.36154 | 1.5961
132 | -0.0048155 | -0.0012067 | 0.0048157 | 0.0012067 | 1.8933e-07 | 1.5353e-09 | 0.0073019 | 0.0073019 | 0.0073019 | 0.98131 | -0.36091 | 0.98135 | -0.36008 | 2.006
133 | 0.00086422 | 0.00021646 | -0.00086421 | -0.00021659 | 6.6917e-09 | -1.2698e-07 | 0.0013105 | 0.0013105 | 0.0013105 | 0.98128 | -0.36154 | 0.98127 | -0.3617 | 0.36003
134 | -0.0057945 | -0.001452 | 0.0057948 | 0.001452 | 2.7407e-07 | 5.5777e-08 | 0.008786 | 0.008786 | 0.008786 | 0.98135 | -0.36008 | 0.9814 | -0.35909 | 2.4137
135 | -0.0057948 | -0.001452 | 0.0058053 | 0.0014542 | 1.0514e-05 | 2.1295e-06 | 0.008786 | 0.0087843 | 0.008786 | 0.9814 | -0.35909 | 0.98335 | -0.32103 | 2.4137

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18906 | 0.047737

## res_load
| p_mw | q_mvar
0 | 0.0025182 | 0.00063111
1 | 0.00053583 | 0.00013429
2 | 0.00035293 | 8.8454e-05
3 | 0.0010424 | 0.00026126
4 | 0.00070124 | 0.00017575
5 | 0.0007614 | 0.00019082
6 | 0.00025502 | 6.3914e-05
7 | 0.00047247 | 0.00011841
8 | 0.00017983 | 4.5069e-05
9 | 0.0017276 | 0.00043298
10 | 0.0014631 | 0.00036669
11 | 0.0024782 | 0.00062109
12 | 0.0034583 | 0.00086673
13 | 0.00032917 | 8.2498e-05
14 | 0.00076129 | 0.0001908
15 | 0.0011811 | 0.00029602
16 | 0.00011825 | 2.9635e-05
17 | 0.00085257 | 0.00021367
18 | 0.00012909 | 3.2354e-05
19 | 0.00088259 | 0.0002212
20 | 0.00012146 | 3.0442e-05
21 | 0.0023149 | 0.00058016
22 | 0.0018402 | 0.00046119
23 | 0.0018127 | 0.0004543
24 | 0.001192 | 0.00029875
25 | 0.0025806 | 0.00064676
26 | 0.0012426 | 0.00031142
27 | 0.0030048 | 0.00075307
28 | 0.0015311 | 0.00038374
29 | 0.002248 | 0.0005634
30 | 0.0011053 | 0.00027702
31 | 0.0015037 | 0.00037686
32 | 0.0014608 | 0.0003661
33 | 0.0012617 | 0.00031622
34 | 0.00127 | 0.0003183
35 | 0.0012686 | 0.00031794
36 | 0.0016975 | 0.00042543
37 | 0.0020381 | 0.00051079
38 | 0.0011399 | 0.00028569
39 | 0.0011282 | 0.00028276
40 | 0.0027407 | 0.00068689
41 | 0.0012691 | 0.00031807
42 | 0.0011301 | 0.00028323
43 | 0.0034341 | 0.00086067
44 | 0.0015937 | 0.00039943
45 | 0.0015514 | 0.00038881
46 | 0.0021186 | 0.00053098
47 | 0.0023741 | 0.00059501
48 | 0.0012239 | 0.00030673
49 | 0.0027971 | 0.00070103
50 | 0.0022481 | 0.00056342
51 | 0.0039177 | 0.00098186
52 | 0.002292 | 0.00057444
53 | 0.0028941 | 0.00072534
54 | 0.0026861 | 0.00067321
55 | 0.001969 | 0.00049348
56 | 0.0015177 | 0.00038038
57 | 0.0012988 | 0.0003255
58 | 0.0023054 | 0.00057778
59 | 0.0011441 | 0.00028674
60 | 0.0011269 | 0.00028243
61 | 0.0020484 | 0.00051339
62 | 0.0011354 | 0.00028457
63 | 0.0015074 | 0.00037779
64 | 0.00075657 | 0.00018961
65 | 0.00099621 | 0.00024967
66 | 0.0020108 | 0.00050395
67 | 0.0016823 | 0.00042162
68 | 0.0021193 | 0.00053113
69 | 0.0013142 | 0.00032938
70 | 0.0011844 | 0.00029685
71 | 0.0020115 | 0.00050414
72 | 0.0015134 | 0.00037929
73 | 0.0019847 | 0.00049742
74 | 0.0025242 | 0.00063262
75 | 0.001147 | 0.00028746
76 | 0.0019079 | 0.00047816
77 | 0.0039213 | 0.00098277
78 | 0.0017264 | 0.00043269
79 | 0.0020397 | 0.0005112
80 | 0.0025326 | 0.00063474
81 | 0.0035778 | 0.00089667
82 | 0.0013971 | 0.00035015
83 | 0.0013954 | 0.00034971
84 | 0.0017853 | 0.00044745
85 | 0.0013449 | 0.00033706
86 | 0.0013542 | 0.0003394
87 | 0.001873 | 0.00046942
88 | 0.0016458 | 0.00041247
89 | 0.0013787 | 0.00034553
90 | 0.0016451 | 0.00041231
91 | 0.0031393 | 0.00078678
92 | 0.0013435 | 0.00033672
93 | 0.0015667 | 0.00039266
94 | 0.00044724 | 0.00011209
95 | 0.001231 | 0.00030852
96 | 0.0015861 | 0.00039751
97 | 0.001173 | 0.00029398
98 | 0.00093009 | 0.0002331
99 | 0.0013962 | 0.00034993
100 | 0.0010082 | 0.00025267
101 | 0.0012735 | 0.00031918
102 | 0.00084726 | 0.00021234
103 | 0.0019391 | 0.00048599
104 | 0.0019295 | 0.00048359
105 | 0.00045041 | 0.00011288
106 | 0.006987 | 0.0017511
107 | 0.0018596 | 0.00046607
108 | 0.0013331 | 0.0003341
109 | 0.00059835 | 0.00014996
110 | 0.00038558 | 9.6634e-05
111 | 0.0029672 | 0.00074366
112 | 0.00097882 | 0.00024531
113 | 0.00086421 | 0.00021659

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1