## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_10-7_1_2_node_36 | 0.4 | n |  | TRUE
1 | bus_LV_10-7_1_2_node_41 | 0.4 | n |  | TRUE
2 | bus_LV_10-7_1_2_node_63 | 0.4 | n |  | TRUE
3 | bus_LV_10-7_1_2_node_37 | 0.4 | n |  | TRUE
4 | bus_LV_10-7_1_2_node_40 | 0.4 | n |  | TRUE
5 | bus_LV_10-7_1_2_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_10-7_1_2_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_10-7_1_2_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_10-7_1_2_node_61 | 0.4 | n |  | TRUE
9 | bus_LV_10-7_1_2_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_10-7_1_2_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_10-7_1_2_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_10-7_1_2_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_10-7_1_2_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_10-7_1_2_node_285 | 0.4 | n |  | TRUE
15 | bus_LV_10-7_1_2_node_81 | 0.4 | n |  | TRUE
16 | bus_LV_10-7_1_2_node_62 | 0.4 | n |  | TRUE
17 | bus_LV_10-7_1_2_node_66 | 0.4 | n |  | TRUE
18 | bus_LV_10-7_1_2_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_10-7_1_2_node_288 | 0.4 | n |  | TRUE
20 | bus_LV_10-7_1_2_node_68 | 0.4 | n |  | TRUE
21 | bus_LV_10-7_1_2_node_69 | 0.4 | n |  | TRUE
22 | bus_LV_10-7_1_2_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_10-7_1_2_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_10-7_1_2_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_10-7_1_2_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_10-7_1_2_node_97 | 0.4 | n |  | TRUE
27 | bus_LV_10-7_1_2_node_76 | 0.4 | n |  | TRUE
28 | bus_LV_10-7_1_2_node_74 | 0.4 | n |  | TRUE
29 | bus_LV_10-7_1_2_node_75 | 0.4 | n |  | TRUE
30 | bus_LV_10-7_1_2_node_77 | 0.4 | n |  | TRUE
31 | bus_LV_10-7_1_2_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_10-7_1_2_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_10-7_1_2_node_79 | 0.4 | n |  | TRUE
34 | bus_LV_10-7_1_2_node_82 | 0.4 | n |  | TRUE
35 | bus_LV_10-7_1_2_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_10-7_1_2_node_84 | 0.4 | n |  | TRUE
37 | bus_LV_10-7_1_2_node_89 | 0.4 | n |  | TRUE
38 | bus_LV_10-7_1_2_node_85 | 0.4 | n |  | TRUE
39 | bus_LV_10-7_1_2_node_86 | 0.4 | n |  | TRUE
40 | bus_LV_10-7_1_2_node_87 | 0.4 | n |  | TRUE
41 | bus_LV_10-7_1_2_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_10-7_1_2_node_92 | 0.4 | n |  | TRUE
43 | bus_LV_10-7_1_2_node_176 | 0.4 | n |  | TRUE
44 | bus_LV_10-7_1_2_node_179 | 0.4 | n |  | TRUE
45 | bus_LV_10-7_1_2_node_90 | 0.4 | n |  | TRUE
46 | bus_LV_10-7_1_2_node_91 | 0.4 | n |  | TRUE
47 | bus_LV_10-7_1_2_node_183 | 0.4 | n |  | TRUE
48 | bus_LV_10-7_1_2_node_186 | 0.4 | n |  | TRUE
49 | bus_LV_10-7_1_2_node_93 | 0.4 | n |  | TRUE
50 | bus_LV_10-7_1_2_node_94 | 0.4 | n |  | TRUE
51 | bus_LV_10-7_1_2_node_95 | 0.4 | n |  | TRUE
52 | bus_LV_10-7_1_2_node_96 | 0.4 | n |  | TRUE
53 | bus_LV_10-7_1_2_node_98 | 0.4 | n |  | TRUE
54 | bus_LV_10-7_1_2_node_99 | 0.4 | n |  | TRUE
55 | bus_LV_10-7_1_2_node_101 | 0.4 | n |  | TRUE
56 | bus_LV_10-7_1_2_node_103 | 0.4 | n |  | TRUE
57 | bus_LV_10-7_1_2_node_169 | 0.4 | n |  | TRUE
58 | bus_LV_10-7_1_2_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_10-7_1_2_node_117 | 0.4 | n |  | TRUE
60 | bus_LV_10-7_1_2_node_118 | 0.4 | n |  | TRUE
61 | bus_LV_10-7_1_2_node_119 | 0.4 | n |  | TRUE
62 | bus_LV_10-7_1_2_node_120 | 0.4 | n |  | TRUE
63 | bus_LV_10-7_1_2_node_121 | 0.4 | n |  | TRUE
64 | bus_LV_10-7_1_2_node_122 | 0.4 | n |  | TRUE
65 | bus_LV_10-7_1_2_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_10-7_1_2_node_124 | 0.4 | n |  | TRUE
67 | bus_LV_10-7_1_2_node_125 | 0.4 | n |  | TRUE
68 | bus_LV_10-7_1_2_node_126 | 0.4 | n |  | TRUE
69 | bus_LV_10-7_1_2_node_164 | 0.4 | n |  | TRUE
70 | bus_LV_10-7_1_2_node_127 | 0.4 | n |  | TRUE
71 | bus_LV_10-7_1_2_node_128 | 0.4 | n |  | TRUE
72 | bus_LV_10-7_1_2_node_129 | 0.4 | n |  | TRUE
73 | bus_LV_10-7_1_2_node_130 | 0.4 | n |  | TRUE
74 | bus_LV_10-7_1_2_node_131 | 0.4 | n |  | TRUE
75 | bus_LV_10-7_1_2_node_132 | 0.4 | n |  | TRUE
76 | bus_LV_10-7_1_2_node_133 | 0.4 | n |  | TRUE
77 | bus_LV_10-7_1_2_node_134 | 0.4 | n |  | TRUE
78 | bus_LV_10-7_1_2_node_173 | 0.4 | n |  | TRUE
79 | bus_LV_10-7_1_2_node_167 | 0.4 | n |  | TRUE
80 | bus_LV_10-7_1_2_node_195 | 0.4 | n |  | TRUE
81 | bus_LV_10-7_1_2_node_143 | 0.4 | n |  | TRUE
82 | bus_LV_10-7_1_2_node_156 | 0.4 | n |  | TRUE
83 | bus_LV_10-7_1_2_node_157 | 0.4 | n |  | TRUE
84 | bus_LV_10-7_1_2_node_168 | 0.4 | n |  | TRUE
85 | bus_LV_10-7_1_2_node_170 | 0.4 | n |  | TRUE
86 | bus_LV_10-7_1_2_node_171 | 0.4 | n |  | TRUE
87 | bus_LV_10-7_1_2_node_172 | 0.4 | n |  | TRUE
88 | bus_LV_10-7_1_2_node_174 | 0.4 | n |  | TRUE
89 | bus_LV_10-7_1_2_node_175 | 0.4 | n |  | TRUE
90 | bus_LV_10-7_1_2_node_177 | 0.4 | n |  | TRUE
91 | bus_LV_10-7_1_2_node_178 | 0.4 | n |  | TRUE
92 | bus_LV_10-7_1_2_node_180 | 0.4 | n |  | TRUE
93 | bus_LV_10-7_1_2_node_181 | 0.4 | n |  | TRUE
94 | bus_LV_10-7_1_2_node_182 | 0.4 | n |  | TRUE
95 | bus_LV_10-7_1_2_node_193 | 0.4 | n |  | TRUE
96 | bus_LV_10-7_1_2_node_189 | 0.4 | n |  | TRUE
97 | bus_LV_10-7_1_2_node_184 | 0.4 | n |  | TRUE
98 | bus_LV_10-7_1_2_node_185 | 0.4 | n |  | TRUE
99 | bus_LV_10-7_1_2_node_187 | 0.4 | n |  | TRUE
100 | bus_LV_10-7_1_2_node_188 | 0.4 | n |  | TRUE
101 | bus_LV_10-7_1_2_node_243 | 0.4 | n |  | TRUE
102 | bus_LV_10-7_1_2_node_190 | 0.4 | n |  | TRUE
103 | bus_LV_10-7_1_2_node_191 | 0.4 | n |  | TRUE
104 | bus_LV_10-7_1_2_node_192 | 0.4 | n |  | TRUE
105 | bus_LV_10-7_1_2_node_197 | 0.4 | n |  | TRUE
106 | bus_LV_10-7_1_2_node_198 | 0.4 | n |  | TRUE
107 | bus_LV_10-7_1_2_node_237 | 0.4 | n |  | TRUE
108 | bus_LV_10-7_1_2_node_194 | 0.4 | n |  | TRUE
109 | bus_LV_10-7_1_2_node_196 | 0.4 | n |  | TRUE
110 | bus_LV_10-7_1_2_node_229 | 0.4 | n |  | TRUE
111 | bus_LV_10-7_1_2_node_230 | 0.4 | n |  | TRUE
112 | bus_LV_10-7_1_2_node_231 | 0.4 | n |  | TRUE
113 | bus_LV_10-7_1_2_node_232 | 0.4 | n |  | TRUE
114 | bus_LV_10-7_1_2_node_233 | 0.4 | n |  | TRUE
115 | bus_LV_10-7_1_2_node_234 | 0.4 | n |  | TRUE
116 | bus_LV_10-7_1_2_node_235 | 0.4 | n |  | TRUE
117 | bus_LV_10-7_1_2_node_236 | 0.4 | n |  | TRUE
118 | bus_LV_10-7_1_2_node_241 | 0.4 | n |  | TRUE
119 | bus_LV_10-7_1_2_node_242 | 0.4 | n |  | TRUE
120 | bus_LV_10-7_1_2_node_244 | 0.4 | n |  | TRUE
121 | bus_LV_10-7_1_2_node_245 | 0.4 | n |  | TRUE
122 | bus_LV_10-7_1_2_node_270 | 0.4 | n |  | TRUE
123 | bus_LV_10-7_1_2_node_269 | 0.4 | n |  | TRUE
124 | bus_LV_10-7_1_2_node_284 | 0.4 | n |  | TRUE
125 | bus_LV_10-7_1_2_node_286 | 0.4 | n |  | TRUE
126 | bus_LV_10-7_1_2_node_287 | 0.4 | n |  | TRUE
127 | bus_LV_10-7_1_2_node_289 | 0.4 | n |  | TRUE
128 | bus_MV_350_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_10-7_1_2_load_63 | 2 | 0.00043236 | 0.00010836 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_10-7_1_2_load_37 | 3 | 0.0017808 | 0.00044632 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_10-7_1_2_load_45 | 6 | 0.0018111 | 0.00045391 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_10-7_1_2_load_61 | 8 | 0.0012124 | 0.00030385 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_10-7_1_2_load_59 | 9 | 0.0054987 | 0.0013781 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_10-7_1_2_load_55 | 10 | 0.0064573 | 0.0016183 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_10-7_1_2_load_56 | 11 | 0.019385 | 0.0048582 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_10-7_1_2_load_57 | 12 | 0.009318 | 0.0023353 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_10-7_1_2_load_58 | 13 | 0.0069914 | 0.0017522 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_10-7_1_2_load_285 | 14 | 0.0034698 | 0.00086962 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_10-7_1_2_load_62 | 16 | 0.00058728 | 0.00014719 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_10-7_1_2_load_66 | 17 | 0.0028327 | 0.00070995 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_10-7_1_2_load_68 | 20 | 0.0021162 | 0.00053037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_10-7_1_2_load_70 | 22 | 0.0027193 | 0.00068153 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_10-7_1_2_load_71 | 23 | 0.0013517 | 0.00033878 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_10-7_1_2_load_72 | 24 | 0.0020641 | 0.00051732 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_10-7_1_2_load_73 | 25 | 0.00087998 | 0.00022054 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_10-7_1_2_load_97 | 26 | 0.0024282 | 0.00060857 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_10-7_1_2_load_76 | 27 | 0.0014464 | 0.00036251 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_10-7_1_2_load_74 | 28 | 0.0017047 | 0.00042724 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_10-7_1_2_load_75 | 29 | 0.0016107 | 0.00040367 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_10-7_1_2_load_78 | 31 | 0.0011552 | 0.00028952 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_10-7_1_2_load_79 | 33 | 0.00122 | 0.00030576 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_10-7_1_2_load_82 | 34 | 0.0020109 | 0.00050398 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_10-7_1_2_load_83 | 35 | 0.0022034 | 0.00055221 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_10-7_1_2_load_84 | 36 | 0.0017354 | 0.00043494 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_10-7_1_2_load_86 | 39 | 0.0022981 | 0.00057596 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_10-7_1_2_load_88 | 41 | 0.0019417 | 0.00048664 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_10-7_1_2_load_92 | 42 | 0.0018749 | 0.0004699 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_10-7_1_2_load_176 | 43 | 0.00066751 | 0.00016729 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_10-7_1_2_load_179 | 44 | 0.0026761 | 0.00067069 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_10-7_1_2_load_90 | 45 | 0.0025054 | 0.00062792 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_10-7_1_2_load_91 | 46 | 0.0016028 | 0.0004017 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_10-7_1_2_load_183 | 47 | 0.00088501 | 0.00022181 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_10-7_1_2_load_93 | 49 | 0.0013233 | 0.00033165 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_10-7_1_2_load_94 | 50 | 0.00087456 | 0.00021918 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_10-7_1_2_load_95 | 51 | 0.0028972 | 0.00072612 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_10-7_1_2_load_96 | 52 | 0.0027176 | 0.0006811 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_10-7_1_2_load_98 | 53 | 0.0023617 | 0.00059189 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_10-7_1_2_load_99 | 54 | 0.001383 | 0.00034662 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_10-7_1_2_load_101 | 55 | 0.0017207 | 0.00043125 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_10-7_1_2_load_103 | 56 | 0.001386 | 0.00034736 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_10-7_1_2_load_116 | 58 | 0.0020201 | 0.00050628 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_10-7_1_2_load_117 | 59 | 0.0016936 | 0.00042444 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_10-7_1_2_load_119 | 61 | 0.0021661 | 0.00054288 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_10-7_1_2_load_121 | 63 | 0.0020548 | 0.00051497 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_10-7_1_2_load_122 | 64 | 0.0022064 | 0.00055297 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_10-7_1_2_load_123 | 65 | 0.0030569 | 0.00076613 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_10-7_1_2_load_124 | 66 | 0.0019475 | 0.00048809 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_10-7_1_2_load_125 | 67 | 0.003448 | 0.00086415 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_10-7_1_2_load_126 | 68 | 0.0002747 | 6.8845e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_10-7_1_2_load_164 | 69 | 0.0051536 | 0.0012916 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_10-7_1_2_load_128 | 71 | 0.00061785 | 0.00015485 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_10-7_1_2_load_129 | 72 | 0.0014629 | 0.00036664 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_10-7_1_2_load_131 | 74 | 0.00034025 | 8.5275e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_10-7_1_2_load_134 | 77 | 0.00081663 | 0.00020467 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_10-7_1_2_load_173 | 78 | 0.00084233 | 0.00021111 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_10-7_1_2_load_167 | 79 | 0.00024275 | 6.0839e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_10-7_1_2_load_195 | 80 | 0.00048893 | 0.00012254 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_10-7_1_2_load_143 | 81 | 0.00092874 | 0.00023276 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_10-7_1_2_load_156 | 82 | 0.00091583 | 0.00022953 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_10-7_1_2_load_157 | 83 | 0.0009289 | 0.00023281 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_10-7_1_2_load_170 | 85 | 0.00066379 | 0.00016636 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_10-7_1_2_load_172 | 87 | 0.00066521 | 0.00016672 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_10-7_1_2_load_174 | 88 | 0.00158 | 0.00039598 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_10-7_1_2_load_177 | 90 | 0.002224 | 0.00055739 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_10-7_1_2_load_178 | 91 | 0.0018723 | 0.00046923 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_10-7_1_2_load_181 | 93 | 0.00053334 | 0.00013367 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_10-7_1_2_load_182 | 94 | 0.0020662 | 0.00051785 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_10-7_1_2_load_193 | 95 | 0.0011616 | 0.00029113 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_10-7_1_2_load_189 | 96 | 0.0030347 | 0.00076056 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_10-7_1_2_load_184 | 97 | 0.0011589 | 0.00029045 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_10-7_1_2_load_185 | 98 | 0.00070154 | 0.00017582 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_10-7_1_2_load_187 | 99 | 0.00082745 | 0.00020738 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_10-7_1_2_load_188 | 100 | 0.00092332 | 0.00023141 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_10-7_1_2_load_243 | 101 | 0.0009306 | 0.00023323 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_10-7_1_2_load_191 | 103 | 0.0027928 | 0.00069994 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_10-7_1_2_load_192 | 104 | 0.0010378 | 0.00026009 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_10-7_1_2_load_197 | 105 | 0.0011632 | 0.00029154 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_10-7_1_2_load_198 | 106 | 0.001027 | 0.0002574 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_10-7_1_2_load_237 | 107 | 0.0007195 | 0.00018032 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_10-7_1_2_load_194 | 108 | 0.0021787 | 0.00054603 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_10-7_1_2_load_196 | 109 | 0.0026879 | 0.00067366 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_10-7_1_2_load_229 | 110 | 0.0074489 | 0.0018669 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_10-7_1_2_load_230 | 111 | 0.0013708 | 0.00034356 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_10-7_1_2_load_231 | 112 | 0.0027289 | 0.00068393 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_10-7_1_2_load_232 | 113 | 0.0021418 | 0.00053679 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_10-7_1_2_load_233 | 114 | 0.00058996 | 0.00014786 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_10-7_1_2_load_234 | 115 | 0.00037879 | 9.4932e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_10-7_1_2_load_235 | 116 | 0.0005619 | 0.00014083 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_10-7_1_2_load_236 | 117 | 0.0011509 | 0.00028844 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_10-7_1_2_load_241 | 118 | 0.0050721 | 0.0012712 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_10-7_1_2_load_242 | 119 | 0.00093761 | 0.00023499 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_10-7_1_2_load_244 | 120 | 0.0018549 | 0.00046488 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_10-7_1_2_load_245 | 121 | 0.00092955 | 0.00023297 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_10-7_1_2_load_270 | 122 | 0.00092068 | 0.00023074 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_10-7_1_2_load_269 | 123 | 0.001794 | 0.00044961 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_10-7_1_2_load_284 | 124 | 0.0099502 | 0.0024938 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_10-7_1_2_load_286 | 125 | 0.0010819 | 0.00027116 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_10-7_1_2_load_289 | 127 | 0.0031226 | 0.0007826 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_10-7_1_2_line_0 |  | 0 | 1 | 0.045393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_10-7_1_2_line_1 |  | 0 | 2 | 0.058864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_10-7_1_2_line_2 |  | 1 | 5 | 0.047874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_10-7_1_2_line_3 |  | 1 | 6 | 0.020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_10-7_1_2_line_4 |  | 1 | 4 | 0.017345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_10-7_1_2_line_5 |  | 2 | 16 | 0.002254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_10-7_1_2_line_6 |  | 3 | 4 | 0.025987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_10-7_1_2_line_7 |  | 5 | 7 | 0.068308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_10-7_1_2_line_8 |  | 5 | 8 | 0.034068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_10-7_1_2_line_9 |  | 6 | 9 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_10-7_1_2_line_10 |  | 7 | 14 | 0.010356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_10-7_1_2_line_11 |  | 8 | 15 | 0.0091022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_10-7_1_2_line_12 |  | 9 | 13 | 0.031371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_10-7_1_2_line_13 |  | 10 | 11 | 0.015359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_10-7_1_2_line_14 |  | 10 | 12 | 0.035038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_10-7_1_2_line_15 |  | 11 | 13 | 0.011538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_10-7_1_2_line_16 |  | 14 | 124 | 0.013473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_10-7_1_2_line_17 |  | 15 | 37 | 0.006555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_10-7_1_2_line_18 |  | 15 | 33 | 0.0018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_10-7_1_2_line_19 |  | 17 | 18 | 0.015057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_10-7_1_2_line_20 |  | 18 | 19 | 0.007087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_10-7_1_2_line_21 |  | 19 | 127 | 0.038618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_10-7_1_2_line_22 |  | 19 | 126 | 0.019285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_10-7_1_2_line_23 |  | 20 | 21 | 0.016326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_10-7_1_2_line_24 |  | 21 | 22 | 0.019545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_10-7_1_2_line_25 |  | 21 | 23 | 0.026926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_10-7_1_2_line_26 |  | 22 | 24 | 0.0090582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_10-7_1_2_line_27 |  | 23 | 25 | 0.0067445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_10-7_1_2_line_28 |  | 24 | 26 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_10-7_1_2_line_29 |  | 25 | 27 | 0.0080511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_10-7_1_2_line_30 |  | 27 | 28 | 0.008866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_10-7_1_2_line_31 |  | 28 | 29 | 0.012989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_10-7_1_2_line_32 |  | 29 | 30 | 0.01333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_10-7_1_2_line_33 |  | 30 | 31 | 0.0064633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_10-7_1_2_line_34 |  | 31 | 32 | 0.033579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_10-7_1_2_line_35 |  | 32 | 34 | 0.041756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_10-7_1_2_line_36 |  | 32 | 35 | 0.025958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_10-7_1_2_line_37 |  | 32 | 36 | 0.023593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_10-7_1_2_line_38 |  | 34 | 38 | 0.00809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_10-7_1_2_line_39 |  | 35 | 39 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_10-7_1_2_line_40 |  | 36 | 40 | 0.018622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_10-7_1_2_line_41 |  | 37 | 46 | 0.016492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_10-7_1_2_line_42 |  | 37 | 38 | 0.027416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_10-7_1_2_line_43 |  | 38 | 41 | 0.022281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_10-7_1_2_line_44 |  | 39 | 42 | 0.0054543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_10-7_1_2_line_45 |  | 40 | 43 | 0.0087016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_10-7_1_2_line_46 |  | 40 | 44 | 0.014872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_10-7_1_2_line_47 |  | 41 | 45 | 0.014768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_10-7_1_2_line_48 |  | 42 | 49 | 0.010428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_10-7_1_2_line_49 |  | 43 | 89 | 0.0049919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_10-7_1_2_line_50 |  | 44 | 90 | 0.00042652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_10-7_1_2_line_51 |  | 45 | 47 | 0.023095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_10-7_1_2_line_52 |  | 46 | 48 | 0.039257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_10-7_1_2_line_53 |  | 47 | 97 | 0.0063493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_10-7_1_2_line_54 |  | 48 | 99 | 0.011496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_10-7_1_2_line_55 |  | 48 | 83 | 0.019641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_10-7_1_2_line_56 |  | 49 | 50 | 0.0086951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_10-7_1_2_line_57 |  | 50 | 51 | 0.015203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_10-7_1_2_line_58 |  | 51 | 52 | 0.016737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_10-7_1_2_line_59 |  | 53 | 54 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_10-7_1_2_line_60 |  | 54 | 55 | 0.0057273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_10-7_1_2_line_61 |  | 55 | 56 | 0.001012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_10-7_1_2_line_62 |  | 56 | 57 | 0.039481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_10-7_1_2_line_63 |  | 57 | 86 | 0.047064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_10-7_1_2_line_64 |  | 58 | 59 | 0.023512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_10-7_1_2_line_65 |  | 58 | 60 | 0.0019517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_10-7_1_2_line_66 |  | 59 | 61 | 0.01076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_10-7_1_2_line_67 |  | 60 | 62 | 0.033581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_10-7_1_2_line_68 |  | 60 | 63 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_10-7_1_2_line_69 |  | 61 | 64 | 0.01519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_10-7_1_2_line_70 |  | 62 | 65 | 0.015017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_10-7_1_2_line_71 |  | 62 | 66 | 0.016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_10-7_1_2_line_72 |  | 63 | 67 | 0.025146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_10-7_1_2_line_73 |  | 66 | 68 | 0.021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_10-7_1_2_line_74 |  | 67 | 69 | 0.001419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_10-7_1_2_line_75 |  | 68 | 70 | 0.020277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_10-7_1_2_line_76 |  | 70 | 71 | 0.018387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_10-7_1_2_line_77 |  | 70 | 72 | 0.0183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_10-7_1_2_line_78 |  | 70 | 73 | 0.009425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_10-7_1_2_line_79 |  | 71 | 74 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_10-7_1_2_line_80 |  | 72 | 75 | 0.022711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_10-7_1_2_line_81 |  | 73 | 76 | 0.010315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_10-7_1_2_line_82 |  | 73 | 77 | 0.029625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_10-7_1_2_line_83 |  | 75 | 78 | 0.04044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_10-7_1_2_line_84 |  | 76 | 79 | 0.01772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_10-7_1_2_line_85 |  | 77 | 80 | 0.0091831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_10-7_1_2_line_86 |  | 78 | 88 | 0.00032064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_10-7_1_2_line_87 |  | 79 | 84 | 0.030306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_10-7_1_2_line_88 |  | 80 | 108 | 0.047888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_10-7_1_2_line_89 |  | 81 | 82 | 0.0012894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_10-7_1_2_line_90 |  | 82 | 83 | 0.00012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_10-7_1_2_line_91 |  | 84 | 85 | 0.031072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_10-7_1_2_line_92 |  | 85 | 87 | 0.024761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_10-7_1_2_line_93 |  | 86 | 87 | 0.0060785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_10-7_1_2_line_94 |  | 88 | 89 | 0.016711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_10-7_1_2_line_95 |  | 90 | 91 | 0.04336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_10-7_1_2_line_96 |  | 91 | 92 | 0.018713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_10-7_1_2_line_97 |  | 92 | 93 | 0.026845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_10-7_1_2_line_98 |  | 92 | 94 | 0.019656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_10-7_1_2_line_99 |  | 93 | 95 | 0.0041931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_10-7_1_2_line_100 |  | 94 | 96 | 0.03973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_10-7_1_2_line_101 |  | 95 | 107 | 0.018985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_10-7_1_2_line_102 |  | 96 | 102 | 0.021609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_10-7_1_2_line_103 |  | 97 | 98 | 0.00096845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_10-7_1_2_line_104 |  | 99 | 100 | 0.011921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_10-7_1_2_line_105 |  | 100 | 101 | 0.0056063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_10-7_1_2_line_106 |  | 101 | 118 | 0.0017218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_10-7_1_2_line_107 |  | 102 | 103 | 0.018095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_10-7_1_2_line_108 |  | 102 | 104 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_10-7_1_2_line_109 |  | 103 | 105 | 0.034081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_10-7_1_2_line_110 |  | 104 | 106 | 0.00429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_10-7_1_2_line_111 |  | 105 | 110 | 0.014909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_10-7_1_2_line_112 |  | 107 | 117 | 0.0021203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_10-7_1_2_line_113 |  | 108 | 109 | 0.0049333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_10-7_1_2_line_114 |  | 110 | 111 | 0.014082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_10-7_1_2_line_115 |  | 112 | 113 | 0.036624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_10-7_1_2_line_116 |  | 113 | 114 | 0.037747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_10-7_1_2_line_117 |  | 114 | 115 | 0.0070618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_10-7_1_2_line_118 |  | 115 | 116 | 0.0122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_10-7_1_2_line_119 |  | 116 | 117 | 0.0091929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_10-7_1_2_line_120 |  | 118 | 119 | 0.0014275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_10-7_1_2_line_121 |  | 119 | 120 | 0.031263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_10-7_1_2_line_122 |  | 120 | 121 | 0.00076016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_10-7_1_2_line_123 |  | 121 | 122 | 0.0033202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_10-7_1_2_line_124 |  | 122 | 123 | 0.0022116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_10-7_1_2_line_125 |  | 124 | 125 | 0.029777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_10-7_1_2_line_126 |  | 125 | 126 | 0.027477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_10-7_1_2_trafo_82 | 0.63 MVA 20/0.4 kV | 128 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2674433.3399 | 1235630.5423 | 2674430.8768 | 1235638.0611 | 2674429.1611 | 1235645.7226 | 2674428.647 | 1235653.5327 | 2674429.4481 | 1235663.2827 | 2674432.1167 | 1235675.0019
1 | 2674433.3399 | 1235630.5423 | 2674376.1068 | 1235616.7816
2 | 2674451.8836 | 1235718.5795 | 2674439.3072 | 1235693.06 | 2674435.5786 | 1235684.4073 | 2674432.1167 | 1235675.0019
3 | 2674432.1167 | 1235675.0019 | 2674414.9947 | 1235682.4482 | 2674413.3252 | 1235683.3793
4 | 2674444.3353 | 1235662.6576 | 2674432.1167 | 1235675.0019
5 | 2674376.1068 | 1235616.7816 | 2674374.2717 | 1235618.0903
6 | 2674444.3353 | 1235662.6576 | 2674446.3639 | 1235636.7498
7 | 2674451.8836 | 1235718.5795 | 2674392.2265 | 1235752.1554
8 | 2674451.8836 | 1235718.5795 | 2674450.2972 | 1235732.836 | 2674447.7042 | 1235744.6783 | 2674444.7437 | 1235751.6784
9 | 2674413.3252 | 1235683.3793 | 2674403.3927 | 1235688.9191
10 | 2674392.2265 | 1235752.1554 | 2674393.7177 | 1235762.4033 | 2674393.7177 | 1235762.4033
11 | 2674440.7104 | 1235759.8345 | 2674444.1165 | 1235753.1614 | 2674444.7437 | 1235751.6784
12 | 2674375.9946 | 1235704.2 | 2674403.3927 | 1235688.9191
13 | 2674352.5038 | 1235717.3017 | 2674365.9175 | 1235709.8204
14 | 2674352.5038 | 1235717.3017 | 2674321.9032 | 1235734.3689
15 | 2674375.9946 | 1235704.2 | 2674365.9175 | 1235709.8204
16 | 2674382.0098 | 1235769.0708 | 2674393.7177 | 1235762.4033
17 | 2674445.1835 | 1235764.6382 | 2674440.7104 | 1235759.8345
18 | 2674440.7104 | 1235759.8345 | 2674439.8571 | 1235761.4629
19 | 2674311.9168 | 1235787.5304 | 2674305.8259 | 1235773.7602
20 | 2674315.0613 | 1235793.8852 | 2674311.9168 | 1235787.5304
21 | 2674326.9483 | 1235829.7585 | 2674325.8738 | 1235814.0231 | 2674315.0613 | 1235793.8852
22 | 2674332.194 | 1235784.9378 | 2674315.0613 | 1235793.8852
23 | 2674350.6929 | 1235862.1221 | 2674336.3336 | 1235869.8906
24 | 2674350.6929 | 1235862.1221 | 2674358.2436 | 1235874.9921 | 2674360.6238 | 1235878.9556
25 | 2674350.6929 | 1235862.1221 | 2674374.261 | 1235849.0998
26 | 2674360.6238 | 1235878.9556 | 2674363.6999 | 1235884.0777 | 2674364.1239 | 1235887.1319
27 | 2674380.1643 | 1235845.838 | 2674374.261 | 1235849.0998
28 | 2674363.6655 | 1235900.7221 | 2674364.9772 | 1235893.2778 | 2674364.1239 | 1235887.1319
29 | 2674380.1643 | 1235845.838 | 2674387.2112 | 1235841.9443
30 | 2674387.2112 | 1235841.9443 | 2674394.9714 | 1235837.6565
31 | 2674394.9714 | 1235837.6565 | 2674406.3404 | 1235831.3747
32 | 2674418.0075 | 1235824.9281 | 2674406.3404 | 1235831.3747
33 | 2674418.0075 | 1235824.9281 | 2674421.5609 | 1235827.63 | 2674423.3462 | 1235828.5302
34 | 2674454.6841 | 1235840.4982 | 2674428.1189 | 1235830.9366 | 2674423.3462 | 1235828.5302
35 | 2674454.6841 | 1235840.4982 | 2674455.1373 | 1235832.7208 | 2674455.0367 | 1235822.6348 | 2674452.2249 | 1235798.9218
36 | 2674454.6841 | 1235840.4982 | 2674452.9295 | 1235852.4733 | 2674450.2791 | 1235861.6575 | 2674448.0534 | 1235865.3322
37 | 2674454.6841 | 1235840.4982 | 2674477.1655 | 1235847.6539
38 | 2674451.2722 | 1235790.8881 | 2674452.2249 | 1235798.9218
39 | 2674448.0534 | 1235865.3322 | 2674448.0534 | 1235865.3322 | 2674445.2648 | 1235866.2201 | 2674440.1665 | 1235866.6231 | 2674434.9538 | 1235866.4262
40 | 2674494.2293 | 1235854.8147 | 2674487.9944 | 1235851.1007 | 2674477.1655 | 1235847.6539
41 | 2674445.1835 | 1235764.6382 | 2674449.6747 | 1235763.1713 | 2674453.6204 | 1235762.3535 | 2674461.351 | 1235762.0229
42 | 2674445.1835 | 1235764.6382 | 2674447.1997 | 1235766.8094 | 2674449.705 | 1235777.6594 | 2674451.2722 | 1235790.8881
43 | 2674451.2722 | 1235790.8881 | 2674473.5266 | 1235791.9687
44 | 2674429.5061 | 1235866.3758 | 2674430.9151 | 1235866.2737 | 2674434.9538 | 1235866.4262
45 | 2674494.2293 | 1235854.8147 | 2674502.79 | 1235853.2547
46 | 2674494.2293 | 1235854.8147 | 2674495.5736 | 1235858.6564 | 2674496.0644 | 1235869.4468
47 | 2674488.2089 | 1235793.1251 | 2674486.1553 | 1235792.5819 | 2674473.5266 | 1235791.9687
48 | 2674429.5061 | 1235866.3758 | 2674422.8024 | 1235866.8614 | 2674419.3497 | 1235868.2109
49 | 2674507.701 | 1235852.3597 | 2674502.79 | 1235853.2547
50 | 2674496.0838 | 1235869.8729 | 2674496.0644 | 1235869.4468
51 | 2674510.5358 | 1235799.0306 | 2674488.2089 | 1235793.1251
52 | 2674496.0067 | 1235748.1193 | 2674488.1848 | 1235755.6709 | 2674480.9505 | 1235760.428 | 2674473.3045 | 1235761.8109 | 2674463.0706 | 1235761.9494 | 2674461.351 | 1235762.0229
53 | 2674510.5358 | 1235799.0306 | 2674516.674 | 1235800.6542
54 | 2674496.0067 | 1235748.1193 | 2674497.952 | 1235744.4746 | 2674502.5127 | 1235738.6926
55 | 2674496.0067 | 1235748.1193 | 2674510.7116 | 1235760.1898 | 2674511.1542 | 1235760.6191
56 | 2674411.2513 | 1235871.3764 | 2674419.3497 | 1235868.2109
57 | 2674398.0147 | 1235878.7666 | 2674407.9188 | 1235872.679 | 2674411.2513 | 1235871.3764
58 | 2674398.0147 | 1235878.7666 | 2674383.7561 | 1235887.5307
59 | 2674691.3939 | 1235792.1243 | 2674705.5934 | 1235806.112
60 | 2674691.3939 | 1235792.1243 | 2674687.3702 | 1235796.2001
61 | 2674687.3702 | 1235796.2001 | 2674686.6592 | 1235796.9202
62 | 2674658.9217 | 1235825.0166 | 2674686.6592 | 1235796.9202
63 | 2674658.9217 | 1235825.0166 | 2674681.5034 | 1235844.3915 | 2674671.6119 | 1235857.0314 | 2674672.6612 | 1235857.8451
64 | 2674597.1191 | 1235787.0847 | 2674612.103 | 1235768.9654
65 | 2674595.8753 | 1235788.5888 | 2674597.1191 | 1235787.0847
66 | 2674612.103 | 1235768.9654 | 2674618.9598 | 1235760.6737
67 | 2674595.8753 | 1235788.5888 | 2674588.4134 | 1235795.1997 | 2674573.5156 | 1235813.5697
68 | 2674595.8753 | 1235788.5888 | 2674584.3781 | 1235779.0359
69 | 2674628.64 | 1235748.9679 | 2674618.9598 | 1235760.6737
70 | 2674573.5156 | 1235813.5697 | 2674571.8517 | 1235812.2813 | 2674562.4302 | 1235804.9803 | 2674561.6561 | 1235804.3585
71 | 2674573.5156 | 1235813.5697 | 2674583.6636 | 1235820.8688 | 2674586.2851 | 1235823.5127
72 | 2674565.0369 | 1235762.9656 | 2674584.3781 | 1235779.0359
73 | 2674599.5639 | 1235840.5324 | 2674598.0526 | 1235838.1835 | 2674592.6168 | 1235829.8985 | 2674586.2851 | 1235823.5127
74 | 2674563.9454 | 1235762.0587 | 2674565.0369 | 1235762.9656
75 | 2674604.7522 | 1235859.1153 | 2674605.8533 | 1235854.6038 | 2674605.086 | 1235850.0132 | 2674601.8606 | 1235844.102 | 2674599.5639 | 1235840.5324
76 | 2674604.7522 | 1235859.1153 | 2674616.9736 | 1235845.3773
77 | 2674604.7522 | 1235859.1153 | 2674595.1656 | 1235854.1249 | 2674587.8233 | 1235852.6338
78 | 2674611.8485 | 1235865.342 | 2674604.7522 | 1235859.1153
79 | 2674628.3267 | 1235832.6153 | 2674616.9736 | 1235845.3773
80 | 2674565.1709 | 1235851.9136 | 2674584.9521 | 1235852.0508 | 2674587.8233 | 1235852.6338
81 | 2674611.8485 | 1235865.342 | 2674618.6912 | 1235873.0777
82 | 2674611.8485 | 1235865.342 | 2674605.8205 | 1235870.4698 | 2674587.1309 | 1235881.5181
83 | 2674565.1709 | 1235851.9136 | 2674524.7319 | 1235852.2275
84 | 2674618.6912 | 1235873.0777 | 2674630.536 | 1235886.2577
85 | 2674587.1309 | 1235881.5181 | 2674579.2257 | 1235886.1913
86 | 2674524.4113 | 1235852.23 | 2674524.7319 | 1235852.2275
87 | 2674651.5773 | 1235907.759 | 2674642.195 | 1235895.555 | 2674630.536 | 1235886.2577
88 | 2674542.1201 | 1235899.4237 | 2674543.5816 | 1235899.9535 | 2674546.7676 | 1235892.7329 | 2674550.7305 | 1235884.5103 | 2674560.2545 | 1235884.8412 | 2674567.9022 | 1235882.7134 | 2674579.2257 | 1235886.1913 | 2674579.2257 | 1235886.1913
89 | 2674511.2473 | 1235760.7093 | 2674512.1727 | 1235761.6071
90 | 2674511.1542 | 1235760.6191 | 2674511.2473 | 1235760.7093
91 | 2674651.5773 | 1235907.759 | 2674653.1981 | 1235902.2422 | 2674648.4692 | 1235893.121 | 2674645.972 | 1235891.2995 | 2674653.4288 | 1235881.9525
92 | 2674668.8705 | 1235862.5968 | 2674653.4288 | 1235881.9525
93 | 2674672.6612 | 1235857.8451 | 2674668.8705 | 1235862.5968
94 | 2674507.701 | 1235852.3597 | 2674524.4113 | 1235852.23
95 | 2674496.0838 | 1235869.8729 | 2674497.2464 | 1235895.436 | 2674496.7324 | 1235913.1987
96 | 2674496.1911 | 1235931.9034 | 2674496.7324 | 1235913.1987
97 | 2674496.1911 | 1235931.9034 | 2674488.4457 | 1235936.9987 | 2674472.2554 | 1235943.8338
98 | 2674496.1911 | 1235931.9034 | 2674495.552 | 1235951.5495
99 | 2674469.4787 | 1235946.9758 | 2674472.2554 | 1235943.8338 | 2674472.2554 | 1235943.8338
100 | 2674495.552 | 1235951.5495 | 2674494.9962 | 1235968.6358 | 2674499.7692 | 1235990.7618
101 | 2674455.1228 | 1235959.0536 | 2674462.9357 | 1235954.3798 | 2674469.4787 | 1235946.9758
102 | 2674500.5551 | 1236012.3466 | 2674499.8953 | 1235991.3462 | 2674499.7692 | 1235990.7618
103 | 2674517.6103 | 1235800.9018 | 2674516.674 | 1235800.6542
104 | 2674509.7908 | 1235729.2585 | 2674509.0418 | 1235730.4151 | 2674502.5127 | 1235738.6926
105 | 2674512.8384 | 1235724.5528 | 2674509.7908 | 1235729.2585
106 | 2674513.6205 | 1235723.0194 | 2674512.8775 | 1235724.4924 | 2674512.8384 | 1235724.5528
107 | 2674500.5551 | 1236012.3466 | 2674494.0285 | 1236017.4239 | 2674486.3941 | 1236023.6097
108 | 2674500.5551 | 1236012.3466 | 2674509.685 | 1236016.9309 | 2674511.2346 | 1236017.639
109 | 2674459.1461 | 1236044.0717 | 2674481.0693 | 1236027.9242 | 2674486.3941 | 1236023.6097
110 | 2674515.1367 | 1236019.4219 | 2674511.2346 | 1236017.639
111 | 2674447.1418 | 1236052.9135 | 2674459.1461 | 1236044.0717
112 | 2674453.3032 | 1235960.1421 | 2674455.1228 | 1235959.0536
113 | 2674539.9755 | 1235903.8665 | 2674542.1201 | 1235899.4237
114 | 2674447.1418 | 1236052.9135 | 2674439.2416 | 1236058.7323 | 2674436.3614 | 1236061.8845
115 | 2674365.019 | 1236011.6744 | 2674397.9038 | 1235995.5535
116 | 2674397.9038 | 1235995.5535 | 2674421.0898 | 1235984.1871 | 2674429.6748 | 1235978.513 | 2674430.8729 | 1235977.402
117 | 2674430.8729 | 1235977.402 | 2674436.051 | 1235972.6002
118 | 2674445.4141 | 1235964.8614 | 2674442.5461 | 1235966.5771 | 2674436.051 | 1235972.6002
119 | 2674453.3032 | 1235960.1421 | 2674445.4141 | 1235964.8614
120 | 2674513.6205 | 1235723.0194 | 2674514.2634 | 1235721.7449
121 | 2674532.2073 | 1235696.7046 | 2674532.2073 | 1235696.7046 | 2674522.0125 | 1235706.3834 | 2674514.2634 | 1235721.7449
122 | 2674532.2073 | 1235696.7046 | 2674532.6658 | 1235696.0983
123 | 2674534.6683 | 1235693.45 | 2674532.6658 | 1235696.0983
124 | 2674536.0022 | 1235691.6859 | 2674534.6683 | 1235693.45
125 | 2674382.0098 | 1235769.0708 | 2674356.1345 | 1235783.8065
126 | 2674332.194 | 1235784.9378 | 2674343.3024 | 1235791.1143 | 2674356.1345 | 1235783.8065

## bus_geodata
| x | y | coords
0 | 2674433.3399 | 1235630.5423
1 | 2674432.1167 | 1235675.002
2 | 2674376.1068 | 1235616.7816
3 | 2674446.3639 | 1235636.7498
4 | 2674444.3353 | 1235662.6576
5 | 2674451.8836 | 1235718.5795
6 | 2674413.3252 | 1235683.3793
7 | 2674392.2265 | 1235752.1554
8 | 2674444.7437 | 1235751.6784
9 | 2674403.3927 | 1235688.9191
10 | 2674352.5038 | 1235717.3017
11 | 2674365.9175 | 1235709.8204
12 | 2674321.9032 | 1235734.3689
13 | 2674375.9946 | 1235704.2
14 | 2674393.7177 | 1235762.4033
15 | 2674440.7104 | 1235759.8345
16 | 2674374.2717 | 1235618.0903
17 | 2674305.8259 | 1235773.7602
18 | 2674311.9168 | 1235787.5304
19 | 2674315.0613 | 1235793.8852
20 | 2674336.3336 | 1235869.8906
21 | 2674350.6929 | 1235862.1221
22 | 2674360.6238 | 1235878.9556
23 | 2674374.261 | 1235849.0998
24 | 2674364.1239 | 1235887.1319
25 | 2674380.1643 | 1235845.838
26 | 2674363.6655 | 1235900.7221
27 | 2674387.2112 | 1235841.9443
28 | 2674394.9714 | 1235837.6565
29 | 2674406.3404 | 1235831.3747
30 | 2674418.0075 | 1235824.9281
31 | 2674423.3462 | 1235828.5302
32 | 2674454.6841 | 1235840.4982
33 | 2674439.8571 | 1235761.4629
34 | 2674452.2249 | 1235798.9218
35 | 2674448.0534 | 1235865.3322
36 | 2674477.1655 | 1235847.6539
37 | 2674445.1835 | 1235764.6382
38 | 2674451.2722 | 1235790.8881
39 | 2674434.9538 | 1235866.4262
40 | 2674494.2293 | 1235854.8147
41 | 2674473.5266 | 1235791.9687
42 | 2674429.5061 | 1235866.3758
43 | 2674502.79 | 1235853.2547
44 | 2674496.0644 | 1235869.4468
45 | 2674488.2089 | 1235793.1251
46 | 2674461.351 | 1235762.0229
47 | 2674510.5358 | 1235799.0306
48 | 2674496.0067 | 1235748.1193
49 | 2674419.3497 | 1235868.2109
50 | 2674411.2513 | 1235871.3764
51 | 2674398.0147 | 1235878.7666
52 | 2674383.7561 | 1235887.5307
53 | 2674705.5934 | 1235806.112
54 | 2674691.3939 | 1235792.1243
55 | 2674687.3702 | 1235796.2001
56 | 2674686.6592 | 1235796.9202
57 | 2674658.9217 | 1235825.0166
58 | 2674597.1191 | 1235787.0847
59 | 2674612.103 | 1235768.9654
60 | 2674595.8753 | 1235788.5888
61 | 2674618.9598 | 1235760.6737
62 | 2674573.5156 | 1235813.5697
63 | 2674584.3781 | 1235779.0359
64 | 2674628.64 | 1235748.9679
65 | 2674561.6561 | 1235804.3585
66 | 2674586.2851 | 1235823.5127
67 | 2674565.0369 | 1235762.9656
68 | 2674599.5639 | 1235840.5324
69 | 2674563.9454 | 1235762.0587
70 | 2674604.7522 | 1235859.1153
71 | 2674616.9736 | 1235845.3773
72 | 2674587.8233 | 1235852.6338
73 | 2674611.8485 | 1235865.342
74 | 2674628.3267 | 1235832.6153
75 | 2674565.1709 | 1235851.9136
76 | 2674618.6912 | 1235873.0777
77 | 2674587.1309 | 1235881.5181
78 | 2674524.7319 | 1235852.2275
79 | 2674630.536 | 1235886.2577
80 | 2674579.2257 | 1235886.1913
81 | 2674512.1727 | 1235761.6071
82 | 2674511.2473 | 1235760.7093
83 | 2674511.1542 | 1235760.6191
84 | 2674651.5773 | 1235907.759
85 | 2674653.4288 | 1235881.9525
86 | 2674672.6612 | 1235857.8451
87 | 2674668.8705 | 1235862.5968
88 | 2674524.4113 | 1235852.23
89 | 2674507.701 | 1235852.3597
90 | 2674496.0838 | 1235869.8729
91 | 2674496.7324 | 1235913.1987
92 | 2674496.1911 | 1235931.9034
93 | 2674472.2554 | 1235943.8338
94 | 2674495.552 | 1235951.5495
95 | 2674469.4787 | 1235946.9758
96 | 2674499.7692 | 1235990.7618
97 | 2674516.674 | 1235800.6542
98 | 2674517.6103 | 1235800.9018
99 | 2674502.5127 | 1235738.6926
100 | 2674509.7908 | 1235729.2585
101 | 2674512.8384 | 1235724.5528
102 | 2674500.5551 | 1236012.3466
103 | 2674486.3941 | 1236023.6097
104 | 2674511.2346 | 1236017.639
105 | 2674459.1461 | 1236044.0717
106 | 2674515.1367 | 1236019.4219
107 | 2674455.1228 | 1235959.0536
108 | 2674542.1201 | 1235899.4237
109 | 2674539.9755 | 1235903.8665
110 | 2674447.1418 | 1236052.9135
111 | 2674436.3614 | 1236061.8845
112 | 2674365.019 | 1236011.6744
113 | 2674397.9038 | 1235995.5535
114 | 2674430.8729 | 1235977.402
115 | 2674436.051 | 1235972.6002
116 | 2674445.4141 | 1235964.8614
117 | 2674453.3032 | 1235960.1421
118 | 2674513.6205 | 1235723.0194
119 | 2674514.2634 | 1235721.7449
120 | 2674532.2073 | 1235696.7046
121 | 2674532.6658 | 1235696.0983
122 | 2674534.6683 | 1235693.45
123 | 2674536.0022 | 1235691.6859
124 | 2674382.0098 | 1235769.0708
125 | 2674356.1345 | 1235783.8065
126 | 2674332.194 | 1235784.9378
127 | 2674326.9483 | 1235829.7585
128 | 2674451.2722 | 1235790.8881

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99122 | -0.16844 | 0 | 0
1 | 0.99127 | -0.16762 | 0 | 0
2 | 0.99117 | -0.16951 | 0.00043236 | 0.00010836
3 | 0.9912 | -0.16899 | 0.0017808 | 0.00044632
4 | 0.99124 | -0.16817 | 0 | 0
5 | 0.99356 | -0.12333 | 0 | 0
6 | 0.99033 | -0.18569 | 0.0018111 | 0.00045391
7 | 0.99228 | -0.14804 | 0 | 0
8 | 0.99583 | -0.07968 | 0.0012124 | 0.00030385
9 | 0.98983 | -0.19533 | 0.0054987 | 0.0013781
10 | 0.98803 | -0.23045 | 0.0064573 | 0.0016183
11 | 0.98825 | -0.22612 | 0.019385 | 0.0048582
12 | 0.98773 | -0.23628 | 0.009318 | 0.0023353
13 | 0.98862 | -0.21888 | 0.0069914 | 0.0017522
14 | 0.99209 | -0.1518 | 0.0034698 | 0.00086962
15 | 0.99645 | -0.067856 | 0 | 0
16 | 0.99117 | -0.16953 | 0.00058728 | 0.00014719
17 | 0.99138 | -0.16562 | 0.0028327 | 0.00070995
18 | 0.99142 | -0.16486 | 0 | 0
19 | 0.99143 | -0.16451 | 0 | 0
20 | 0.99411 | -0.11288 | 0.0021162 | 0.00053037
21 | 0.99414 | -0.11227 | 0 | 0
22 | 0.99401 | -0.11476 | 0.0027193 | 0.00068153
23 | 0.99437 | -0.10785 | 0.0013517 | 0.00033878
24 | 0.99398 | -0.11548 | 0.0020641 | 0.00051732
25 | 0.99444 | -0.10658 | 0.00087998 | 0.00022054
26 | 0.99394 | -0.11607 | 0.0024282 | 0.00060857
27 | 0.99452 | -0.10493 | 0.0014464 | 0.00036251
28 | 0.99463 | -0.1029 | 0.0017047 | 0.00042724
29 | 0.9948 | -0.099536 | 0.0016107 | 0.00040367
30 | 0.995 | -0.095704 | 0 | 0
31 | 0.99509 | -0.093846 | 0.0011552 | 0.00028952
32 | 0.99563 | -0.083519 | 0 | 0
33 | 0.99645 | -0.067896 | 0.00122 | 0.00030576
34 | 1 | 0 | -0.21862 | -0.055068
35 | 0.99529 | -0.089999 | 0.0022034 | 0.00055221
36 | 0.99384 | -0.11784 | 0.0017354 | 0.00043494
37 | 0.9969 | -0.059211 | 0 | 0
38 | 0.99925 | -0.014243 | 0 | 0
39 | 0.99515 | -0.092795 | 0.0022981 | 0.00057596
40 | 0.99246 | -0.14444 | 0 | 0
41 | 0.99911 | -0.017042 | 0.0019417 | 0.00048664
42 | 0.9951 | -0.093726 | 0.0018749 | 0.0004699
43 | 0.99211 | -0.15124 | 0.00066751 | 0.00016729
44 | 0.99196 | -0.1541 | 0.0026761 | 0.00067069
45 | 0.99904 | -0.018396 | 0.0025054 | 0.00062792
46 | 0.99662 | -0.064584 | 0.0016028 | 0.0004017
47 | 0.99898 | -0.019504 | 0.00088501 | 0.00022181
48 | 0.99602 | -0.076279 | 0 | 0
49 | 0.99503 | -0.09516 | 0.0013233 | 0.00033165
50 | 0.99498 | -0.096154 | 0.00087456 | 0.00021918
51 | 0.9949 | -0.097657 | 0.0028972 | 0.00072612
52 | 0.99486 | -0.098458 | 0.0027176 | 0.0006811
53 | 0.98656 | -0.25891 | 0.0023617 | 0.00059189
54 | 0.9866 | -0.25806 | 0.001383 | 0.00034662
55 | 0.98662 | -0.25768 | 0.0017207 | 0.00043125
56 | 0.98662 | -0.25758 | 0.001386 | 0.00034736
57 | 0.98687 | -0.25274 | 0 | 0
58 | 0.98634 | -0.26303 | 0.0020201 | 0.00050628
59 | 0.98621 | -0.26558 | 0.0016936 | 0.00042444
60 | 0.98636 | -0.26274 | 0 | 0
61 | 0.98617 | -0.26643 | 0.0021661 | 0.00054288
62 | 0.98694 | -0.25147 | 0 | 0
63 | 0.98621 | -0.2656 | 0.0020548 | 0.00051497
64 | 0.98614 | -0.26703 | 0.0022064 | 0.00055297
65 | 0.98689 | -0.25229 | 0.0030569 | 0.00076613
66 | 0.98726 | -0.24514 | 0.0019475 | 0.00048809
67 | 0.98601 | -0.26947 | 0.003448 | 0.00086415
68 | 0.98773 | -0.23593 | 0.0002747 | 6.8845e-05
69 | 0.986 | -0.26961 | 0.0051536 | 0.0012916
70 | 0.98818 | -0.22723 | 0 | 0
71 | 0.98817 | -0.22755 | 0.00061785 | 0.00015485
72 | 0.98885 | -0.21431 | 0.0014629 | 0.00036664
73 | 0.98806 | -0.22969 | 0 | 0
74 | 0.98816 | -0.22765 | 0.00034025 | 8.5275e-05
75 | 0.9897 | -0.1977 | 0 | 0
76 | 0.98798 | -0.23124 | 0 | 0
77 | 0.98789 | -0.23296 | 0.00081663 | 0.00020467
78 | 0.99123 | -0.1682 | 0.00084233 | 0.00021111
79 | 0.98784 | -0.23391 | 0.00024275 | 6.0839e-05
80 | 0.98784 | -0.23384 | 0.00048893 | 0.00012254
81 | 0.99596 | -0.077261 | 0.00092874 | 0.00023276
82 | 0.99597 | -0.07724 | 0.00091583 | 0.00022953
83 | 0.99597 | -0.077236 | 0.0009289 | 0.00023281
84 | 0.98761 | -0.23834 | 0 | 0
85 | 0.98738 | -0.24289 | 0.00066379 | 0.00016636
86 | 0.98717 | -0.24697 | 0 | 0
87 | 0.98721 | -0.24622 | 0.00066521 | 0.00016672
88 | 0.99124 | -0.16797 | 0.00158 | 0.00039598
89 | 0.99191 | -0.15508 | 0 | 0
90 | 0.99195 | -0.15436 | 0.002224 | 0.00055739
91 | 0.99068 | -0.17881 | 0.0018723 | 0.00046923
92 | 0.99017 | -0.18875 | 0 | 0
93 | 0.98993 | -0.19351 | 0.00053334 | 0.00013367
94 | 0.98981 | -0.19573 | 0.0020662 | 0.00051785
95 | 0.98989 | -0.19422 | 0.0011616 | 0.00029113
96 | 0.98916 | -0.20837 | 0.0030347 | 0.00076056
97 | 0.99897 | -0.01971 | 0.0011589 | 0.00029045
98 | 0.99897 | -0.019722 | 0.00070154 | 0.00017582
99 | 0.99587 | -0.079146 | 0.00082745 | 0.00020738
100 | 0.99572 | -0.081946 | 0.00092332 | 0.00023141
101 | 0.99566 | -0.083172 | 0.0009306 | 0.00023323
102 | 0.98887 | -0.21409 | 0 | 0
103 | 0.98865 | -0.21821 | 0.0027928 | 0.00069994
104 | 0.98884 | -0.21453 | 0.0010378 | 0.00026009
105 | 0.98834 | -0.22428 | 0.0011632 | 0.00029154
106 | 0.98884 | -0.21461 | 0.001027 | 0.0002574
107 | 0.98975 | -0.19701 | 0.0007195 | 0.00018032
108 | 0.98763 | -0.238 | 0.0021787 | 0.00054603
109 | 0.98762 | -0.23824 | 0.0026879 | 0.00067366
110 | 0.98822 | -0.22663 | 0.0074489 | 0.0018669
111 | 0.9882 | -0.22697 | 0.0013708 | 0.00034356
112 | 0.98932 | -0.20536 | 0.0027289 | 0.00068393
113 | 0.98941 | -0.20358 | 0.0021418 | 0.00053679
114 | 0.98958 | -0.2003 | 0.00058996 | 0.00014786
115 | 0.98961 | -0.19961 | 0.00037879 | 9.4932e-05
116 | 0.98968 | -0.19835 | 0.0005619 | 0.00014083
117 | 0.98973 | -0.1973 | 0.0011509 | 0.00028844
118 | 0.99564 | -0.083521 | 0.0050721 | 0.0012712
119 | 0.99563 | -0.083682 | 0.00093761 | 0.00023499
120 | 0.99548 | -0.086706 | 0.0018549 | 0.00046488
121 | 0.99547 | -0.086755 | 0.00092955 | 0.00023297
122 | 0.99546 | -0.086913 | 0.00092068 | 0.00023074
123 | 0.99546 | -0.086983 | 0.001794 | 0.00044961
124 | 0.99188 | -0.15585 | 0.0099502 | 0.0024938
125 | 0.99169 | -0.15957 | 0.0010819 | 0.00027116
126 | 0.99154 | -0.16247 | 0 | 0
127 | 0.99132 | -0.16664 | 0.0031226 | 0.0007826
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010197 | -0.00025479 | 0.0010197 | 0.00025423 | 3.9867e-08 | -5.5963e-07 | 0.0015305 | 0.0015303 | 0.0015305 | 0.99122 | -0.16844 | 0.99127 | -0.16762 | 0.42046
1 | 0.0010197 | 0.00025479 | -0.0010196 | -0.00025552 | 5.1715e-08 | -7.2562e-07 | 0.0015305 | 0.0015307 | 0.0015307 | 0.99122 | -0.16844 | 0.99117 | -0.16951 | 0.42054
2 | -0.052392 | -0.013178 | 0.052503 | 0.013248 | 0.00011109 | 7.0479e-05 | 0.078664 | 0.078663 | 0.078664 | 0.99127 | -0.16762 | 0.99356 | -0.12333 | 21.6109
3 | 0.049591 | 0.012478 | -0.049548 | -0.012451 | 4.2794e-05 | 2.7123e-05 | 0.07446 | 0.07446 | 0.07446 | 0.99127 | -0.16762 | 0.99033 | -0.18569 | 20.4561
4 | 0.001781 | 0.00044583 | -0.0017809 | -0.00044603 | 4.6483e-08 | -1.9384e-07 | 0.0026733 | 0.0026733 | 0.0026733 | 0.99127 | -0.16762 | 0.99124 | -0.16817 | 0.73443
5 | 0.00058728 | 0.00014716 | -0.00058728 | -0.00014719 | 6.5706e-10 | -2.863e-08 | 0.00088166 | 0.00088167 | 0.00088167 | 0.99117 | -0.16951 | 0.99117 | -0.16953 | 0.24222
6 | -0.0017808 | -0.00044632 | 0.0017809 | 0.00044603 | 6.9649e-08 | -2.904e-07 | 0.0026735 | 0.0026733 | 0.0026735 | 0.9912 | -0.16899 | 0.99124 | -0.16817 | 0.73446
7 | 0.020492 | 0.005146 | -0.020467 | -0.0051315 | 2.4132e-05 | 1.4561e-05 | 0.030693 | 0.030693 | 0.030693 | 0.99356 | -0.12333 | 0.99228 | -0.14804 | 8.4322
8 | -0.072995 | -0.018394 | 0.073147 | 0.018492 | 0.00015278 | 9.7336e-05 | 0.10936 | 0.10936 | 0.10936 | 0.99356 | -0.12333 | 0.99583 | -0.07968 | 30.043
9 | 0.047737 | 0.011997 | -0.047715 | -0.011983 | 2.1949e-05 | 1.3901e-05 | 0.071739 | 0.071739 | 0.071739 | 0.99033 | -0.18569 | 0.98983 | -0.19533 | 19.7085
10 | 0.020467 | 0.0051315 | -0.020464 | -0.0051292 | 3.6585e-06 | 2.2077e-06 | 0.030693 | 0.030693 | 0.030693 | 0.99228 | -0.14804 | 0.99209 | -0.1518 | 8.4322
11 | -0.07436 | -0.018796 | 0.074402 | 0.018822 | 4.2183e-05 | 2.6879e-05 | 0.11117 | 0.11117 | 0.11117 | 0.99583 | -0.07968 | 0.99645 | -0.067856 | 30.5406
12 | 0.042217 | 0.010605 | -0.042169 | -0.010575 | 4.7396e-05 | 2.9931e-05 | 0.063473 | 0.063473 | 0.063473 | 0.98983 | -0.19533 | 0.98862 | -0.21888 | 17.4376
13 | -0.015778 | -0.0039549 | 0.015781 | 0.0039568 | 3.2522e-06 | 1.8847e-06 | 0.023762 | 0.023762 | 0.023762 | 0.98803 | -0.23045 | 0.98825 | -0.22612 | 6.5281
14 | 0.0093206 | 0.0023365 | -0.009318 | -0.0023353 | 2.5892e-06 | 1.2085e-06 | 0.014037 | 0.014038 | 0.014038 | 0.98803 | -0.23045 | 0.98773 | -0.23628 | 3.8565
15 | -0.035166 | -0.008815 | 0.035178 | 0.0088226 | 1.2131e-05 | 7.6162e-06 | 0.05295 | 0.05295 | 0.05295 | 0.98825 | -0.22612 | 0.98862 | -0.21888 | 14.5467
16 | 0.016994 | 0.0042596 | -0.016991 | -0.0042577 | 3.2826e-06 | 1.9269e-06 | 0.025489 | 0.025489 | 0.025489 | 0.99209 | -0.1518 | 0.99188 | -0.15585 | 7.0025
17 | -0.075622 | -0.019128 | 0.075653 | 0.019148 | 3.1382e-05 | 1.9999e-05 | 0.11299 | 0.11299 | 0.11299 | 0.99645 | -0.067856 | 0.9969 | -0.059211 | 31.0411
18 | 0.00122 | 0.00030574 | -0.00122 | -0.00030576 | 2.2884e-09 | -2.2484e-08 | 0.0018218 | 0.0018218 | 0.0018218 | 0.99645 | -0.067856 | 0.99645 | -0.067896 | 0.50051
19 | -0.0028327 | -0.00070995 | 0.0028328 | 0.00070982 | 1.0207e-07 | -1.2883e-07 | 0.0042518 | 0.0042518 | 0.0042518 | 0.99138 | -0.16562 | 0.99142 | -0.16486 | 1.1681
20 | -0.0028328 | -0.00070982 | 0.0028329 | 0.00070976 | 4.8043e-08 | -6.0641e-08 | 0.0042518 | 0.0042517 | 0.0042518 | 0.99142 | -0.16486 | 0.99143 | -0.16451 | 1.1681
21 | 0.0031229 | 0.00078231 | -0.0031226 | -0.0007826 | 3.1815e-07 | -2.9433e-07 | 0.004687 | 0.0046872 | 0.0046872 | 0.99143 | -0.16451 | 0.99132 | -0.16664 | 1.2877
22 | -0.0059558 | -0.0014921 | 0.0059564 | 0.0014922 | 5.7783e-07 | 1.2109e-07 | 0.0089387 | 0.0089386 | 0.0089387 | 0.99143 | -0.16451 | 0.99154 | -0.16247 | 2.4557
23 | -0.0021162 | -0.00053037 | 0.0021163 | 0.0005302 | 6.1427e-08 | -1.7236e-07 | 0.0031676 | 0.0031675 | 0.0031676 | 0.99411 | -0.11288 | 0.99414 | -0.11227 | 0.87022
24 | 0.0072128 | 0.0018076 | -0.0072119 | -0.0018073 | 8.5425e-07 | 2.9333e-07 | 0.010796 | 0.010796 | 0.010796 | 0.99414 | -0.11227 | 0.99401 | -0.11476 | 2.9659
25 | -0.009329 | -0.0023378 | 0.009331 | 0.0023387 | 1.9688e-06 | 9.1079e-07 | 0.013963 | 0.013963 | 0.013963 | 0.99414 | -0.11227 | 0.99437 | -0.10785 | 3.8361
26 | 0.0044926 | 0.0011257 | -0.0044924 | -0.0011258 | 1.5364e-07 | -1.9088e-08 | 0.0067252 | 0.0067253 | 0.0067253 | 0.99401 | -0.11476 | 0.99398 | -0.11548 | 1.8476
27 | -0.010683 | -0.0026774 | 0.010683 | 0.0026778 | 6.4635e-07 | 3.2617e-07 | 0.015986 | 0.015986 | 0.015986 | 0.99437 | -0.10785 | 0.99444 | -0.10658 | 4.3918
28 | 0.0024283 | 0.00060844 | -0.0024282 | -0.00060857 | 6.8207e-08 | -1.3474e-07 | 0.0036352 | 0.0036353 | 0.0036353 | 0.99398 | -0.11548 | 0.99394 | -0.11607 | 0.9987
29 | -0.011563 | -0.0028983 | 0.011564 | 0.0028988 | 9.039e-07 | 4.7403e-07 | 0.017303 | 0.017303 | 0.017303 | 0.99444 | -0.10658 | 0.99452 | -0.10493 | 4.7535
30 | -0.013011 | -0.0032613 | 0.013012 | 0.003262 | 1.2599e-06 | 6.9131e-07 | 0.019467 | 0.019467 | 0.019467 | 0.99452 | -0.10493 | 0.99463 | -0.1029 | 5.3481
31 | -0.014717 | -0.0036892 | 0.014719 | 0.0036906 | 2.3612e-06 | 1.3426e-06 | 0.022017 | 0.022017 | 0.022017 | 0.99463 | -0.1029 | 0.9948 | -0.099536 | 6.0487
32 | -0.01633 | -0.0040942 | 0.016333 | 0.004096 | 2.9824e-06 | 1.7357e-06 | 0.024426 | 0.024426 | 0.024426 | 0.9948 | -0.099536 | 0.995 | -0.095704 | 6.7106
33 | -0.016333 | -0.004096 | 0.016334 | 0.0040968 | 1.4461e-06 | 8.4156e-07 | 0.024426 | 0.024426 | 0.024426 | 0.995 | -0.095704 | 0.99509 | -0.093846 | 6.7105
34 | -0.017489 | -0.0043863 | 0.017498 | 0.0043914 | 8.6131e-06 | 5.0759e-06 | 0.026154 | 0.026154 | 0.026154 | 0.99509 | -0.093846 | 0.99563 | -0.083519 | 7.1851
35 | -0.1148 | -0.028984 | 0.11526 | 0.029279 | 0.00046137 | 0.00029473 | 0.17165 | 0.17165 | 0.17165 | 0.99563 | -0.083519 | 1 | 0 | 47.1569
36 | 0.014197 | 0.0035598 | -0.014192 | -0.0035574 | 4.3826e-06 | 2.4674e-06 | 0.021218 | 0.021219 | 0.021219 | 0.99563 | -0.083519 | 0.99529 | -0.089999 | 5.8293
37 | 0.083106 | 0.021033 | -0.08297 | -0.020946 | 0.00013665 | 8.7149e-05 | 0.12428 | 0.12428 | 0.12428 | 0.99563 | -0.083519 | 0.99384 | -0.11784 | 34.1426
38 | 0.10171 | 0.025789 | -0.10164 | -0.025745 | 6.9582e-05 | 4.4427e-05 | 0.15145 | 0.15145 | 0.15145 | 1 | 0 | 0.99925 | -0.014243 | 41.6063
39 | 0.011989 | 0.0030052 | -0.011987 | -0.0030043 | 1.5973e-06 | 8.4998e-07 | 0.017924 | 0.017925 | 0.017925 | 0.99529 | -0.089999 | 0.99515 | -0.092795 | 4.9243
40 | 0.081234 | 0.020511 | -0.081131 | -0.020445 | 0.00010339 | 6.5931e-05 | 0.12168 | 0.12168 | 0.12168 | 0.99384 | -0.11784 | 0.99246 | -0.14444 | 33.4288
41 | 0.018586 | 0.004664 | -0.018582 | -0.0046612 | 4.7606e-06 | 2.8318e-06 | 0.027745 | 0.027745 | 0.027745 | 0.9969 | -0.059211 | 0.99662 | -0.064584 | 7.6222
42 | -0.09424 | -0.023812 | 0.094443 | 0.023942 | 0.00020363 | 0.00012996 | 0.14073 | 0.14073 | 0.14073 | 0.9969 | -0.059211 | 0.99925 | -0.014243 | 38.6633
43 | 0.0071941 | 0.0018027 | -0.0071931 | -0.0018024 | 9.5888e-07 | 3.2186e-07 | 0.010713 | 0.010713 | 0.010713 | 0.99925 | -0.014243 | 0.99911 | -0.017042 | 2.9431
44 | 0.0096894 | 0.0024283 | -0.009689 | -0.0024281 | 4.2934e-07 | 2.0392e-07 | 0.014488 | 0.014488 | 0.014488 | 0.99515 | -0.092795 | 0.9951 | -0.093726 | 3.9803
45 | 0.044348 | 0.011192 | -0.044334 | -0.011183 | 1.4439e-05 | 9.1284e-06 | 0.06652 | 0.06652 | 0.06652 | 0.99246 | -0.14444 | 0.99211 | -0.15124 | 18.2746
46 | 0.036783 | 0.0092532 | -0.036766 | -0.0092425 | 1.6969e-05 | 1.0668e-05 | 0.055161 | 0.055161 | 0.055161 | 0.99246 | -0.14444 | 0.99196 | -0.1541 | 15.1542
47 | 0.0052514 | 0.0013157 | -0.0052511 | -0.0013157 | 3.3875e-07 | 2.3414e-08 | 0.007821 | 0.0078211 | 0.0078211 | 0.99911 | -0.017042 | 0.99904 | -0.018396 | 2.1486
48 | 0.007814 | 0.0019582 | -0.0078135 | -0.001958 | 5.3392e-07 | 2.0624e-07 | 0.011685 | 0.011685 | 0.011685 | 0.9951 | -0.093726 | 0.99503 | -0.09516 | 3.2101
49 | 0.043666 | 0.011015 | -0.043658 | -0.01101 | 8.0357e-06 | 5.0784e-06 | 0.065518 | 0.065518 | 0.065518 | 0.99211 | -0.15124 | 0.99191 | -0.15508 | 17.9996
50 | 0.03409 | 0.0085718 | -0.034089 | -0.0085716 | 4.1842e-07 | 2.6229e-07 | 0.051147 | 0.051147 | 0.051147 | 0.99196 | -0.1541 | 0.99195 | -0.15436 | 14.0514
51 | 0.0027456 | 0.00068778 | -0.0027455 | -0.00068799 | 1.4483e-07 | -2.0969e-07 | 0.0040893 | 0.0040894 | 0.0040894 | 0.99904 | -0.018396 | 0.99898 | -0.019504 | 1.1235
52 | 0.016979 | 0.0042595 | -0.016969 | -0.0042539 | 9.4616e-06 | 5.5442e-06 | 0.025352 | 0.025352 | 0.025352 | 0.99662 | -0.064584 | 0.99602 | -0.076279 | 6.9648
53 | 0.0018605 | 0.00046619 | -0.0018604 | -0.00046626 | 1.8285e-08 | -7.1425e-08 | 0.0027712 | 0.0027712 | 0.0027712 | 0.99898 | -0.019504 | 0.99897 | -0.01971 | 0.76132
54 | 0.014196 | 0.003559 | -0.014194 | -0.0035579 | 1.939e-06 | 1.0914e-06 | 0.021208 | 0.021208 | 0.021208 | 0.99602 | -0.076279 | 0.99587 | -0.079146 | 5.8265
55 | 0.0027736 | 0.00069491 | -0.0027735 | -0.00069508 | 1.2646e-07 | -1.7468e-07 | 0.0041436 | 0.0041437 | 0.0041437 | 0.99602 | -0.076279 | 0.99597 | -0.077236 | 1.1384
56 | 0.0064902 | 0.0016264 | -0.0064899 | -0.0016263 | 3.0716e-07 | 8.3647e-08 | 0.0097058 | 0.0097058 | 0.0097058 | 0.99503 | -0.09516 | 0.99498 | -0.096154 | 2.6664
57 | 0.0056154 | 0.0014071 | -0.005615 | -0.0014071 | 4.0208e-07 | 5.9889e-08 | 0.0083979 | 0.0083979 | 0.0083979 | 0.99498 | -0.096154 | 0.9949 | -0.097657 | 2.3071
58 | 0.0027177 | 0.00068095 | -0.0027176 | -0.0006811 | 1.037e-07 | -1.5096e-07 | 0.0040647 | 0.0040648 | 0.0040648 | 0.9949 | -0.097657 | 0.99486 | -0.098458 | 1.1167
59 | -0.0023617 | -0.00059189 | 0.0023617 | 0.00059169 | 9.4836e-08 | -1.9382e-07 | 0.0035621 | 0.003562 | 0.0035621 | 0.98656 | -0.25891 | 0.9866 | -0.25806 | 0.97859
60 | -0.0037448 | -0.00093831 | 0.0037448 | 0.00093828 | 6.8509e-08 | -2.9293e-08 | 0.0056479 | 0.0056479 | 0.0056479 | 0.9866 | -0.25806 | 0.98662 | -0.25768 | 1.5516
61 | -0.0054655 | -0.0013695 | 0.0054656 | 0.0013695 | 2.5786e-08 | 3.5793e-09 | 0.008243 | 0.008243 | 0.008243 | 0.98662 | -0.25768 | 0.98662 | -0.25758 | 2.2646
62 | -0.0068516 | -0.0017169 | 0.0068531 | 0.0017174 | 1.5809e-06 | 5.0744e-07 | 0.010333 | 0.010333 | 0.010333 | 0.98662 | -0.25758 | 0.98687 | -0.25274 | 2.8388
63 | -0.0068531 | -0.0017174 | 0.006855 | 0.001718 | 1.8844e-06 | 6.0451e-07 | 0.010333 | 0.010333 | 0.010333 | 0.98687 | -0.25274 | 0.98717 | -0.24697 | 2.8388
64 | 0.0060671 | 0.0015203 | -0.0060663 | -0.0015201 | 7.3865e-07 | 1.7268e-07 | 0.0091528 | 0.0091529 | 0.0091529 | 0.98634 | -0.26303 | 0.98621 | -0.26558 | 2.5145
65 | -0.0080871 | -0.0020266 | 0.0080872 | 0.0020266 | 1.0894e-07 | 4.4811e-08 | 0.0122 | 0.0122 | 0.0122 | 0.98634 | -0.26303 | 0.98636 | -0.26274 | 3.3517
66 | 0.0043728 | 0.0010957 | -0.0043726 | -0.0010957 | 1.7563e-07 | -2.4881e-08 | 0.0065976 | 0.0065977 | 0.0065977 | 0.98621 | -0.26558 | 0.98617 | -0.26643 | 1.8125
67 | -0.018747 | -0.0046988 | 0.018757 | 0.0047048 | 1.0072e-05 | 6.0173e-06 | 0.028281 | 0.028281 | 0.028281 | 0.98636 | -0.26274 | 0.98694 | -0.25147 | 7.7696
68 | 0.010659 | 0.0026722 | -0.010658 | -0.0026714 | 1.4496e-06 | 7.3698e-07 | 0.016081 | 0.016081 | 0.016081 | 0.98636 | -0.26274 | 0.98621 | -0.2656 | 4.4179
69 | 0.0022065 | 0.00055282 | -0.0022064 | -0.00055297 | 6.3137e-08 | -1.5339e-07 | 0.0033292 | 0.0033293 | 0.0033293 | 0.98617 | -0.26643 | 0.98614 | -0.26703 | 0.91464
70 | 0.003057 | 0.00076601 | -0.0030569 | -0.00076613 | 1.1963e-07 | -1.1532e-07 | 0.004609 | 0.0046091 | 0.0046091 | 0.98694 | -0.25147 | 0.98689 | -0.25229 | 1.2662
71 | -0.021814 | -0.0054708 | 0.02182 | 0.0054748 | 6.5813e-06 | 4.0046e-06 | 0.03289 | 0.03289 | 0.03289 | 0.98694 | -0.25147 | 0.98726 | -0.24514 | 9.0358
72 | 0.0086032 | 0.0021565 | -0.0086016 | -0.0021558 | 1.589e-06 | 6.9614e-07 | 0.012981 | 0.012981 | 0.012981 | 0.98621 | -0.2656 | 0.98601 | -0.26947 | 3.5662
73 | -0.023768 | -0.0059629 | 0.023778 | 0.0059693 | 1.0442e-05 | 6.4051e-06 | 0.035825 | 0.035825 | 0.035825 | 0.98726 | -0.24514 | 0.98773 | -0.23593 | 9.8422
74 | 0.0051536 | 0.0012916 | -0.0051536 | -0.0012916 | 3.2189e-08 | 2.5015e-09 | 0.0077775 | 0.0077775 | 0.0077775 | 0.98601 | -0.26947 | 0.986 | -0.26961 | 2.1367
75 | -0.024053 | -0.0060382 | 0.024063 | 0.0060443 | 9.9859e-06 | 6.1313e-06 | 0.036239 | 0.036239 | 0.036239 | 0.98773 | -0.23593 | 0.98818 | -0.22723 | 9.9558
76 | 0.00095812 | 0.00023968 | -0.00095811 | -0.00023991 | 1.435e-08 | -2.2637e-07 | 0.0014426 | 0.0014427 | 0.0014427 | 0.98818 | -0.22723 | 0.98817 | -0.22755 | 0.39634
77 | -0.039631 | -0.0099467 | 0.039655 | 0.0099621 | 2.4443e-05 | 1.5409e-05 | 0.059681 | 0.059681 | 0.059681 | 0.98818 | -0.22723 | 0.98885 | -0.21431 | 16.396
78 | 0.014609 | 0.0036627 | -0.014608 | -0.0036618 | 1.7106e-06 | 9.7404e-07 | 0.022 | 0.022 | 0.022 | 0.98818 | -0.22723 | 0.98806 | -0.22969 | 6.0439
79 | 0.00034025 | 8.5057e-05 | -0.00034025 | -8.5275e-05 | 1.6813e-09 | -2.1774e-07 | 0.00051229 | 0.00051237 | 0.00051237 | 0.98817 | -0.22755 | 0.98816 | -0.22765 | 0.14076
80 | -0.041118 | -0.010329 | 0.041151 | 0.010349 | 3.2615e-05 | 2.0582e-05 | 0.061883 | 0.061882 | 0.061883 | 0.98885 | -0.21431 | 0.9897 | -0.1977 | 17.0007
81 | 0.0084334 | 0.0021146 | -0.0084328 | -0.0021144 | 6.24e-07 | 2.6726e-07 | 0.012701 | 0.012701 | 0.012701 | 0.98806 | -0.22969 | 0.98798 | -0.23124 | 3.4893
82 | 0.0061744 | 0.0015471 | -0.0061734 | -0.0015469 | 9.6056e-07 | 2.3539e-07 | 0.0092985 | 0.0092987 | 0.0092987 | 0.98806 | -0.22969 | 0.98789 | -0.23296 | 2.5546
83 | -0.041151 | -0.010349 | 0.041209 | 0.010386 | 5.8074e-05 | 3.6647e-05 | 0.061882 | 0.061882 | 0.061882 | 0.9897 | -0.1977 | 0.99123 | -0.1682 | 17.0007
84 | 0.0084328 | 0.0021144 | -0.0084317 | -0.0021139 | 1.072e-06 | 4.5919e-07 | 0.012701 | 0.012701 | 0.012701 | 0.98798 | -0.23124 | 0.98784 | -0.23391 | 3.4894
85 | 0.0053568 | 0.0013422 | -0.0053566 | -0.0013422 | 2.2419e-07 | 2.5913e-08 | 0.0080686 | 0.0080686 | 0.0080686 | 0.98789 | -0.23296 | 0.98784 | -0.23384 | 2.2167
86 | -0.042051 | -0.010597 | 0.042051 | 0.010597 | 4.7946e-07 | 3.0272e-07 | 0.063147 | 0.063147 | 0.063147 | 0.99123 | -0.1682 | 0.99124 | -0.16797 | 17.348
87 | 0.008189 | 0.0020531 | -0.0081872 | -0.0020523 | 1.7293e-06 | 7.1889e-07 | 0.012336 | 0.012336 | 0.012336 | 0.98784 | -0.23391 | 0.98761 | -0.23834 | 3.3889
88 | 0.0048676 | 0.0012197 | -0.0048667 | -0.0012197 | 9.6546e-07 | 4.9546e-09 | 0.0073322 | 0.0073324 | 0.0073324 | 0.98784 | -0.23384 | 0.98763 | -0.238 | 2.0144
89 | -0.00092874 | -0.00023276 | 0.00092874 | 0.00023275 | 9.3095e-10 | -1.6183e-08 | 0.0013876 | 0.0013876 | 0.0013876 | 0.99596 | -0.077261 | 0.99597 | -0.07724 | 0.3812
90 | -0.0018446 | -0.00046228 | 0.0018446 | 0.00046227 | 3.6967e-10 | -1.4503e-09 | 0.0027559 | 0.0027559 | 0.0027559 | 0.99597 | -0.07724 | 0.99597 | -0.077236 | 0.75711
91 | 0.0081872 | 0.0020523 | -0.0081855 | -0.0020516 | 1.7731e-06 | 7.3728e-07 | 0.012336 | 0.012336 | 0.012336 | 0.98761 | -0.23834 | 0.98738 | -0.24289 | 3.389
92 | 0.0075217 | 0.0018853 | -0.0075205 | -0.0018848 | 1.1931e-06 | 4.4695e-07 | 0.011336 | 0.011336 | 0.011336 | 0.98738 | -0.24289 | 0.98721 | -0.24622 | 3.1142
93 | -0.006855 | -0.001718 | 0.0068553 | 0.0017181 | 2.4338e-07 | 7.8045e-08 | 0.010333 | 0.010333 | 0.010333 | 0.98717 | -0.24697 | 0.98721 | -0.24622 | 2.8387
94 | -0.043631 | -0.010993 | 0.043658 | 0.01101 | 2.69e-05 | 1.7001e-05 | 0.065519 | 0.065518 | 0.065519 | 0.99124 | -0.16797 | 0.99191 | -0.15508 | 17.9996
95 | 0.031865 | 0.0080142 | -0.031828 | -0.007991 | 3.7168e-05 | 2.3229e-05 | 0.047811 | 0.047811 | 0.047811 | 0.99195 | -0.15436 | 0.99068 | -0.17881 | 13.1349
96 | 0.029956 | 0.0075217 | -0.029942 | -0.0075129 | 1.4209e-05 | 8.853e-06 | 0.044999 | 0.044999 | 0.044999 | 0.99068 | -0.17881 | 0.99017 | -0.18875 | 12.3624
97 | 0.0099723 | 0.0024995 | -0.0099701 | -0.0024984 | 2.261e-06 | 1.1018e-06 | 0.014986 | 0.014986 | 0.014986 | 0.99017 | -0.18875 | 0.98993 | -0.19351 | 4.1172
98 | 0.019969 | 0.0050134 | -0.019963 | -0.0050094 | 6.6397e-06 | 3.9967e-06 | 0.030013 | 0.030013 | 0.030013 | 0.99017 | -0.18875 | 0.98981 | -0.19573 | 8.2453
99 | 0.0094367 | 0.0023647 | -0.0094364 | -0.0023646 | 3.1638e-07 | 1.4858e-07 | 0.014185 | 0.014185 | 0.014185 | 0.98993 | -0.19351 | 0.98989 | -0.19422 | 3.8969
100 | 0.017896 | 0.0044915 | -0.017886 | -0.0044851 | 1.0786e-05 | 6.3929e-06 | 0.026907 | 0.026907 | 0.026907 | 0.98981 | -0.19573 | 0.98916 | -0.20837 | 7.3919
101 | 0.0082748 | 0.0020735 | -0.0082737 | -0.002073 | 1.1015e-06 | 4.6095e-07 | 0.012439 | 0.012439 | 0.012439 | 0.98989 | -0.19422 | 0.98975 | -0.19701 | 3.4172
102 | 0.014851 | 0.0037246 | -0.014847 | -0.0037223 | 4.0447e-06 | 2.3113e-06 | 0.022342 | 0.022342 | 0.022342 | 0.98916 | -0.20837 | 0.98887 | -0.21409 | 6.1378
103 | 0.00070154 | 0.00017581 | -0.00070154 | -0.00017582 | 3.9653e-10 | -1.2425e-08 | 0.001045 | 0.001045 | 0.001045 | 0.99897 | -0.01971 | 0.99897 | -0.019722 | 0.28708
104 | 0.013366 | 0.0033505 | -0.013364 | -0.0033495 | 1.7831e-06 | 9.8609e-07 | 0.019972 | 0.019972 | 0.019972 | 0.99587 | -0.079146 | 0.99572 | -0.081946 | 5.4868
105 | 0.012441 | 0.0031181 | -0.01244 | -0.0031178 | 7.2672e-07 | 3.9219e-07 | 0.018592 | 0.018592 | 0.018592 | 0.99572 | -0.081946 | 0.99566 | -0.083172 | 5.1078
106 | 0.01151 | 0.0028845 | -0.01151 | -0.0028844 | 1.9105e-07 | 9.9877e-08 | 0.017201 | 0.017201 | 0.017201 | 0.99566 | -0.083172 | 0.99564 | -0.083521 | 4.7257
107 | 0.012782 | 0.003205 | -0.01278 | -0.0032036 | 2.5105e-06 | 1.3746e-06 | 0.019235 | 0.019235 | 0.019235 | 0.98887 | -0.21409 | 0.98865 | -0.21821 | 5.2843
108 | 0.0020648 | 0.00051731 | -0.0020648 | -0.00051743 | 4.3152e-08 | -1.253e-07 | 0.003107 | 0.0031071 | 0.0031071 | 0.98887 | -0.21409 | 0.98884 | -0.21453 | 0.85359
109 | 0.0099868 | 0.0025036 | -0.0099839 | -0.0025022 | 2.8877e-06 | 1.4112e-06 | 0.015031 | 0.015031 | 0.015031 | 0.98865 | -0.21821 | 0.98834 | -0.22428 | 4.1295
110 | 0.001027 | 0.00025734 | -0.001027 | -0.0002574 | 3.8424e-09 | -5.2574e-08 | 0.0015454 | 0.0015455 | 0.0015455 | 0.98884 | -0.21453 | 0.98884 | -0.21461 | 0.42458
111 | 0.0088207 | 0.0022107 | -0.0088197 | -0.0022103 | 9.8602e-07 | 4.4002e-07 | 0.01328 | 0.01328 | 0.01328 | 0.98834 | -0.22428 | 0.98822 | -0.22663 | 3.6484
112 | 0.0075542 | 0.0018927 | -0.0075541 | -0.0018926 | 1.0255e-07 | 3.8386e-08 | 0.011357 | 0.011357 | 0.011357 | 0.98975 | -0.19701 | 0.98973 | -0.1973 | 3.1201
113 | 0.002688 | 0.00067362 | -0.0026879 | -0.00067366 | 3.0342e-08 | -4.371e-08 | 0.0040498 | 0.0040499 | 0.0040499 | 0.98763 | -0.238 | 0.98762 | -0.23824 | 1.1126
114 | 0.0013708 | 0.00034339 | -0.0013708 | -0.00034356 | 2.2498e-08 | -1.6601e-07 | 0.0020641 | 0.0020641 | 0.0020641 | 0.98822 | -0.22663 | 0.9882 | -0.22697 | 0.56707
115 | -0.0027289 | -0.00068393 | 0.0027292 | 0.00068361 | 2.3137e-07 | -3.2223e-07 | 0.0041045 | 0.0041044 | 0.0041045 | 0.98932 | -0.20536 | 0.98941 | -0.20358 | 1.1276
116 | -0.004871 | -0.0012204 | 0.0048717 | 0.0012204 | 7.5959e-07 | 1.2804e-09 | 0.0073255 | 0.0073254 | 0.0073255 | 0.98941 | -0.20358 | 0.98958 | -0.2003 | 2.0125
117 | -0.0054617 | -0.0013683 | 0.0054619 | 0.0013683 | 1.7861e-07 | 2.358e-08 | 0.0082125 | 0.0082125 | 0.0082125 | 0.98958 | -0.2003 | 0.98961 | -0.19961 | 2.2562
118 | -0.0058407 | -0.0014632 | 0.005841 | 0.0014633 | 3.5284e-07 | 6.9059e-08 | 0.008782 | 0.008782 | 0.008782 | 0.98961 | -0.19961 | 0.98968 | -0.19835 | 2.4126
119 | -0.0064029 | -0.0016041 | 0.0064032 | 0.0016042 | 3.1948e-07 | 8.6334e-08 | 0.0096268 | 0.0096267 | 0.0096268 | 0.98968 | -0.19835 | 0.98973 | -0.1973 | 2.6447
120 | 0.0064376 | 0.0016132 | -0.0064375 | -0.0016132 | 4.955e-08 | 1.3148e-08 | 0.0096211 | 0.0096211 | 0.0096211 | 0.99564 | -0.083521 | 0.99563 | -0.083682 | 2.6432
121 | 0.0054999 | 0.0013782 | -0.0054991 | -0.0013781 | 7.9212e-07 | 1.0045e-07 | 0.0082198 | 0.00822 | 0.00822 | 0.99563 | -0.083682 | 0.99548 | -0.086706 | 2.2582
122 | 0.0036442 | 0.00091326 | -0.0036442 | -0.00091326 | 8.4585e-09 | -4.4691e-09 | 0.0054473 | 0.0054473 | 0.0054473 | 0.99548 | -0.086706 | 0.99547 | -0.086755 | 1.4965
123 | 0.0027147 | 0.0006803 | -0.0027146 | -0.00068033 | 2.0501e-08 | -3.0044e-08 | 0.0040578 | 0.0040578 | 0.0040578 | 0.99547 | -0.086755 | 0.99546 | -0.086913 | 1.1148
124 | 0.001794 | 0.00044958 | -0.001794 | -0.00044961 | 5.9639e-09 | -2.4935e-08 | 0.0026816 | 0.0026816 | 0.0026816 | 0.99546 | -0.086913 | 0.99546 | -0.086983 | 0.73671
125 | 0.0070404 | 0.0017639 | -0.0070392 | -0.0017635 | 1.2457e-06 | 4.1295e-07 | 0.010562 | 0.010562 | 0.010562 | 0.99188 | -0.15585 | 0.99169 | -0.15957 | 2.9016
126 | 0.0059572 | 0.0014924 | -0.0059564 | -0.0014922 | 8.2327e-07 | 1.7243e-07 | 0.0089385 | 0.0089386 | 0.0089386 | 0.99169 | -0.15957 | 0.99154 | -0.16247 | 2.4557

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.22063 | 0.055572

## res_load
| p_mw | q_mvar
0 | 0.00043236 | 0.00010836
1 | 0.0017808 | 0.00044632
2 | 0.0018111 | 0.00045391
3 | 0.0012124 | 0.00030385
4 | 0.0054987 | 0.0013781
5 | 0.0064573 | 0.0016183
6 | 0.019385 | 0.0048582
7 | 0.009318 | 0.0023353
8 | 0.0069914 | 0.0017522
9 | 0.0034698 | 0.00086962
10 | 0.00058728 | 0.00014719
11 | 0.0028327 | 0.00070995
12 | 0.0021162 | 0.00053037
13 | 0.0027193 | 0.00068153
14 | 0.0013517 | 0.00033878
15 | 0.0020641 | 0.00051732
16 | 0.00087998 | 0.00022054
17 | 0.0024282 | 0.00060857
18 | 0.0014464 | 0.00036251
19 | 0.0017047 | 0.00042724
20 | 0.0016107 | 0.00040367
21 | 0.0011552 | 0.00028952
22 | 0.00122 | 0.00030576
23 | 0.0020109 | 0.00050398
24 | 0.0022034 | 0.00055221
25 | 0.0017354 | 0.00043494
26 | 0.0022981 | 0.00057596
27 | 0.0019417 | 0.00048664
28 | 0.0018749 | 0.0004699
29 | 0.00066751 | 0.00016729
30 | 0.0026761 | 0.00067069
31 | 0.0025054 | 0.00062792
32 | 0.0016028 | 0.0004017
33 | 0.00088501 | 0.00022181
34 | 0.0013233 | 0.00033165
35 | 0.00087456 | 0.00021918
36 | 0.0028972 | 0.00072612
37 | 0.0027176 | 0.0006811
38 | 0.0023617 | 0.00059189
39 | 0.001383 | 0.00034662
40 | 0.0017207 | 0.00043125
41 | 0.001386 | 0.00034736
42 | 0.0020201 | 0.00050628
43 | 0.0016936 | 0.00042444
44 | 0.0021661 | 0.00054288
45 | 0.0020548 | 0.00051497
46 | 0.0022064 | 0.00055297
47 | 0.0030569 | 0.00076613
48 | 0.0019475 | 0.00048809
49 | 0.003448 | 0.00086415
50 | 0.0002747 | 6.8845e-05
51 | 0.0051536 | 0.0012916
52 | 0.00061785 | 0.00015485
53 | 0.0014629 | 0.00036664
54 | 0.00034025 | 8.5275e-05
55 | 0.00081663 | 0.00020467
56 | 0.00084233 | 0.00021111
57 | 0.00024275 | 6.0839e-05
58 | 0.00048893 | 0.00012254
59 | 0.00092874 | 0.00023276
60 | 0.00091583 | 0.00022953
61 | 0.0009289 | 0.00023281
62 | 0.00066379 | 0.00016636
63 | 0.00066521 | 0.00016672
64 | 0.00158 | 0.00039598
65 | 0.002224 | 0.00055739
66 | 0.0018723 | 0.00046923
67 | 0.00053334 | 0.00013367
68 | 0.0020662 | 0.00051785
69 | 0.0011616 | 0.00029113
70 | 0.0030347 | 0.00076056
71 | 0.0011589 | 0.00029045
72 | 0.00070154 | 0.00017582
73 | 0.00082745 | 0.00020738
74 | 0.00092332 | 0.00023141
75 | 0.0009306 | 0.00023323
76 | 0.0027928 | 0.00069994
77 | 0.0010378 | 0.00026009
78 | 0.0011632 | 0.00029154
79 | 0.001027 | 0.0002574
80 | 0.0007195 | 0.00018032
81 | 0.0021787 | 0.00054603
82 | 0.0026879 | 0.00067366
83 | 0.0074489 | 0.0018669
84 | 0.0013708 | 0.00034356
85 | 0.0027289 | 0.00068393
86 | 0.0021418 | 0.00053679
87 | 0.00058996 | 0.00014786
88 | 0.00037879 | 9.4932e-05
89 | 0.0005619 | 0.00014083
90 | 0.0011509 | 0.00028844
91 | 0.0050721 | 0.0012712
92 | 0.00093761 | 0.00023499
93 | 0.0018549 | 0.00046488
94 | 0.00092955 | 0.00023297
95 | 0.00092068 | 0.00023074
96 | 0.001794 | 0.00044961
97 | 0.0099502 | 0.0024938
98 | 0.0010819 | 0.00027116
99 | 0.0031226 | 0.0007826

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1