## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_10-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_10-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_10-9_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_10-9_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_10-9_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_10-9_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_10-9_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_10-9_0_3_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_10-9_0_3_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_10-9_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_10-9_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_10-9_0_3_node_81 | 0.4 | n |  | TRUE
12 | bus_LV_10-9_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_10-9_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_10-9_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_10-9_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_10-9_0_3_node_75 | 0.4 | n |  | TRUE
17 | bus_LV_10-9_0_3_node_82 | 0.4 | n |  | TRUE
18 | bus_LV_10-9_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_10-9_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_10-9_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_10-9_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_10-9_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_10-9_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_10-9_0_3_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_10-9_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_10-9_0_3_node_84 | 0.4 | n |  | TRUE
27 | bus_LV_10-9_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_10-9_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_10-9_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_10-9_0_3_node_92 | 0.4 | n |  | TRUE
31 | bus_LV_10-9_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_10-9_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_10-9_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_10-9_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_10-9_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_10-9_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_10-9_0_3_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_10-9_0_3_node_88 | 0.4 | n |  | TRUE
39 | bus_LV_10-9_0_3_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_10-9_0_3_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_10-9_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_10-9_0_3_node_50 | 0.4 | n |  | TRUE
43 | bus_LV_10-9_0_3_node_89 | 0.4 | n |  | TRUE
44 | bus_LV_10-9_0_3_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_10-9_0_3_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_10-9_0_3_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_10-9_0_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_10-9_0_3_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_10-9_0_3_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_10-9_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_10-9_0_3_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_10-9_0_3_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_10-9_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_10-9_0_3_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_10-9_0_3_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_10-9_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_10-9_0_3_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_10-9_0_3_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_10-9_0_3_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_10-9_0_3_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_10-9_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_10-9_0_3_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_10-9_0_3_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_10-9_0_3_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_10-9_0_3_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_10-9_0_3_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_10-9_0_3_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_10-9_0_3_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_10-9_0_3_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_10-9_0_3_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_10-9_0_3_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_10-9_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_10-9_0_3_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_10-9_0_3_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_10-9_0_3_node_79 | 0.4 | n |  | TRUE
76 | bus_LV_10-9_0_3_node_80 | 0.4 | n |  | TRUE
77 | bus_LV_10-9_0_3_node_76 | 0.4 | n |  | TRUE
78 | bus_LV_10-9_0_3_node_94 | 0.4 | n |  | TRUE
79 | bus_LV_10-9_0_3_node_83 | 0.4 | n |  | TRUE
80 | bus_LV_10-9_0_3_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_10-9_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_10-9_0_3_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_10-9_0_3_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_10-9_0_3_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_10-9_0_3_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_10-9_0_3_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_10-9_0_3_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_10-9_0_3_node_91 | 0.4 | n |  | TRUE
89 | bus_LV_10-9_0_3_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_10-9_0_3_node_78 | 0.4 | n |  | TRUE
91 | bus_MV_349_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_10-9_0_3_load_0 | 0 | 0.0022245 | 0.00055751 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_10-9_0_3_load_1 | 1 | 0.001582 | 0.00039648 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_10-9_0_3_load_4 | 3 | 0.0019108 | 0.00047888 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_10-9_0_3_load_12 | 6 | 0.001633 | 0.00040927 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_10-9_0_3_load_9 | 7 | 0.0066544 | 0.0016677 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_10-9_0_3_load_13 | 8 | 0.0014202 | 0.00035594 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_10-9_0_3_load_8 | 9 | 0.0044947 | 0.0011265 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_10-9_0_3_load_6 | 10 | 0.0020414 | 0.00051161 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_10-9_0_3_load_81 | 11 | 0.0013109 | 0.00032855 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_10-9_0_3_load_10 | 12 | 0.0036583 | 0.00091685 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_10-9_0_3_load_14 | 13 | 0.00075145 | 0.00018833 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_10-9_0_3_load_7 | 14 | 0.0010237 | 0.00025656 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_10-9_0_3_load_11 | 15 | 0.0016304 | 0.00040862 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_10-9_0_3_load_75 | 16 | 0.0013528 | 0.00033905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_10-9_0_3_load_16 | 18 | 0.00075311 | 0.00018875 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_10-9_0_3_load_15 | 19 | 0.002551 | 0.00063935 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_10-9_0_3_load_18 | 21 | 0.0049201 | 0.0012331 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_10-9_0_3_load_19 | 22 | 0.004031 | 0.0010103 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_10-9_0_3_load_24 | 23 | 0.0047627 | 0.0011937 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_10-9_0_3_load_22 | 25 | 0.0064183 | 0.0016086 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_10-9_0_3_load_84 | 26 | 0.0045831 | 0.0011486 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_10-9_0_3_load_20 | 27 | 0.0066951 | 0.001678 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_10-9_0_3_load_21 | 28 | 0.008211 | 0.0020579 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_10-9_0_3_load_23 | 29 | 0.0041845 | 0.0010487 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_10-9_0_3_load_92 | 30 | 0.012679 | 0.0031778 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_10-9_0_3_load_29 | 31 | 0.0080656 | 0.0020214 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_10-9_0_3_load_25 | 32 | 0.0052811 | 0.0013236 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_10-9_0_3_load_28 | 35 | 0.012822 | 0.0032136 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_10-9_0_3_load_31 | 36 | 0.0052547 | 0.001317 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_10-9_0_3_load_32 | 37 | 0.0014627 | 0.00036658 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_10-9_0_3_load_88 | 38 | 0.0032168 | 0.00080622 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_10-9_0_3_load_30 | 39 | 0.0041233 | 0.0010334 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_10-9_0_3_load_38 | 41 | 0.0051486 | 0.0012903 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_10-9_0_3_load_50 | 42 | 0.0033891 | 0.00084938 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_10-9_0_3_load_89 | 43 | 0.012637 | 0.0031672 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_10-9_0_3_load_48 | 45 | 0.00067775 | 0.00016986 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_10-9_0_3_load_39 | 46 | 0.001475 | 0.00036966 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_10-9_0_3_load_33 | 48 | 0.00094362 | 0.00023649 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_10-9_0_3_load_35 | 50 | 0.0045216 | 0.0011332 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_10-9_0_3_load_36 | 51 | 0.0022024 | 0.00055198 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_10-9_0_3_load_37 | 52 | 0.0013793 | 0.00034569 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_10-9_0_3_load_40 | 53 | 0.0012454 | 0.00031214 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_10-9_0_3_load_41 | 54 | 0.0025271 | 0.00063334 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_10-9_0_3_load_42 | 55 | 0.00028403 | 7.1186e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_10-9_0_3_load_43 | 56 | 0.00067946 | 0.00017029 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_10-9_0_3_load_44 | 57 | 0.00023784 | 5.9607e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_10-9_0_3_load_46 | 58 | 0.002764 | 0.00069271 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_10-9_0_3_load_47 | 59 | 0.0033984 | 0.00085173 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_10-9_0_3_load_56 | 60 | 0.012404 | 0.0031088 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_10-9_0_3_load_51 | 61 | 0.00023802 | 5.9653e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_10-9_0_3_load_54 | 63 | 0.0014699 | 0.00036839 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_10-9_0_3_load_55 | 64 | 0.0014974 | 0.00037528 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_10-9_0_3_load_57 | 65 | 0.0014688 | 0.00036813 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_10-9_0_3_load_58 | 67 | 0.0058566 | 0.0014678 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_10-9_0_3_load_63 | 68 | 0.00022105 | 5.54e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_10-9_0_3_load_60 | 69 | 0.0043487 | 0.0010899 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_10-9_0_3_load_61 | 70 | 0.0019829 | 0.00049696 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_10-9_0_3_load_65 | 71 | 0.0045646 | 0.001144 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_10-9_0_3_load_79 | 75 | 0.0067595 | 0.0016941 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_10-9_0_3_load_80 | 76 | 0.0038522 | 0.00096546 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_10-9_0_3_load_76 | 77 | 0.0032817 | 0.00082246 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_10-9_0_3_load_94 | 78 | 0.0014563 | 0.00036499 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_10-9_0_3_load_83 | 79 | 0.0051014 | 0.0012785 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_10-9_0_3_load_77 | 80 | 0.0041333 | 0.0010359 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_10-9_0_3_load_70 | 81 | 0.0017194 | 0.00043092 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_10-9_0_3_load_71 | 82 | 0.0021343 | 0.0005349 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_10-9_0_3_load_72 | 83 | 0.002309 | 0.0005787 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_10-9_0_3_load_73 | 84 | 0.0014792 | 0.00037073 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_10-9_0_3_load_74 | 85 | 0.0020235 | 0.00050714 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_10-9_0_3_load_90 | 86 | 0.0018197 | 0.00045607 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_10-9_0_3_load_86 | 87 | 0.004477 | 0.0011221 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_10-9_0_3_load_91 | 88 | 0.008083 | 0.0020258 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_10-9_0_3_load_87 | 89 | 0.0016929 | 0.00042429 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_10-9_0_3_load_78 | 90 | 0.004457 | 0.001117 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_10-9_0_3_line_0 |  | 0 | 1 | 0.00085915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_10-9_0_3_line_1 |  | 0 | 2 | 0.023669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_10-9_0_3_line_2 |  | 2 | 3 | 0.00014439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_10-9_0_3_line_3 |  | 2 | 4 | 0.036163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_10-9_0_3_line_4 |  | 3 | 8 | 0.011092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_10-9_0_3_line_5 |  | 4 | 9 | 0.01631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_10-9_0_3_line_6 |  | 4 | 10 | 0.034756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_10-9_0_3_line_7 |  | 5 | 6 | 0.016489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_10-9_0_3_line_8 |  | 5 | 7 | 0.015357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_10-9_0_3_line_9 |  | 6 | 11 | 0.018656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_10-9_0_3_line_10 |  | 7 | 12 | 0.002792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_10-9_0_3_line_11 |  | 8 | 13 | 0.007366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_10-9_0_3_line_12 |  | 10 | 14 | 0.02039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_10-9_0_3_line_13 |  | 11 | 17 | 0.015173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_10-9_0_3_line_14 |  | 12 | 15 | 0.020366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_10-9_0_3_line_15 |  | 13 | 18 | 0.00040702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_10-9_0_3_line_16 |  | 15 | 16 | 0.014683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_10-9_0_3_line_17 |  | 17 | 89 | 0.0057633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_10-9_0_3_line_18 |  | 17 | 24 | 0.019799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_10-9_0_3_line_19 |  | 18 | 19 | 0.010041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_10-9_0_3_line_20 |  | 19 | 20 | 0.025002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_10-9_0_3_line_21 |  | 20 | 21 | 0.025518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_10-9_0_3_line_22 |  | 20 | 22 | 0.027016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_10-9_0_3_line_23 |  | 21 | 23 | 0.0065831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_10-9_0_3_line_24 |  | 22 | 24 | 0.0027622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_10-9_0_3_line_25 |  | 23 | 25 | 0.014319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_10-9_0_3_line_26 |  | 24 | 26 | 0.051644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_10-9_0_3_line_27 |  | 25 | 27 | 0.016929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_10-9_0_3_line_28 |  | 27 | 28 | 0.0057659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_10-9_0_3_line_29 |  | 28 | 29 | 0.019776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_10-9_0_3_line_30 |  | 29 | 30 | 0.034209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_10-9_0_3_line_31 |  | 30 | 31 | 0.0018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_10-9_0_3_line_32 |  | 31 | 33 | 0.047532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_10-9_0_3_line_33 |  | 32 | 33 | 0.031751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_10-9_0_3_line_34 |  | 32 | 34 | 0.010347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_10-9_0_3_line_35 |  | 33 | 35 | 0.019776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_10-9_0_3_line_36 |  | 34 | 36 | 0.020611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_10-9_0_3_line_37 |  | 34 | 37 | 0.014412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_10-9_0_3_line_38 |  | 35 | 38 | 0.0075673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_10-9_0_3_line_39 |  | 36 | 41 | 0.0052867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_10-9_0_3_line_40 |  | 37 | 42 | 0.0069517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_10-9_0_3_line_41 |  | 38 | 43 | 0.028036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_10-9_0_3_line_42 |  | 39 | 40 | 0.027443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_10-9_0_3_line_43 |  | 40 | 44 | 0.013326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_10-9_0_3_line_44 |  | 40 | 45 | 0.022069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_10-9_0_3_line_45 |  | 41 | 46 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_10-9_0_3_line_46 |  | 42 | 47 | 0.046113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_10-9_0_3_line_47 |  | 43 | 90 | 0.003349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_10-9_0_3_line_48 |  | 44 | 60 | 0.012587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_10-9_0_3_line_49 |  | 44 | 61 | 0.039266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_10-9_0_3_line_50 |  | 45 | 59 | 0.0097576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_10-9_0_3_line_51 |  | 46 | 53 | 0.0062807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_10-9_0_3_line_52 |  | 47 | 59 | 0.016649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_10-9_0_3_line_53 |  | 47 | 56 | 0.002841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_10-9_0_3_line_54 |  | 48 | 49 | 0.040762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_10-9_0_3_line_55 |  | 49 | 50 | 0.031296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_10-9_0_3_line_56 |  | 50 | 51 | 0.0034992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_10-9_0_3_line_57 |  | 51 | 52 | 0.013317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_10-9_0_3_line_58 |  | 52 | 53 | 0.0031231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_10-9_0_3_line_59 |  | 54 | 55 | 0.010195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_10-9_0_3_line_60 |  | 54 | 56 | 0.016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_10-9_0_3_line_61 |  | 55 | 57 | 0.0082097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_10-9_0_3_line_62 |  | 57 | 58 | 0.00089165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_10-9_0_3_line_63 |  | 60 | 66 | 0.10434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_10-9_0_3_line_64 |  | 61 | 62 | 0.064066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_10-9_0_3_line_65 |  | 62 | 63 | 0.023804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_10-9_0_3_line_66 |  | 62 | 64 | 0.13169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_10-9_0_3_line_67 |  | 63 | 65 | 0.017905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_10-9_0_3_line_68 |  | 65 | 67 | 0.10807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_10-9_0_3_line_69 |  | 66 | 68 | 0.1261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_10-9_0_3_line_70 |  | 68 | 70 | 0.005817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_10-9_0_3_line_71 |  | 69 | 70 | 0.0077772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_10-9_0_3_line_72 |  | 71 | 72 | 0.10769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_10-9_0_3_line_73 |  | 72 | 73 | 0.074627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_10-9_0_3_line_74 |  | 72 | 74 | 0.078569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_10-9_0_3_line_75 |  | 73 | 75 | 0.020814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_10-9_0_3_line_76 |  | 73 | 76 | 0.049294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_10-9_0_3_line_77 |  | 73 | 77 | 0.030864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_10-9_0_3_line_78 |  | 74 | 78 | 0.034846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_10-9_0_3_line_79 |  | 75 | 79 | 0.021681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_10-9_0_3_line_80 |  | 77 | 80 | 0.022457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_10-9_0_3_line_81 |  | 80 | 90 | 0.006179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_10-9_0_3_line_82 |  | 81 | 82 | 0.033105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_10-9_0_3_line_83 |  | 81 | 83 | 0.019782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_10-9_0_3_line_84 |  | 82 | 84 | 0.034267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_10-9_0_3_line_85 |  | 83 | 85 | 0.022928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_10-9_0_3_line_86 |  | 84 | 86 | 0.0070341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_10-9_0_3_line_87 |  | 85 | 87 | 0.052229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_10-9_0_3_line_88 |  | 86 | 88 | 0.028572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_10-9_0_3_line_89 |  | 87 | 89 | 0.019144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_10-9_0_3_trafo_92 | 0.63 MVA 20/0.4 kV | 91 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2675084.9132 | 1235251.4732 | 2675084.0998 | 1235251.7497
1 | 2675062.9633 | 1235261.9086 | 2675071.5604 | 1235256.0132 | 2675084.0998 | 1235251.7497
2 | 2675063.0647 | 1235262.0115 | 2675062.9633 | 1235261.9086
3 | 2675053.346 | 1235231.155 | 2675059.2398 | 1235236.7332 | 2675064.6832 | 1235248.599 | 2675065.9991 | 1235256.4655 | 2675062.2726 | 1235260.8659 | 2675062.9633 | 1235261.9086
4 | 2675063.0647 | 1235262.0115 | 2675069.1733 | 1235268.2136 | 2675070.7711 | 1235269.9867
5 | 2675053.346 | 1235231.155 | 2675039.4992 | 1235222.5362
6 | 2675053.346 | 1235231.155 | 2675076.0894 | 1235213.8748 | 2675080.2243 | 1235209.2646
7 | 2675103.23 | 1235230.7515 | 2675114.1888 | 1235243.0724
8 | 2675103.23 | 1235230.7515 | 2675112.4758 | 1235227.4216 | 2675117.4552 | 1235225.0169
9 | 2675114.1888 | 1235243.0724 | 2675116.6928 | 1235245.8876 | 2675124.9735 | 1235258.26
10 | 2675117.4552 | 1235225.0169 | 2675119.9694 | 1235223.8027 | 2675119.9694 | 1235223.8027
11 | 2675070.7711 | 1235269.9867 | 2675075.702 | 1235275.4589
12 | 2675093.8389 | 1235194.0855 | 2675080.2243 | 1235209.2646
13 | 2675134.5298 | 1235270.0408 | 2675125.4063 | 1235258.9067 | 2675124.9735 | 1235258.26
14 | 2675137.401 | 1235213.2721 | 2675129.1063 | 1235218.3145 | 2675119.9694 | 1235223.8027
15 | 2675075.9745 | 1235275.7613 | 2675075.702 | 1235275.4589
16 | 2675137.401 | 1235213.2721 | 2675140.5019 | 1235211.3871 | 2675148.2476 | 1235206.982 | 2675149.9568 | 1235205.6884
17 | 2675134.5298 | 1235270.0408 | 2675138.4934 | 1235265.8568
18 | 2675120.7558 | 1235284.2986 | 2675134.5298 | 1235270.0408
19 | 2675082.4915 | 1235283.3968 | 2675078.5781 | 1235278.6507 | 2675075.9745 | 1235275.7613
20 | 2675097.7424 | 1235303.1874 | 2675091.3999 | 1235294.2011 | 2675082.4915 | 1235283.3968
21 | 2675097.7424 | 1235303.1874 | 2675104.1745 | 1235312.275 | 2675112.5201 | 1235323.9911
22 | 2675097.7424 | 1235303.1874 | 2675107.0465 | 1235295.8444 | 2675112.3613 | 1235291.5308 | 2675118.6631 | 1235286.1016
23 | 2675112.5201 | 1235323.9911 | 2675113.4853 | 1235325.346 | 2675116.4664 | 1235329.2595
24 | 2675120.7558 | 1235284.2986 | 2675118.6631 | 1235286.1016
25 | 2675125.6175 | 1235340.2642 | 2675119.352 | 1235333.0477 | 2675116.4664 | 1235329.2595
26 | 2675120.7558 | 1235284.2986 | 2675148.4491 | 1235289.1632 | 2675171.4775 | 1235293.9789
27 | 2675125.6175 | 1235340.2642 | 2675125.8721 | 1235340.5575 | 2675126.8659 | 1235341.5708 | 2675130.8113 | 1235345.6012 | 2675136.0796 | 1235350.3488 | 2675137.9396 | 1235351.849
28 | 2675137.9396 | 1235351.849 | 2675142.4276 | 1235355.4687
29 | 2675157.8205 | 1235367.8836 | 2675142.4276 | 1235355.4687
30 | 2675184.1616 | 1235389.71 | 2675180.5323 | 1235386.6915 | 2675164.1295 | 1235373.0524 | 2675160.8415 | 1235370.3201 | 2675157.8205 | 1235367.8836
31 | 2675184.1616 | 1235389.71 | 2675185.6151 | 1235390.9189
32 | 2675222.7142 | 1235420.6263 | 2675211.1731 | 1235411.5741 | 2675198.3431 | 1235401.5048 | 2675185.6151 | 1235390.9189
33 | 2675222.7142 | 1235420.6263 | 2675195.6461 | 1235437.2231
34 | 2675186.8251 | 1235442.6317 | 2675195.6461 | 1235437.2231
35 | 2675222.7142 | 1235420.6263 | 2675238.7388 | 1235409.037
36 | 2675186.8251 | 1235442.6317 | 2675168.153 | 1235451.3593
37 | 2675186.8251 | 1235442.6317 | 2675194.2651 | 1235454.9754
38 | 2675244.8705 | 1235404.6024 | 2675238.7388 | 1235409.037
39 | 2675168.153 | 1235451.3593 | 2675163.3637 | 1235453.5978
40 | 2675197.8536 | 1235460.9292 | 2675194.2651 | 1235454.9754
41 | 2675244.8705 | 1235404.6024 | 2675254.3076 | 1235397.7773 | 2675267.2959 | 1235387.7812
42 | 2675267.5108 | 1235484.6931 | 2675255.5932 | 1235463.561 | 2675253.8255 | 1235460.915
43 | 2675267.5108 | 1235484.6931 | 2675273.0562 | 1235496.8161
44 | 2675267.5108 | 1235484.6931 | 2675246.6361 | 1235491.8544
45 | 2675140.4033 | 1235464.3297 | 2675163.3637 | 1235453.5978
46 | 2675221.658 | 1235500.4233 | 2675197.8536 | 1235460.9292
47 | 2675267.2959 | 1235387.7812 | 2675269.9499 | 1235385.7386
48 | 2675273.0562 | 1235496.8161 | 2675285.539 | 1235498.4309
49 | 2675273.0562 | 1235496.8161 | 2675277.5808 | 1235513.6517 | 2675279.1539 | 1235523.8897 | 2675279.9841 | 1235531.2386 | 2675280.1432 | 1235535.3142
50 | 2675237.4065 | 1235495.0207 | 2675246.6361 | 1235491.8544
51 | 2675140.4033 | 1235464.3297 | 2675134.7135 | 1235466.9892
52 | 2675221.658 | 1235500.4233 | 2675237.4065 | 1235495.0207
53 | 2675221.658 | 1235500.4233 | 2675219.078 | 1235501.6127
54 | 2675088.2975 | 1235488.6843 | 2675070.2389 | 1235452.1411
55 | 2675088.2975 | 1235488.6843 | 2675116.6496 | 1235475.4323
56 | 2675119.8196 | 1235473.9507 | 2675116.6496 | 1235475.4323
57 | 2675131.8842 | 1235468.3116 | 2675119.8196 | 1235473.9507
58 | 2675131.8842 | 1235468.3116 | 2675134.7135 | 1235466.9892
59 | 2675203.8047 | 1235508.6532 | 2675194.546 | 1235512.9212
60 | 2675203.8047 | 1235508.6532 | 2675219.078 | 1235501.6127
61 | 2675194.546 | 1235512.9212 | 2675187.0903 | 1235516.358
62 | 2675186.2806 | 1235516.7313 | 2675187.0903 | 1235516.358
63 | 2675336.2596 | 1235589.414 | 2675302.599 | 1235523.4642 | 2675285.539 | 1235498.4309
64 | 2675262.3272 | 1235596.3042 | 2675271.1555 | 1235574.5232 | 2675275.3613 | 1235563.9581 | 2675276.6075 | 1235559.3819 | 2675279.0914 | 1235549.7178 | 2675279.8106 | 1235543.1335 | 2675280.2812 | 1235538.8476 | 2675280.1432 | 1235535.3142
65 | 2675262.3272 | 1235596.3042 | 2675254.8077 | 1235592.4396 | 2675248.9188 | 1235592.4984 | 2675244.6105 | 1235593.8337 | 2675240.1574 | 1235595.9958
66 | 2675262.3272 | 1235596.3042 | 2675228.4617 | 1235679.0989 | 2675224.6497 | 1235690.8588 | 2675220.9427 | 1235705.6776 | 2675218.7488 | 1235717.558 | 2675218.5368 | 1235720.0699
67 | 2675224.0502 | 1235603.8165 | 2675240.1574 | 1235595.9958
68 | 2675224.0502 | 1235603.8165 | 2675205.354 | 1235612.8943 | 2675167.3136 | 1235632.76 | 2675158.8764 | 1235637.4232 | 2675154.3651 | 1235638.0665 | 2675149.7467 | 1235636.407 | 2675131.7026 | 1235619.7452 | 2675131.1546 | 1235619.2976
69 | 2675336.2596 | 1235589.414 | 2675330.6703 | 1235639.8333 | 2675328.7838 | 1235662.6585 | 2675330.3736 | 1235668.5938 | 2675333.8305 | 1235678.878 | 2675353.2007 | 1235708.6013
70 | 2675356.3766 | 1235713.4748 | 2675353.2007 | 1235708.6013
71 | 2675360.6228 | 1235719.9905 | 2675356.3766 | 1235713.4748
72 | 2675386.6566 | 1235339.6814 | 2675475.3683 | 1235278.6302
73 | 2675313.5763 | 1235345.3699 | 2675318.9454 | 1235341.5686 | 2675326.4171 | 1235339.0727 | 2675347.7951 | 1235337.576 | 2675366.6988 | 1235337.8159 | 2675386.6566 | 1235339.6814
74 | 2675450.0455 | 1235384.9058 | 2675443.7506 | 1235380.5562 | 2675431.6412 | 1235368.005 | 2675416.7662 | 1235355.6855 | 2675399.637 | 1235344.4494 | 2675386.6566 | 1235339.6814
75 | 2675313.5763 | 1235345.3699 | 2675301.9862 | 1235338.396 | 2675295.5917 | 1235334.9016
76 | 2675313.5763 | 1235345.3699 | 2675310.762 | 1235332.7366 | 2675311.1018 | 1235318.4756 | 2675311.4567 | 1235302.4246 | 2675311.8365 | 1235296.4059
77 | 2675313.5763 | 1235345.3699 | 2675297.9041 | 1235361.2822 | 2675291.5982 | 1235367.0262
78 | 2675455.0367 | 1235417.9919 | 2675452.6721 | 1235415.8604 | 2675450.0503 | 1235411.3351 | 2675449.8398 | 1235405.862 | 2675450.0726 | 1235398.8602 | 2675450.0513 | 1235391.5994 | 2675450.0455 | 1235384.9058
79 | 2675278.4284 | 1235321.744 | 2675285.8581 | 1235328.1735 | 2675292.8835 | 1235333.4217 | 2675295.5917 | 1235334.9016
80 | 2675291.5982 | 1235367.0262 | 2675277.0767 | 1235380.2536 | 2675274.8466 | 1235381.97
81 | 2675274.8466 | 1235381.97 | 2675269.9499 | 1235385.7386
82 | 2675217.0659 | 1235183.1447 | 2675239.9936 | 1235159.2646
83 | 2675217.0659 | 1235183.1447 | 2675203.3652 | 1235197.4145
84 | 2675239.9936 | 1235159.2646 | 2675263.7263 | 1235134.5461
85 | 2675203.3652 | 1235197.4145 | 2675200.8947 | 1235199.9876 | 2675187.5794 | 1235214.0429
86 | 2675268.5979 | 1235129.4721 | 2675263.7263 | 1235134.5461
87 | 2675151.6597 | 1235251.9588 | 2675187.5794 | 1235214.0429
88 | 2675287.6178 | 1235108.1697 | 2675277.2973 | 1235120.4113 | 2675268.5979 | 1235129.4721
89 | 2675151.6597 | 1235251.9588 | 2675138.4934 | 1235265.8568

## bus_geodata
| x | y | coords
0 | 2675084.0998 | 1235251.7497
1 | 2675084.9132 | 1235251.4732
2 | 2675062.9633 | 1235261.9086
3 | 2675063.0647 | 1235262.0115
4 | 2675053.346 | 1235231.155
5 | 2675103.23 | 1235230.7515
6 | 2675114.1888 | 1235243.0724
7 | 2675117.4552 | 1235225.0169
8 | 2675070.7711 | 1235269.9867
9 | 2675039.4992 | 1235222.5362
10 | 2675080.2243 | 1235209.2646
11 | 2675124.9735 | 1235258.26
12 | 2675119.9694 | 1235223.8027
13 | 2675075.702 | 1235275.4589
14 | 2675093.8389 | 1235194.0855
15 | 2675137.401 | 1235213.2721
16 | 2675149.9568 | 1235205.6884
17 | 2675134.5298 | 1235270.0408
18 | 2675075.9745 | 1235275.7613
19 | 2675082.4915 | 1235283.3968
20 | 2675097.7424 | 1235303.1874
21 | 2675112.5201 | 1235323.9911
22 | 2675118.6631 | 1235286.1016
23 | 2675116.4664 | 1235329.2595
24 | 2675120.7558 | 1235284.2986
25 | 2675125.6175 | 1235340.2642
26 | 2675171.4775 | 1235293.9789
27 | 2675137.9396 | 1235351.849
28 | 2675142.4276 | 1235355.4687
29 | 2675157.8205 | 1235367.8836
30 | 2675184.1616 | 1235389.71
31 | 2675185.6151 | 1235390.9189
32 | 2675195.6461 | 1235437.2231
33 | 2675222.7142 | 1235420.6263
34 | 2675186.8251 | 1235442.6317
35 | 2675238.7388 | 1235409.037
36 | 2675168.153 | 1235451.3593
37 | 2675194.2651 | 1235454.9754
38 | 2675244.8705 | 1235404.6024
39 | 2675253.8255 | 1235460.915
40 | 2675267.5108 | 1235484.6931
41 | 2675163.3637 | 1235453.5978
42 | 2675197.8536 | 1235460.9292
43 | 2675267.2959 | 1235387.7812
44 | 2675273.0562 | 1235496.8161
45 | 2675246.6361 | 1235491.8544
46 | 2675140.4033 | 1235464.3297
47 | 2675221.658 | 1235500.4233
48 | 2675070.2389 | 1235452.1411
49 | 2675088.2975 | 1235488.6843
50 | 2675116.6496 | 1235475.4323
51 | 2675119.8196 | 1235473.9506
52 | 2675131.8842 | 1235468.3116
53 | 2675134.7135 | 1235466.9892
54 | 2675203.8047 | 1235508.6532
55 | 2675194.546 | 1235512.9212
56 | 2675219.078 | 1235501.6127
57 | 2675187.0903 | 1235516.358
58 | 2675186.2806 | 1235516.7313
59 | 2675237.4065 | 1235495.0207
60 | 2675285.539 | 1235498.4309
61 | 2675280.1432 | 1235535.3142
62 | 2675262.3272 | 1235596.3042
63 | 2675240.1574 | 1235595.9958
64 | 2675218.5368 | 1235720.0699
65 | 2675224.0502 | 1235603.8165
66 | 2675336.2596 | 1235589.414
67 | 2675131.1546 | 1235619.2976
68 | 2675353.2007 | 1235708.6013
69 | 2675360.6228 | 1235719.9905
70 | 2675356.3766 | 1235713.4748
71 | 2675475.3683 | 1235278.6302
72 | 2675386.6566 | 1235339.6814
73 | 2675313.5763 | 1235345.3699
74 | 2675450.0455 | 1235384.9058
75 | 2675295.5917 | 1235334.9016
76 | 2675311.8365 | 1235296.4059
77 | 2675291.5982 | 1235367.0262
78 | 2675455.0367 | 1235417.9919
79 | 2675278.4284 | 1235321.744
80 | 2675274.8466 | 1235381.97
81 | 2675217.0659 | 1235183.1447
82 | 2675239.9936 | 1235159.2646
83 | 2675203.3652 | 1235197.4145
84 | 2675263.7263 | 1235134.5461
85 | 2675187.5794 | 1235214.0429
86 | 2675268.5979 | 1235129.4721
87 | 2675151.6597 | 1235251.9588
88 | 2675287.6178 | 1235108.1697
89 | 2675138.4934 | 1235265.8568
90 | 2675269.9499 | 1235385.7386
91 | 2675184.1616 | 1235389.71

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98907 | -0.20999 | 0.0022245 | 0.00055751
1 | 0.98907 | -0.21002 | 0.001582 | 0.00039648
2 | 0.98915 | -0.20839 | 0 | 0
3 | 0.98915 | -0.20836 | 0.0019108 | 0.00047888
4 | 0.9889 | -0.21326 | 0 | 0
5 | 0.98715 | -0.24723 | 0 | 0
6 | 0.98735 | -0.24331 | 0.001633 | 0.00040927
7 | 0.98696 | -0.25089 | 0.0066544 | 0.0016677
8 | 0.98929 | -0.20574 | 0.0014202 | 0.00035594
9 | 0.98883 | -0.21457 | 0.0044947 | 0.0011265
10 | 0.9888 | -0.21516 | 0.0020414 | 0.00051161
11 | 0.98761 | -0.23833 | 0.0013109 | 0.00032855
12 | 0.98695 | -0.25122 | 0.0036583 | 0.00091685
13 | 0.98939 | -0.20381 | 0.00075145 | 0.00018833
14 | 0.98878 | -0.21553 | 0.0010237 | 0.00025656
15 | 0.98689 | -0.25231 | 0.0016304 | 0.00040862
16 | 0.98687 | -0.25266 | 0.0013528 | 0.00033905
17 | 0.98783 | -0.23393 | 0 | 0
18 | 0.98939 | -0.2037 | 0.00075311 | 0.00018875
19 | 0.98954 | -0.2008 | 0.002551 | 0.00063935
20 | 0.98997 | -0.19245 | 0 | 0
21 | 0.9916 | -0.16103 | 0.0049201 | 0.0012331
22 | 0.98872 | -0.2168 | 0.004031 | 0.0010103
23 | 0.99205 | -0.15236 | 0.0047627 | 0.0011937
24 | 0.9886 | -0.21909 | 0 | 0
25 | 0.99309 | -0.13234 | 0.0064183 | 0.0016086
26 | 0.98838 | -0.22332 | 0.0045831 | 0.0011486
27 | 0.99441 | -0.1068 | 0.0066951 | 0.001678
28 | 0.9949 | -0.097437 | 0.008211 | 0.0020579
29 | 0.99672 | -0.062549 | 0.0041845 | 0.0010487
30 | 1 | 0 | -0.25543 | -0.064512
31 | 0.99987 | -0.0024203 | 0.0080656 | 0.0020214
32 | 0.99159 | -0.16112 | 0.0052811 | 0.0013236
33 | 0.99382 | -0.11815 | 0 | 0
34 | 0.99092 | -0.1742 | 0 | 0
35 | 0.9927 | -0.13992 | 0.012822 | 0.0032136
36 | 0.9905 | -0.18231 | 0.0052547 | 0.001317
37 | 0.99027 | -0.18675 | 0.0014627 | 0.00036658
38 | 0.99235 | -0.14654 | 0.0032168 | 0.00080622
39 | 0.98642 | -0.26147 | 0.0041233 | 0.0010334
40 | 0.98652 | -0.25944 | 0 | 0
41 | 0.99042 | -0.1839 | 0.0051486 | 0.0012903
42 | 0.98996 | -0.19264 | 0.0033891 | 0.00084938
43 | 0.99117 | -0.16952 | 0.012637 | 0.0031672
44 | 0.98616 | -0.26649 | 0 | 0
45 | 0.9872 | -0.24616 | 0.00067775 | 0.00016986
46 | 0.99014 | -0.1892 | 0.001475 | 0.00036966
47 | 0.98809 | -0.22896 | 0 | 0
48 | 0.98988 | -0.19422 | 0.00094362 | 0.00023649
49 | 0.98992 | -0.19354 | 0 | 0
50 | 0.98995 | -0.19301 | 0.0045216 | 0.0011332
51 | 0.98996 | -0.19267 | 0.0022024 | 0.00055198
52 | 0.99006 | -0.19086 | 0.0013793 | 0.00034569
53 | 0.99008 | -0.19035 | 0.0012454 | 0.00031214
54 | 0.98798 | -0.23103 | 0.0025271 | 0.00063334
55 | 0.98795 | -0.23163 | 0.00028403 | 7.1186e-05
56 | 0.98807 | -0.22929 | 0.00067946 | 0.00017029
57 | 0.98793 | -0.23207 | 0.00023784 | 5.9607e-05
58 | 0.98793 | -0.23212 | 0.002764 | 0.00069271
59 | 0.98751 | -0.24017 | 0.0033984 | 0.00085173
60 | 0.98594 | -0.27077 | 0.012404 | 0.0031088
61 | 0.98578 | -0.27391 | 0.00023802 | 5.9653e-05
62 | 0.98517 | -0.28576 | 0 | 0
63 | 0.98498 | -0.28952 | 0.0014699 | 0.00036839
64 | 0.98499 | -0.2893 | 0.0014974 | 0.00037528
65 | 0.98486 | -0.29188 | 0.0014688 | 0.00036813
66 | 0.98531 | -0.28305 | 0 | 0
67 | 0.98428 | -0.30326 | 0.0058566 | 0.0014678
68 | 0.98455 | -0.2979 | 0.00022105 | 5.54e-05
69 | 0.98448 | -0.29917 | 0.0043487 | 0.0010899
70 | 0.98452 | -0.29856 | 0.0019829 | 0.00049696
71 | 0.98891 | -0.21341 | 0.0045646 | 0.001144
72 | 0.98936 | -0.20465 | 0 | 0
73 | 0.98977 | -0.19664 | 0 | 0
74 | 0.98925 | -0.20669 | 0 | 0
75 | 0.98954 | -0.20103 | 0.0067595 | 0.0016941
76 | 0.98959 | -0.20002 | 0.0038522 | 0.00096546
77 | 0.99038 | -0.1847 | 0.0032817 | 0.00082246
78 | 0.98921 | -0.20759 | 0.0014563 | 0.00036499
79 | 0.98944 | -0.203 | 0.0051014 | 0.0012785
80 | 0.9909 | -0.17472 | 0.0041333 | 0.0010359
81 | 0.98569 | -0.27573 | 0.0017194 | 0.00043092
82 | 0.98527 | -0.28376 | 0.0021343 | 0.0005349
83 | 0.98596 | -0.27032 | 0.002309 | 0.0005787
84 | 0.98491 | -0.29077 | 0.0014792 | 0.00037073
85 | 0.98633 | -0.26311 | 0.0020235 | 0.00050714
86 | 0.98485 | -0.29202 | 0.0018197 | 0.00045607
87 | 0.98727 | -0.24481 | 0.004477 | 0.0011221
88 | 0.98464 | -0.29617 | 0.008083 | 0.0020258
89 | 0.9877 | -0.23658 | 0.0016929 | 0.00042429
90 | 0.99106 | -0.17152 | 0.004457 | 0.001117
91 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.001582 | 0.00039647 | -0.001582 | -0.00039648 | 1.8248e-09 | -9.8584e-09 | 0.00238 | 0.00238 | 0.00238 | 0.98907 | -0.20999 | 0.98907 | -0.21002 | 0.65385
1 | -0.0038065 | -0.00095398 | 0.0038068 | 0.00095386 | 2.9107e-07 | -1.175e-07 | 0.0057267 | 0.0057266 | 0.0057267 | 0.98907 | -0.20999 | 0.98915 | -0.20839 | 1.5733
2 | -0.011369 | -0.0028486 | 0.011369 | 0.0028486 | 1.5837e-08 | 8.2823e-09 | 0.017102 | 0.017102 | 0.017102 | 0.98915 | -0.20839 | 0.98915 | -0.20836 | 4.6985
3 | 0.0075621 | 0.0018948 | -0.0075604 | -0.0018941 | 1.7549e-06 | 6.5909e-07 | 0.011376 | 0.011376 | 0.011376 | 0.98915 | -0.20839 | 0.9889 | -0.21326 | 3.1253
4 | -0.01328 | -0.0033275 | 0.013281 | 0.0033284 | 1.66e-06 | 9.1997e-07 | 0.019977 | 0.019977 | 0.019977 | 0.98915 | -0.20836 | 0.98929 | -0.20574 | 5.4881
5 | 0.004495 | 0.0011265 | -0.0044947 | -0.0011265 | 2.7981e-07 | -3.0161e-08 | 0.0067637 | 0.0067638 | 0.0067638 | 0.9889 | -0.21326 | 0.98883 | -0.21457 | 1.8582
6 | 0.0030653 | 0.00076765 | -0.0030651 | -0.00076792 | 2.7727e-07 | -2.6841e-07 | 0.0046123 | 0.0046124 | 0.0046124 | 0.9889 | -0.21326 | 0.9888 | -0.21516 | 1.2671
7 | -0.013298 | -0.0033332 | 0.013301 | 0.0033346 | 2.4848e-06 | 1.3794e-06 | 0.020046 | 0.020046 | 0.020046 | 0.98715 | -0.24723 | 0.98735 | -0.24331 | 5.5072
8 | 0.013298 | 0.0033332 | -0.013296 | -0.003332 | 2.3141e-06 | 1.2848e-06 | 0.020046 | 0.020046 | 0.020046 | 0.98715 | -0.24723 | 0.98696 | -0.25089 | 5.5072
9 | -0.014934 | -0.0037439 | 0.014937 | 0.0037459 | 3.5438e-06 | 2.0294e-06 | 0.022507 | 0.022507 | 0.022507 | 0.98735 | -0.24331 | 0.98761 | -0.23833 | 6.1832
10 | 0.0066418 | 0.0016642 | -0.0066417 | -0.0016642 | 1.0498e-07 | 3.151e-08 | 0.010014 | 0.010014 | 0.010014 | 0.98696 | -0.25089 | 0.98695 | -0.25122 | 2.751
11 | -0.014702 | -0.0036844 | 0.014703 | 0.0036852 | 1.3507e-06 | 7.6986e-07 | 0.022113 | 0.022113 | 0.022113 | 0.98929 | -0.20574 | 0.98939 | -0.20381 | 6.075
12 | 0.0010237 | 0.00025631 | -0.0010237 | -0.00025656 | 1.8146e-08 | -2.4993e-07 | 0.0015404 | 0.0015405 | 0.0015405 | 0.9888 | -0.21516 | 0.98878 | -0.21553 | 0.42322
13 | -0.016248 | -0.0040745 | 0.016252 | 0.0040764 | 3.4103e-06 | 1.9884e-06 | 0.024482 | 0.024482 | 0.024482 | 0.98761 | -0.23833 | 0.98783 | -0.23393 | 6.7258
14 | 0.0029834 | 0.00074733 | -0.0029832 | -0.00074749 | 1.5451e-07 | -1.6135e-07 | 0.0044979 | 0.004498 | 0.004498 | 0.98695 | -0.25122 | 0.98689 | -0.25231 | 1.2357
15 | -0.015454 | -0.0038735 | 0.015454 | 0.0038735 | 8.2458e-08 | 4.7546e-08 | 0.023243 | 0.023243 | 0.023243 | 0.98939 | -0.20381 | 0.98939 | -0.2037 | 6.3855
16 | 0.0013528 | 0.00033887 | -0.0013528 | -0.00033905 | 2.2909e-08 | -1.7295e-07 | 0.0020397 | 0.0020398 | 0.0020398 | 0.98689 | -0.25231 | 0.98687 | -0.25266 | 0.56038
17 | 0.025789 | 0.0064804 | -0.025786 | -0.0064784 | 3.2626e-06 | 2.0143e-06 | 0.038853 | 0.038853 | 0.038853 | 0.98783 | -0.23393 | 0.9877 | -0.23658 | 10.674
18 | -0.042041 | -0.010557 | 0.042071 | 0.010576 | 2.9783e-05 | 1.8807e-05 | 0.063335 | 0.063335 | 0.063335 | 0.98783 | -0.23393 | 0.9886 | -0.21909 | 17.3998
19 | -0.016208 | -0.0040623 | 0.01621 | 0.0040636 | 2.2373e-06 | 1.3029e-06 | 0.024376 | 0.024376 | 0.024376 | 0.98939 | -0.2037 | 0.98954 | -0.2008 | 6.6966
20 | -0.018761 | -0.0047029 | 0.018768 | 0.0047074 | 7.4623e-06 | 4.4545e-06 | 0.028212 | 0.028212 | 0.028212 | 0.98954 | -0.2008 | 0.98997 | -0.19245 | 7.7505
21 | -0.069518 | -0.017483 | 0.069623 | 0.017549 | 0.00010453 | 6.6568e-05 | 0.10451 | 0.10451 | 0.10451 | 0.98997 | -0.19245 | 0.9916 | -0.16103 | 28.7124
22 | 0.05075 | 0.012775 | -0.050691 | -0.012738 | 5.8982e-05 | 3.7401e-05 | 0.076302 | 0.076302 | 0.076302 | 0.98997 | -0.19245 | 0.98872 | -0.2168 | 20.962
23 | -0.074543 | -0.018782 | 0.074574 | 0.018802 | 3.091e-05 | 1.9697e-05 | 0.1119 | 0.1119 | 0.1119 | 0.9916 | -0.16103 | 0.99205 | -0.15236 | 30.7408
24 | 0.04666 | 0.011727 | -0.046655 | -0.011724 | 5.1097e-06 | 3.2348e-06 | 0.070235 | 0.070235 | 0.070235 | 0.98872 | -0.2168 | 0.9886 | -0.21909 | 19.2953
25 | -0.079336 | -0.019996 | 0.079413 | 0.020044 | 7.609e-05 | 4.8513e-05 | 0.11904 | 0.11904 | 0.11904 | 0.99205 | -0.15236 | 0.99309 | -0.13234 | 32.7033
26 | 0.0045841 | 0.0011486 | -0.0045831 | -0.0011486 | 9.22e-07 | -7.1946e-08 | 0.0068997 | 0.0069 | 0.0069 | 0.9886 | -0.21909 | 0.98838 | -0.22332 | 1.8956
27 | -0.085831 | -0.021653 | 0.085936 | 0.02172 | 0.00010508 | 6.7034e-05 | 0.12866 | 0.12866 | 0.12866 | 0.99309 | -0.13234 | 0.99441 | -0.1068 | 35.3454
28 | -0.092631 | -0.023398 | 0.092673 | 0.023424 | 4.1581e-05 | 2.6537e-05 | 0.13868 | 0.13868 | 0.13868 | 0.99441 | -0.1068 | 0.9949 | -0.097437 | 38.0976
29 | -0.10088 | -0.025482 | 0.10105 | 0.02559 | 0.00016899 | 0.0001079 | 0.15096 | 0.15096 | 0.15096 | 0.9949 | -0.097437 | 0.99672 | -0.062549 | 41.4714
30 | -0.10524 | -0.026639 | 0.10555 | 0.026841 | 0.00031703 | 0.00020245 | 0.1572 | 0.1572 | 0.1572 | 0.99672 | -0.062549 | 1 | 0 | 43.1877
31 | 0.14822 | 0.03767 | -0.14821 | -0.037659 | 1.7273e-05 | 1.1005e-05 | 0.22074 | 0.22074 | 0.22074 | 1 | 0 | 0.99987 | -0.0024203 | 30.3219
32 | 0.14014 | 0.035638 | -0.13936 | -0.035141 | 0.00077666 | 0.00049644 | 0.20874 | 0.20874 | 0.20874 | 0.99987 | -0.0024203 | 0.99382 | -0.11815 | 57.3463
33 | -0.076752 | -0.019328 | 0.07691 | 0.019429 | 0.00015804 | 0.00010074 | 0.11521 | 0.11521 | 0.11521 | 0.99159 | -0.16112 | 0.99382 | -0.11815 | 31.651
34 | 0.071471 | 0.018005 | -0.071427 | -0.017976 | 4.4661e-05 | 2.845e-05 | 0.10728 | 0.10728 | 0.10728 | 0.99159 | -0.16112 | 0.99092 | -0.1742 | 29.4739
35 | 0.062454 | 0.015713 | -0.062389 | -0.015671 | 6.4877e-05 | 4.1265e-05 | 0.093531 | 0.093531 | 0.093531 | 0.99382 | -0.11815 | 0.9927 | -0.13992 | 25.6954
36 | 0.022185 | 0.0055638 | -0.022176 | -0.0055586 | 8.5789e-06 | 5.2251e-06 | 0.033316 | 0.033316 | 0.033316 | 0.99092 | -0.1742 | 0.9905 | -0.18231 | 9.1527
37 | 0.049242 | 0.012412 | -0.049212 | -0.012394 | 2.9571e-05 | 1.874e-05 | 0.073969 | 0.073969 | 0.073969 | 0.99092 | -0.1742 | 0.99027 | -0.18675 | 20.3212
38 | 0.049567 | 0.012458 | -0.049551 | -0.012448 | 1.567e-05 | 9.9312e-06 | 0.074311 | 0.074311 | 0.074311 | 0.9927 | -0.13992 | 0.99235 | -0.14654 | 20.4151
39 | 0.016922 | 0.0042416 | -0.01692 | -0.0042409 | 1.2812e-06 | 7.5193e-07 | 0.025422 | 0.025422 | 0.025422 | 0.9905 | -0.18231 | 0.99042 | -0.1839 | 6.984
40 | 0.047749 | 0.012027 | -0.047736 | -0.012019 | 1.3428e-05 | 8.5048e-06 | 0.071771 | 0.071772 | 0.071772 | 0.99027 | -0.18675 | 0.98996 | -0.19264 | 19.7174
41 | 0.046334 | 0.011642 | -0.046283 | -0.011609 | 5.0765e-05 | 3.2128e-05 | 0.069487 | 0.069488 | 0.069488 | 0.99235 | -0.14654 | 0.99117 | -0.16952 | 19.09
42 | -0.0041233 | -0.0010334 | 0.0041237 | 0.0010333 | 3.9815e-07 | -9.554e-08 | 0.0062201 | 0.00622 | 0.0062201 | 0.98642 | -0.26147 | 0.98652 | -0.25944 | 1.7088
43 | 0.029526 | 0.0074063 | -0.029516 | -0.0074001 | 9.9124e-06 | 6.1738e-06 | 0.044537 | 0.044537 | 0.044537 | 0.98652 | -0.25944 | 0.98616 | -0.26649 | 12.2355
44 | -0.033649 | -0.0084396 | 0.033671 | 0.0084529 | 2.1321e-05 | 1.3363e-05 | 0.050757 | 0.050757 | 0.050757 | 0.98652 | -0.25944 | 0.9872 | -0.24616 | 13.9443
45 | 0.011772 | 0.0029505 | -0.011769 | -0.0029489 | 2.973e-06 | 1.5767e-06 | 0.017686 | 0.017687 | 0.017687 | 0.99042 | -0.1839 | 0.99014 | -0.1892 | 4.8589
46 | 0.044347 | 0.011169 | -0.04427 | -0.011121 | 7.688e-05 | 4.8612e-05 | 0.066677 | 0.066678 | 0.066678 | 0.98996 | -0.19264 | 0.98809 | -0.22896 | 18.318
47 | 0.033646 | 0.0084422 | -0.033643 | -0.0084402 | 3.2048e-06 | 2.0079e-06 | 0.050515 | 0.050515 | 0.050515 | 0.99117 | -0.16952 | 0.99106 | -0.17152 | 13.8778
48 | 0.01897 | 0.0047559 | -0.018966 | -0.0047536 | 3.8673e-06 | 2.3145e-06 | 0.028624 | 0.028624 | 0.028624 | 0.98616 | -0.26649 | 0.98594 | -0.27077 | 7.8637
49 | 0.010546 | 0.0026442 | -0.010542 | -0.0026423 | 3.7288e-06 | 1.8857e-06 | 0.015913 | 0.015914 | 0.015914 | 0.98616 | -0.26649 | 0.98578 | -0.27391 | 4.3719
50 | -0.034348 | -0.0086228 | 0.034358 | 0.008629 | 9.8102e-06 | 6.1537e-06 | 0.051779 | 0.051779 | 0.051779 | 0.9872 | -0.24616 | 0.98751 | -0.24017 | 14.2249
51 | 0.010294 | 0.0025793 | -0.010293 | -0.002579 | 5.6366e-07 | 2.7996e-07 | 0.01547 | 0.01547 | 0.01547 | 0.99014 | -0.1892 | 0.99008 | -0.19035 | 4.25
52 | 0.037777 | 0.0094934 | -0.037757 | -0.0094807 | 2.0214e-05 | 1.2724e-05 | 0.056899 | 0.056899 | 0.056899 | 0.98809 | -0.22896 | 0.98751 | -0.24017 | 15.6317
53 | 0.0064931 | 0.0016271 | -0.006493 | -0.0016271 | 1.0186e-07 | 2.8804e-08 | 0.0097782 | 0.0097782 | 0.0097782 | 0.98809 | -0.22896 | 0.98807 | -0.22929 | 2.6863
54 | -0.00094362 | -0.00023649 | 0.00094365 | 0.00023599 | 3.0752e-08 | -5.0434e-07 | 0.0014185 | 0.0014183 | 0.0014185 | 0.98988 | -0.19422 | 0.98992 | -0.19354 | 0.38969
55 | -0.00094365 | -0.00023599 | 0.00094367 | 0.0002356 | 2.3605e-08 | -3.8725e-07 | 0.0014183 | 0.0014181 | 0.0014183 | 0.98992 | -0.19354 | 0.98995 | -0.19301 | 0.38964
56 | -0.0054652 | -0.0013688 | 0.0054653 | 0.0013688 | 8.8548e-08 | 1.1681e-08 | 0.0082146 | 0.0082146 | 0.0082146 | 0.98995 | -0.19301 | 0.98996 | -0.19267 | 2.2568
57 | -0.0076678 | -0.0019208 | 0.0076684 | 0.0019211 | 6.6334e-07 | 2.533e-07 | 0.011525 | 0.011525 | 0.011525 | 0.98996 | -0.19267 | 0.99006 | -0.19086 | 3.1662
58 | -0.0090478 | -0.0022668 | 0.009048 | 0.0022669 | 2.1656e-07 | 9.8433e-08 | 0.013598 | 0.013598 | 0.013598 | 0.99006 | -0.19086 | 0.99008 | -0.19035 | 3.7357
59 | 0.003286 | 0.00082336 | -0.0032859 | -0.00082343 | 9.3639e-08 | -7.0622e-08 | 0.004949 | 0.0049491 | 0.0049491 | 0.98798 | -0.23103 | 0.98795 | -0.23163 | 1.3596
60 | -0.0058131 | -0.0014567 | 0.0058135 | 0.0014568 | 4.8341e-07 | 9.3997e-08 | 0.0087551 | 0.008755 | 0.0087551 | 0.98798 | -0.23103 | 0.98807 | -0.22929 | 2.4052
61 | 0.0030019 | 0.00075225 | -0.0030018 | -0.00075231 | 6.2934e-08 | -6.4846e-08 | 0.0045213 | 0.0045213 | 0.0045213 | 0.98795 | -0.23163 | 0.98793 | -0.23207 | 1.2421
62 | 0.002764 | 0.00069271 | -0.002764 | -0.00069271 | 5.795e-09 | -7.7081e-09 | 0.0041631 | 0.0041631 | 0.0041631 | 0.98793 | -0.23207 | 0.98793 | -0.23212 | 1.1437
63 | 0.0065614 | 0.0016448 | -0.0065575 | -0.0016436 | 3.8371e-06 | 1.126e-06 | 0.0099028 | 0.0099033 | 0.0099033 | 0.98594 | -0.27077 | 0.98531 | -0.28305 | 2.7207
64 | 0.010304 | 0.0025826 | -0.010299 | -0.0025797 | 5.8125e-06 | 2.9037e-06 | 0.015554 | 0.015555 | 0.015555 | 0.98578 | -0.27391 | 0.98517 | -0.28576 | 4.2732
65 | 0.0088009 | 0.002206 | -0.0087993 | -0.0022053 | 1.5774e-06 | 7.0649e-07 | 0.013293 | 0.013293 | 0.013293 | 0.98517 | -0.28576 | 0.98498 | -0.28952 | 3.652
66 | 0.0014976 | 0.00037376 | -0.0014974 | -0.00037528 | 2.5263e-07 | -1.5149e-06 | 0.0022615 | 0.0022621 | 0.0022621 | 0.98517 | -0.28576 | 0.98499 | -0.2893 | 0.62145
67 | 0.0073294 | 0.0018369 | -0.0073286 | -0.0018366 | 8.2323e-07 | 2.9899e-07 | 0.011073 | 0.011073 | 0.011073 | 0.98498 | -0.28952 | 0.98486 | -0.29188 | 3.042
68 | 0.0058598 | 0.0014685 | -0.0058566 | -0.0014678 | 3.1768e-06 | 6.5875e-07 | 0.0088534 | 0.0088539 | 0.0088539 | 0.98486 | -0.29188 | 0.98428 | -0.30326 | 2.4324
69 | 0.0065575 | 0.0016436 | -0.0065529 | -0.0016423 | 4.6381e-06 | 1.3635e-06 | 0.0099033 | 0.0099038 | 0.0099038 | 0.98531 | -0.28305 | 0.98455 | -0.2979 | 2.7208
70 | 0.0063319 | 0.0015869 | -0.0063317 | -0.0015868 | 1.9977e-07 | 5.388e-08 | 0.0095697 | 0.0095698 | 0.0095698 | 0.98455 | -0.2979 | 0.98452 | -0.29856 | 2.6291
71 | -0.0043487 | -0.0010899 | 0.0043488 | 0.0010899 | 1.26e-07 | -1.8255e-08 | 0.0065728 | 0.0065728 | 0.0065728 | 0.98448 | -0.29917 | 0.98452 | -0.29856 | 1.8057
72 | -0.0045646 | -0.001144 | 0.0045665 | 0.0011438 | 1.905e-06 | -1.6309e-07 | 0.0068684 | 0.0068679 | 0.0068684 | 0.98891 | -0.21341 | 0.98936 | -0.20465 | 1.8869
73 | -0.0060231 | -0.0015075 | 0.0060254 | 0.001508 | 2.2961e-06 | 5.1076e-07 | 0.0090581 | 0.0090578 | 0.0090581 | 0.98936 | -0.20465 | 0.98977 | -0.19664 | 2.4885
74 | 0.0014565 | 0.00036367 | -0.0014564 | -0.00036459 | 1.4136e-07 | -9.1837e-07 | 0.0021902 | 0.0021905 | 0.0021905 | 0.98936 | -0.20465 | 0.98925 | -0.20669 | 0.6018
75 | 0.011864 | 0.002974 | -0.011861 | -0.0029726 | 2.4831e-06 | 1.3217e-06 | 0.017836 | 0.017836 | 0.017836 | 0.98977 | -0.19664 | 0.98954 | -0.20103 | 4.9001
76 | 0.0038528 | 0.00096522 | -0.0038522 | -0.00096546 | 6.202e-07 | -2.3649e-07 | 0.0057922 | 0.0057924 | 0.0057924 | 0.98977 | -0.19664 | 0.98959 | -0.20002 | 1.5913
77 | -0.021742 | -0.0054472 | 0.021754 | 0.0054547 | 1.2366e-05 | 7.5171e-06 | 0.032686 | 0.032686 | 0.032686 | 0.98977 | -0.19664 | 0.99038 | -0.1847 | 8.9797
78 | 0.0014564 | 0.00036459 | -0.0014563 | -0.00036499 | 6.2707e-08 | -4.0723e-07 | 0.0021905 | 0.0021907 | 0.0021907 | 0.98925 | -0.20669 | 0.98921 | -0.20759 | 0.60184
79 | 0.0051019 | 0.0012786 | -0.0051014 | -0.0012785 | 4.7854e-07 | 2.7775e-08 | 0.0076719 | 0.007672 | 0.007672 | 0.98954 | -0.20103 | 0.98944 | -0.203 | 2.1077
80 | -0.025036 | -0.0062772 | 0.025048 | 0.0062845 | 1.1916e-05 | 7.3373e-06 | 0.037617 | 0.037617 | 0.037617 | 0.99038 | -0.1847 | 0.9909 | -0.17472 | 10.3343
81 | -0.029181 | -0.0073204 | 0.029186 | 0.0073232 | 4.45e-06 | 2.7684e-06 | 0.043823 | 0.043823 | 0.043823 | 0.9909 | -0.17472 | 0.99106 | -0.17152 | 12.0394
82 | 0.013527 | 0.0033933 | -0.013522 | -0.0033904 | 5.1778e-06 | 2.892e-06 | 0.020423 | 0.020423 | 0.020423 | 0.98569 | -0.27573 | 0.98527 | -0.28376 | 5.6106
83 | -0.015247 | -0.0038243 | 0.015251 | 0.0038265 | 3.9305e-06 | 2.2633e-06 | 0.023018 | 0.023018 | 0.023018 | 0.98569 | -0.27573 | 0.98596 | -0.27032 | 6.3237
84 | 0.011388 | 0.0028555 | -0.011384 | -0.0028535 | 3.8013e-06 | 1.9966e-06 | 0.017199 | 0.017199 | 0.017199 | 0.98527 | -0.28376 | 0.98491 | -0.29077 | 4.7251
85 | -0.01756 | -0.0044052 | 0.017566 | 0.0044088 | 6.0393e-06 | 3.5726e-06 | 0.026503 | 0.026503 | 0.026503 | 0.98596 | -0.27032 | 0.98633 | -0.26311 | 7.281
86 | 0.009905 | 0.0024828 | -0.0099044 | -0.0024825 | 5.907e-07 | 2.8854e-07 | 0.014965 | 0.014965 | 0.014965 | 0.98491 | -0.29077 | 0.98485 | -0.29202 | 4.1112
87 | -0.019589 | -0.0049159 | 0.019606 | 0.0049262 | 1.7109e-05 | 1.0282e-05 | 0.029556 | 0.029555 | 0.029556 | 0.98633 | -0.26311 | 0.98727 | -0.24481 | 8.1196
88 | 0.0080846 | 0.0020265 | -0.008083 | -0.0020258 | 1.5988e-06 | 6.5972e-07 | 0.012215 | 0.012215 | 0.012215 | 0.98485 | -0.29202 | 0.98464 | -0.29617 | 3.3559
89 | -0.024084 | -0.0060483 | 0.024093 | 0.0060541 | 9.4614e-06 | 5.8104e-06 | 0.036303 | 0.036303 | 0.036303 | 0.98727 | -0.24481 | 0.9877 | -0.23658 | 9.9734

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26811 | 0.067689

## res_load
| p_mw | q_mvar
0 | 0.0022245 | 0.00055751
1 | 0.001582 | 0.00039648
2 | 0.0019108 | 0.00047888
3 | 0.001633 | 0.00040927
4 | 0.0066544 | 0.0016677
5 | 0.0014202 | 0.00035594
6 | 0.0044947 | 0.0011265
7 | 0.0020414 | 0.00051161
8 | 0.0013109 | 0.00032855
9 | 0.0036583 | 0.00091685
10 | 0.00075145 | 0.00018833
11 | 0.0010237 | 0.00025656
12 | 0.0016304 | 0.00040862
13 | 0.0013528 | 0.00033905
14 | 0.00075311 | 0.00018875
15 | 0.002551 | 0.00063935
16 | 0.0049201 | 0.0012331
17 | 0.004031 | 0.0010103
18 | 0.0047627 | 0.0011937
19 | 0.0064183 | 0.0016086
20 | 0.0045831 | 0.0011486
21 | 0.0066951 | 0.001678
22 | 0.008211 | 0.0020579
23 | 0.0041845 | 0.0010487
24 | 0.012679 | 0.0031778
25 | 0.0080656 | 0.0020214
26 | 0.0052811 | 0.0013236
27 | 0.012822 | 0.0032136
28 | 0.0052547 | 0.001317
29 | 0.0014627 | 0.00036658
30 | 0.0032168 | 0.00080622
31 | 0.0041233 | 0.0010334
32 | 0.0051486 | 0.0012903
33 | 0.0033891 | 0.00084938
34 | 0.012637 | 0.0031672
35 | 0.00067775 | 0.00016986
36 | 0.001475 | 0.00036966
37 | 0.00094362 | 0.00023649
38 | 0.0045216 | 0.0011332
39 | 0.0022024 | 0.00055198
40 | 0.0013793 | 0.00034569
41 | 0.0012454 | 0.00031214
42 | 0.0025271 | 0.00063334
43 | 0.00028403 | 7.1186e-05
44 | 0.00067946 | 0.00017029
45 | 0.00023784 | 5.9607e-05
46 | 0.002764 | 0.00069271
47 | 0.0033984 | 0.00085173
48 | 0.012404 | 0.0031088
49 | 0.00023802 | 5.9653e-05
50 | 0.0014699 | 0.00036839
51 | 0.0014974 | 0.00037528
52 | 0.0014688 | 0.00036813
53 | 0.0058566 | 0.0014678
54 | 0.00022105 | 5.54e-05
55 | 0.0043487 | 0.0010899
56 | 0.0019829 | 0.00049696
57 | 0.0045646 | 0.001144
58 | 0.0067595 | 0.0016941
59 | 0.0038522 | 0.00096546
60 | 0.0032817 | 0.00082246
61 | 0.0014563 | 0.00036499
62 | 0.0051014 | 0.0012785
63 | 0.0041333 | 0.0010359
64 | 0.0017194 | 0.00043092
65 | 0.0021343 | 0.0005349
66 | 0.002309 | 0.0005787
67 | 0.0014792 | 0.00037073
68 | 0.0020235 | 0.00050714
69 | 0.0018197 | 0.00045607
70 | 0.004477 | 0.0011221
71 | 0.008083 | 0.0020258
72 | 0.0016929 | 0.00042429
73 | 0.004457 | 0.001117

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1