## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_101-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_101-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_101-1_0_5_node_143 | 0.4 | n |  | TRUE
3 | bus_LV_101-1_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_101-1_0_5_node_137 | 0.4 | n |  | TRUE
5 | bus_LV_101-1_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_101-1_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_101-1_0_5_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_101-1_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_101-1_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_101-1_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_101-1_0_5_node_54 | 0.4 | n |  | TRUE
12 | bus_LV_101-1_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_101-1_0_5_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_101-1_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_101-1_0_5_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_101-1_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_101-1_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_101-1_0_5_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_101-1_0_5_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_101-1_0_5_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_101-1_0_5_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_101-1_0_5_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_101-1_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_101-1_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_101-1_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_101-1_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_101-1_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_101-1_0_5_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_101-1_0_5_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_101-1_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_101-1_0_5_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_101-1_0_5_node_123 | 0.4 | n |  | TRUE
33 | bus_LV_101-1_0_5_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_101-1_0_5_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_101-1_0_5_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_101-1_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_101-1_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_101-1_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_101-1_0_5_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_101-1_0_5_node_104 | 0.4 | n |  | TRUE
41 | bus_LV_101-1_0_5_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_101-1_0_5_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_101-1_0_5_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_101-1_0_5_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_101-1_0_5_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_101-1_0_5_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_101-1_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_101-1_0_5_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_101-1_0_5_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_101-1_0_5_node_57 | 0.4 | n |  | TRUE
51 | bus_LV_101-1_0_5_node_154 | 0.4 | n |  | TRUE
52 | bus_LV_101-1_0_5_node_153 | 0.4 | n |  | TRUE
53 | bus_LV_101-1_0_5_node_158 | 0.4 | n |  | TRUE
54 | bus_LV_101-1_0_5_node_119 | 0.4 | n |  | TRUE
55 | bus_LV_101-1_0_5_node_77 | 0.4 | n |  | TRUE
56 | bus_LV_101-1_0_5_node_161 | 0.4 | n |  | TRUE
57 | bus_LV_101-1_0_5_node_162 | 0.4 | n |  | TRUE
58 | bus_LV_101-1_0_5_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_101-1_0_5_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_101-1_0_5_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_101-1_0_5_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_101-1_0_5_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_101-1_0_5_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_101-1_0_5_node_139 | 0.4 | n |  | TRUE
65 | bus_LV_101-1_0_5_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_101-1_0_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_101-1_0_5_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_101-1_0_5_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_101-1_0_5_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_101-1_0_5_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_101-1_0_5_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_101-1_0_5_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_101-1_0_5_node_89 | 0.4 | n |  | TRUE
74 | bus_LV_101-1_0_5_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_101-1_0_5_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_101-1_0_5_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_101-1_0_5_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_101-1_0_5_node_144 | 0.4 | n |  | TRUE
79 | bus_LV_101-1_0_5_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_101-1_0_5_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_101-1_0_5_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_101-1_0_5_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_101-1_0_5_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_101-1_0_5_node_140 | 0.4 | n |  | TRUE
85 | bus_LV_101-1_0_5_node_114 | 0.4 | n |  | TRUE
86 | bus_LV_101-1_0_5_node_115 | 0.4 | n |  | TRUE
87 | bus_LV_101-1_0_5_node_101 | 0.4 | n |  | TRUE
88 | bus_LV_101-1_0_5_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_101-1_0_5_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_101-1_0_5_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_101-1_0_5_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_101-1_0_5_node_131 | 0.4 | n |  | TRUE
93 | bus_LV_101-1_0_5_node_142 | 0.4 | n |  | TRUE
94 | bus_LV_101-1_0_5_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_101-1_0_5_node_145 | 0.4 | n |  | TRUE
96 | bus_LV_101-1_0_5_node_146 | 0.4 | n |  | TRUE
97 | bus_LV_101-1_0_5_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_101-1_0_5_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_101-1_0_5_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_101-1_0_5_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_101-1_0_5_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_101-1_0_5_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_101-1_0_5_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_101-1_0_5_node_134 | 0.4 | n |  | TRUE
105 | bus_LV_101-1_0_5_node_132 | 0.4 | n |  | TRUE
106 | bus_LV_101-1_0_5_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_101-1_0_5_node_160 | 0.4 | n |  | TRUE
108 | bus_LV_101-1_0_5_node_133 | 0.4 | n |  | TRUE
109 | bus_LV_101-1_0_5_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_101-1_0_5_node_84 | 0.4 | n |  | TRUE
111 | bus_LV_101-1_0_5_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_101-1_0_5_node_87 | 0.4 | n |  | TRUE
113 | bus_LV_101-1_0_5_node_138 | 0.4 | n |  | TRUE
114 | bus_LV_101-1_0_5_node_135 | 0.4 | n |  | TRUE
115 | bus_LV_101-1_0_5_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_101-1_0_5_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_101-1_0_5_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_101-1_0_5_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_101-1_0_5_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_101-1_0_5_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_101-1_0_5_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_101-1_0_5_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_101-1_0_5_node_130 | 0.4 | n |  | TRUE
124 | bus_LV_101-1_0_5_node_141 | 0.4 | n |  | TRUE
125 | bus_LV_101-1_0_5_node_127 | 0.4 | n |  | TRUE
126 | bus_LV_101-1_0_5_node_149 | 0.4 | n |  | TRUE
127 | bus_LV_101-1_0_5_node_129 | 0.4 | n |  | TRUE
128 | bus_LV_101-1_0_5_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_101-1_0_5_node_150 | 0.4 | n |  | TRUE
130 | bus_LV_101-1_0_5_node_98 | 0.4 | n |  | TRUE
131 | bus_LV_101-1_0_5_node_99 | 0.4 | n |  | TRUE
132 | bus_LV_101-1_0_5_node_100 | 0.4 | n |  | TRUE
133 | bus_LV_101-1_0_5_node_102 | 0.4 | n |  | TRUE
134 | bus_LV_101-1_0_5_node_103 | 0.4 | n |  | TRUE
135 | bus_LV_101-1_0_5_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_101-1_0_5_node_118 | 0.4 | n |  | TRUE
137 | bus_LV_101-1_0_5_node_124 | 0.4 | n |  | TRUE
138 | bus_LV_101-1_0_5_node_116 | 0.4 | n |  | TRUE
139 | bus_LV_101-1_0_5_node_107 | 0.4 | n |  | TRUE
140 | bus_LV_101-1_0_5_node_110 | 0.4 | n |  | TRUE
141 | bus_LV_101-1_0_5_node_156 | 0.4 | n |  | TRUE
142 | bus_LV_101-1_0_5_node_108 | 0.4 | n |  | TRUE
143 | bus_LV_101-1_0_5_node_109 | 0.4 | n |  | TRUE
144 | bus_LV_101-1_0_5_node_113 | 0.4 | n |  | TRUE
145 | bus_LV_101-1_0_5_node_112 | 0.4 | n |  | TRUE
146 | bus_LV_101-1_0_5_node_128 | 0.4 | n |  | TRUE
147 | bus_LV_101-1_0_5_node_111 | 0.4 | n |  | TRUE
148 | bus_LV_101-1_0_5_node_117 | 0.4 | n |  | TRUE
149 | bus_LV_101-1_0_5_node_120 | 0.4 | n |  | TRUE
150 | bus_LV_101-1_0_5_node_121 | 0.4 | n |  | TRUE
151 | bus_LV_101-1_0_5_node_122 | 0.4 | n |  | TRUE
152 | bus_LV_101-1_0_5_node_157 | 0.4 | n |  | TRUE
153 | bus_LV_101-1_0_5_node_136 | 0.4 | n |  | TRUE
154 | bus_LV_101-1_0_5_node_147 | 0.4 | n |  | TRUE
155 | bus_LV_101-1_0_5_node_148 | 0.4 | n |  | TRUE
156 | bus_LV_101-1_0_5_node_151 | 0.4 | n |  | TRUE
157 | bus_LV_101-1_0_5_node_152 | 0.4 | n |  | TRUE
158 | bus_LV_101-1_0_5_node_155 | 0.4 | n |  | TRUE
159 | bus_LV_101-1_0_5_node_159 | 0.4 | n |  | TRUE
160 | bus_MV_352_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_101-1_0_5_load_0 | 0 | 0.0011158 | 0.00027965 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_101-1_0_5_load_1 | 1 | 0.0008829 | 0.00022128 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_101-1_0_5_load_143 | 2 | 0.0003673 | 9.2053e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_101-1_0_5_load_2 | 3 | 0.0031525 | 0.00079008 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_101-1_0_5_load_137 | 4 | 0.00133 | 0.00033333 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_101-1_0_5_load_6 | 5 | 0.00099853 | 0.00025025 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_101-1_0_5_load_4 | 6 | 0.00039964 | 0.00010016 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_101-1_0_5_load_3 | 7 | 0.00037083 | 9.2939e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_101-1_0_5_load_7 | 8 | 0.0014607 | 0.00036609 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_101-1_0_5_load_8 | 9 | 0.0028128 | 0.00070495 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_101-1_0_5_load_9 | 10 | 0.001143 | 0.00028647 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_101-1_0_5_load_54 | 11 | 0.0015706 | 0.00039363 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_101-1_0_5_load_11 | 12 | 0.0023757 | 0.00059542 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_101-1_0_5_load_43 | 13 | 0.0013768 | 0.00034506 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_101-1_0_5_load_12 | 14 | 0.0023787 | 0.00059616 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_101-1_0_5_load_13 | 16 | 0.0022179 | 0.00055585 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_101-1_0_5_load_22 | 17 | 0.0075836 | 0.0019006 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_101-1_0_5_load_20 | 18 | 0.0039679 | 0.00099444 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_101-1_0_5_load_34 | 19 | 0.0021173 | 0.00053064 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_101-1_0_5_load_47 | 20 | 0.01301 | 0.0032605 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_101-1_0_5_load_45 | 21 | 0.0077967 | 0.001954 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_101-1_0_5_load_33 | 22 | 0.0026698 | 0.0006691 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_101-1_0_5_load_14 | 23 | 0.0031708 | 0.00079468 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_101-1_0_5_load_15 | 24 | 0.014564 | 0.0036502 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_101-1_0_5_load_16 | 25 | 0.004333 | 0.001086 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_101-1_0_5_load_17 | 26 | 0.0063371 | 0.0015882 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_101-1_0_5_load_18 | 27 | 0.0012523 | 0.00031386 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_101-1_0_5_load_25 | 28 | 0.0034017 | 0.00085254 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_101-1_0_5_load_28 | 29 | 0.0021153 | 0.00053013 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_101-1_0_5_load_26 | 30 | 0.0026189 | 0.00065637 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_101-1_0_5_load_78 | 33 | 0.00039923 | 0.00010006 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_101-1_0_5_load_19 | 35 | 0.0038649 | 0.00096863 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_101-1_0_5_load_23 | 37 | 0.0042764 | 0.0010718 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_101-1_0_5_load_24 | 38 | 0.0018824 | 0.00047178 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_101-1_0_5_load_104 | 40 | 0.010973 | 0.0027501 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_101-1_0_5_load_53 | 41 | 0.0020687 | 0.00051846 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_101-1_0_5_load_49 | 42 | 0.0053233 | 0.0013342 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_101-1_0_5_load_59 | 43 | 0.0022589 | 0.00056614 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_101-1_0_5_load_27 | 44 | 0.010422 | 0.0026121 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_101-1_0_5_load_55 | 45 | 0.009781 | 0.0024513 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_101-1_0_5_load_31 | 48 | 0.0025237 | 0.0006325 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_101-1_0_5_load_58 | 49 | 0.0044162 | 0.0011068 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_101-1_0_5_load_57 | 50 | 0.0020204 | 0.00050637 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_101-1_0_5_load_154 | 51 | 0.0017497 | 0.00043851 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_101-1_0_5_load_153 | 52 | 0.0022121 | 0.00055442 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_101-1_0_5_load_158 | 53 | 0.0007373 | 0.00018479 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_101-1_0_5_load_77 | 55 | 0.0033645 | 0.00084321 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_101-1_0_5_load_161 | 56 | 0.0077637 | 0.0019458 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_101-1_0_5_load_35 | 58 | 0.00073096 | 0.0001832 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_101-1_0_5_load_41 | 62 | 0.0046203 | 0.001158 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_101-1_0_5_load_139 | 64 | 0.0060853 | 0.0015251 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_101-1_0_5_load_40 | 65 | 0.001939 | 0.00048596 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_101-1_0_5_load_64 | 66 | 0.002485 | 0.0006228 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_101-1_0_5_load_44 | 67 | 0.0091113 | 0.0022835 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_101-1_0_5_load_46 | 68 | 0.0076255 | 0.0019111 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_101-1_0_5_load_52 | 71 | 0.0024648 | 0.00061775 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_101-1_0_5_load_89 | 73 | 0.0052019 | 0.0013037 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_101-1_0_5_load_75 | 74 | 0.0023819 | 0.00059697 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_101-1_0_5_load_63 | 76 | 0.0021104 | 0.00052892 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_101-1_0_5_load_60 | 77 | 0.0016726 | 0.00041918 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_101-1_0_5_load_144 | 78 | 0.001155 | 0.00028946 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_101-1_0_5_load_61 | 79 | 0.0032283 | 0.00080909 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_101-1_0_5_load_62 | 80 | 0.00088555 | 0.00022194 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_101-1_0_5_load_68 | 81 | 0.0017774 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_101-1_0_5_load_140 | 84 | 0.0094041 | 0.0023569 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_101-1_0_5_load_115 | 86 | 0.0082088 | 0.0020573 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_101-1_0_5_load_101 | 87 | 0.001705 | 0.00042731 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_101-1_0_5_load_69 | 88 | 0.00207 | 0.00051879 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_101-1_0_5_load_70 | 89 | 0.0023773 | 0.0005958 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_101-1_0_5_load_72 | 90 | 0.0012716 | 0.0003187 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_101-1_0_5_load_74 | 91 | 0.0017964 | 0.00045021 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_101-1_0_5_load_131 | 92 | 0.0026835 | 0.00067255 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_101-1_0_5_load_142 | 93 | 0.0012705 | 0.00031841 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_101-1_0_5_load_88 | 94 | 0.0015012 | 0.00037624 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_101-1_0_5_load_145 | 95 | 0.0012928 | 0.00032401 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_101-1_0_5_load_146 | 96 | 0.0011573 | 0.00029004 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_101-1_0_5_load_86 | 97 | 0.002221 | 0.00055663 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_101-1_0_5_load_76 | 98 | 0.00039024 | 9.7804e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_101-1_0_5_load_79 | 99 | 0.0007502 | 0.00018802 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_101-1_0_5_load_80 | 100 | 0.0011499 | 0.0002882 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_101-1_0_5_load_81 | 101 | 0.00096497 | 0.00024184 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_101-1_0_5_load_83 | 103 | 0.00056813 | 0.00014239 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_101-1_0_5_load_134 | 104 | 0.0012505 | 0.00031342 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_101-1_0_5_load_132 | 105 | 0.0030421 | 0.00076241 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_101-1_0_5_load_105 | 106 | 0.00087625 | 0.00021961 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_101-1_0_5_load_160 | 107 | 0.00096696 | 0.00024234 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_101-1_0_5_load_84 | 110 | 0.0015035 | 0.00037682 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_101-1_0_5_load_85 | 111 | 0.00088268 | 0.00022122 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_101-1_0_5_load_87 | 112 | 0.0017131 | 0.00042934 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_101-1_0_5_load_138 | 113 | 0.0019565 | 0.00049036 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_101-1_0_5_load_90 | 115 | 0.0030945 | 0.00077555 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_101-1_0_5_load_91 | 116 | 0.0044713 | 0.0011206 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_101-1_0_5_load_92 | 117 | 0.0022124 | 0.00055447 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_101-1_0_5_load_93 | 118 | 0.002311 | 0.00057918 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_101-1_0_5_load_95 | 120 | 0.0017431 | 0.00043687 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_101-1_0_5_load_97 | 122 | 0.0011627 | 0.00029139 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_101-1_0_5_load_130 | 123 | 0.0010501 | 0.00026317 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_101-1_0_5_load_141 | 124 | 0.001606 | 0.0004025 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_101-1_0_5_load_127 | 125 | 0.0017538 | 0.00043955 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_101-1_0_5_load_149 | 126 | 0.0024747 | 0.00062021 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_101-1_0_5_load_129 | 127 | 0.0018908 | 0.00047387 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_101-1_0_5_load_125 | 128 | 0.0027085 | 0.00067881 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_101-1_0_5_load_150 | 129 | 0.00066491 | 0.00016664 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_101-1_0_5_load_98 | 130 | 0.00061978 | 0.00015533 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_101-1_0_5_load_99 | 131 | 0.0017398 | 0.00043603 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_101-1_0_5_load_102 | 133 | 0.00038227 | 9.5806e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_101-1_0_5_load_103 | 134 | 0.00073959 | 0.00018536 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_101-1_0_5_load_126 | 135 | 0.00064047 | 0.00016052 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_101-1_0_5_load_118 | 136 | 0.0011807 | 0.00029592 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_101-1_0_5_load_124 | 137 | 0.0030494 | 0.00076425 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_101-1_0_5_load_116 | 138 | 0.00049721 | 0.00012461 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_101-1_0_5_load_107 | 139 | 0.0024528 | 0.00061472 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_101-1_0_5_load_110 | 140 | 0.0015877 | 0.00039791 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_101-1_0_5_load_156 | 141 | 0.0014218 | 0.00035634 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_101-1_0_5_load_108 | 142 | 0.0016476 | 0.00041293 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_101-1_0_5_load_109 | 143 | 0.0048891 | 0.0012253 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_101-1_0_5_load_112 | 145 | 0.00095933 | 0.00024043 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_101-1_0_5_load_111 | 147 | 0.0047477 | 0.0011899 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_101-1_0_5_load_117 | 148 | 0.00064631 | 0.00016198 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_101-1_0_5_load_120 | 149 | 0.00088984 | 0.00022302 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_101-1_0_5_load_121 | 150 | 0.0018222 | 0.00045669 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_101-1_0_5_load_157 | 152 | 0.00056933 | 0.00014269 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_101-1_0_5_load_136 | 153 | 0.0013279 | 0.0003328 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_101-1_0_5_load_147 | 154 | 0.0013596 | 0.00034074 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_101-1_0_5_load_151 | 156 | 0.0012897 | 0.00032322 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_101-1_0_5_load_152 | 157 | 0.0016712 | 0.00041883 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_101-1_0_5_load_155 | 158 | 0.00095399 | 0.00023909 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_101-1_0_5_load_159 | 159 | 0.00079191 | 0.00019847 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 90 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_101-1_0_5_line_0 |  | 0 | 1 | 0.027657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_101-1_0_5_line_1 |  | 0 | 2 | 0.21203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_101-1_0_5_line_2 |  | 1 | 3 | 0.014619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_101-1_0_5_line_3 |  | 2 | 4 | 0.065847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_101-1_0_5_line_4 |  | 3 | 5 | 0.015109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_101-1_0_5_line_5 |  | 4 | 144 | 0.03261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_101-1_0_5_line_6 |  | 5 | 6 | 0.019581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_101-1_0_5_line_7 |  | 6 | 7 | 0.0015027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_101-1_0_5_line_8 |  | 8 | 9 | 0.018754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_101-1_0_5_line_9 |  | 8 | 10 | 0.017988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_101-1_0_5_line_10 |  | 8 | 11 | 0.032918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_101-1_0_5_line_11 |  | 10 | 12 | 0.041386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_101-1_0_5_line_12 |  | 11 | 13 | 0.0029394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_101-1_0_5_line_13 |  | 12 | 14 | 0.022065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_101-1_0_5_line_14 |  | 13 | 15 | 0.024594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_101-1_0_5_line_15 |  | 14 | 16 | 0.024854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_101-1_0_5_line_16 |  | 15 | 65 | 0.0093312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_101-1_0_5_line_17 |  | 16 | 19 | 0.018634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_101-1_0_5_line_18 |  | 17 | 18 | 0.0083515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_101-1_0_5_line_19 |  | 18 | 35 | 0.011117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_101-1_0_5_line_20 |  | 19 | 22 | 0.058821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_101-1_0_5_line_21 |  | 20 | 21 | 0.025223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_101-1_0_5_line_22 |  | 21 | 67 | 0.015349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_101-1_0_5_line_23 |  | 23 | 24 | 0.030399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_101-1_0_5_line_24 |  | 23 | 25 | 0.013276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_101-1_0_5_line_25 |  | 24 | 26 | 0.0081314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_101-1_0_5_line_26 |  | 25 | 27 | 0.016972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_101-1_0_5_line_27 |  | 26 | 28 | 0.01121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_101-1_0_5_line_28 |  | 27 | 29 | 0.018418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_101-1_0_5_line_29 |  | 28 | 30 | 0.0026314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_101-1_0_5_line_30 |  | 29 | 34 | 0.01599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_101-1_0_5_line_31 |  | 30 | 44 | 0.012025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_101-1_0_5_line_32 |  | 31 | 32 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_101-1_0_5_line_33 |  | 31 | 33 | 0.01962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_101-1_0_5_line_34 |  | 32 | 53 | 0.018847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_101-1_0_5_line_35 |  | 32 | 54 | 0.039987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_101-1_0_5_line_36 |  | 33 | 55 | 0.0058819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_101-1_0_5_line_37 |  | 34 | 47 | 0.030655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_101-1_0_5_line_38 |  | 34 | 48 | 0.032798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_101-1_0_5_line_39 |  | 35 | 36 | 0.022948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_101-1_0_5_line_40 |  | 36 | 37 | 0.0097764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_101-1_0_5_line_41 |  | 36 | 38 | 0.022628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_101-1_0_5_line_42 |  | 37 | 39 | 0.0088376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_101-1_0_5_line_43 |  | 38 | 40 | 0.015254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_101-1_0_5_line_44 |  | 39 | 41 | 0.019618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_101-1_0_5_line_45 |  | 39 | 42 | 0.014233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_101-1_0_5_line_46 |  | 40 | 43 | 0.034774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_101-1_0_5_line_47 |  | 41 | 73 | 0.0032869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_101-1_0_5_line_48 |  | 42 | 70 | 0.027899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_101-1_0_5_line_49 |  | 43 | 60 | 0.0058049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_101-1_0_5_line_50 |  | 44 | 45 | 0.014986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_101-1_0_5_line_51 |  | 45 | 46 | 0.0022681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_101-1_0_5_line_52 |  | 46 | 76 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_101-1_0_5_line_53 |  | 46 | 77 | 0.0065576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_101-1_0_5_line_54 |  | 47 | 49 | 0.020379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_101-1_0_5_line_55 |  | 47 | 50 | 0.021455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_101-1_0_5_line_56 |  | 48 | 51 | 0.028385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_101-1_0_5_line_57 |  | 51 | 52 | 0.023694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_101-1_0_5_line_58 |  | 52 | 158 | 0.0064085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_101-1_0_5_line_59 |  | 53 | 152 | 0.0056303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_101-1_0_5_line_60 |  | 54 | 149 | 0.018636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_101-1_0_5_line_61 |  | 54 | 148 | 0.020286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_101-1_0_5_line_62 |  | 55 | 98 | 0.013147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_101-1_0_5_line_63 |  | 56 | 57 | 0.0065939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_101-1_0_5_line_64 |  | 57 | 69 | 0.044427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_101-1_0_5_line_65 |  | 58 | 59 | 0.012236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_101-1_0_5_line_66 |  | 59 | 60 | 0.011961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_101-1_0_5_line_67 |  | 59 | 61 | 0.018919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_101-1_0_5_line_68 |  | 60 | 62 | 0.044395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_101-1_0_5_line_69 |  | 61 | 63 | 0.009691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_101-1_0_5_line_70 |  | 61 | 64 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_101-1_0_5_line_71 |  | 62 | 65 | 0.0076489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_101-1_0_5_line_72 |  | 63 | 66 | 0.033272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_101-1_0_5_line_73 |  | 66 | 82 | 0.03517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_101-1_0_5_line_74 |  | 67 | 68 | 0.0039725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_101-1_0_5_line_75 |  | 68 | 69 | 0.018502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_101-1_0_5_line_76 |  | 69 | 70 | 0.01757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_101-1_0_5_line_77 |  | 70 | 71 | 0.030449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_101-1_0_5_line_78 |  | 71 | 72 | 0.015264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_101-1_0_5_line_79 |  | 72 | 74 | 0.017736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_101-1_0_5_line_80 |  | 72 | 75 | 0.00373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_101-1_0_5_line_81 |  | 74 | 94 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_101-1_0_5_line_82 |  | 75 | 91 | 0.013654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_101-1_0_5_line_83 |  | 76 | 78 | 0.036119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_101-1_0_5_line_84 |  | 77 | 79 | 0.0148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_101-1_0_5_line_85 |  | 79 | 80 | 0.0093308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_101-1_0_5_line_86 |  | 80 | 81 | 0.021202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_101-1_0_5_line_87 |  | 81 | 82 | 0.0013553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_101-1_0_5_line_88 |  | 82 | 83 | 0.004538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_101-1_0_5_line_89 |  | 83 | 84 | 0.018442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_101-1_0_5_line_90 |  | 85 | 86 | 0.015313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_101-1_0_5_line_91 |  | 85 | 87 | 0.017079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_101-1_0_5_line_92 |  | 86 | 116 | 0.0071733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_101-1_0_5_line_93 |  | 87 | 131 | 0.0025831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_101-1_0_5_line_94 |  | 88 | 89 | 0.01407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_101-1_0_5_line_95 |  | 89 | 90 | 0.0056876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_101-1_0_5_line_96 |  | 90 | 92 | 0.021864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_101-1_0_5_line_97 |  | 92 | 93 | 0.0043552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_101-1_0_5_line_98 |  | 93 | 124 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_101-1_0_5_line_99 |  | 94 | 97 | 0.0066024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_101-1_0_5_line_100 |  | 95 | 96 | 0.023101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_101-1_0_5_line_101 |  | 96 | 156 | 0.0192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_101-1_0_5_line_102 |  | 97 | 110 | 0.0062587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_101-1_0_5_line_103 |  | 99 | 100 | 0.014377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_101-1_0_5_line_104 |  | 99 | 101 | 0.01017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_101-1_0_5_line_105 |  | 100 | 102 | 0.021484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_101-1_0_5_line_106 |  | 101 | 103 | 0.0038696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_101-1_0_5_line_107 |  | 102 | 104 | 0.016282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_101-1_0_5_line_108 |  | 102 | 105 | 0.014549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_101-1_0_5_line_109 |  | 103 | 106 | 0.02114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_101-1_0_5_line_110 |  | 104 | 107 | 0.020585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_101-1_0_5_line_111 |  | 105 | 108 | 0.022973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_101-1_0_5_line_112 |  | 106 | 109 | 0.022599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_101-1_0_5_line_113 |  | 108 | 114 | 0.002931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_101-1_0_5_line_114 |  | 108 | 153 | 0.015479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_101-1_0_5_line_115 |  | 109 | 139 | 0.0095232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_101-1_0_5_line_116 |  | 110 | 111 | 0.022618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_101-1_0_5_line_117 |  | 111 | 112 | 0.0050717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_101-1_0_5_line_118 |  | 112 | 113 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_101-1_0_5_line_119 |  | 113 | 114 | 0.017449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_101-1_0_5_line_120 |  | 115 | 116 | 0.032057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_101-1_0_5_line_121 |  | 117 | 118 | 0.0019482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_101-1_0_5_line_122 |  | 117 | 119 | 0.028292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_101-1_0_5_line_123 |  | 118 | 120 | 0.0083217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_101-1_0_5_line_124 |  | 119 | 121 | 0.015996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_101-1_0_5_line_125 |  | 119 | 122 | 0.017415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_101-1_0_5_line_126 |  | 120 | 123 | 0.011043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_101-1_0_5_line_127 |  | 121 | 124 | 0.012669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_101-1_0_5_line_128 |  | 121 | 125 | 0.013986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_101-1_0_5_line_129 |  | 122 | 126 | 0.0074296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_101-1_0_5_line_130 |  | 123 | 127 | 0.015985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_101-1_0_5_line_131 |  | 125 | 128 | 0.012302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_101-1_0_5_line_132 |  | 126 | 129 | 0.011142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_101-1_0_5_line_133 |  | 127 | 151 | 0.022536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_101-1_0_5_line_134 |  | 128 | 137 | 0.01636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_101-1_0_5_line_135 |  | 129 | 157 | 0.0092763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_101-1_0_5_line_136 |  | 130 | 131 | 0.031787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_101-1_0_5_line_137 |  | 130 | 132 | 0.013684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_101-1_0_5_line_138 |  | 132 | 133 | 0.01042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_101-1_0_5_line_139 |  | 132 | 134 | 0.018791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_101-1_0_5_line_140 |  | 133 | 135 | 0.013071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_101-1_0_5_line_141 |  | 134 | 136 | 0.030586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_101-1_0_5_line_142 |  | 135 | 137 | 0.025276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_101-1_0_5_line_143 |  | 136 | 138 | 0.0081025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_101-1_0_5_line_144 |  | 138 | 148 | 0.018498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_101-1_0_5_line_145 |  | 139 | 142 | 0.020136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_101-1_0_5_line_146 |  | 140 | 141 | 0.029604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_101-1_0_5_line_147 |  | 141 | 146 | 0.003233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_101-1_0_5_line_148 |  | 142 | 143 | 0.0049182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_101-1_0_5_line_149 |  | 143 | 144 | 0.022505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_101-1_0_5_line_150 |  | 144 | 145 | 0.036861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_101-1_0_5_line_151 |  | 145 | 147 | 0.029709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_101-1_0_5_line_152 |  | 146 | 151 | 0.022222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
153 | LV_101-1_0_5_line_153 |  | 149 | 150 | 0.030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_101-1_0_5_line_154 |  | 152 | 159 | 0.0052525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_101-1_0_5_line_155 |  | 153 | 154 | 0.00027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_101-1_0_5_line_156 |  | 154 | 155 | 0.022492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
157 | LV_101-1_0_5_line_157 |  | 155 | 157 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_101-1_0_5_line_158 |  | 155 | 156 | 0.009416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_101-1_0_5_trafo_72 | 0.63 MVA 20/0.4 kV | 160 | 90 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2677025.3966 | 1262056.6231 | 2677038.0593 | 1262081.211
1 | 2676882.9372 | 1261899.5846 | 2677025.3966 | 1262056.6231
2 | 2677044.7524 | 1262094.2072 | 2677038.0593 | 1262081.211
3 | 2676882.9372 | 1261899.5846 | 2676861.3126 | 1261848.6878 | 2676855.9156 | 1261839.6259
4 | 2677044.7524 | 1262094.2072 | 2677051.6702 | 1262107.6398
5 | 2676830.7529 | 1261819.5241 | 2676844.7886 | 1261827.8016 | 2676854.4916 | 1261837.2348 | 2676855.9156 | 1261839.6259
6 | 2677060.6351 | 1262125.0474 | 2677060.6351 | 1262125.0474 | 2677051.6702 | 1262107.6398
7 | 2677059.3141 | 1262125.7637 | 2677060.6351 | 1262125.0474
8 | 2676511.912 | 1261560.2645 | 2676512.1364 | 1261557.9513 | 2676512.1999 | 1261541.5216
9 | 2676511.912 | 1261560.2645 | 2676510.1754 | 1261578.1687
10 | 2676543.6135 | 1261551.3979 | 2676511.912 | 1261560.2645
11 | 2676510.1754 | 1261578.1687 | 2676508.8843 | 1261591.4793 | 2676508.0865 | 1261598.9747 | 2676504.2822 | 1261619.0938
12 | 2676543.6135 | 1261551.3979 | 2676545.1008 | 1261548.8625
13 | 2676500.8142 | 1261640.8284 | 2676500.758 | 1261637.7317 | 2676504.2822 | 1261619.0938
14 | 2676557.5449 | 1261527.6489 | 2676545.1008 | 1261548.8625
15 | 2676500.8142 | 1261640.8284 | 2676501.1188 | 1261657.6071 | 2676503.8108 | 1261665.2177
16 | 2676557.5449 | 1261527.6489 | 2676558.562 | 1261525.9163 | 2676565.0488 | 1261522.5198
17 | 2676503.8108 | 1261665.2177 | 2676510.0249 | 1261682.7852
18 | 2676556.9606 | 1261590.2335 | 2676565.2318 | 1261591.3893
19 | 2676576.2421 | 1261592.9279 | 2676565.2318 | 1261591.3893
20 | 2676517.4622 | 1261740.8046 | 2676517.234 | 1261723.0209 | 2676513.1349 | 1261691.5773 | 2676510.0249 | 1261682.7852
21 | 2676557.6921 | 1261653.0353 | 2676568.8379 | 1261655.2701 | 2676570.0022 | 1261662.5352 | 2676570.7098 | 1261668.9937
22 | 2676570.7098 | 1261668.9937 | 2676585.8386 | 1261671.5835
23 | 2676818.7694 | 1261461.71 | 2676813.9564 | 1261462.3222 | 2676788.5803 | 1261465.275
24 | 2676818.7694 | 1261461.71 | 2676831.9392 | 1261460.0347
25 | 2676788.5803 | 1261465.275 | 2676788.4253 | 1261465.2931 | 2676780.6195 | 1261466.9287
26 | 2676848.7752 | 1261457.8932 | 2676831.9392 | 1261460.0347
27 | 2676769.6481 | 1261469.2277 | 2676780.6195 | 1261466.9287
28 | 2676848.7752 | 1261457.8932 | 2676867.0343 | 1261455.4819
29 | 2676769.6481 | 1261469.2277 | 2676767.888 | 1261469.5965 | 2676767.1037 | 1261469.8774
30 | 2676882.8866 | 1261453.3884 | 2676867.0343 | 1261455.4819
31 | 2676755.7825 | 1261473.9317 | 2676767.1037 | 1261469.8774
32 | 2676846.1473 | 1261507.597 | 2676844.2054 | 1261524.24
33 | 2676846.1473 | 1261507.597 | 2676833.5627 | 1261507.0553 | 2676826.5955 | 1261506.1637
34 | 2676844.2054 | 1261524.24 | 2676861.0914 | 1261524.882 | 2676863.0361 | 1261524.7587
35 | 2676844.2054 | 1261524.24 | 2676843.3392 | 1261564.2148
36 | 2676820.7612 | 1261505.4171 | 2676826.5955 | 1261506.1637
37 | 2676882.8866 | 1261453.3884 | 2676913.2287 | 1261448.4345
38 | 2676882.8866 | 1261453.3884 | 2676887.3103 | 1261485.8869
39 | 2676598.9692 | 1261596.1039 | 2676576.2421 | 1261592.9279
40 | 2676598.9692 | 1261596.1039 | 2676601.2206 | 1261605.6175
41 | 2676598.9692 | 1261596.1039 | 2676595.5721 | 1261580.8816 | 2676595.1677 | 1261573.8616
42 | 2676603.2557 | 1261614.2176 | 2676601.2206 | 1261605.6175
43 | 2676595.5558 | 1261558.6761 | 2676594.6862 | 1261565.5029 | 2676595.1677 | 1261573.8616
44 | 2676603.2557 | 1261614.2176 | 2676612.997 | 1261612.031 | 2676620.1775 | 1261605.608
45 | 2676603.2557 | 1261614.2176 | 2676605.628 | 1261628.2519
46 | 2676595.5558 | 1261558.6761 | 2676596.6743 | 1261549.8945 | 2676601.9086 | 1261535.5735 | 2676607.0232 | 1261526.2043
47 | 2676622.6273 | 1261603.4166 | 2676620.1775 | 1261605.608
48 | 2676608.6604 | 1261655.9417 | 2676607.8539 | 1261641.4201 | 2676605.628 | 1261628.2519
49 | 2676609.8047 | 1261521.1092 | 2676607.0232 | 1261526.2043
50 | 2676755.7825 | 1261473.9317 | 2676755.7825 | 1261473.9317 | 2676742.3639 | 1261480.605
51 | 2676740.3331 | 1261481.6149 | 2676742.3639 | 1261480.605
52 | 2676740.3331 | 1261481.6149 | 2676746.05 | 1261491.6745 | 2676751.4607 | 1261491.9655
53 | 2676740.3331 | 1261481.6149 | 2676734.8725 | 1261485.2458
54 | 2676913.2287 | 1261448.4345 | 2676915.2783 | 1261468.7099
55 | 2676913.2287 | 1261448.4345 | 2676911.9994 | 1261427.015
56 | 2676891.1387 | 1261514.0121 | 2676887.3103 | 1261485.8869
57 | 2676894.3344 | 1261537.4897 | 2676891.1387 | 1261514.0121
58 | 2676895.1988 | 1261543.8396 | 2676894.3344 | 1261537.4897
59 | 2676868.6551 | 1261524.4024 | 2676863.0361 | 1261524.7587
60 | 2676843.3392 | 1261564.2148 | 2676843.2319 | 1261582.8507
61 | 2676843.3392 | 1261564.2148 | 2676823.1057 | 1261562.755
62 | 2676807.7207 | 1261503.7483 | 2676820.7612 | 1261505.4171
63 | 2676602.5123 | 1261717.5424 | 2676601.4997 | 1261724.0581
64 | 2676608.2143 | 1261673.5049 | 2676607.3989 | 1261682.9348 | 2676605.7744 | 1261697.2358 | 2676602.5123 | 1261717.5424
65 | 2676609.9522 | 1261512.0486 | 2676599.9481 | 1261505.0026
66 | 2676609.8047 | 1261521.1092 | 2676610.3996 | 1261519.9716 | 2676613.5813 | 1261514.6087 | 2676609.9522 | 1261512.0486
67 | 2676620.9765 | 1261502.1616 | 2676613.5813 | 1261514.6087 | 2676609.9522 | 1261512.0486
68 | 2676609.8047 | 1261521.1092 | 2676581.9947 | 1261510.9748 | 2676572.6976 | 1261522.4855 | 2676572.6976 | 1261522.4855
69 | 2676628.1744 | 1261495.6499 | 2676620.9765 | 1261502.1616
70 | 2676620.9765 | 1261502.1616 | 2676624.4352 | 1261507.3993 | 2676626.9783 | 1261505.9533 | 2676630.9324 | 1261504.9482 | 2676634.6634 | 1261505.4525 | 2676634.6634 | 1261505.4525
71 | 2676565.0488 | 1261522.5198 | 2676572.6976 | 1261522.4855
72 | 2676628.1744 | 1261495.6499 | 2676631.2155 | 1261498.8028 | 2676634.7737 | 1261501.0172 | 2676642.685 | 1261503.9886 | 2676652.0715 | 1261505.9339 | 2676658.7319 | 1261506.1256
73 | 2676693.8202 | 1261506.3307 | 2676687.2756 | 1261507.2021 | 2676676.8646 | 1261506.9781 | 2676666.1349 | 1261506.3386 | 2676658.7319 | 1261506.1256
74 | 2676589.7542 | 1261672.2538 | 2676585.8386 | 1261671.5835
75 | 2676608.2143 | 1261673.5049 | 2676589.7542 | 1261672.2538 | 2676589.7542 | 1261672.2538
76 | 2676608.2143 | 1261673.5049 | 2676608.6604 | 1261655.9417
77 | 2676608.6604 | 1261655.9417 | 2676613.7851 | 1261656.464 | 2676622.9453 | 1261658.9956 | 2676638.1081 | 1261663.4162
78 | 2676652.7625 | 1261667.6885 | 2676638.1081 | 1261663.4162
79 | 2676652.7625 | 1261667.6885 | 2676651.5247 | 1261673.0766 | 2676649.5363 | 1261685.1207
80 | 2676653.5933 | 1261664.052 | 2676652.7625 | 1261667.6885
81 | 2676650.8766 | 1261698.0761 | 2676649.2514 | 1261686.8465 | 2676649.5363 | 1261685.1207
82 | 2676653.5933 | 1261664.052 | 2676666.0099 | 1261669.7322
83 | 2676782.1451 | 1261507.8996 | 2676776.4299 | 1261505.2568 | 2676762.1345 | 1261492.5394 | 2676751.4607 | 1261491.9655
84 | 2676734.8725 | 1261485.2458 | 2676722.5481 | 1261493.4404
85 | 2676722.5481 | 1261493.4404 | 2676719.7799 | 1261495.2811 | 2676714.6904 | 1261498.471
86 | 2676695.1514 | 1261506.0767 | 2676702.1146 | 1261504.7482 | 2676709.0906 | 1261501.9809 | 2676714.6904 | 1261498.471
87 | 2676693.8202 | 1261506.3307 | 2676695.1514 | 1261506.0767
88 | 2676693.8202 | 1261506.3307 | 2676693.8668 | 1261510.8681
89 | 2676693.8668 | 1261510.8681 | 2676688.3573 | 1261510.9523 | 2676681.5913 | 1261510.3086 | 2676675.4557 | 1261510.3348
90 | 2676694.2313 | 1261548.9908 | 2676679.5866 | 1261553.4663
91 | 2676694.2313 | 1261548.9908 | 2676711.1871 | 1261546.9442
92 | 2676679.5866 | 1261553.4663 | 2676672.7265 | 1261555.5628
93 | 2676711.1871 | 1261546.9442 | 2676713.7516 | 1261546.6347
94 | 2676667.9646 | 1261638.4027 | 2676680.2157 | 1261631.4832
95 | 2676685.8905 | 1261631.1016 | 2676680.2157 | 1261631.4832 | 2676680.2157 | 1261631.4832
96 | 2676685.8905 | 1261631.1016 | 2676694.7714 | 1261630.5045 | 2676706.9173 | 1261635.0329
97 | 2676706.9173 | 1261635.0329 | 2676710.9981 | 1261636.5543
98 | 2676729.6163 | 1261643.7859 | 2676713.7439 | 1261637.578 | 2676710.9981 | 1261636.5543
99 | 2676650.8766 | 1261698.0761 | 2676650.8766 | 1261698.0761 | 2676654.7256 | 1261703.4405
100 | 2676708.7234 | 1261689.2725 | 2676687.7165 | 1261679.6624
101 | 2676708.7234 | 1261689.2725 | 2676717.834 | 1261693.4404 | 2676726.1042 | 1261697.429
102 | 2676658.3742 | 1261708.5257 | 2676654.7256 | 1261703.4405
103 | 2676787.6112 | 1261762.7247 | 2676779.6618 | 1261762.3617 | 2676773.7754 | 1261759.8014
104 | 2676797.7707 | 1261763.1888 | 2676787.6112 | 1261762.7247
105 | 2676754.074 | 1261751.2323 | 2676773.7754 | 1261759.8014
106 | 2676797.7707 | 1261763.1888 | 2676801.6362 | 1261763.3653
107 | 2676754.074 | 1261751.2323 | 2676760.962 | 1261736.4787
108 | 2676754.074 | 1261751.2323 | 2676740.6667 | 1261745.5826
109 | 2676822.7539 | 1261764.3298 | 2676801.6362 | 1261763.3653
110 | 2676774.7935 | 1261723.5355 | 2676765.5294 | 1261726.6955 | 2676760.962 | 1261736.4787
111 | 2676719.496 | 1261736.6616 | 2676740.6667 | 1261745.5826
112 | 2676845.3289 | 1261765.3609 | 2676822.7539 | 1261764.3298
113 | 2676719.496 | 1261736.6616 | 2676716.7674 | 1261735.5698
114 | 2676719.496 | 1261736.6616 | 2676725.6033 | 1261722.4381
115 | 2676845.3289 | 1261765.3609 | 2676845.3867 | 1261774.8839
116 | 2676658.3742 | 1261708.5257 | 2676658.3742 | 1261708.5257 | 2676672.6556 | 1261715.9053 | 2676678.6216 | 1261718.5909
117 | 2676683.2463 | 1261720.6727 | 2676678.6216 | 1261718.5909
118 | 2676683.2463 | 1261720.6727 | 2676700.7861 | 1261728.5685
119 | 2676716.7674 | 1261735.5698 | 2676709.2811 | 1261732.3926 | 2676700.7861 | 1261728.5685
120 | 2676647.075 | 1261573.8008 | 2676649.8784 | 1261569.8987 | 2676666.7616 | 1261557.3857 | 2676672.7265 | 1261555.5628
121 | 2676784.7034 | 1261657.3767 | 2676786.6249 | 1261657.6985
122 | 2676756.7999 | 1261652.7035 | 2676784.7034 | 1261657.3767
123 | 2676794.8714 | 1261658.7641 | 2676790.9882 | 1261658.4293 | 2676786.6249 | 1261657.6985
124 | 2676741.2294 | 1261648.8431 | 2676756.7999 | 1261652.7035
125 | 2676756.7999 | 1261652.7035 | 2676753.29 | 1261669.7615
126 | 2676805.8739 | 1261659.7129 | 2676794.8714 | 1261658.7641
127 | 2676741.2294 | 1261648.8431 | 2676731.9171 | 1261644.6858 | 2676729.6163 | 1261643.7859
128 | 2676741.2294 | 1261648.8431 | 2676742.1587 | 1261634.8882
129 | 2676751.7927 | 1261677.0386 | 2676753.29 | 1261669.7615
130 | 2676805.8739 | 1261659.7129 | 2676820.1395 | 1261660.943 | 2676821.8042 | 1261661.009
131 | 2676742.9762 | 1261622.6135 | 2676742.1587 | 1261634.8882
132 | 2676751.7927 | 1261677.0386 | 2676749.5471 | 1261687.9524
133 | 2676844.3226 | 1261661.9022 | 2676821.8042 | 1261661.009
134 | 2676744.0633 | 1261606.2898 | 2676742.9762 | 1261622.6135
135 | 2676744.6691 | 1261694.9832 | 2676748.6285 | 1261692.4167 | 2676749.5471 | 1261687.9524
136 | 2676744.1087 | 1261546.6913 | 2676740.3975 | 1261543.4185 | 2676713.7516 | 1261546.6347
137 | 2676747.3038 | 1261557.63 | 2676749.4195 | 1261551.3749 | 2676744.1087 | 1261546.6913
138 | 2676747.3038 | 1261557.63 | 2676746.6114 | 1261568.0272
139 | 2676747.3038 | 1261557.63 | 2676766.0688 | 1261558.6249
140 | 2676746.6114 | 1261568.0272 | 2676745.7428 | 1261581.0694
141 | 2676766.0688 | 1261558.6249 | 2676766.4681 | 1261558.6461 | 2676793.5245 | 1261560.6209 | 2676796.5742 | 1261560.8409
142 | 2676744.0633 | 1261606.2898 | 2676745.7428 | 1261581.0694
143 | 2676804.6557 | 1261561.424 | 2676796.5742 | 1261560.8409
144 | 2676804.6557 | 1261561.424 | 2676823.1057 | 1261562.755
145 | 2676845.3867 | 1261774.8839 | 2676845.4153 | 1261779.584 | 2676841.9096 | 1261794.6165
146 | 2676845.2325 | 1261716.9438 | 2676845.2506 | 1261692.5376 | 2676845.1788 | 1261687.3401
147 | 2676845.1342 | 1261684.1074 | 2676845.1788 | 1261687.3401
148 | 2676841.9096 | 1261794.6165 | 2676840.7925 | 1261799.4062
149 | 2676830.7529 | 1261819.5241 | 2676840.6194 | 1261800.1485 | 2676840.7925 | 1261799.4062
150 | 2676830.7529 | 1261819.5241 | 2676825.8438 | 1261833.7379 | 2676816.2433 | 1261853.3362
151 | 2676803.1738 | 1261880.016 | 2676816.2433 | 1261853.3362
152 | 2676844.3226 | 1261661.9022 | 2676845.1342 | 1261684.1074
153 | 2676843.2319 | 1261582.8507 | 2676843.2134 | 1261586.0743 | 2676843.4907 | 1261612.9233
154 | 2676873.8971 | 1261524.07 | 2676868.6551 | 1261524.4024
155 | 2676725.6033 | 1261722.4381 | 2676725.7111 | 1261722.1871
156 | 2676734.5854 | 1261701.5193 | 2676725.7111 | 1261722.1871
157 | 2676734.5854 | 1261701.5193 | 2676744.6691 | 1261694.9832
158 | 2676734.5854 | 1261701.5193 | 2676726.1042 | 1261697.429

## bus_geodata
| x | y | coords
0 | 2677025.3966 | 1262056.6231
1 | 2677038.0593 | 1262081.211
2 | 2676882.9372 | 1261899.5846
3 | 2677044.7524 | 1262094.2072
4 | 2676855.9156 | 1261839.6259
5 | 2677051.6702 | 1262107.6398
6 | 2677060.6351 | 1262125.0474
7 | 2677059.3141 | 1262125.7637
8 | 2676511.912 | 1261560.2645
9 | 2676512.1999 | 1261541.5216
10 | 2676510.1754 | 1261578.1687
11 | 2676543.6135 | 1261551.3979
12 | 2676504.2822 | 1261619.0938
13 | 2676545.1008 | 1261548.8625
14 | 2676500.8142 | 1261640.8284
15 | 2676557.5449 | 1261527.6489
16 | 2676503.8108 | 1261665.2177
17 | 2676556.9606 | 1261590.2335
18 | 2676565.2318 | 1261591.3893
19 | 2676510.0249 | 1261682.7852
20 | 2676557.6921 | 1261653.0353
21 | 2676570.7098 | 1261668.9937
22 | 2676517.4622 | 1261740.8046
23 | 2676818.7694 | 1261461.71
24 | 2676788.5803 | 1261465.275
25 | 2676831.9392 | 1261460.0347
26 | 2676780.6195 | 1261466.9287
27 | 2676848.7752 | 1261457.8932
28 | 2676769.6481 | 1261469.2277
29 | 2676867.0343 | 1261455.4819
30 | 2676767.1037 | 1261469.8774
31 | 2676846.1473 | 1261507.597
32 | 2676844.2054 | 1261524.24
33 | 2676826.5955 | 1261506.1637
34 | 2676882.8866 | 1261453.3884
35 | 2676576.2421 | 1261592.9279
36 | 2676598.9692 | 1261596.1039
37 | 2676601.2206 | 1261605.6175
38 | 2676595.1677 | 1261573.8616
39 | 2676603.2557 | 1261614.2176
40 | 2676595.5558 | 1261558.6761
41 | 2676620.1775 | 1261605.608
42 | 2676605.628 | 1261628.2519
43 | 2676607.0232 | 1261526.2043
44 | 2676755.7825 | 1261473.9317
45 | 2676742.3639 | 1261480.605
46 | 2676740.3331 | 1261481.6149
47 | 2676913.2287 | 1261448.4345
48 | 2676887.3103 | 1261485.8869
49 | 2676915.2783 | 1261468.7099
50 | 2676911.9994 | 1261427.015
51 | 2676891.1387 | 1261514.0121
52 | 2676894.3344 | 1261537.4897
53 | 2676863.0361 | 1261524.7587
54 | 2676843.3392 | 1261564.2148
55 | 2676820.7612 | 1261505.4171
56 | 2676601.4997 | 1261724.0581
57 | 2676602.5123 | 1261717.5424
58 | 2676599.9481 | 1261505.0026
59 | 2676609.9522 | 1261512.0486
60 | 2676609.8047 | 1261521.1092
61 | 2676620.9765 | 1261502.1616
62 | 2676572.6976 | 1261522.4855
63 | 2676628.1744 | 1261495.6499
64 | 2676634.6634 | 1261505.4525
65 | 2676565.0488 | 1261522.5198
66 | 2676658.7319 | 1261506.1256
67 | 2676585.8386 | 1261671.5835
68 | 2676589.7542 | 1261672.2538
69 | 2676608.2143 | 1261673.5049
70 | 2676608.6604 | 1261655.9417
71 | 2676638.1081 | 1261663.4162
72 | 2676652.7625 | 1261667.6885
73 | 2676622.6273 | 1261603.4166
74 | 2676649.5363 | 1261685.1207
75 | 2676653.5933 | 1261664.052
76 | 2676751.4607 | 1261491.9655
77 | 2676734.8725 | 1261485.2458
78 | 2676782.1451 | 1261507.8996
79 | 2676722.5481 | 1261493.4404
80 | 2676714.6904 | 1261498.471
81 | 2676695.1514 | 1261506.0767
82 | 2676693.8202 | 1261506.3307
83 | 2676693.8668 | 1261510.8681
84 | 2676675.4557 | 1261510.3348
85 | 2676694.2313 | 1261548.9908
86 | 2676679.5866 | 1261553.4663
87 | 2676711.1871 | 1261546.9442
88 | 2676667.9646 | 1261638.4027
89 | 2676680.2157 | 1261631.4832
90 | 2676685.8905 | 1261631.1016
91 | 2676666.0099 | 1261669.7322
92 | 2676706.9173 | 1261635.0329
93 | 2676710.9981 | 1261636.5543
94 | 2676650.8766 | 1261698.0761
95 | 2676687.7165 | 1261679.6624
96 | 2676708.7234 | 1261689.2725
97 | 2676654.7256 | 1261703.4405
98 | 2676807.7207 | 1261503.7483
99 | 2676787.6112 | 1261762.7247
100 | 2676773.7754 | 1261759.8014
101 | 2676797.7707 | 1261763.1888
102 | 2676754.074 | 1261751.2323
103 | 2676801.6362 | 1261763.3653
104 | 2676760.962 | 1261736.4787
105 | 2676740.6667 | 1261745.5826
106 | 2676822.7539 | 1261764.3298
107 | 2676774.7935 | 1261723.5355
108 | 2676719.496 | 1261736.6616
109 | 2676845.3289 | 1261765.3609
110 | 2676658.3742 | 1261708.5257
111 | 2676678.6216 | 1261718.5909
112 | 2676683.2463 | 1261720.6727
113 | 2676700.7861 | 1261728.5685
114 | 2676716.7674 | 1261735.5698
115 | 2676647.075 | 1261573.8008
116 | 2676672.7265 | 1261555.5628
117 | 2676784.7034 | 1261657.3767
118 | 2676786.6249 | 1261657.6985
119 | 2676756.7999 | 1261652.7035
120 | 2676794.8714 | 1261658.7641
121 | 2676741.2294 | 1261648.8431
122 | 2676753.29 | 1261669.7615
123 | 2676805.8739 | 1261659.7129
124 | 2676729.6163 | 1261643.7859
125 | 2676742.1587 | 1261634.8882
126 | 2676751.7927 | 1261677.0386
127 | 2676821.8042 | 1261661.009
128 | 2676742.9762 | 1261622.6135
129 | 2676749.5471 | 1261687.9524
130 | 2676744.1087 | 1261546.6913
131 | 2676713.7516 | 1261546.6347
132 | 2676747.3038 | 1261557.63
133 | 2676746.6114 | 1261568.0272
134 | 2676766.0688 | 1261558.6249
135 | 2676745.7428 | 1261581.0694
136 | 2676796.5742 | 1261560.8409
137 | 2676744.0633 | 1261606.2898
138 | 2676804.6557 | 1261561.424
139 | 2676845.3867 | 1261774.8839
140 | 2676845.2325 | 1261716.9438
141 | 2676845.1788 | 1261687.3401
142 | 2676841.9096 | 1261794.6165
143 | 2676840.7926 | 1261799.4062
144 | 2676830.7529 | 1261819.5241
145 | 2676816.2433 | 1261853.3362
146 | 2676845.1342 | 1261684.1074
147 | 2676803.1738 | 1261880.016
148 | 2676823.1057 | 1261562.755
149 | 2676843.2319 | 1261582.8507
150 | 2676843.4907 | 1261612.9233
151 | 2676844.3226 | 1261661.9022
152 | 2676868.6551 | 1261524.4024
153 | 2676725.6033 | 1261722.4381
154 | 2676725.7111 | 1261722.1871
155 | 2676734.5854 | 1261701.5193
156 | 2676726.1042 | 1261697.429
157 | 2676744.6691 | 1261694.9832
158 | 2676895.1988 | 1261543.8396
159 | 2676873.8971 | 1261524.07
160 | 2676653.5933 | 1261664.052

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98219 | -0.34136 | 0.0011158 | 0.00027965
1 | 0.98204 | -0.34426 | 0.0008829 | 0.00022128
2 | 0.98354 | -0.31486 | 0.0003673 | 9.2053e-05
3 | 0.98198 | -0.34556 | 0.0031525 | 0.00079008
4 | 0.98399 | -0.30621 | 0.00133 | 0.00033333
5 | 0.98195 | -0.34605 | 0.00099853 | 0.00025025
6 | 0.98194 | -0.34632 | 0.00039964 | 0.00010016
7 | 0.98194 | -0.34633 | 0.00037083 | 9.2939e-05
8 | 0.97299 | -0.52029 | 0.0014607 | 0.00036609
9 | 0.97294 | -0.52126 | 0.0028128 | 0.00070495
10 | 0.97277 | -0.52456 | 0.001143 | 0.00028647
11 | 0.97352 | -0.50988 | 0.0015706 | 0.00039363
12 | 0.97232 | -0.53354 | 0.0023757 | 0.00059542
13 | 0.97357 | -0.50887 | 0.0013768 | 0.00034506
14 | 0.97213 | -0.53736 | 0.0023787 | 0.00059616
15 | 0.97403 | -0.49977 | 0 | 0
16 | 0.97196 | -0.54057 | 0.0022179 | 0.00055585
17 | 0.9769 | -0.44347 | 0.0075836 | 0.0019006
18 | 0.97696 | -0.44232 | 0.0039679 | 0.00099444
19 | 0.97188 | -0.54222 | 0.0021173 | 0.00053064
20 | 0.97827 | -0.41677 | 0.01301 | 0.0032605
21 | 0.97857 | -0.4108 | 0.0077967 | 0.001954
22 | 0.97173 | -0.54511 | 0.0026698 | 0.0006691
23 | 0.9707 | -0.56552 | 0.0031708 | 0.00079468
24 | 0.97088 | -0.56203 | 0.014564 | 0.0036502
25 | 0.97063 | -0.56684 | 0.004333 | 0.001086
26 | 0.97095 | -0.56055 | 0.0063371 | 0.0015882
27 | 0.97056 | -0.5682 | 0.0012523 | 0.00031386
28 | 0.97107 | -0.55819 | 0.0034017 | 0.00085254
29 | 0.9705 | -0.56956 | 0.0021153 | 0.00053013
30 | 0.9711 | -0.55759 | 0.0026189 | 0.00065637
31 | 0.99344 | -0.1248 | 0 | 0
32 | 0.9935 | -0.12357 | 0 | 0
33 | 0.99337 | -0.12624 | 0.00039923 | 0.00010006
34 | 0.97044 | -0.57059 | 0 | 0
35 | 0.97708 | -0.43997 | 0.0038649 | 0.00096863
36 | 0.9774 | -0.43351 | 0 | 0
37 | 0.97776 | -0.42644 | 0.0042764 | 0.0010718
38 | 0.97665 | -0.44831 | 0.0018824 | 0.00047178
39 | 0.9781 | -0.41988 | 0 | 0
40 | 0.97614 | -0.45817 | 0.010973 | 0.0027501
41 | 0.97797 | -0.42248 | 0.0020687 | 0.00051846
42 | 0.97866 | -0.40885 | 0.0053233 | 0.0013342
43 | 0.97509 | -0.47894 | 0.0022589 | 0.00056614
44 | 0.97125 | -0.55472 | 0.010422 | 0.0026121
45 | 0.97146 | -0.55042 | 0.009781 | 0.0024513
46 | 0.9715 | -0.54967 | 0 | 0
47 | 0.9704 | -0.5715 | 0 | 0
48 | 0.97039 | -0.57172 | 0.0025237 | 0.0006325
49 | 0.97036 | -0.57234 | 0.0044162 | 0.0011068
50 | 0.97036 | -0.5723 | 0.0020204 | 0.00050637
51 | 0.97035 | -0.57237 | 0.0017497 | 0.00043851
52 | 0.97034 | -0.57271 | 0.0022121 | 0.00055442
53 | 0.99347 | -0.12427 | 0.0007373 | 0.00018479
54 | 0.99373 | -0.11916 | 0 | 0
55 | 0.99335 | -0.12663 | 0.0033645 | 0.00084321
56 | 0.97925 | -0.3974 | 0.0077637 | 0.0019458
57 | 0.9793 | -0.39647 | 0 | 0
58 | 0.97462 | -0.48807 | 0.00073096 | 0.0001832
59 | 0.97463 | -0.48791 | 0 | 0
60 | 0.97491 | -0.48235 | 0 | 0
61 | 0.97419 | -0.49666 | 0 | 0
62 | 0.97436 | -0.49322 | 0.0046203 | 0.001158
63 | 0.97397 | -0.50087 | 0 | 0
64 | 0.97409 | -0.49856 | 0.0060853 | 0.0015251
65 | 0.9742 | -0.49632 | 0.001939 | 0.00048596
66 | 0.97324 | -0.51534 | 0.002485 | 0.0006228
67 | 0.97887 | -0.40499 | 0.0091113 | 0.0022835
68 | 0.97898 | -0.40283 | 0.0076255 | 0.0019111
69 | 0.97962 | -0.3902 | 0 | 0
70 | 0.97981 | -0.38659 | 0 | 0
71 | 0.98137 | -0.35611 | 0.0024648 | 0.00061775
72 | 0.98216 | -0.34069 | 0 | 0
73 | 0.97795 | -0.42279 | 0.0052019 | 0.0013037
74 | 0.98309 | -0.32267 | 0.0023819 | 0.00059697
75 | 0.98216 | -0.34081 | 0 | 0
76 | 0.97145 | -0.55069 | 0.0021104 | 0.00052892
77 | 0.97162 | -0.54739 | 0.0016726 | 0.00041918
78 | 0.97141 | -0.55146 | 0.001155 | 0.00028946
79 | 0.97188 | -0.54214 | 0.0032283 | 0.00080909
80 | 0.97206 | -0.5387 | 0.00088555 | 0.00022194
81 | 0.97246 | -0.53078 | 0.0017774 | 0.00044547
82 | 0.97248 | -0.53027 | 0 | 0
83 | 0.97244 | -0.53105 | 0 | 0
84 | 0.97228 | -0.53425 | 0.0094041 | 0.0023569
85 | 0.99438 | -0.10656 | 0 | 0
86 | 0.99433 | -0.10762 | 0.0082088 | 0.0020573
87 | 0.99445 | -0.10537 | 0.001705 | 0.00042731
88 | 0.99995 | -0.00094865 | 0.00207 | 0.00051879
89 | 0.99998 | -0.00044093 | 0.0023773 | 0.0005958
90 | 1 | 0 | -0.35321 | -0.090532
91 | 0.98214 | -0.34126 | 0.0017964 | 0.00045021
92 | 0.99827 | -0.032532 | 0.0026835 | 0.00067255
93 | 0.99793 | -0.038975 | 0.0012705 | 0.00031841
94 | 0.98379 | -0.30925 | 0.0015012 | 0.00037624
95 | 0.99047 | -0.18081 | 0.0012928 | 0.00032401
96 | 0.99049 | -0.18028 | 0.0011573 | 0.00029004
97 | 0.98414 | -0.30244 | 0.002221 | 0.00055663
98 | 0.99334 | -0.12672 | 0.00039024 | 9.7804e-05
99 | 0.98651 | -0.25705 | 0.0007502 | 0.00018802
100 | 0.98686 | -0.25023 | 0.0011499 | 0.0002882
101 | 0.98627 | -0.26174 | 0.00096497 | 0.00024184
102 | 0.98741 | -0.23961 | 0 | 0
103 | 0.98618 | -0.26346 | 0.00056813 | 0.00014239
104 | 0.98737 | -0.24025 | 0.0012505 | 0.00031342
105 | 0.98781 | -0.23184 | 0.0030421 | 0.00076241
106 | 0.98571 | -0.27263 | 0.00087625 | 0.00021961
107 | 0.98736 | -0.24061 | 0.00096696 | 0.00024234
108 | 0.98815 | -0.2251 | 0 | 0
109 | 0.98522 | -0.2821 | 0 | 0
110 | 0.98448 | -0.29593 | 0.0015035 | 0.00037682
111 | 0.9857 | -0.27229 | 0.00088268 | 0.00022122
112 | 0.98598 | -0.26698 | 0.0017131 | 0.00042934
113 | 0.98703 | -0.2467 | 0.0019565 | 0.00049036
114 | 0.98799 | -0.2282 | 0 | 0
115 | 0.99419 | -0.11033 | 0.0030945 | 0.00077555
116 | 0.99428 | -0.10858 | 0.0044713 | 0.0011206
117 | 0.99422 | -0.10942 | 0.0022124 | 0.00055447
118 | 0.99421 | -0.10951 | 0.002311 | 0.00057918
119 | 0.99429 | -0.1079 | 0 | 0
120 | 0.9942 | -0.10979 | 0.0017431 | 0.00043687
121 | 0.99539 | -0.087131 | 0 | 0
122 | 0.99315 | -0.12962 | 0.0011627 | 0.00029139
123 | 0.99418 | -0.11008 | 0.0010501 | 0.00026317
124 | 0.99637 | -0.068467 | 0.001606 | 0.0004025
125 | 0.99526 | -0.089618 | 0.0017538 | 0.00043955
126 | 0.99266 | -0.13886 | 0.0024747 | 0.00062021
127 | 0.99416 | -0.11043 | 0.0018908 | 0.00047387
128 | 0.99515 | -0.091712 | 0.0027085 | 0.00067881
129 | 0.99194 | -0.15262 | 0.00066491 | 0.00016664
130 | 0.99459 | -0.10248 | 0.00061978 | 0.00015533
131 | 0.99446 | -0.10517 | 0.0017398 | 0.00043603
132 | 0.99466 | -0.10128 | 0 | 0
133 | 0.99473 | -0.099821 | 0.00038227 | 9.5806e-05
134 | 0.99445 | -0.10527 | 0.00073959 | 0.00018536
135 | 0.99483 | -0.097964 | 0.00064047 | 0.00016052
136 | 0.99414 | -0.11136 | 0.0011807 | 0.00029592
137 | 0.99502 | -0.094301 | 0.0030494 | 0.00076425
138 | 0.99406 | -0.11281 | 0.00049721 | 0.00012461
139 | 0.98502 | -0.28609 | 0.0024528 | 0.00061472
140 | 0.99408 | -0.11212 | 0.0015877 | 0.00039791
141 | 0.99412 | -0.11129 | 0.0014218 | 0.00035634
142 | 0.98463 | -0.29364 | 0.0016476 | 0.00041293
143 | 0.98454 | -0.29534 | 0.0048891 | 0.0012253
144 | 0.98425 | -0.30115 | 0 | 0
145 | 0.98405 | -0.30493 | 0.00095933 | 0.00024043
146 | 0.99413 | -0.11112 | 0 | 0
147 | 0.98392 | -0.30747 | 0.0047477 | 0.0011899
148 | 0.9939 | -0.11595 | 0.00064631 | 0.00016198
149 | 0.99369 | -0.12005 | 0.00088984 | 0.00022302
150 | 0.99364 | -0.12102 | 0.0018222 | 0.00045669
151 | 0.99415 | -0.11073 | 0 | 0
152 | 0.99346 | -0.12441 | 0.00056933 | 0.00014269
153 | 0.98913 | -0.20645 | 0.0013279 | 0.0003328
154 | 0.98914 | -0.20612 | 0.0013596 | 0.00034074
155 | 0.99057 | -0.17882 | 0 | 0
156 | 0.99054 | -0.17944 | 0.0012897 | 0.00032322
157 | 0.99134 | -0.16406 | 0.0016712 | 0.00041883
158 | 0.97034 | -0.57274 | 0.00095399 | 0.00023909
159 | 0.99346 | -0.12448 | 0.00079191 | 0.00019847
160 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0058055 | 0.0014545 | -0.0058047 | -0.0014543 | 8.0228e-07 | 1.6348e-07 | 0.0087951 | 0.0087953 | 0.0087953 | 0.98219 | -0.34136 | 0.98204 | -0.34426 | 2.4163
1 | -0.0069213 | -0.0017341 | 0.0069301 | 0.001737 | 8.7413e-06 | 2.9072e-06 | 0.010486 | 0.010485 | 0.010486 | 0.98219 | -0.34136 | 0.98354 | -0.31486 | 2.8807
2 | 0.0049218 | 0.001233 | -0.0049215 | -0.001233 | 3.0488e-07 | 1.0174e-08 | 0.0074575 | 0.0074575 | 0.0074575 | 0.98204 | -0.34426 | 0.98198 | -0.34556 | 2.0488
3 | -0.0072974 | -0.0018291 | 0.0073004 | 0.0018302 | 3.0097e-06 | 1.0902e-06 | 0.01104 | 0.01104 | 0.01104 | 0.98354 | -0.31486 | 0.98399 | -0.30621 | 3.0331
4 | 0.001769 | 0.00044293 | -0.001769 | -0.00044309 | 4.0712e-08 | -1.6508e-07 | 0.0026805 | 0.0026806 | 0.0026806 | 0.98198 | -0.34556 | 0.98195 | -0.34605 | 0.73643
5 | -0.0086304 | -0.0021635 | 0.0086325 | 0.0021644 | 2.083e-06 | 9.1878e-07 | 0.013051 | 0.013051 | 0.013051 | 0.98399 | -0.30621 | 0.98425 | -0.30115 | 3.5855
6 | 0.00077048 | 0.00019284 | -0.00077047 | -0.00019308 | 1.0009e-08 | -2.4128e-07 | 0.0011675 | 0.0011676 | 0.0011676 | 0.98195 | -0.34605 | 0.98194 | -0.34632 | 0.32076
7 | 0.00037083 | 9.292e-05 | -0.00037083 | -9.2939e-05 | 1.7803e-10 | -1.8894e-08 | 0.00056195 | 0.00056195 | 0.00056195 | 0.98194 | -0.34632 | 0.98194 | -0.34633 | 0.15438
8 | 0.0028129 | 0.0007048 | -0.0028128 | -0.00070495 | 1.3014e-07 | -1.4962e-07 | 0.0043018 | 0.0043019 | 0.0043019 | 0.97299 | -0.52029 | 0.97294 | -0.52126 | 1.1818
9 | 0.012914 | 0.0032385 | -0.012911 | -0.0032371 | 2.6311e-06 | 1.4606e-06 | 0.01975 | 0.01975 | 0.01975 | 0.97299 | -0.52029 | 0.97277 | -0.52456 | 5.4258
10 | -0.017187 | -0.0043094 | 0.017196 | 0.0043145 | 8.5289e-06 | 5.0494e-06 | 0.026285 | 0.026285 | 0.026285 | 0.97299 | -0.52029 | 0.97352 | -0.50988 | 7.2213
11 | 0.011768 | 0.0029506 | -0.011763 | -0.0029479 | 5.0292e-06 | 2.7052e-06 | 0.018001 | 0.018002 | 0.018002 | 0.97277 | -0.52456 | 0.97232 | -0.53354 | 4.9455
12 | -0.018766 | -0.0047081 | 0.018767 | 0.0047086 | 9.0705e-07 | 5.4396e-07 | 0.028686 | 0.028686 | 0.028686 | 0.97352 | -0.50988 | 0.97357 | -0.50887 | 7.8808
13 | 0.0093871 | 0.0023525 | -0.0093854 | -0.0023516 | 1.7077e-06 | 8.1928e-07 | 0.014366 | 0.014366 | 0.014366 | 0.97232 | -0.53354 | 0.97213 | -0.53736 | 3.9467
14 | -0.020144 | -0.0050537 | 0.020153 | 0.005059 | 8.7436e-06 | 5.2899e-06 | 0.03079 | 0.03079 | 0.03079 | 0.97357 | -0.50887 | 0.97403 | -0.49977 | 8.4589
15 | 0.0070067 | 0.0017555 | -0.0070056 | -0.0017551 | 1.0721e-06 | 3.7802e-07 | 0.010725 | 0.010725 | 0.010725 | 0.97213 | -0.53736 | 0.97196 | -0.54057 | 2.9464
16 | -0.020153 | -0.005059 | 0.020156 | 0.005061 | 3.3174e-06 | 2.007e-06 | 0.03079 | 0.03079 | 0.03079 | 0.97403 | -0.49977 | 0.9742 | -0.49632 | 8.4588
17 | 0.0047878 | 0.0011993 | -0.0047874 | -0.0011992 | 3.754e-07 | 9.3264e-09 | 0.0073295 | 0.0073296 | 0.0073296 | 0.97196 | -0.54057 | 0.97188 | -0.54222 | 2.0136
18 | -0.0075836 | -0.0019006 | 0.007584 | 0.0019008 | 4.179e-07 | 1.6288e-07 | 0.011551 | 0.011551 | 0.011551 | 0.9769 | -0.44347 | 0.97696 | -0.44232 | 3.1735
19 | -0.011552 | -0.0028952 | 0.011553 | 0.0028959 | 1.2906e-06 | 6.8678e-07 | 0.017595 | 0.017595 | 0.017595 | 0.97696 | -0.44232 | 0.97708 | -0.43997 | 4.8338
20 | 0.0026701 | 0.00066861 | -0.0026698 | -0.0006691 | 3.6864e-07 | -4.9286e-07 | 0.0040879 | 0.0040882 | 0.0040882 | 0.97188 | -0.54222 | 0.97173 | -0.54511 | 1.1231
21 | -0.01301 | -0.0032605 | 0.013013 | 0.0032626 | 3.7038e-06 | 2.0536e-06 | 0.019788 | 0.019788 | 0.019788 | 0.97827 | -0.41677 | 0.97857 | -0.4108 | 5.4364
22 | -0.02081 | -0.0052166 | 0.020816 | 0.0052201 | 5.7636e-06 | 3.4958e-06 | 0.031644 | 0.031644 | 0.031644 | 0.97857 | -0.4108 | 0.97887 | -0.40499 | 8.6934
23 | -0.024753 | -0.0061957 | 0.024757 | 0.0061969 | 4.1026e-06 | 1.1222e-06 | 0.037942 | 0.037941 | 0.037942 | 0.9707 | -0.56552 | 0.97088 | -0.56203 | 2.6059
24 | 0.021582 | 0.0054011 | -0.021581 | -0.0054008 | 1.3621e-06 | 2.153e-07 | 0.033081 | 0.033081 | 0.033081 | 0.9707 | -0.56552 | 0.97063 | -0.56684 | 2.2721
25 | -0.039321 | -0.009847 | 0.039324 | 0.0098484 | 2.7685e-06 | 1.3696e-06 | 0.060263 | 0.060263 | 0.060263 | 0.97088 | -0.56203 | 0.97095 | -0.56055 | 4.1389
26 | 0.017248 | 0.0043149 | -0.017247 | -0.004315 | 1.1122e-06 | -1.2723e-07 | 0.026439 | 0.026439 | 0.026439 | 0.97063 | -0.56684 | 0.97056 | -0.5682 | 1.8159
27 | -0.045661 | -0.011437 | 0.045666 | 0.011439 | 5.1457e-06 | 2.7386e-06 | 0.069975 | 0.069975 | 0.069975 | 0.97095 | -0.56055 | 0.97107 | -0.55819 | 4.806
28 | 0.015994 | 0.0040012 | -0.015993 | -0.0040014 | 1.038e-06 | -2.4604e-07 | 0.024519 | 0.024519 | 0.024519 | 0.97056 | -0.5682 | 0.9705 | -0.56956 | 1.684
29 | -0.049068 | -0.012292 | 0.049069 | 0.012293 | 1.3946e-06 | 7.6232e-07 | 0.075187 | 0.075187 | 0.075187 | 0.97107 | -0.55819 | 0.9711 | -0.55759 | 5.1639
30 | 0.013878 | 0.0034713 | -0.013877 | -0.0034716 | 6.7858e-07 | -3.5599e-07 | 0.021276 | 0.021276 | 0.021276 | 0.9705 | -0.56956 | 0.97044 | -0.57059 | 1.4613
31 | -0.051688 | -0.012949 | 0.051695 | 0.012953 | 7.0715e-06 | 3.9306e-06 | 0.0792 | 0.0792 | 0.0792 | 0.9711 | -0.55759 | 0.97125 | -0.55472 | 5.4396
32 | -0.0041543 | -0.0010408 | 0.0041545 | 0.0010407 | 2.4329e-07 | -6.1273e-08 | 0.0062223 | 0.0062222 | 0.0062223 | 0.99344 | -0.1248 | 0.9935 | -0.12357 | 1.7094
33 | 0.0041543 | 0.0010408 | -0.004154 | -0.0010409 | 2.8487e-07 | -7.1702e-08 | 0.0062223 | 0.0062224 | 0.0062224 | 0.99344 | -0.1248 | 0.99337 | -0.12624 | 1.7095
34 | 0.0020986 | 0.00052561 | -0.0020986 | -0.00052581 | 6.9822e-08 | -1.9936e-07 | 0.0031431 | 0.0031432 | 0.0031432 | 0.9935 | -0.12357 | 0.99347 | -0.12427 | 0.86351
35 | -0.0062532 | -0.0015664 | 0.0062545 | 0.0015667 | 1.3152e-06 | 3.2379e-07 | 0.0093653 | 0.0093651 | 0.0093653 | 0.9935 | -0.12357 | 0.99373 | -0.11916 | 2.5729
36 | 0.0037548 | 0.00094081 | -0.0037547 | -0.00094085 | 6.9775e-08 | -3.1488e-08 | 0.0056244 | 0.0056244 | 0.0056244 | 0.99337 | -0.12624 | 0.99335 | -0.12663 | 1.5452
37 | 0.0064372 | 0.0016112 | -0.0064369 | -0.0016126 | 2.7996e-07 | -1.3358e-06 | 0.0098696 | 0.0098701 | 0.0098701 | 0.97044 | -0.57059 | 0.9704 | -0.5715 | 0.67789
38 | 0.0074401 | 0.0018604 | -0.0074397 | -0.0018618 | 4.0009e-07 | -1.3648e-06 | 0.011407 | 0.011407 | 0.011407 | 0.97044 | -0.57059 | 0.97039 | -0.57172 | 0.78346
39 | -0.015418 | -0.0038646 | 0.015423 | 0.0038673 | 4.7446e-06 | 2.749e-06 | 0.023481 | 0.023481 | 0.023481 | 0.97708 | -0.43997 | 0.9774 | -0.43351 | 6.4508
40 | -0.15933 | -0.040178 | 0.15939 | 0.040212 | 5.3969e-05 | 3.405e-05 | 0.24266 | 0.24266 | 0.24266 | 0.9774 | -0.43351 | 0.97776 | -0.42644 | 16.6662
41 | 0.14391 | 0.03631 | -0.14381 | -0.036246 | 0.00010191 | 6.409e-05 | 0.21918 | 0.21918 | 0.21918 | 0.9774 | -0.43351 | 0.97665 | -0.44831 | 15.0535
42 | -0.16366 | -0.041283 | 0.16372 | 0.041316 | 5.1439e-05 | 3.2477e-05 | 0.24917 | 0.24917 | 0.24917 | 0.97776 | -0.42644 | 0.9781 | -0.41988 | 17.1132
43 | 0.14193 | 0.035774 | -0.14186 | -0.035732 | 6.6916e-05 | 4.2063e-05 | 0.21631 | 0.21631 | 0.21631 | 0.97665 | -0.44831 | 0.97614 | -0.45817 | 14.8566
44 | 0.0072715 | 0.0018225 | -0.0072706 | -0.0018222 | 9.003e-07 | 3.3e-07 | 0.011062 | 0.011063 | 0.011063 | 0.9781 | -0.41988 | 0.97797 | -0.42248 | 3.0392
45 | -0.17099 | -0.043138 | 0.17108 | 0.043196 | 9.0364e-05 | 5.7118e-05 | 0.26023 | 0.26023 | 0.26023 | 0.9781 | -0.41988 | 0.97866 | -0.40885 | 17.8729
46 | 0.13089 | 0.032982 | -0.13076 | -0.032901 | 0.00012986 | 8.1376e-05 | 0.19958 | 0.19959 | 0.19959 | 0.97614 | -0.45817 | 0.97509 | -0.47894 | 13.7078
47 | 0.0052019 | 0.0013037 | -0.0052019 | -0.0013037 | 7.7216e-08 | 8.177e-09 | 0.0079149 | 0.007915 | 0.007915 | 0.97797 | -0.42248 | 0.97795 | -0.42279 | 2.1744
48 | -0.1764 | -0.04453 | 0.17659 | 0.044649 | 0.00018831 | 0.00011912 | 0.26832 | 0.26832 | 0.26832 | 0.97866 | -0.40885 | 0.97981 | -0.38659 | 18.4288
49 | 0.1285 | 0.032335 | -0.12848 | -0.032322 | 2.0936e-05 | 1.3109e-05 | 0.19614 | 0.19614 | 0.19614 | 0.97509 | -0.47894 | 0.97491 | -0.48235 | 13.471
50 | -0.062118 | -0.015565 | 0.062131 | 0.015572 | 1.2725e-05 | 7.4018e-06 | 0.095168 | 0.095167 | 0.095168 | 0.97125 | -0.55472 | 0.97146 | -0.55042 | 6.5362
51 | -0.071911 | -0.018024 | 0.071914 | 0.018025 | 2.5799e-06 | 1.5388e-06 | 0.11015 | 0.11015 | 0.11015 | 0.97146 | -0.55042 | 0.9715 | -0.54967 | 7.5652
52 | 0.0032656 | 0.00081785 | -0.0032654 | -0.00081796 | 1.5937e-07 | -1.0835e-07 | 0.0050015 | 0.0050016 | 0.0050016 | 0.9715 | -0.54967 | 0.97145 | -0.55069 | 1.3741
53 | -0.07518 | -0.018843 | 0.075188 | 0.018848 | 8.1517e-06 | 4.8922e-06 | 0.11515 | 0.11515 | 0.11515 | 0.9715 | -0.54967 | 0.97162 | -0.54739 | 7.9087
54 | 0.0044164 | 0.0011064 | -0.0044162 | -0.0011068 | 1.7523e-07 | -3.9135e-07 | 0.006772 | 0.0067721 | 0.0067721 | 0.9704 | -0.5715 | 0.97036 | -0.57234 | 0.93024
55 | 0.0020205 | 0.00050615 | -0.0020204 | -0.00050637 | 7.7229e-08 | -2.1562e-07 | 0.0030982 | 0.0030983 | 0.0030983 | 0.9704 | -0.5715 | 0.97036 | -0.5723 | 0.85117
56 | 0.004916 | 0.0012293 | -0.0049159 | -0.0012306 | 1.5119e-07 | -1.3058e-06 | 0.0075373 | 0.0075378 | 0.0075378 | 0.97039 | -0.57172 | 0.97035 | -0.57237 | 0.51771
57 | 0.0031662 | 0.00079206 | -0.0031661 | -0.00079319 | 5.2358e-08 | -1.1372e-06 | 0.0048548 | 0.0048552 | 0.0048552 | 0.97035 | -0.57237 | 0.97034 | -0.57271 | 0.33346
58 | 0.000954 | 0.00023878 | -0.00095399 | -0.00023909 | 1.2858e-09 | -3.1582e-07 | 0.0014628 | 0.001463 | 0.001463 | 0.97034 | -0.57271 | 0.97034 | -0.57274 | 0.10048
59 | 0.0013613 | 0.00034103 | -0.0013612 | -0.00034109 | 8.7767e-09 | -6.7286e-08 | 0.0020388 | 0.0020389 | 0.0020389 | 0.99347 | -0.12427 | 0.99346 | -0.12441 | 0.56013
60 | 0.0027122 | 0.0006792 | -0.0027121 | -0.00067937 | 1.1526e-07 | -1.6766e-07 | 0.0040611 | 0.0040612 | 0.0040612 | 0.99373 | -0.11916 | 0.99369 | -0.12005 | 1.1157
61 | -0.0089667 | -0.0022459 | 0.0089681 | 0.0022465 | 1.3713e-06 | 6.1478e-07 | 0.013426 | 0.013426 | 0.013426 | 0.99373 | -0.11916 | 0.9939 | -0.11595 | 3.6885
62 | 0.00039024 | 9.7634e-05 | -0.00039024 | -9.7804e-05 | 1.6846e-09 | -1.6911e-07 | 0.00058452 | 0.00058458 | 0.00058458 | 0.99335 | -0.12663 | 0.99334 | -0.12672 | 0.1606
63 | -0.0077637 | -0.0019458 | 0.0077641 | 0.0019459 | 3.4414e-07 | 1.3729e-07 | 0.011797 | 0.011797 | 0.011797 | 0.97925 | -0.3974 | 0.9793 | -0.39647 | 3.241
64 | -0.0077641 | -0.0019459 | 0.0077664 | 0.0019468 | 2.3186e-06 | 9.2477e-07 | 0.011797 | 0.011797 | 0.011797 | 0.9793 | -0.39647 | 0.97962 | -0.3902 | 3.241
65 | -0.00073096 | -0.0001832 | 0.00073097 | 0.00018305 | 5.7147e-09 | -1.4883e-07 | 0.001116 | 0.001116 | 0.001116 | 0.97462 | -0.48807 | 0.97463 | -0.48791 | 0.3066
66 | -0.10172 | -0.02559 | 0.10174 | 0.025607 | 2.7055e-05 | 1.6719e-05 | 0.15533 | 0.15533 | 0.15533 | 0.97463 | -0.48791 | 0.97491 | -0.48235 | 10.6683
67 | 0.10099 | 0.025407 | -0.10094 | -0.025381 | 4.2183e-05 | 2.6054e-05 | 0.15422 | 0.15422 | 0.15422 | 0.97463 | -0.48791 | 0.97419 | -0.49666 | 10.5917
68 | 0.026733 | 0.0067147 | -0.026719 | -0.0067069 | 1.3862e-05 | 7.765e-06 | 0.040807 | 0.040808 | 0.040808 | 0.97491 | -0.48235 | 0.97436 | -0.49322 | 5.6055
69 | 0.094858 | 0.023856 | -0.094839 | -0.023844 | 1.9081e-05 | 1.1729e-05 | 0.14492 | 0.14492 | 0.14492 | 0.97419 | -0.49666 | 0.97397 | -0.50087 | 9.9533
70 | 0.0060858 | 0.0015253 | -0.0060853 | -0.0015251 | 5.5239e-07 | 1.4131e-07 | 0.0092958 | 0.0092958 | 0.0092958 | 0.97419 | -0.49666 | 0.97409 | -0.49856 | 2.5538
71 | 0.022098 | 0.0055489 | -0.022095 | -0.0055469 | 3.2676e-06 | 1.996e-06 | 0.033752 | 0.033752 | 0.033752 | 0.97436 | -0.49322 | 0.9742 | -0.49632 | 9.2725
72 | 0.094839 | 0.023844 | -0.094773 | -0.023804 | 6.5509e-05 | 4.0271e-05 | 0.14492 | 0.14492 | 0.14492 | 0.97397 | -0.50087 | 0.97324 | -0.51534 | 9.9533
73 | 0.092288 | 0.023181 | -0.092223 | -0.023141 | 6.5665e-05 | 4.0279e-05 | 0.14112 | 0.14112 | 0.14112 | 0.97324 | -0.51534 | 0.97248 | -0.53027 | 9.6924
74 | -0.029927 | -0.0075036 | 0.02993 | 0.0075055 | 3.0833e-06 | 1.9234e-06 | 0.045494 | 0.045494 | 0.045494 | 0.97887 | -0.40499 | 0.97898 | -0.40283 | 12.4985
75 | -0.037556 | -0.0094167 | 0.037578 | 0.0094309 | 2.261e-05 | 1.4238e-05 | 0.057085 | 0.057085 | 0.057085 | 0.97898 | -0.40283 | 0.97962 | -0.3902 | 15.6827
76 | -0.045345 | -0.011378 | 0.045352 | 0.011382 | 7.8154e-06 | 4.1169e-06 | 0.068882 | 0.068882 | 0.068882 | 0.97962 | -0.3902 | 0.97981 | -0.38659 | 4.7309
77 | -0.22194 | -0.056031 | 0.22227 | 0.056237 | 0.00032459 | 0.0002062 | 0.3372 | 0.3372 | 0.3372 | 0.97981 | -0.38659 | 0.98137 | -0.35611 | 23.1597
78 | -0.22473 | -0.056855 | 0.2249 | 0.05696 | 0.00016635 | 0.00010569 | 0.34094 | 0.34094 | 0.34094 | 0.98137 | -0.35611 | 0.98216 | -0.34069 | 23.4163
79 | -0.22669 | -0.05741 | 0.22689 | 0.057535 | 0.00019637 | 0.00012478 | 0.34366 | 0.34366 | 0.34366 | 0.98216 | -0.34069 | 0.98309 | -0.32267 | 23.6032
80 | 0.0017964 | 0.00045003 | -0.0017964 | -0.00045007 | 1.0361e-08 | -4.0574e-08 | 0.0027216 | 0.0027216 | 0.0027216 | 0.98216 | -0.34069 | 0.98216 | -0.34081 | 0.74769
81 | -0.22927 | -0.058132 | 0.22942 | 0.058226 | 0.00014806 | 9.4092e-05 | 0.34727 | 0.34727 | 0.34727 | 0.98309 | -0.32267 | 0.98379 | -0.30925 | 23.8508
82 | 0.0017964 | 0.00045007 | -0.0017964 | -0.00045021 | 3.7927e-08 | -1.4852e-07 | 0.0027216 | 0.0027217 | 0.0027217 | 0.98216 | -0.34081 | 0.98214 | -0.34126 | 0.74771
83 | 0.001155 | 0.00028904 | -0.001155 | -0.00028946 | 4.2391e-08 | -4.2004e-07 | 0.001769 | 0.0017692 | 0.0017692 | 0.97145 | -0.55069 | 0.97141 | -0.55146 | 0.48604
84 | -0.07686 | -0.019267 | 0.07688 | 0.019279 | 1.9225e-05 | 1.1571e-05 | 0.11771 | 0.11771 | 0.11771 | 0.97162 | -0.54739 | 0.97188 | -0.54214 | 8.0846
85 | -0.080108 | -0.020088 | 0.080121 | 0.020096 | 1.316e-05 | 7.9599e-06 | 0.12265 | 0.12265 | 0.12265 | 0.97188 | -0.54214 | 0.97206 | -0.5387 | 8.4241
86 | -0.081007 | -0.020318 | 0.081037 | 0.020336 | 3.0568e-05 | 1.8512e-05 | 0.12401 | 0.12401 | 0.12401 | 0.97206 | -0.5387 | 0.97246 | -0.53078 | 8.5172
87 | -0.082815 | -0.020782 | 0.082817 | 0.020783 | 2.0406e-06 | 1.2387e-06 | 0.12673 | 0.12673 | 0.12673 | 0.97246 | -0.53078 | 0.97248 | -0.53027 | 8.7039
88 | 0.0094059 | 0.0023578 | -0.0094056 | -0.0023576 | 3.525e-07 | 1.693e-07 | 0.014392 | 0.014392 | 0.014392 | 0.97248 | -0.53027 | 0.97244 | -0.53105 | 3.9539
89 | 0.0094056 | 0.0023576 | -0.0094041 | -0.0023569 | 1.4326e-06 | 6.8808e-07 | 0.014392 | 0.014392 | 0.014392 | 0.97244 | -0.53105 | 0.97228 | -0.53425 | 3.954
90 | 0.015776 | 0.0039531 | -0.015775 | -0.0039534 | 8.0008e-07 | -2.825e-07 | 0.023607 | 0.023607 | 0.023607 | 0.99438 | -0.10656 | 0.99433 | -0.10762 | 1.6214
91 | -0.015776 | -0.0039531 | 0.015777 | 0.0039528 | 8.9231e-07 | -3.1519e-07 | 0.023607 | 0.023607 | 0.023607 | 0.99438 | -0.10656 | 0.99445 | -0.10537 | 1.6214
92 | 0.0075664 | 0.001896 | -0.007566 | -0.0018959 | 3.4488e-07 | 1.2769e-07 | 0.011323 | 0.011323 | 0.011323 | 0.99433 | -0.10762 | 0.99428 | -0.10858 | 3.1107
93 | -0.017482 | -0.0043801 | 0.017482 | 0.00438 | 1.657e-07 | -2.8006e-08 | 0.026158 | 0.026158 | 0.026158 | 0.99445 | -0.10537 | 0.99446 | -0.10517 | 1.7966
94 | -0.00207 | -0.00051879 | 0.00207 | 0.00051863 | 5.0062e-08 | -1.5254e-07 | 0.0030803 | 0.0030802 | 0.0030803 | 0.99995 | -0.00094865 | 0.99998 | -0.00044093 | 0.84624
95 | -0.0044473 | -0.0011144 | 0.0044474 | 0.0011144 | 9.3407e-08 | -1.4835e-08 | 0.0066177 | 0.0066177 | 0.0066177 | 0.99998 | -0.00044093 | 1 | 0 | 1.8181
96 | 0.34712 | 0.089417 | -0.34657 | -0.089067 | 0.00054866 | 0.00035 | 0.51737 | 0.51738 | 0.51738 | 1 | 0 | 0.99827 | -0.032532 | 35.534
97 | 0.34388 | 0.088395 | -0.34378 | -0.088326 | 0.00010761 | 6.8643e-05 | 0.51338 | 0.51338 | 0.51338 | 0.99827 | -0.032532 | 0.99793 | -0.038975 | 35.2593
98 | 0.34251 | 0.088008 | -0.34202 | -0.087695 | 0.00048988 | 0.00031248 | 0.51148 | 0.51148 | 0.51148 | 0.99793 | -0.038975 | 0.99637 | -0.068467 | 35.1292
99 | -0.23092 | -0.058602 | 0.231 | 0.05865 | 7.5624e-05 | 4.8064e-05 | 0.34954 | 0.34954 | 0.34954 | 0.98379 | -0.30925 | 0.98414 | -0.30244 | 24.0067
100 | -0.0012928 | -0.00032401 | 0.0012928 | 0.00032373 | 3.2676e-08 | -2.7641e-07 | 0.0019422 | 0.0019421 | 0.0019422 | 0.99047 | -0.18081 | 0.99049 | -0.18028 | 0.53358
101 | -0.0024501 | -0.00061377 | 0.0024502 | 0.00061359 | 9.7543e-08 | -1.8471e-07 | 0.0036807 | 0.0036806 | 0.0036807 | 0.99049 | -0.18028 | 0.99054 | -0.17944 | 1.0112
102 | -0.23322 | -0.059207 | 0.23329 | 0.059254 | 7.3072e-05 | 4.6448e-05 | 0.3529 | 0.3529 | 0.3529 | 0.98414 | -0.30244 | 0.98448 | -0.29593 | 24.2374
103 | -0.026537 | -0.006668 | 0.026545 | 0.0066733 | 8.6403e-06 | 5.3462e-06 | 0.040033 | 0.040033 | 0.040033 | 0.98651 | -0.25705 | 0.98686 | -0.25023 | 10.9981
104 | 0.025786 | 0.00648 | -0.025781 | -0.0064764 | 5.7715e-06 | 3.5639e-06 | 0.038901 | 0.038901 | 0.038901 | 0.98651 | -0.25705 | 0.98627 | -0.26174 | 10.6872
105 | -0.027695 | -0.0069615 | 0.027709 | 0.0069703 | 1.4054e-05 | 8.7202e-06 | 0.041767 | 0.041767 | 0.041767 | 0.98686 | -0.25023 | 0.98741 | -0.23961 | 11.4744
106 | 0.024816 | 0.0062346 | -0.024814 | -0.0062333 | 2.0347e-06 | 1.2528e-06 | 0.037446 | 0.037446 | 0.037446 | 0.98627 | -0.26174 | 0.98618 | -0.26346 | 10.2873
107 | 0.0022176 | 0.00055534 | -0.0022175 | -0.00055551 | 6.8187e-08 | -1.6462e-07 | 0.0033417 | 0.0033418 | 0.0033418 | 0.98741 | -0.23961 | 0.98737 | -0.24025 | 0.91808
108 | -0.029927 | -0.0075256 | 0.029938 | 0.0075325 | 1.1101e-05 | 6.9188e-06 | 0.045108 | 0.045108 | 0.045108 | 0.98741 | -0.23961 | 0.98781 | -0.23184 | 12.3924
109 | 0.024245 | 0.0060909 | -0.024235 | -0.0060844 | 1.0612e-05 | 6.5224e-06 | 0.036588 | 0.036588 | 0.036588 | 0.98618 | -0.26346 | 0.98571 | -0.27263 | 10.0518
110 | 0.00096698 | 0.00024209 | -0.00096696 | -0.00024234 | 1.6392e-08 | -2.5279e-07 | 0.0014572 | 0.0014573 | 0.0014573 | 0.98737 | -0.24025 | 0.98736 | -0.24061 | 0.40035
111 | -0.03298 | -0.0082949 | 0.032991 | 0.0083012 | 1.0636e-05 | 6.2187e-06 | 0.049691 | 0.049691 | 0.049691 | 0.98781 | -0.23184 | 0.98815 | -0.2251 | 6.8257
112 | 0.023359 | 0.0058648 | -0.023348 | -0.0058583 | 1.0539e-05 | 6.4573e-06 | 0.035266 | 0.035266 | 0.035266 | 0.98571 | -0.27263 | 0.98522 | -0.2821 | 9.6884
113 | 0.24016 | 0.061287 | -0.24012 | -0.061264 | 3.6015e-05 | 2.29e-05 | 0.36203 | 0.36203 | 0.36203 | 0.98815 | -0.2251 | 0.98799 | -0.2282 | 24.865
114 | -0.27315 | -0.069588 | 0.27339 | 0.069745 | 0.000246 | 0.00015665 | 0.41173 | 0.41172 | 0.41173 | 0.98815 | -0.2251 | 0.98913 | -0.20645 | 28.2778
115 | 0.023348 | 0.0058583 | -0.023344 | -0.0058556 | 4.4414e-06 | 2.7213e-06 | 0.035266 | 0.035266 | 0.035266 | 0.98522 | -0.2821 | 0.98502 | -0.28609 | 9.6884
116 | -0.23479 | -0.05963 | 0.23506 | 0.0598 | 0.00026748 | 0.00017004 | 0.35517 | 0.35517 | 0.35517 | 0.98448 | -0.29593 | 0.9857 | -0.27229 | 24.3934
117 | -0.23594 | -0.060022 | 0.236 | 0.06006 | 6.0429e-05 | 3.8416e-05 | 0.3565 | 0.3565 | 0.3565 | 0.9857 | -0.27229 | 0.98598 | -0.26698 | 24.4849
118 | -0.23772 | -0.060489 | 0.23795 | 0.060637 | 0.00023252 | 0.00014783 | 0.35909 | 0.35909 | 0.35909 | 0.98598 | -0.26698 | 0.98703 | -0.2467 | 24.6625
119 | -0.23991 | -0.061128 | 0.24012 | 0.061264 | 0.00021441 | 0.00013633 | 0.36204 | 0.36203 | 0.36204 | 0.98703 | -0.2467 | 0.98799 | -0.2282 | 24.865
120 | -0.0030945 | -0.00077555 | 0.0030948 | 0.0007753 | 2.5786e-07 | -2.5069e-07 | 0.0046316 | 0.0046314 | 0.0046316 | 0.99419 | -0.11033 | 0.99428 | -0.10858 | 1.2724
121 | 0.010005 | 0.0025033 | -0.010005 | -0.0025033 | 4.0946e-08 | -7.4853e-08 | 0.014973 | 0.014973 | 0.014973 | 0.99422 | -0.10942 | 0.99421 | -0.10951 | 1.0283
122 | -0.012217 | -0.0030577 | 0.012218 | 0.0030568 | 8.8666e-07 | -9.0022e-07 | 0.018284 | 0.018283 | 0.018284 | 0.99422 | -0.10942 | 0.99429 | -0.1079 | 1.2558
123 | 0.0076939 | 0.0019242 | -0.0076938 | -0.0019245 | 1.0343e-07 | -3.6546e-07 | 0.011514 | 0.011514 | 0.011514 | 0.99421 | -0.10951 | 0.9942 | -0.10979 | 0.7908
124 | -0.29936 | -0.076765 | 0.29966 | 0.076957 | 0.00030182 | 0.00019233 | 0.44862 | 0.44862 | 0.44862 | 0.99429 | -0.1079 | 0.99539 | -0.087131 | 30.8121
125 | 0.28714 | 0.073708 | -0.28684 | -0.073515 | 0.00030236 | 0.00019261 | 0.43034 | 0.43034 | 0.43034 | 0.99429 | -0.1079 | 0.99315 | -0.12962 | 29.5564
126 | 0.0059507 | 0.0014877 | -0.0059506 | -0.0014882 | 8.2103e-08 | -5.2026e-07 | 0.0089051 | 0.0089053 | 0.0089053 | 0.9942 | -0.10979 | 0.99418 | -0.11008 | 0.61163
127 | -0.3401 | -0.087096 | 0.34041 | 0.087293 | 0.00030781 | 0.00019634 | 0.50908 | 0.50908 | 0.50908 | 0.99539 | -0.087131 | 0.99637 | -0.068467 | 34.9645
128 | 0.040443 | 0.010139 | -0.040438 | -0.010137 | 4.7929e-06 | 2.3403e-06 | 0.06046 | 0.06046 | 0.06046 | 0.99539 | -0.087131 | 0.99526 | -0.089618 | 4.1525
129 | 0.28567 | 0.073224 | -0.28555 | -0.073143 | 0.00012795 | 8.1504e-05 | 0.4286 | 0.4286 | 0.4286 | 0.99315 | -0.12962 | 0.99266 | -0.13886 | 29.4368
130 | 0.0049005 | 0.001225 | -0.0049005 | -0.0012258 | 8.0599e-08 | -7.7749e-07 | 0.0073336 | 0.0073339 | 0.0073339 | 0.99418 | -0.11008 | 0.99416 | -0.11043 | 0.5037
131 | 0.038685 | 0.0096972 | -0.038681 | -0.0096954 | 3.8581e-06 | 1.8298e-06 | 0.057838 | 0.057838 | 0.057838 | 0.99526 | -0.089618 | 0.99515 | -0.091712 | 3.9724
132 | 0.28307 | 0.072522 | -0.28288 | -0.072402 | 0.00018858 | 0.00012012 | 0.42489 | 0.42489 | 0.42489 | 0.99266 | -0.13886 | 0.99194 | -0.15262 | 29.1821
133 | 0.0030097 | 0.00075191 | -0.0030096 | -0.00075305 | 4.2862e-08 | -1.1414e-06 | 0.0045039 | 0.0045043 | 0.0045043 | 0.99416 | -0.11043 | 0.99415 | -0.11073 | 0.30936
134 | 0.035972 | 0.0090166 | -0.035968 | -0.0090146 | 4.4374e-06 | 1.9898e-06 | 0.053788 | 0.053789 | 0.053789 | 0.99515 | -0.091712 | 0.99502 | -0.094301 | 3.6943
135 | 0.28222 | 0.072236 | -0.28206 | -0.072136 | 0.00015626 | 9.9531e-05 | 0.42389 | 0.42389 | 0.42389 | 0.99194 | -0.15262 | 0.99134 | -0.16406 | 29.1136
136 | 0.019224 | 0.004816 | -0.019222 | -0.0048161 | 2.4651e-06 | -7.2236e-08 | 0.028761 | 0.028761 | 0.028761 | 0.99459 | -0.10248 | 0.99446 | -0.10517 | 1.9754
137 | -0.019844 | -0.0049713 | 0.019845 | 0.0049713 | 1.1307e-06 | 1.3238e-08 | 0.029688 | 0.029688 | 0.029688 | 0.99459 | -0.10248 | 0.99466 | -0.10128 | 2.039
138 | -0.031885 | -0.0079896 | 0.031887 | 0.0079905 | 2.2227e-06 | 8.8146e-07 | 0.047699 | 0.047699 | 0.047699 | 0.99466 | -0.10128 | 0.99473 | -0.099821 | 3.2761
139 | 0.01204 | 0.0030183 | -0.012037 | -0.0030171 | 2.2861e-06 | 1.2193e-06 | 0.018012 | 0.018012 | 0.018012 | 0.99466 | -0.10128 | 0.99445 | -0.10527 | 4.9483
140 | -0.032269 | -0.0080863 | 0.032272 | 0.0080875 | 2.8553e-06 | 1.1486e-06 | 0.048271 | 0.048271 | 0.048271 | 0.99473 | -0.099821 | 0.99483 | -0.097964 | 3.3153
141 | 0.011298 | 0.0028317 | -0.011294 | -0.00283 | 3.2779e-06 | 1.7012e-06 | 0.016905 | 0.016905 | 0.016905 | 0.99445 | -0.10527 | 0.99414 | -0.11136 | 4.6443
142 | -0.032913 | -0.008248 | 0.032918 | 0.0082504 | 5.7427e-06 | 2.3624e-06 | 0.049229 | 0.049228 | 0.049229 | 0.99483 | -0.097964 | 0.99502 | -0.094301 | 3.3811
143 | 0.010114 | 0.0025341 | -0.010113 | -0.0025338 | 6.9628e-07 | 3.4057e-07 | 0.015138 | 0.015138 | 0.015138 | 0.99414 | -0.11136 | 0.99406 | -0.11281 | 4.1588
144 | 0.0096158 | 0.0024091 | -0.0096144 | -0.0024085 | 1.4372e-06 | 6.8001e-07 | 0.014394 | 0.014394 | 0.014394 | 0.99406 | -0.11281 | 0.9939 | -0.11595 | 3.9543
145 | 0.020891 | 0.0052409 | -0.020883 | -0.0052363 | 7.5213e-06 | 4.5574e-06 | 0.031561 | 0.031561 | 0.031561 | 0.98502 | -0.28609 | 0.98463 | -0.29364 | 8.6705
146 | -0.0015877 | -0.00039791 | 0.0015877 | 0.00039756 | 6.2698e-08 | -3.4369e-07 | 0.0023766 | 0.0023764 | 0.0023766 | 0.99408 | -0.11212 | 0.99412 | -0.11129 | 0.6529
147 | -0.0030096 | -0.00075391 | 0.0030096 | 0.00075388 | 2.4601e-08 | -2.6173e-08 | 0.0045046 | 0.0045046 | 0.0045046 | 0.99412 | -0.11129 | 0.99413 | -0.11112 | 1.2375
148 | 0.019236 | 0.0048234 | -0.019234 | -0.0048225 | 1.5587e-06 | 9.35e-07 | 0.029071 | 0.029071 | 0.029071 | 0.98463 | -0.29364 | 0.98454 | -0.29534 | 7.9865
149 | 0.014345 | 0.0035972 | -0.014341 | -0.0035949 | 3.9673e-06 | 2.253e-06 | 0.021682 | 0.021682 | 0.021682 | 0.98454 | -0.29534 | 0.98425 | -0.30115 | 5.9565
150 | 0.0057086 | 0.0014305 | -0.0057076 | -0.0014303 | 1.0296e-06 | 1.9057e-07 | 0.0086304 | 0.0086306 | 0.0086306 | 0.98425 | -0.30115 | 0.98405 | -0.30493 | 2.371
151 | 0.0047483 | 0.0011899 | -0.0047477 | -0.0011899 | 5.7434e-07 | -9.7983e-09 | 0.00718 | 0.0071801 | 0.0071801 | 0.98405 | -0.30493 | 0.98392 | -0.30747 | 1.9726
152 | -0.0030096 | -0.00075388 | 0.0030096 | 0.00075305 | 5.6361e-08 | -8.2832e-07 | 0.0045046 | 0.0045043 | 0.0045046 | 0.99413 | -0.11112 | 0.99415 | -0.11073 | 0.41251
153 | 0.0018223 | 0.00045635 | -0.0018222 | -0.00045669 | 8.3976e-08 | -3.3582e-07 | 0.0027287 | 0.0027288 | 0.0027288 | 0.99369 | -0.12005 | 0.99364 | -0.12102 | 0.74968
154 | 0.00079192 | 0.00019841 | -0.00079191 | -0.00019847 | 2.7712e-09 | -6.6237e-08 | 0.0011861 | 0.0011861 | 0.0011861 | 0.99346 | -0.12441 | 0.99346 | -0.12448 | 0.32586
155 | -0.27472 | -0.070077 | 0.27473 | 0.07008 | 4.3832e-06 | 2.7912e-06 | 0.41372 | 0.41372 | 0.41372 | 0.98913 | -0.20645 | 0.98914 | -0.20612 | 28.415
156 | -0.27609 | -0.070421 | 0.27645 | 0.070653 | 0.00036451 | 0.00023213 | 0.41577 | 0.41577 | 0.41577 | 0.98914 | -0.20612 | 0.99057 | -0.17882 | 28.5555
157 | -0.28019 | -0.07159 | 0.28039 | 0.071717 | 0.00020004 | 0.00012741 | 0.42139 | 0.42139 | 0.42139 | 0.99057 | -0.17882 | 0.99134 | -0.16406 | 28.9413
158 | 0.00374 | 0.00093676 | -0.0037399 | -0.00093681 | 1.1144e-07 | -4.9884e-08 | 0.005618 | 0.005618 | 0.005618 | 0.99057 | -0.17882 | 0.99054 | -0.17944 | 1.5434

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35448 | 0.09085

## res_load
| p_mw | q_mvar
0 | 0.0011158 | 0.00027965
1 | 0.0008829 | 0.00022128
2 | 0.0003673 | 9.2053e-05
3 | 0.0031525 | 0.00079008
4 | 0.00133 | 0.00033333
5 | 0.00099853 | 0.00025025
6 | 0.00039964 | 0.00010016
7 | 0.00037083 | 9.2939e-05
8 | 0.0014607 | 0.00036609
9 | 0.0028128 | 0.00070495
10 | 0.001143 | 0.00028647
11 | 0.0015706 | 0.00039363
12 | 0.0023757 | 0.00059542
13 | 0.0013768 | 0.00034506
14 | 0.0023787 | 0.00059616
15 | 0.0022179 | 0.00055585
16 | 0.0075836 | 0.0019006
17 | 0.0039679 | 0.00099444
18 | 0.0021173 | 0.00053064
19 | 0.01301 | 0.0032605
20 | 0.0077967 | 0.001954
21 | 0.0026698 | 0.0006691
22 | 0.0031708 | 0.00079468
23 | 0.014564 | 0.0036502
24 | 0.004333 | 0.001086
25 | 0.0063371 | 0.0015882
26 | 0.0012523 | 0.00031386
27 | 0.0034017 | 0.00085254
28 | 0.0021153 | 0.00053013
29 | 0.0026189 | 0.00065637
30 | 0.00039923 | 0.00010006
31 | 0.0038649 | 0.00096863
32 | 0.0042764 | 0.0010718
33 | 0.0018824 | 0.00047178
34 | 0.010973 | 0.0027501
35 | 0.0020687 | 0.00051846
36 | 0.0053233 | 0.0013342
37 | 0.0022589 | 0.00056614
38 | 0.010422 | 0.0026121
39 | 0.009781 | 0.0024513
40 | 0.0025237 | 0.0006325
41 | 0.0044162 | 0.0011068
42 | 0.0020204 | 0.00050637
43 | 0.0017497 | 0.00043851
44 | 0.0022121 | 0.00055442
45 | 0.0007373 | 0.00018479
46 | 0.0033645 | 0.00084321
47 | 0.0077637 | 0.0019458
48 | 0.00073096 | 0.0001832
49 | 0.0046203 | 0.001158
50 | 0.0060853 | 0.0015251
51 | 0.001939 | 0.00048596
52 | 0.002485 | 0.0006228
53 | 0.0091113 | 0.0022835
54 | 0.0076255 | 0.0019111
55 | 0.0024648 | 0.00061775
56 | 0.0052019 | 0.0013037
57 | 0.0023819 | 0.00059697
58 | 0.0021104 | 0.00052892
59 | 0.0016726 | 0.00041918
60 | 0.001155 | 0.00028946
61 | 0.0032283 | 0.00080909
62 | 0.00088555 | 0.00022194
63 | 0.0017774 | 0.00044547
64 | 0.0094041 | 0.0023569
65 | 0.0082088 | 0.0020573
66 | 0.001705 | 0.00042731
67 | 0.00207 | 0.00051879
68 | 0.0023773 | 0.0005958
69 | 0.0012716 | 0.0003187
70 | 0.0017964 | 0.00045021
71 | 0.0026835 | 0.00067255
72 | 0.0012705 | 0.00031841
73 | 0.0015012 | 0.00037624
74 | 0.0012928 | 0.00032401
75 | 0.0011573 | 0.00029004
76 | 0.002221 | 0.00055663
77 | 0.00039024 | 9.7804e-05
78 | 0.0007502 | 0.00018802
79 | 0.0011499 | 0.0002882
80 | 0.00096497 | 0.00024184
81 | 0.00056813 | 0.00014239
82 | 0.0012505 | 0.00031342
83 | 0.0030421 | 0.00076241
84 | 0.00087625 | 0.00021961
85 | 0.00096696 | 0.00024234
86 | 0.0015035 | 0.00037682
87 | 0.00088268 | 0.00022122
88 | 0.0017131 | 0.00042934
89 | 0.0019565 | 0.00049036
90 | 0.0030945 | 0.00077555
91 | 0.0044713 | 0.0011206
92 | 0.0022124 | 0.00055447
93 | 0.002311 | 0.00057918
94 | 0.0017431 | 0.00043687
95 | 0.0011627 | 0.00029139
96 | 0.0010501 | 0.00026317
97 | 0.001606 | 0.0004025
98 | 0.0017538 | 0.00043955
99 | 0.0024747 | 0.00062021
100 | 0.0018908 | 0.00047387
101 | 0.0027085 | 0.00067881
102 | 0.00066491 | 0.00016664
103 | 0.00061978 | 0.00015533
104 | 0.0017398 | 0.00043603
105 | 0.00038227 | 9.5806e-05
106 | 0.00073959 | 0.00018536
107 | 0.00064047 | 0.00016052
108 | 0.0011807 | 0.00029592
109 | 0.0030494 | 0.00076425
110 | 0.00049721 | 0.00012461
111 | 0.0024528 | 0.00061472
112 | 0.0015877 | 0.00039791
113 | 0.0014218 | 0.00035634
114 | 0.0016476 | 0.00041293
115 | 0.0048891 | 0.0012253
116 | 0.00095933 | 0.00024043
117 | 0.0047477 | 0.0011899
118 | 0.00064631 | 0.00016198
119 | 0.00088984 | 0.00022302
120 | 0.0018222 | 0.00045669
121 | 0.00056933 | 0.00014269
122 | 0.0013279 | 0.0003328
123 | 0.0013596 | 0.00034074
124 | 0.0012897 | 0.00032322
125 | 0.0016712 | 0.00041883
126 | 0.00095399 | 0.00023909
127 | 0.00079191 | 0.00019847

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1