## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1023-1_2_2_node_48 | 0.4 | n |  | TRUE
1 | bus_LV_1023-1_2_2_node_49 | 0.4 | n |  | TRUE
2 | bus_LV_1023-1_2_2_node_50 | 0.4 | n |  | TRUE
3 | bus_LV_1023-1_2_2_node_51 | 0.4 | n |  | TRUE
4 | bus_LV_1023-1_2_2_node_170 | 0.4 | n |  | TRUE
5 | bus_LV_1023-1_2_2_node_126 | 0.4 | n |  | TRUE
6 | bus_LV_1023-1_2_2_node_146 | 0.4 | n |  | TRUE
7 | bus_LV_1023-1_2_2_node_52 | 0.4 | n |  | TRUE
8 | bus_LV_1023-1_2_2_node_53 | 0.4 | n |  | TRUE
9 | bus_LV_1023-1_2_2_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_1023-1_2_2_node_115 | 0.4 | n |  | TRUE
11 | bus_LV_1023-1_2_2_node_55 | 0.4 | n |  | TRUE
12 | bus_LV_1023-1_2_2_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_1023-1_2_2_node_57 | 0.4 | n |  | TRUE
14 | bus_LV_1023-1_2_2_node_58 | 0.4 | n |  | TRUE
15 | bus_LV_1023-1_2_2_node_59 | 0.4 | n |  | TRUE
16 | bus_LV_1023-1_2_2_node_165 | 0.4 | n |  | TRUE
17 | bus_LV_1023-1_2_2_node_67 | 0.4 | n |  | TRUE
18 | bus_LV_1023-1_2_2_node_88 | 0.4 | n |  | TRUE
19 | bus_LV_1023-1_2_2_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_1023-1_2_2_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_1023-1_2_2_node_62 | 0.4 | n |  | TRUE
22 | bus_LV_1023-1_2_2_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1023-1_2_2_node_64 | 0.4 | n |  | TRUE
24 | bus_LV_1023-1_2_2_node_113 | 0.4 | n |  | TRUE
25 | bus_LV_1023-1_2_2_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_1023-1_2_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1023-1_2_2_node_68 | 0.4 | n |  | TRUE
28 | bus_LV_1023-1_2_2_node_123 | 0.4 | n |  | TRUE
29 | bus_LV_1023-1_2_2_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_1023-1_2_2_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_1023-1_2_2_node_71 | 0.4 | n |  | TRUE
32 | bus_LV_1023-1_2_2_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_1023-1_2_2_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_1023-1_2_2_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_1023-1_2_2_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_1023-1_2_2_node_122 | 0.4 | n |  | TRUE
37 | bus_LV_1023-1_2_2_node_143 | 0.4 | n |  | TRUE
38 | bus_LV_1023-1_2_2_node_273 | 0.4 | n |  | TRUE
39 | bus_LV_1023-1_2_2_node_291 | 0.4 | n |  | TRUE
40 | bus_LV_1023-1_2_2_node_81 | 0.4 | n |  | TRUE
41 | bus_LV_1023-1_2_2_node_82 | 0.4 | n |  | TRUE
42 | bus_LV_1023-1_2_2_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_1023-1_2_2_node_85 | 0.4 | n |  | TRUE
44 | bus_LV_1023-1_2_2_node_87 | 0.4 | n |  | TRUE
45 | bus_LV_1023-1_2_2_node_98 | 0.4 | n |  | TRUE
46 | bus_LV_1023-1_2_2_node_133 | 0.4 | n |  | TRUE
47 | bus_LV_1023-1_2_2_node_86 | 0.4 | n |  | TRUE
48 | bus_LV_1023-1_2_2_node_172 | 0.4 | n |  | TRUE
49 | bus_LV_1023-1_2_2_node_89 | 0.4 | n |  | TRUE
50 | bus_LV_1023-1_2_2_node_114 | 0.4 | n |  | TRUE
51 | bus_LV_1023-1_2_2_node_90 | 0.4 | n |  | TRUE
52 | bus_LV_1023-1_2_2_node_91 | 0.4 | n |  | TRUE
53 | bus_LV_1023-1_2_2_node_92 | 0.4 | n |  | TRUE
54 | bus_LV_1023-1_2_2_node_93 | 0.4 | n |  | TRUE
55 | bus_LV_1023-1_2_2_node_94 | 0.4 | n |  | TRUE
56 | bus_LV_1023-1_2_2_node_148 | 0.4 | n |  | TRUE
57 | bus_LV_1023-1_2_2_node_145 | 0.4 | n |  | TRUE
58 | bus_LV_1023-1_2_2_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_1023-1_2_2_node_96 | 0.4 | n |  | TRUE
60 | bus_LV_1023-1_2_2_node_97 | 0.4 | n |  | TRUE
61 | bus_LV_1023-1_2_2_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_1023-1_2_2_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_1023-1_2_2_node_150 | 0.4 | n |  | TRUE
64 | bus_LV_1023-1_2_2_node_174 | 0.4 | n |  | TRUE
65 | bus_LV_1023-1_2_2_node_101 | 0.4 | n |  | TRUE
66 | bus_LV_1023-1_2_2_node_102 | 0.4 | n |  | TRUE
67 | bus_LV_1023-1_2_2_node_103 | 0.4 | n |  | TRUE
68 | bus_LV_1023-1_2_2_node_104 | 0.4 | n |  | TRUE
69 | bus_LV_1023-1_2_2_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_1023-1_2_2_node_149 | 0.4 | n |  | TRUE
71 | bus_LV_1023-1_2_2_node_166 | 0.4 | n |  | TRUE
72 | bus_LV_1023-1_2_2_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_1023-1_2_2_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_1023-1_2_2_node_108 | 0.4 | n |  | TRUE
75 | bus_LV_1023-1_2_2_node_109 | 0.4 | n |  | TRUE
76 | bus_LV_1023-1_2_2_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_1023-1_2_2_node_111 | 0.4 | n |  | TRUE
78 | bus_LV_1023-1_2_2_node_112 | 0.4 | n |  | TRUE
79 | bus_LV_1023-1_2_2_node_301 | 0.4 | n |  | TRUE
80 | bus_LV_1023-1_2_2_node_300 | 0.4 | n |  | TRUE
81 | bus_LV_1023-1_2_2_node_306 | 0.4 | n |  | TRUE
82 | bus_LV_1023-1_2_2_node_116 | 0.4 | n |  | TRUE
83 | bus_LV_1023-1_2_2_node_119 | 0.4 | n |  | TRUE
84 | bus_LV_1023-1_2_2_node_120 | 0.4 | n |  | TRUE
85 | bus_LV_1023-1_2_2_node_121 | 0.4 | n |  | TRUE
86 | bus_LV_1023-1_2_2_node_139 | 0.4 | n |  | TRUE
87 | bus_LV_1023-1_2_2_node_124 | 0.4 | n |  | TRUE
88 | bus_LV_1023-1_2_2_node_140 | 0.4 | n |  | TRUE
89 | bus_LV_1023-1_2_2_node_125 | 0.4 | n |  | TRUE
90 | bus_LV_1023-1_2_2_node_127 | 0.4 | n |  | TRUE
91 | bus_LV_1023-1_2_2_node_128 | 0.4 | n |  | TRUE
92 | bus_LV_1023-1_2_2_node_129 | 0.4 | n |  | TRUE
93 | bus_LV_1023-1_2_2_node_130 | 0.4 | n |  | TRUE
94 | bus_LV_1023-1_2_2_node_152 | 0.4 | n |  | TRUE
95 | bus_LV_1023-1_2_2_node_160 | 0.4 | n |  | TRUE
96 | bus_LV_1023-1_2_2_node_131 | 0.4 | n |  | TRUE
97 | bus_LV_1023-1_2_2_node_132 | 0.4 | n |  | TRUE
98 | bus_LV_1023-1_2_2_node_134 | 0.4 | n |  | TRUE
99 | bus_LV_1023-1_2_2_node_135 | 0.4 | n |  | TRUE
100 | bus_LV_1023-1_2_2_node_136 | 0.4 | n |  | TRUE
101 | bus_LV_1023-1_2_2_node_137 | 0.4 | n |  | TRUE
102 | bus_LV_1023-1_2_2_node_138 | 0.4 | n |  | TRUE
103 | bus_LV_1023-1_2_2_node_154 | 0.4 | n |  | TRUE
104 | bus_LV_1023-1_2_2_node_141 | 0.4 | n |  | TRUE
105 | bus_LV_1023-1_2_2_node_142 | 0.4 | n |  | TRUE
106 | bus_LV_1023-1_2_2_node_144 | 0.4 | n |  | TRUE
107 | bus_LV_1023-1_2_2_node_147 | 0.4 | n |  | TRUE
108 | bus_LV_1023-1_2_2_node_179 | 0.4 | n |  | TRUE
109 | bus_LV_1023-1_2_2_node_175 | 0.4 | n |  | TRUE
110 | bus_LV_1023-1_2_2_node_151 | 0.4 | n |  | TRUE
111 | bus_LV_1023-1_2_2_node_155 | 0.4 | n |  | TRUE
112 | bus_LV_1023-1_2_2_node_156 | 0.4 | n |  | TRUE
113 | bus_LV_1023-1_2_2_node_157 | 0.4 | n |  | TRUE
114 | bus_LV_1023-1_2_2_node_158 | 0.4 | n |  | TRUE
115 | bus_LV_1023-1_2_2_node_159 | 0.4 | n |  | TRUE
116 | bus_LV_1023-1_2_2_node_169 | 0.4 | n |  | TRUE
117 | bus_LV_1023-1_2_2_node_255 | 0.4 | n |  | TRUE
118 | bus_LV_1023-1_2_2_node_264 | 0.4 | n |  | TRUE
119 | bus_LV_1023-1_2_2_node_259 | 0.4 | n |  | TRUE
120 | bus_LV_1023-1_2_2_node_260 | 0.4 | n |  | TRUE
121 | bus_LV_1023-1_2_2_node_261 | 0.4 | n |  | TRUE
122 | bus_LV_1023-1_2_2_node_270 | 0.4 | n |  | TRUE
123 | bus_LV_1023-1_2_2_node_271 | 0.4 | n |  | TRUE
124 | bus_LV_1023-1_2_2_node_272 | 0.4 | n |  | TRUE
125 | bus_MV_353_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1023-1_2_2_load_48 | 0 | 0.00065206 | 0.00016342 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1023-1_2_2_load_50 | 2 | 0.0037552 | 0.00094115 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1023-1_2_2_load_170 | 4 | 0.00028562 | 7.1583e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1023-1_2_2_load_146 | 6 | 0.00089773 | 0.00022499 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1023-1_2_2_load_52 | 7 | 0.00075214 | 0.0001885 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1023-1_2_2_load_53 | 8 | 0.00022227 | 5.5705e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1023-1_2_2_load_54 | 9 | 0.012385 | 0.003104 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1023-1_2_2_load_55 | 11 | 0.0018949 | 0.00047492 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1023-1_2_2_load_56 | 12 | 0.0017106 | 0.00042871 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1023-1_2_2_load_57 | 13 | 0.0031495 | 0.00078934 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1023-1_2_2_load_59 | 15 | 0.0016469 | 0.00041276 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1023-1_2_2_load_67 | 17 | 0.0003733 | 9.3557e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1023-1_2_2_load_88 | 18 | 0.0050466 | 0.0012648 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1023-1_2_2_load_60 | 19 | 0.00084919 | 0.00021283 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1023-1_2_2_load_61 | 20 | 0.00072856 | 0.0001826 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1023-1_2_2_load_63 | 22 | 0.0010027 | 0.0002513 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1023-1_2_2_load_64 | 23 | 0.003061 | 0.00076716 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1023-1_2_2_load_113 | 24 | 0.00052067 | 0.00013049 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1023-1_2_2_load_65 | 25 | 0.0012836 | 0.0003217 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1023-1_2_2_load_66 | 26 | 0.0036274 | 0.00090912 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1023-1_2_2_load_68 | 27 | 0.0013876 | 0.00034776 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1023-1_2_2_load_123 | 28 | 0.0016837 | 0.00042198 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1023-1_2_2_load_69 | 29 | 0.00077472 | 0.00019416 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1023-1_2_2_load_73 | 33 | 0.0012043 | 0.00030183 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1023-1_2_2_load_76 | 35 | 0.00029736 | 7.4525e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1023-1_2_2_load_122 | 36 | 9.8057e-05 | 2.4575e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1023-1_2_2_load_143 | 37 | 0.00087438 | 0.00021914 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1023-1_2_2_load_273 | 38 | 0.00070464 | 0.0001766 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1023-1_2_2_load_291 | 39 | 0.0013841 | 0.00034689 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1023-1_2_2_load_81 | 40 | 0.0016972 | 0.00042536 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1023-1_2_2_load_82 | 41 | 0.0037059 | 0.00092878 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1023-1_2_2_load_98 | 45 | 0.00051346 | 0.00012869 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1023-1_2_2_load_133 | 46 | 0.0014042 | 0.00035193 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1023-1_2_2_load_172 | 48 | 0.00068024 | 0.00017048 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1023-1_2_2_load_89 | 49 | 0.0048304 | 0.0012106 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1023-1_2_2_load_114 | 50 | 0.0029943 | 0.00075043 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1023-1_2_2_load_90 | 51 | 0.0023862 | 0.00059805 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1023-1_2_2_load_91 | 52 | 0.0017086 | 0.00042822 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1023-1_2_2_load_92 | 53 | 0.0027365 | 0.00068584 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1023-1_2_2_load_93 | 54 | 0.0015589 | 0.00039068 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1023-1_2_2_load_94 | 55 | 0.0027742 | 0.00069528 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1023-1_2_2_load_148 | 56 | 0.00094736 | 0.00023743 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1023-1_2_2_load_145 | 57 | 0.0021943 | 0.00054994 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1023-1_2_2_load_95 | 58 | 0.0022051 | 0.00055265 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1023-1_2_2_load_96 | 59 | 0.0025941 | 0.00065015 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1023-1_2_2_load_99 | 61 | 0.0006905 | 0.00017305 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1023-1_2_2_load_100 | 62 | 0.00086512 | 0.00021682 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1023-1_2_2_load_150 | 63 | 0.00056417 | 0.00014139 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1023-1_2_2_load_174 | 64 | 0.0010682 | 0.00026771 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1023-1_2_2_load_101 | 65 | 0.00037124 | 9.304e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1023-1_2_2_load_102 | 66 | 0.0026442 | 0.0006627 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1023-1_2_2_load_103 | 67 | 0.00047111 | 0.00011807 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1023-1_2_2_load_104 | 68 | 0.00048478 | 0.0001215 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1023-1_2_2_load_105 | 69 | 0.00047746 | 0.00011966 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1023-1_2_2_load_166 | 71 | 0.00072559 | 0.00018185 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1023-1_2_2_load_106 | 72 | 0.0012749 | 0.00031952 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1023-1_2_2_load_109 | 75 | 0.00018162 | 4.5517e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1023-1_2_2_load_301 | 79 | 0.00018592 | 4.6597e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1023-1_2_2_load_300 | 80 | 0.00021858 | 5.4781e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1023-1_2_2_load_306 | 81 | 0.00080425 | 0.00020157 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1023-1_2_2_load_116 | 82 | 0.00093287 | 0.0002338 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1023-1_2_2_load_119 | 83 | 0.0001482 | 3.7143e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1023-1_2_2_load_121 | 85 | 0.00019054 | 4.7755e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1023-1_2_2_load_139 | 86 | 0.00050764 | 0.00012723 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1023-1_2_2_load_140 | 88 | 0.0023735 | 0.00059485 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1023-1_2_2_load_125 | 89 | 0.00097079 | 0.0002433 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1023-1_2_2_load_128 | 91 | 0.00050399 | 0.00012631 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1023-1_2_2_load_129 | 92 | 0.0021495 | 0.00053873 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1023-1_2_2_load_130 | 93 | 0.004489 | 0.001125 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1023-1_2_2_load_152 | 94 | 0.0011382 | 0.00028525 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1023-1_2_2_load_160 | 95 | 0.00076504 | 0.00019174 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1023-1_2_2_load_131 | 96 | 0.0028563 | 0.00071586 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1023-1_2_2_load_132 | 97 | 0.001621 | 0.00040626 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1023-1_2_2_load_134 | 98 | 0.0018925 | 0.0004743 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1023-1_2_2_load_135 | 99 | 0.0007944 | 0.00019909 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1023-1_2_2_load_136 | 100 | 0.001004 | 0.00025163 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1023-1_2_2_load_137 | 101 | 0.0026833 | 0.00067249 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1023-1_2_2_load_138 | 102 | 0.0083046 | 0.0020813 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1023-1_2_2_load_154 | 103 | 0.00088847 | 0.00022267 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1023-1_2_2_load_141 | 104 | 0.00090916 | 0.00022786 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1023-1_2_2_load_142 | 105 | 0.0013157 | 0.00032974 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1023-1_2_2_load_144 | 106 | 0.002525 | 0.00063282 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1023-1_2_2_load_147 | 107 | 0.00053803 | 0.00013484 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1023-1_2_2_load_179 | 108 | 0.0004917 | 0.00012323 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1023-1_2_2_load_175 | 109 | 0.00062717 | 0.00015718 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1023-1_2_2_load_151 | 110 | 0.0010995 | 0.00027556 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1023-1_2_2_load_155 | 111 | 0.00025827 | 6.4729e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1023-1_2_2_load_156 | 112 | 0.00065393 | 0.00016389 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1023-1_2_2_load_157 | 113 | 0.00051338 | 0.00012866 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1023-1_2_2_load_159 | 115 | 0.0010835 | 0.00027155 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1023-1_2_2_load_169 | 116 | 0.00037288 | 9.3453e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1023-1_2_2_load_255 | 117 | 0.00058086 | 0.00014558 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1023-1_2_2_load_259 | 119 | 0.0003057 | 7.6616e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1023-1_2_2_load_260 | 120 | 0.00082637 | 0.00020711 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1023-1_2_2_load_270 | 122 | 0.00049948 | 0.00012518 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1023-1_2_2_load_271 | 123 | 0.00068417 | 0.00017147 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1023-1_2_2_load_272 | 124 | 0.0002221 | 5.5664e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1023-1_2_2_line_0 |  | 0 | 1 | 0.086722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1023-1_2_2_line_1 |  | 0 | 2 | 0.0077368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1023-1_2_2_line_2 |  | 1 | 3 | 0.11662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1023-1_2_2_line_3 |  | 1 | 4 | 0.22602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1023-1_2_2_line_4 |  | 3 | 5 | 0.15456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1023-1_2_2_line_5 |  | 3 | 6 | 0.027582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1023-1_2_2_line_6 |  | 4 | 76 | 0.0067621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1023-1_2_2_line_7 |  | 4 | 114 | 0.10855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1023-1_2_2_line_8 |  | 5 | 91 | 0.030255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1023-1_2_2_line_9 |  | 5 | 89 | 0.078531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1023-1_2_2_line_10 |  | 6 | 107 | 0.02235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1023-1_2_2_line_11 |  | 6 | 82 | 0.17033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1023-1_2_2_line_12 |  | 7 | 8 | 0.042051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1023-1_2_2_line_13 |  | 7 | 9 | 0.025923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1023-1_2_2_line_14 |  | 9 | 10 | 0.09423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1023-1_2_2_line_15 |  | 10 | 82 | 0.092571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1023-1_2_2_line_16 |  | 10 | 23 | 0.020667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1023-1_2_2_line_17 |  | 10 | 50 | 0.15903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1023-1_2_2_line_18 |  | 11 | 12 | 0.0062467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1023-1_2_2_line_19 |  | 11 | 13 | 0.0034573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1023-1_2_2_line_20 |  | 12 | 14 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1023-1_2_2_line_21 |  | 13 | 15 | 0.0071387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1023-1_2_2_line_22 |  | 14 | 16 | 0.015228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1023-1_2_2_line_23 |  | 14 | 17 | 0.0012508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1023-1_2_2_line_24 |  | 15 | 18 | 0.028392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1023-1_2_2_line_25 |  | 16 | 116 | 0.016982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1023-1_2_2_line_26 |  | 16 | 106 | 0.031969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1023-1_2_2_line_27 |  | 17 | 25 | 0.031234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1023-1_2_2_line_28 |  | 18 | 49 | 0.018863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1023-1_2_2_line_29 |  | 19 | 20 | 0.03193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1023-1_2_2_line_30 |  | 19 | 21 | 0.084026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1023-1_2_2_line_31 |  | 20 | 22 | 0.023988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1023-1_2_2_line_32 |  | 21 | 23 | 0.076209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1023-1_2_2_line_33 |  | 22 | 24 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1023-1_2_2_line_34 |  | 24 | 44 | 0.0048582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1023-1_2_2_line_35 |  | 25 | 26 | 0.027122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1023-1_2_2_line_36 |  | 26 | 27 | 0.025632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1023-1_2_2_line_37 |  | 27 | 28 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1023-1_2_2_line_38 |  | 28 | 87 | 0.070237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1023-1_2_2_line_39 |  | 29 | 30 | 0.0052093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1023-1_2_2_line_40 |  | 29 | 31 | 0.16723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1023-1_2_2_line_41 |  | 30 | 32 | 0.004299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1023-1_2_2_line_42 |  | 30 | 33 | 0.013411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1023-1_2_2_line_43 |  | 31 | 34 | 0.11914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1023-1_2_2_line_44 |  | 31 | 35 | 0.036518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1023-1_2_2_line_45 |  | 32 | 36 | 0.012734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1023-1_2_2_line_46 |  | 33 | 37 | 0.021424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1023-1_2_2_line_47 |  | 34 | 38 | 0.026721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1023-1_2_2_line_48 |  | 34 | 39 | 0.029553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1023-1_2_2_line_49 |  | 36 | 84 | 0.021053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1023-1_2_2_line_50 |  | 37 | 104 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1023-1_2_2_line_51 |  | 38 | 123 | 0.012509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1023-1_2_2_line_52 |  | 39 | 118 | 0.049197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1023-1_2_2_line_53 |  | 40 | 41 | 0.050378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1023-1_2_2_line_54 |  | 40 | 42 | 0.019497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1023-1_2_2_line_55 |  | 42 | 43 | 0.020567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1023-1_2_2_line_56 |  | 42 | 44 | 0.025541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1023-1_2_2_line_57 |  | 43 | 45 | 0.0096839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1023-1_2_2_line_58 |  | 43 | 46 | 0.017426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1023-1_2_2_line_59 |  | 44 | 47 | 0.055744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1023-1_2_2_line_60 |  | 46 | 96 | 0.020978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1023-1_2_2_line_61 |  | 47 | 48 | 0.031058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1023-1_2_2_line_62 |  | 49 | 50 | 0.004858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1023-1_2_2_line_63 |  | 51 | 52 | 0.013709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1023-1_2_2_line_64 |  | 51 | 53 | 0.016567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1023-1_2_2_line_65 |  | 52 | 54 | 0.011635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1023-1_2_2_line_66 |  | 53 | 55 | 0.015811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1023-1_2_2_line_67 |  | 54 | 56 | 0.0085613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1023-1_2_2_line_68 |  | 55 | 57 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1023-1_2_2_line_69 |  | 56 | 64 | 0.017477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1023-1_2_2_line_70 |  | 57 | 98 | 0.026707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1023-1_2_2_line_71 |  | 58 | 59 | 0.02088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1023-1_2_2_line_72 |  | 58 | 60 | 0.012825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1023-1_2_2_line_73 |  | 60 | 61 | 0.018204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1023-1_2_2_line_74 |  | 60 | 62 | 0.0088175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1023-1_2_2_line_75 |  | 61 | 63 | 0.013124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1023-1_2_2_line_76 |  | 62 | 64 | 0.030286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1023-1_2_2_line_77 |  | 63 | 110 | 0.013832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1023-1_2_2_line_78 |  | 65 | 66 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1023-1_2_2_line_79 |  | 65 | 67 | 0.012832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1023-1_2_2_line_80 |  | 66 | 68 | 0.003461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1023-1_2_2_line_81 |  | 67 | 69 | 0.0042725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1023-1_2_2_line_82 |  | 68 | 70 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1023-1_2_2_line_83 |  | 69 | 71 | 0.022369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1023-1_2_2_line_84 |  | 70 | 108 | 0.013236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1023-1_2_2_line_85 |  | 70 | 109 | 0.040401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1023-1_2_2_line_86 |  | 72 | 73 | 0.021436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1023-1_2_2_line_87 |  | 72 | 74 | 0.027398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1023-1_2_2_line_88 |  | 73 | 75 | 0.0011021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1023-1_2_2_line_89 |  | 73 | 76 | 0.01768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1023-1_2_2_line_90 |  | 74 | 77 | 0.006018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1023-1_2_2_line_91 |  | 74 | 78 | 0.029265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1023-1_2_2_line_92 |  | 77 | 79 | 0.010236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1023-1_2_2_line_93 |  | 77 | 80 | 0.012418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1023-1_2_2_line_94 |  | 78 | 81 | 0.02458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1023-1_2_2_line_95 |  | 83 | 84 | 0.020334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1023-1_2_2_line_96 |  | 84 | 85 | 0.030633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1023-1_2_2_line_97 |  | 85 | 86 | 0.005579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1023-1_2_2_line_98 |  | 86 | 101 | 0.012809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1023-1_2_2_line_99 |  | 87 | 88 | 0.020471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1023-1_2_2_line_100 |  | 88 | 103 | 0.026402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1023-1_2_2_line_101 |  | 89 | 90 | 0.022569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1023-1_2_2_line_102 |  | 90 | 92 | 0.061165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1023-1_2_2_line_103 |  | 90 | 93 | 0.048208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1023-1_2_2_line_104 |  | 92 | 94 | 0.0094823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1023-1_2_2_line_105 |  | 93 | 95 | 0.071873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1023-1_2_2_line_106 |  | 95 | 115 | 0.048658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1023-1_2_2_line_107 |  | 96 | 97 | 0.0033145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1023-1_2_2_line_108 |  | 97 | 98 | 0.015901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1023-1_2_2_line_109 |  | 99 | 100 | 0.01784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1023-1_2_2_line_110 |  | 99 | 101 | 0.0040929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1023-1_2_2_line_111 |  | 100 | 102 | 0.0083029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1023-1_2_2_line_112 |  | 104 | 105 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1023-1_2_2_line_113 |  | 105 | 106 | 0.0090077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1023-1_2_2_line_114 |  | 108 | 116 | 0.0186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1023-1_2_2_line_115 |  | 111 | 112 | 0.034431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1023-1_2_2_line_116 |  | 111 | 113 | 0.011603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1023-1_2_2_line_117 |  | 113 | 114 | 0.0037435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1023-1_2_2_line_118 |  | 117 | 118 | 0.0297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1023-1_2_2_line_119 |  | 118 | 121 | 0.067418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1023-1_2_2_line_120 |  | 119 | 120 | 0.032855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1023-1_2_2_line_121 |  | 119 | 121 | 0.053614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1023-1_2_2_line_122 |  | 122 | 123 | 0.0032497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1023-1_2_2_line_123 |  | 122 | 124 | 0.0082009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1023-1_2_2_trafo_64 | 0.63 MVA 20/0.4 kV | 125 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2668159.4874 | 1222454.534 | 2668139.8692 | 1222405.1444 | 2668132.7224 | 1222394.0222 | 2668118.5999 | 1222379.3588
1 | 2668113.2329 | 1222373.7863 | 2668118.5999 | 1222379.3588
2 | 2668059.1807 | 1222458.1337 | 2668088.5953 | 1222484.6425 | 2668159.4874 | 1222454.534
3 | 2668364.7139 | 1222359.8303 | 2668159.4874 | 1222454.534
4 | 2668022.0633 | 1222531.5235 | 2668009.6858 | 1222520.8086 | 2668006.153 | 1222510.0392 | 2668025.6753 | 1222508.8169 | 2668046.7496 | 1222503.8655 | 2668064.7826 | 1222495.5773 | 2668088.5953 | 1222484.6425 | 2668059.1807 | 1222458.1337
5 | 2668059.1807 | 1222458.1337 | 2668036.7418 | 1222474.1733
6 | 2668369.4012 | 1222364.7042 | 2668364.7139 | 1222359.8303
7 | 2668343.9061 | 1222254.5186 | 2668344.4703 | 1222256.2484 | 2668350.8975 | 1222298.9718 | 2668354.3496 | 1222330.5984 | 2668356.3218 | 1222344.4633 | 2668358.0955 | 1222349.8538 | 2668362.7302 | 1222357.7676 | 2668364.7139 | 1222359.8303
8 | 2668022.0633 | 1222531.5235 | 2668017.609 | 1222538.3326 | 2668012.9167 | 1222543.4045 | 2668010.2655 | 1222545.0864 | 2668007.5862 | 1222545.2559 | 2668004.4251 | 1222544.4304 | 2667999.5327 | 1222540.758
9 | 2668022.0633 | 1222531.5235 | 2668066.0291 | 1222563.6687 | 2668085.4514 | 1222577.8812
10 | 2668024.3622 | 1222492.3024 | 2668027.2875 | 1222485.2201 | 2668030.6478 | 1222479.8884 | 2668034.7472 | 1222475.5991 | 2668036.7418 | 1222474.1733
11 | 2667932.686 | 1222339.3225 | 2668036.7418 | 1222474.1733
12 | 2667943.8036 | 1222213.0378 | 2667972.6848 | 1222182.4735
13 | 2667925.9996 | 1222231.8793 | 2667943.8036 | 1222213.0378
14 | 2667853.2572 | 1222291.7775 | 2667925.9996 | 1222231.8793
15 | 2667853.2572 | 1222291.7775 | 2667932.686 | 1222339.3225
16 | 2667853.2572 | 1222291.7775 | 2667838.791 | 1222306.5375
17 | 2667853.2572 | 1222291.7775 | 2667825.636 | 1222271.461 | 2667790.3527 | 1222241.2288 | 2667761.3019 | 1222209.8559 | 2667737.7248 | 1222183.2924
18 | 2667697.9336 | 1222134.9152 | 2667694.2573 | 1222129.8649
19 | 2667697.9336 | 1222134.9152 | 2667699.9684 | 1222137.7104
20 | 2667678.8721 | 1222111.1888 | 2667694.0611 | 1222129.5955 | 2667694.2573 | 1222129.8649
21 | 2667704.1697 | 1222143.4819 | 2667699.9684 | 1222137.7104
22 | 2667690.0871 | 1222100.8541 | 2667678.8721 | 1222111.1888
23 | 2667678.8721 | 1222111.1888 | 2667678.0226 | 1222112.1069
24 | 2667704.1697 | 1222143.4819 | 2667712.2847 | 1222154.6298 | 2667721.9786 | 1222165.5516
25 | 2667690.0871 | 1222100.8541 | 2667679.8825 | 1222087.7075 | 2667679.7957 | 1222087.3791
26 | 2667690.0871 | 1222100.8541 | 2667713.9534 | 1222083.9478 | 2667716.3974 | 1222082.7506
27 | 2667678.0226 | 1222112.1069 | 2667656.8084 | 1222135.0313
28 | 2667734.5 | 1222179.6591 | 2667721.9786 | 1222165.5516
29 | 2667786.1144 | 1222449.2524 | 2667785.3669 | 1222449.9171 | 2667770.645 | 1222461.8684 | 2667761.5438 | 1222469.6396
30 | 2667804.2659 | 1222370.2478 | 2667804.2503 | 1222378.275 | 2667800.6515 | 1222404.5509 | 2667800.7995 | 1222425.5216 | 2667798.0071 | 1222434.2732 | 2667791.9337 | 1222444.077 | 2667786.1144 | 1222449.2524
31 | 2667743.301 | 1222485.2168 | 2667761.5438 | 1222469.6396
32 | 2667804.2659 | 1222370.2478 | 2667804.2849 | 1222359.9191 | 2667805.2974 | 1222346.9445 | 2667807.4461 | 1222341.4321 | 2667818.0185 | 1222328.2218 | 2667829.7966 | 1222315.7145 | 2667838.791 | 1222306.5375
33 | 2667736.8312 | 1222498.1345 | 2667739.6022 | 1222490.9895 | 2667743.301 | 1222485.2168 | 2667743.301 | 1222485.2168
34 | 2667736.591 | 1222502.9852 | 2667736.8203 | 1222498.1625 | 2667736.8312 | 1222498.1345
35 | 2667640.8053 | 1222156.9287 | 2667656.8084 | 1222135.0313 | 2667656.8084 | 1222135.0313
36 | 2667640.8053 | 1222156.9287 | 2667632.5603 | 1222168.2105 | 2667625.8542 | 1222177.7471
37 | 2667625.8542 | 1222177.7471 | 2667616.1779 | 1222191.5077
38 | 2667575.7779 | 1222248.9623 | 2667608.1279 | 1222202.9554 | 2667616.1779 | 1222191.5077
39 | 2667789.2563 | 1222048.426 | 2667794.0171 | 1222046.3115
40 | 2667946.8467 | 1221978.4322 | 2667794.0171 | 1222046.3115
41 | 2667789.2563 | 1222048.426 | 2667791.2457 | 1222052.24
42 | 2667789.2563 | 1222048.426 | 2667777.0746 | 1222054.0347
43 | 2667946.8467 | 1221978.4322 | 2667923.7471 | 1221861.5605
44 | 2667946.8467 | 1221978.4322 | 2667980.1901 | 1221963.5407
45 | 2667791.2457 | 1222052.24 | 2667792.3815 | 1222054.421 | 2667797.7268 | 1222058.629 | 2667801.1854 | 1222058.9328
46 | 2667757.6144 | 1222062.9947 | 2667777.0746 | 1222054.0347
47 | 2667923.7471 | 1221861.5605 | 2667950.2253 | 1221857.9644
48 | 2667923.7471 | 1221861.5605 | 2667918.1826 | 1221832.5362
49 | 2667822.1578 | 1222060.7751 | 2667801.1854 | 1222058.9328
50 | 2667757.6144 | 1222062.9947 | 2667742.8328 | 1222069.8005 | 2667738.289 | 1222072.0263
51 | 2667950.2253 | 1221857.9644 | 2667962.62 | 1221856.281
52 | 2667908.9194 | 1221784.2196 | 2667918.1826 | 1221832.5362
53 | 2667699.5015 | 1222521.5607 | 2667688.9609 | 1222527.4039 | 2667656.826 | 1222548.2899
54 | 2667716.5542 | 1222512.1077 | 2667699.5015 | 1222521.5607
55 | 2667716.5542 | 1222512.1077 | 2667708.3115 | 1222493.2574
56 | 2667716.5542 | 1222512.1077 | 2667737.9371 | 1222506.0025 | 2667736.591 | 1222502.9852
57 | 2667708.3115 | 1222493.2574 | 2667708.0378 | 1222483.5774
58 | 2667708.3115 | 1222493.2574 | 2667691.1416 | 1222496.2352
59 | 2667736.591 | 1222502.9852 | 2667737.9371 | 1222506.0025 | 2667758.3045 | 1222501.8314 | 2667789.9076 | 1222500.101
60 | 2667691.1416 | 1222496.2352 | 2667670.4724 | 1222499.8198
61 | 2667789.9076 | 1222500.101 | 2667791.7143 | 1222507.96 | 2667792.8249 | 1222515.0105 | 2667793.2153 | 1222520.6852 | 2667791.8482 | 1222530.7616
62 | 2667734.5 | 1222179.6591 | 2667737.7248 | 1222183.2924
63 | 2667647.2579 | 1222425.1401 | 2667646.0725 | 1222411.4827
64 | 2667648.6904 | 1222441.6453 | 2667647.2579 | 1222425.1401
65 | 2667646.4926 | 1222399.9952 | 2667645.4566 | 1222404.3862 | 2667646.0725 | 1222411.4827
66 | 2667648.6904 | 1222441.6453 | 2667650.0576 | 1222457.3972
67 | 2667654.1432 | 1222396.8912 | 2667649.4707 | 1222397.5719 | 2667646.4926 | 1222399.9952 | 2667646.4926 | 1222399.9952
68 | 2667651.1887 | 1222470.4298 | 2667650.0576 | 1222457.3972
69 | 2667654.1432 | 1222396.8912 | 2667654.1432 | 1222396.8912 | 2667670.2269 | 1222403.7297
70 | 2667651.1887 | 1222470.4298 | 2667653.498 | 1222497.037 | 2667653.498 | 1222497.037
71 | 2667706.5753 | 1222431.8507 | 2667707.1654 | 1222452.7223
72 | 2667706.2128 | 1222419.0304 | 2667706.5753 | 1222431.8507
73 | 2667706.2128 | 1222419.0304 | 2667722.9146 | 1222426.2707
74 | 2667706.2128 | 1222419.0304 | 2667698.0983 | 1222415.5802
75 | 2667722.9146 | 1222426.2707 | 2667734.9555 | 1222431.4905
76 | 2667698.0983 | 1222415.5802 | 2667670.2269 | 1222403.7297
77 | 2667734.9555 | 1222431.4905 | 2667747.6464 | 1222436.992
78 | 2667639.4029 | 1222056.9757 | 2667651.0143 | 1222055.5034
79 | 2667628.1328 | 1222062.982 | 2667638.541 | 1222057.085 | 2667639.4029 | 1222056.9757
80 | 2667654.4746 | 1222055.5748 | 2667651.0143 | 1222055.5034 | 2667651.0143 | 1222055.5034
81 | 2667628.1328 | 1222062.982 | 2667624.4155 | 1222065.0882
82 | 2667674.9559 | 1222055.9979 | 2667654.4746 | 1222055.5748
83 | 2667624.4155 | 1222065.0882 | 2667611.3772 | 1222072.4753 | 2667604.1234 | 1222073.8519
84 | 2667674.9559 | 1222055.9979 | 2667676.3201 | 1222069.163
85 | 2667674.9559 | 1222055.9979 | 2667670.783 | 1222015.8127
86 | 2668386.9138 | 1222362.8374 | 2668389.8384 | 1222353.8763 | 2668395.2728 | 1222343.1664
87 | 2668407.7859 | 1222318.7932 | 2668402.0152 | 1222329.8785 | 2668395.2728 | 1222343.1664
88 | 2668386.9138 | 1222362.8374 | 2668386.5703 | 1222363.8845
89 | 2668386.9138 | 1222362.8374 | 2668376.8927 | 1222364.9237 | 2668369.4012 | 1222364.7042
90 | 2668409.1277 | 1222312.927 | 2668407.7859 | 1222318.7932
91 | 2668427.3126 | 1222297.4593 | 2668425.2607 | 1222298.4586 | 2668422.1192 | 1222301.8692 | 2668413.589 | 1222314.1346 | 2668407.7859 | 1222318.7932
92 | 2668414.4679 | 1222304.3162 | 2668413.5767 | 1222306.6296 | 2668411.3574 | 1222308.9946 | 2668409.1277 | 1222312.927
93 | 2668409.1277 | 1222312.927 | 2668408.5076 | 1222309.4621 | 2668407.0478 | 1222307.7776 | 2668404.0655 | 1222306.5759 | 2668400.6461 | 1222306.0884
94 | 2668426.2965 | 1222319.2061 | 2668430.9325 | 1222305.217 | 2668431.0329 | 1222301.1044 | 2668430.6437 | 1222299.3321 | 2668429.4361 | 1222298.1508 | 2668427.3126 | 1222297.4593
95 | 2667822.1578 | 1222060.7751 | 2667842.4877 | 1222061.2
96 | 2667822.1578 | 1222060.7751 | 2667823.9485 | 1222068.7228 | 2667821.8123 | 1222073.7906 | 2667808.168 | 1222083.9086
97 | 2667803.6867 | 1222087.2317 | 2667808.168 | 1222083.9086
98 | 2667803.6867 | 1222087.2317 | 2667794.081 | 1222094.3548 | 2667793.4351 | 1222094.9083
99 | 2667575.7779 | 1222248.9623 | 2667592.9425 | 1222260.1167
100 | 2667617.9188 | 1222268.3981 | 2667616.262 | 1222268.1562 | 2667594.5493 | 1222261.1609 | 2667592.9425 | 1222260.1167
101 | 2668103.6916 | 1222591.1725 | 2668092.7317 | 1222583.2087 | 2668085.4514 | 1222577.8812
102 | 2668103.6916 | 1222591.1725 | 2668113.4207 | 1222648.3649 | 2668113.8765 | 1222651.4828
103 | 2668103.6916 | 1222591.1725 | 2668117.9601 | 1222597.662 | 2668149.4589 | 1222605.7997
104 | 2668115.248 | 1222660.8654 | 2668113.8765 | 1222651.4828
105 | 2668149.4589 | 1222605.7997 | 2668157.6325 | 1222607.9113 | 2668170.6322 | 1222609.2832 | 2668220.8921 | 1222606.1265
106 | 2668220.8921 | 1222606.1265 | 2668239.9461 | 1222604.9297 | 2668252.4547 | 1222606.7965 | 2668268.5439 | 1222612.03
107 | 2667670.4724 | 1222499.8198 | 2667667.2066 | 1222500.3862
108 | 2667653.498 | 1222497.037 | 2667655.1786 | 1222499.9913 | 2667659.3379 | 1222501.7508 | 2667667.2066 | 1222500.3862
109 | 2667790.3275 | 1222097.5719 | 2667781.9702 | 1222104.7348 | 2667776.8675 | 1222109.2793
110 | 2667790.3275 | 1222097.5719 | 2667793.4351 | 1222094.9083
111 | 2667770.6672 | 1222114.8015 | 2667776.8675 | 1222109.2793
112 | 2667738.289 | 1222072.0263 | 2667724.4866 | 1222078.7878
113 | 2667716.3974 | 1222082.7506 | 2667724.4866 | 1222078.7878
114 | 2667679.7957 | 1222087.3791 | 2667677.1843 | 1222077.5036 | 2667676.3201 | 1222069.163
115 | 2668332.5798 | 1222246.0721 | 2668326.1699 | 1222246.7657 | 2668298.6094 | 1222251.6159
116 | 2668332.5798 | 1222246.0721 | 2668332.5798 | 1222246.0721 | 2668337.7114 | 1222247.0427 | 2668342.7486 | 1222250.9586 | 2668342.7486 | 1222250.9586
117 | 2668343.9061 | 1222254.5186 | 2668342.7486 | 1222250.9586
118 | 2667908.9194 | 1221784.2196 | 2667914.651 | 1221769.8758 | 2667919.3488 | 1221756.4191
119 | 2667908.9194 | 1221784.2196 | 2667896.8327 | 1221801.7264 | 2667885.5619 | 1221812.894 | 2667872.9969 | 1221823.8022 | 2667861.4576 | 1221831.2422
120 | 2667811.5455 | 1221850.2576 | 2667800.5594 | 1221853.8744 | 2667779.7876 | 1221858.5373
121 | 2667861.4576 | 1221831.2422 | 2667851.2857 | 1221837.1746 | 2667811.5455 | 1221850.2576
122 | 2667965.8401 | 1221855.8437 | 2667962.62 | 1221856.281
123 | 2667973.9665 | 1221854.74 | 2667965.8401 | 1221855.8437

## bus_geodata
| x | y | coords
0 | 2668118.5999 | 1222379.3588
1 | 2668159.4874 | 1222454.534
2 | 2668113.2329 | 1222373.7863
3 | 2668059.1807 | 1222458.1337
4 | 2668364.7139 | 1222359.8303
5 | 2668022.0633 | 1222531.5235
6 | 2668036.7418 | 1222474.1733
7 | 2667943.8036 | 1222213.0378
8 | 2667972.6848 | 1222182.4735
9 | 2667925.9996 | 1222231.8793
10 | 2667853.2572 | 1222291.7775
11 | 2667697.9336 | 1222134.9152
12 | 2667694.2573 | 1222129.8649
13 | 2667699.9684 | 1222137.7104
14 | 2667678.8721 | 1222111.1888
15 | 2667704.1697 | 1222143.4819
16 | 2667690.0871 | 1222100.8541
17 | 2667678.0226 | 1222112.1069
18 | 2667721.9786 | 1222165.5516
19 | 2667786.1144 | 1222449.2524
20 | 2667761.5438 | 1222469.6396
21 | 2667804.2659 | 1222370.2478
22 | 2667743.301 | 1222485.2168
23 | 2667838.791 | 1222306.5375
24 | 2667736.8312 | 1222498.1345
25 | 2667656.8084 | 1222135.0313
26 | 2667640.8053 | 1222156.9287
27 | 2667625.8542 | 1222177.7471
28 | 2667616.1779 | 1222191.5077
29 | 2667794.0171 | 1222046.3115
30 | 2667789.2563 | 1222048.426
31 | 2667946.8467 | 1221978.4322
32 | 2667791.2457 | 1222052.24
33 | 2667777.0746 | 1222054.0347
34 | 2667923.7471 | 1221861.5605
35 | 2667980.1901 | 1221963.5407
36 | 2667801.1854 | 1222058.9328
37 | 2667757.6144 | 1222062.9947
38 | 2667950.2253 | 1221857.9644
39 | 2667918.1826 | 1221832.5362
40 | 2667699.5015 | 1222521.5607
41 | 2667656.826 | 1222548.2899
42 | 2667716.5542 | 1222512.1077
43 | 2667708.3115 | 1222493.2574
44 | 2667736.591 | 1222502.9852
45 | 2667708.0378 | 1222483.5774
46 | 2667691.1416 | 1222496.2352
47 | 2667789.9076 | 1222500.101
48 | 2667791.8482 | 1222530.7616
49 | 2667734.5 | 1222179.6591
50 | 2667737.7248 | 1222183.2924
51 | 2667647.2579 | 1222425.1401
52 | 2667646.0725 | 1222411.4827
53 | 2667648.6904 | 1222441.6453
54 | 2667646.4926 | 1222399.9952
55 | 2667650.0576 | 1222457.3972
56 | 2667654.1432 | 1222396.8912
57 | 2667651.1887 | 1222470.4298
58 | 2667706.5753 | 1222431.8507
59 | 2667707.1654 | 1222452.7223
60 | 2667706.2128 | 1222419.0304
61 | 2667722.9146 | 1222426.2707
62 | 2667698.0983 | 1222415.5802
63 | 2667734.9555 | 1222431.4905
64 | 2667670.2269 | 1222403.7297
65 | 2667639.4029 | 1222056.9757
66 | 2667651.0143 | 1222055.5034
67 | 2667628.1328 | 1222062.982
68 | 2667654.4746 | 1222055.5748
69 | 2667624.4155 | 1222065.0882
70 | 2667674.9559 | 1222055.9979
71 | 2667604.1234 | 1222073.8519
72 | 2668395.2728 | 1222343.1664
73 | 2668386.9138 | 1222362.8374
74 | 2668407.7859 | 1222318.7932
75 | 2668386.5703 | 1222363.8845
76 | 2668369.4012 | 1222364.7042
77 | 2668409.1277 | 1222312.927
78 | 2668427.3126 | 1222297.4593
79 | 2668414.468 | 1222304.3162
80 | 2668400.6461 | 1222306.0884
81 | 2668426.2965 | 1222319.2061
82 | 2667932.686 | 1222339.3225
83 | 2667842.4877 | 1222061.2
84 | 2667822.1578 | 1222060.7751
85 | 2667808.168 | 1222083.9086
86 | 2667803.6867 | 1222087.2317
87 | 2667575.7779 | 1222248.9623
88 | 2667592.9425 | 1222260.1167
89 | 2668085.4514 | 1222577.8812
90 | 2668103.6916 | 1222591.1725
91 | 2667999.5327 | 1222540.758
92 | 2668113.8765 | 1222651.4828
93 | 2668149.4589 | 1222605.7997
94 | 2668115.248 | 1222660.8654
95 | 2668220.8921 | 1222606.1265
96 | 2667670.4724 | 1222499.8198
97 | 2667667.2066 | 1222500.3862
98 | 2667653.498 | 1222497.037
99 | 2667790.3275 | 1222097.5719
100 | 2667776.8675 | 1222109.2793
101 | 2667793.4351 | 1222094.9083
102 | 2667770.6672 | 1222114.8015
103 | 2667617.9188 | 1222268.3981
104 | 2667738.289 | 1222072.0263
105 | 2667724.4866 | 1222078.7878
106 | 2667716.3974 | 1222082.7506
107 | 2668024.3622 | 1222492.3024
108 | 2667676.3201 | 1222069.163
109 | 2667670.783 | 1222015.8127
110 | 2667747.6464 | 1222436.992
111 | 2668332.5798 | 1222246.0721
112 | 2668298.6094 | 1222251.6159
113 | 2668342.7486 | 1222250.9586
114 | 2668343.9061 | 1222254.5186
115 | 2668268.5439 | 1222612.03
116 | 2667679.7957 | 1222087.3791
117 | 2667919.3488 | 1221756.4191
118 | 2667908.9194 | 1221784.2196
119 | 2667811.5455 | 1221850.2576
120 | 2667779.7876 | 1221858.5373
121 | 2667861.4576 | 1221831.2422
122 | 2667965.8401 | 1221855.8437
123 | 2667962.62 | 1221856.281
124 | 2667973.9665 | 1221854.74
125 | 2667838.791 | 1222306.5375

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99106 | -0.17188 | 0.00065206 | 0.00016342
1 | 0.99141 | -0.1651 | 0 | 0
2 | 0.99104 | -0.1724 | 0.0037552 | 0.00094115
3 | 0.99235 | -0.14691 | 0 | 0
4 | 0.99051 | -0.18271 | 0.00028562 | 7.1583e-05
5 | 0.99078 | -0.17736 | 0 | 0
6 | 0.99285 | -0.13718 | 0.00089773 | 0.00022499
7 | 0.99689 | -0.059357 | 0.00075214 | 0.0001885
8 | 0.99688 | -0.059522 | 0.00022227 | 5.5705e-05
9 | 0.99692 | -0.058914 | 0.012385 | 0.003104
10 | 0.99806 | -0.036855 | 0 | 0
11 | 0.98511 | -0.28575 | 0.0018949 | 0.00047492
12 | 0.98484 | -0.29101 | 0.0017106 | 0.00042871
13 | 0.98526 | -0.28272 | 0.0031495 | 0.00078934
14 | 0.98383 | -0.31067 | 0 | 0
15 | 0.98561 | -0.27607 | 0.0016469 | 0.00041276
16 | 0.98336 | -0.31987 | 0 | 0
17 | 0.98382 | -0.31093 | 0.0003733 | 9.3557e-05
18 | 0.98701 | -0.24882 | 0.0050466 | 0.0012648
19 | 0.99399 | -0.11488 | 0.00084919 | 0.00021283
20 | 0.99281 | -0.13746 | 0.00072856 | 0.0001826
21 | 0.99714 | -0.054466 | 0 | 0
22 | 0.99195 | -0.15414 | 0.0010027 | 0.0002513
23 | 1 | 0 | -0.14625 | -0.03686
24 | 0.99144 | -0.164 | 0.00052067 | 0.00013049
25 | 0.98349 | -0.31726 | 0.0012836 | 0.0003217
26 | 0.98324 | -0.32214 | 0.0036274 | 0.00090912
27 | 0.98309 | -0.32506 | 0.0013876 | 0.00034776
28 | 0.98302 | -0.32657 | 0.0016837 | 0.00042198
29 | 0.9809 | -0.36795 | 0.00077472 | 0.00019416
30 | 0.98093 | -0.36735 | 0 | 0
31 | 0.98005 | -0.38469 | 0 | 0
32 | 0.98088 | -0.36842 | 0 | 0
33 | 0.98118 | -0.36249 | 0.0012043 | 0.00030183
34 | 0.97947 | -0.39598 | 0 | 0
35 | 0.98004 | -0.38489 | 0.00029736 | 7.4525e-05
36 | 0.98071 | -0.37159 | 9.8057e-05 | 2.4575e-05
37 | 0.9816 | -0.35425 | 0.00087438 | 0.00021914
38 | 0.97942 | -0.39701 | 0.00070464 | 0.0001766
39 | 0.97939 | -0.39765 | 0.0013841 | 0.00034689
40 | 0.9903 | -0.18595 | 0.0016972 | 0.00042536
41 | 0.99013 | -0.18927 | 0.0037059 | 0.00092878
42 | 0.9904 | -0.18408 | 0 | 0
43 | 0.9898 | -0.19566 | 0 | 0
44 | 0.99127 | -0.16725 | 0 | 0
45 | 0.9898 | -0.19575 | 0.00051346 | 0.00012869
46 | 0.9893 | -0.20533 | 0.0014042 | 0.00035193
47 | 0.99124 | -0.16793 | 0 | 0
48 | 0.99122 | -0.1683 | 0.00068024 | 0.00017048
49 | 0.98803 | -0.22906 | 0.0048304 | 0.0012106
50 | 0.98831 | -0.22356 | 0.0029943 | 0.00075043
51 | 0.98694 | -0.2512 | 0.0023862 | 0.00059805
52 | 0.98678 | -0.25447 | 0.0017086 | 0.00042822
53 | 0.98718 | -0.24655 | 0.0027365 | 0.00068584
54 | 0.98665 | -0.25689 | 0.0015589 | 0.00039068
55 | 0.98745 | -0.24134 | 0.0027742 | 0.00069528
56 | 0.98657 | -0.25842 | 0.00094736 | 0.00023743
57 | 0.9877 | -0.23639 | 0.0021943 | 0.00054994
58 | 0.98609 | -0.26786 | 0.0022051 | 0.00055265
59 | 0.98604 | -0.26883 | 0.0025941 | 0.00065015
60 | 0.98615 | -0.26675 | 0 | 0
61 | 0.98611 | -0.26752 | 0.0006905 | 0.00017305
62 | 0.9862 | -0.26562 | 0.00086512 | 0.00021682
63 | 0.98609 | -0.26791 | 0.00056417 | 0.00014139
64 | 0.98643 | -0.26127 | 0.0010682 | 0.00026771
65 | 0.98294 | -0.32805 | 0.00037124 | 9.304e-05
66 | 0.98296 | -0.32762 | 0.0026442 | 0.0006627
67 | 0.98292 | -0.32844 | 0.00047111 | 0.00011807
68 | 0.98298 | -0.32733 | 0.00048478 | 0.0001215
69 | 0.98292 | -0.32853 | 0.00047746 | 0.00011966
70 | 0.98308 | -0.32541 | 0 | 0
71 | 0.9829 | -0.32882 | 0.00072559 | 0.00018185
72 | 0.9904 | -0.18482 | 0.0012749 | 0.00031952
73 | 0.99045 | -0.18387 | 0 | 0
74 | 0.99037 | -0.18541 | 0 | 0
75 | 0.99045 | -0.18388 | 0.00018162 | 4.5517e-05
76 | 0.99049 | -0.18303 | 0 | 0
77 | 0.99037 | -0.18545 | 0 | 0
78 | 0.99035 | -0.18583 | 0 | 0
79 | 0.99036 | -0.18549 | 0.00018592 | 4.6597e-05
80 | 0.99036 | -0.1855 | 0.00021858 | 5.4781e-05
81 | 0.99033 | -0.18618 | 0.00080425 | 0.00020157
82 | 0.99617 | -0.073049 | 0.00093287 | 0.0002338
83 | 0.98045 | -0.37685 | 0.0001482 | 3.7143e-05
84 | 0.98045 | -0.37679 | 0 | 0
85 | 0.98007 | -0.38429 | 0.00019054 | 4.7755e-05
86 | 0.98 | -0.38563 | 0.00050764 | 0.00012723
87 | 0.98281 | -0.3307 | 0 | 0
88 | 0.98274 | -0.33191 | 0.0023735 | 0.00059485
89 | 0.99001 | -0.19216 | 0.00097079 | 0.0002433
90 | 0.98982 | -0.19603 | 0 | 0
91 | 0.99076 | -0.17763 | 0.00050399 | 0.00012631
92 | 0.98963 | -0.19961 | 0.0021495 | 0.00053873
93 | 0.98954 | -0.20147 | 0.004489 | 0.001125
94 | 0.98962 | -0.1998 | 0.0011382 | 0.00028525
95 | 0.98941 | -0.20384 | 0.00076504 | 0.00019174
96 | 0.98873 | -0.21646 | 0.0028563 | 0.00071586
97 | 0.98865 | -0.21805 | 0.001621 | 0.00040626
98 | 0.98828 | -0.22523 | 0.0018925 | 0.0004743
99 | 0.97981 | -0.38936 | 0.0007944 | 0.00019909
100 | 0.97965 | -0.39237 | 0.001004 | 0.00025163
101 | 0.97985 | -0.38861 | 0.0026833 | 0.00067249
102 | 0.97959 | -0.39362 | 0.0083046 | 0.0020813
103 | 0.98272 | -0.33233 | 0.00088847 | 0.00022267
104 | 0.98204 | -0.34572 | 0.00090916 | 0.00022786
105 | 0.98236 | -0.33933 | 0.0013157 | 0.00032974
106 | 0.98256 | -0.33537 | 0.002525 | 0.00063282
107 | 0.99284 | -0.1374 | 0.00053803 | 0.00013484
108 | 0.98315 | -0.32403 | 0.0004917 | 0.00012323
109 | 0.98305 | -0.32587 | 0.00062717 | 0.00015718
110 | 0.98607 | -0.26819 | 0.0010995 | 0.00027556
111 | 0.99035 | -0.18575 | 0.00025827 | 6.4729e-05
112 | 0.99033 | -0.18615 | 0.00065393 | 0.00016389
113 | 0.99036 | -0.18556 | 0.00051338 | 0.00012866
114 | 0.99036 | -0.18547 | 0 | 0
115 | 0.98937 | -0.20477 | 0.0010835 | 0.00027155
116 | 0.98325 | -0.32192 | 0.00037288 | 9.3453e-05
117 | 0.9793 | -0.3995 | 0.00058086 | 0.00014558
118 | 0.97931 | -0.39918 | 0 | 0
119 | 0.97918 | -0.40168 | 0.0003057 | 7.6616e-05
120 | 0.97916 | -0.40218 | 0.00082637 | 0.00020711
121 | 0.97924 | -0.40058 | 0 | 0
122 | 0.9794 | -0.39737 | 0.00049948 | 0.00012518
123 | 0.97941 | -0.39732 | 0.00068417 | 0.00017147
124 | 0.9794 | -0.3974 | 0.0002221 | 5.5664e-05
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0044074 | -0.0011045 | 0.0044088 | 0.0011043 | 1.424e-06 | -2.0652e-07 | 0.0066174 | 0.006617 | 0.0066174 | 0.99106 | -0.17188 | 0.99141 | -0.1651 | 1.818
1 | 0.0037553 | 0.00094111 | -0.0037552 | -0.00094115 | 9.2236e-08 | -4.0661e-08 | 0.0056384 | 0.0056384 | 0.0056384 | 0.99106 | -0.17188 | 0.99104 | -0.1724 | 1.549
2 | -0.0087895 | -0.0021969 | 0.0087971 | 0.0022003 | 7.6081e-06 | 3.364e-06 | 0.01319 | 0.01319 | 0.01319 | 0.99141 | -0.1651 | 0.99235 | -0.14691 | 3.6237
3 | 0.0043807 | 0.0010926 | -0.004377 | -0.0010931 | 3.6626e-06 | -5.6782e-07 | 0.0065731 | 0.0065741 | 0.0065741 | 0.99141 | -0.1651 | 0.99051 | -0.18271 | 1.8061
4 | 0.011128 | 0.002793 | -0.011112 | -0.0027847 | 1.6141e-05 | 8.3367e-06 | 0.016688 | 0.016688 | 0.016688 | 0.99235 | -0.14691 | 0.99078 | -0.17736 | 4.5847
5 | -0.019925 | -0.0049932 | 0.019934 | 0.0049988 | 9.2328e-06 | 5.5525e-06 | 0.029877 | 0.029877 | 0.029877 | 0.99235 | -0.14691 | 0.99285 | -0.13718 | 8.208
6 | 0.0026656 | 0.00066617 | -0.0026656 | -0.00066623 | 4.065e-08 | -6.102e-08 | 0.0040038 | 0.0040038 | 0.0040038 | 0.99051 | -0.18271 | 0.99049 | -0.18303 | 1.1
7 | 0.0014258 | 0.00035538 | -0.0014256 | -0.00035666 | 1.8668e-07 | -1.2775e-06 | 0.0021412 | 0.0021417 | 0.0021417 | 0.99051 | -0.18271 | 0.99036 | -0.18547 | 0.58839
8 | 0.000504 | 0.00012593 | -0.00050399 | -0.00012631 | 6.4993e-09 | -3.8547e-07 | 0.0007568 | 0.00075694 | 0.00075694 | 0.99078 | -0.17736 | 0.99076 | -0.17763 | 0.20795
9 | 0.010608 | 0.0026587 | -0.0106 | -0.002655 | 7.4747e-06 | 3.7732e-06 | 0.015931 | 0.015932 | 0.015932 | 0.99078 | -0.17736 | 0.99001 | -0.19216 | 4.3769
10 | 0.00053804 | 0.00013456 | -0.00053803 | -0.00013484 | 5.4491e-09 | -2.8555e-07 | 0.00080627 | 0.00080637 | 0.00080637 | 0.99285 | -0.13718 | 0.99284 | -0.1374 | 0.22153
11 | -0.02137 | -0.0053583 | 0.021435 | 0.0053981 | 6.5523e-05 | 3.9724e-05 | 0.032029 | 0.032028 | 0.032029 | 0.99285 | -0.13718 | 0.99617 | -0.073049 | 8.7991
12 | 0.00022227 | 5.5158e-05 | -0.00022227 | -5.5705e-05 | 1.7347e-09 | -5.4714e-07 | 0.00033158 | 0.00033177 | 0.00033177 | 0.99689 | -0.059357 | 0.99688 | -0.059522 | 0.091145
13 | -0.00097441 | -0.00024366 | 0.00097443 | 0.00024334 | 2.0557e-08 | -3.2483e-07 | 0.0014543 | 0.0014541 | 0.0014543 | 0.99689 | -0.059357 | 0.99692 | -0.058914 | 0.39952
14 | -0.01336 | -0.0033474 | 0.013374 | 0.0033551 | 1.405e-05 | 7.7621e-06 | 0.019941 | 0.01994 | 0.019941 | 0.99692 | -0.058914 | 0.99806 | -0.036855 | 5.4782
15 | 0.022407 | 0.0056555 | -0.022368 | -0.0056319 | 3.8775e-05 | 2.3608e-05 | 0.033421 | 0.033421 | 0.033421 | 0.99806 | -0.036855 | 0.99617 | -0.073049 | 9.1817
16 | -0.1031 | -0.026223 | 0.10328 | 0.02634 | 0.00018345 | 0.00011713 | 0.15385 | 0.15385 | 0.15385 | 0.99806 | -0.036855 | 1 | 0 | 42.2666
17 | 0.067321 | 0.017213 | -0.066718 | -0.016829 | 0.00060221 | 0.00038336 | 0.10049 | 0.10049 | 0.10049 | 0.99806 | -0.036855 | 0.98831 | -0.22356 | 27.6073
18 | 0.04699 | 0.011821 | -0.046978 | -0.011814 | 1.1807e-05 | 7.4768e-06 | 0.070994 | 0.070994 | 0.070994 | 0.98511 | -0.28575 | 0.98484 | -0.29101 | 19.5039
19 | -0.048885 | -0.012296 | 0.048892 | 0.0123 | 7.0721e-06 | 4.4821e-06 | 0.073856 | 0.073856 | 0.073856 | 0.98511 | -0.28575 | 0.98526 | -0.28272 | 20.2902
20 | 0.045267 | 0.011385 | -0.045225 | -0.011358 | 4.2466e-05 | 2.6871e-05 | 0.06841 | 0.06841 | 0.06841 | 0.98484 | -0.29101 | 0.98383 | -0.31067 | 18.7939
21 | -0.052041 | -0.01309 | 0.052058 | 0.0131 | 1.6544e-05 | 1.0497e-05 | 0.078613 | 0.078613 | 0.078613 | 0.98526 | -0.28272 | 0.98561 | -0.27607 | 21.597
22 | 0.033599 | 0.008444 | -0.033585 | -0.0084348 | 1.4752e-05 | 9.248e-06 | 0.050826 | 0.050826 | 0.050826 | 0.98383 | -0.31067 | 0.98336 | -0.31987 | 13.9633
23 | 0.011626 | 0.0029139 | -0.011625 | -0.0029139 | 1.4502e-07 | 7.6929e-08 | 0.017583 | 0.017583 | 0.017583 | 0.98383 | -0.31067 | 0.98382 | -0.31093 | 4.8306
24 | -0.053705 | -0.013513 | 0.053775 | 0.013557 | 7.0027e-05 | 4.4455e-05 | 0.081099 | 0.081099 | 0.081099 | 0.98561 | -0.27607 | 0.98701 | -0.24882 | 22.2801
25 | 0.0066684 | 0.0016701 | -0.0066678 | -0.0016699 | 6.4838e-07 | 1.9955e-07 | 0.01009 | 0.01009 | 0.01009 | 0.98336 | -0.31987 | 0.98325 | -0.32192 | 2.7721
26 | 0.026916 | 0.0067647 | -0.026896 | -0.0067524 | 1.9894e-05 | 1.2327e-05 | 0.040736 | 0.040736 | 0.040736 | 0.98336 | -0.31987 | 0.98256 | -0.33537 | 11.1913
27 | 0.011252 | 0.0028203 | -0.011249 | -0.0028185 | 3.3925e-06 | 1.7747e-06 | 0.017019 | 0.017019 | 0.017019 | 0.98382 | -0.31093 | 0.98349 | -0.31726 | 4.6755
28 | -0.058821 | -0.014822 | 0.058877 | 0.014858 | 5.5662e-05 | 3.5383e-05 | 0.088708 | 0.088708 | 0.088708 | 0.98701 | -0.24882 | 0.98803 | -0.22906 | 24.3702
29 | 0.040237 | 0.010163 | -0.040194 | -0.010136 | 4.3486e-05 | 2.7418e-05 | 0.060264 | 0.060264 | 0.060264 | 0.99399 | -0.11488 | 0.99281 | -0.13746 | 16.5561
30 | -0.041087 | -0.010376 | 0.041206 | 0.010451 | 0.00011931 | 7.5268e-05 | 0.061535 | 0.061535 | 0.061535 | 0.99399 | -0.11488 | 0.99714 | -0.054466 | 16.9053
31 | 0.039465 | 0.0099533 | -0.039434 | -0.0099335 | 3.1497e-05 | 1.9848e-05 | 0.059172 | 0.059172 | 0.059172 | 0.99281 | -0.13746 | 0.99195 | -0.15414 | 16.2561
32 | -0.041206 | -0.010451 | 0.041314 | 0.01052 | 0.00010821 | 6.8259e-05 | 0.061535 | 0.061534 | 0.061535 | 0.99714 | -0.054466 | 1 | 0 | 16.9052
33 | 0.038431 | 0.0096822 | -0.038413 | -0.0096708 | 1.8107e-05 | 1.1401e-05 | 0.057668 | 0.057668 | 0.057668 | 0.99195 | -0.15414 | 0.99144 | -0.164 | 15.8429
34 | 0.037892 | 0.0095403 | -0.037886 | -0.0095366 | 5.8956e-06 | 3.7106e-06 | 0.056887 | 0.056887 | 0.056887 | 0.99144 | -0.164 | 0.99127 | -0.16725 | 15.6282
35 | 0.0099651 | 0.0024968 | -0.0099627 | -0.0024957 | 2.3119e-06 | 1.1356e-06 | 0.015077 | 0.015077 | 0.015077 | 0.98349 | -0.31726 | 0.98324 | -0.32214 | 4.142
36 | 0.0063353 | 0.0015866 | -0.0063344 | -0.0015863 | 8.835e-07 | 2.404e-07 | 0.0095873 | 0.0095874 | 0.0095874 | 0.98324 | -0.32214 | 0.98309 | -0.32506 | 2.6339
37 | 0.0049469 | 0.0012386 | -0.0049465 | -0.0012386 | 3.5363e-07 | 1.3047e-08 | 0.0074872 | 0.0074873 | 0.0074873 | 0.98309 | -0.32506 | 0.98302 | -0.32657 | 2.0569
38 | 0.0032628 | 0.00081658 | -0.0032622 | -0.00081706 | 6.4243e-07 | -4.7908e-07 | 0.0049386 | 0.0049389 | 0.0049389 | 0.98302 | -0.32657 | 0.98281 | -0.3307 | 1.3568
39 | -0.0062874 | -0.0015708 | 0.0062875 | 0.0015709 | 1.7764e-07 | 4.7933e-08 | 0.0095361 | 0.0095361 | 0.0095361 | 0.9809 | -0.36795 | 0.98093 | -0.36735 | 2.6198
40 | 0.0055126 | 0.0013766 | -0.0055082 | -0.0013759 | 4.384e-06 | 6.9673e-07 | 0.0083608 | 0.0083616 | 0.0083616 | 0.9809 | -0.36795 | 0.98005 | -0.38469 | 2.2971
41 | 0.013747 | 0.0034496 | -0.013746 | -0.0034492 | 7.0112e-07 | 3.9445e-07 | 0.020854 | 0.020854 | 0.020854 | 0.98093 | -0.36735 | 0.98088 | -0.36842 | 5.7292
42 | -0.020034 | -0.0050205 | 0.020039 | 0.0050233 | 4.6447e-06 | 2.8033e-06 | 0.03039 | 0.03039 | 0.03039 | 0.98093 | -0.36735 | 0.98118 | -0.36249 | 8.349
43 | 0.0052109 | 0.0013019 | -0.0052081 | -0.0013016 | 2.7957e-06 | 2.8888e-07 | 0.0079103 | 0.0079108 | 0.0079108 | 0.98005 | -0.38469 | 0.97947 | -0.39598 | 2.1733
44 | 0.00029736 | 7.4066e-05 | -0.00029736 | -7.4525e-05 | 2.7904e-09 | -4.5837e-07 | 0.00045132 | 0.00045148 | 0.00045148 | 0.98005 | -0.38469 | 0.98004 | -0.38489 | 0.12403
45 | 0.013746 | 0.0034492 | -0.013744 | -0.0034481 | 2.0768e-06 | 1.1684e-06 | 0.020854 | 0.020854 | 0.020854 | 0.98088 | -0.36842 | 0.98071 | -0.37159 | 5.7292
46 | -0.021243 | -0.0053251 | 0.021251 | 0.0053302 | 8.3385e-06 | 5.066e-06 | 0.032217 | 0.032217 | 0.032217 | 0.98118 | -0.36249 | 0.9816 | -0.35425 | 8.8508
47 | 0.0021105 | 0.00052836 | -0.0021104 | -0.00052863 | 1.03e-07 | -2.7038e-07 | 0.0032061 | 0.0032062 | 0.0032062 | 0.97947 | -0.39598 | 0.97942 | -0.39701 | 0.88083
48 | 0.0030976 | 0.00077323 | -0.0030973 | -0.00077345 | 2.4531e-07 | -2.1493e-07 | 0.0047047 | 0.0047049 | 0.0047049 | 0.97947 | -0.39598 | 0.97939 | -0.39765 | 1.2925
49 | 0.013646 | 0.0034235 | -0.013642 | -0.0034216 | 3.3848e-06 | 1.9007e-06 | 0.020706 | 0.020706 | 0.020706 | 0.98071 | -0.37159 | 0.98045 | -0.37679 | 5.6884
50 | -0.022126 | -0.0055493 | 0.022135 | 0.0055548 | 9.0003e-06 | 5.4904e-06 | 0.033542 | 0.033542 | 0.033542 | 0.9816 | -0.35425 | 0.98204 | -0.34572 | 9.2149
51 | 0.0014058 | 0.00035203 | -0.0014058 | -0.00035217 | 2.1395e-08 | -1.4372e-07 | 0.0021357 | 0.0021357 | 0.0021357 | 0.97942 | -0.39701 | 0.97941 | -0.39732 | 0.58673
52 | 0.0017132 | 0.00042656 | -0.0017131 | -0.0004271 | 1.2491e-07 | -5.391e-07 | 0.0026019 | 0.0026022 | 0.0026022 | 0.97939 | -0.39765 | 0.97931 | -0.39918 | 0.71488
53 | 0.0037065 | 0.00092851 | -0.0037059 | -0.00092878 | 5.8596e-07 | -2.7304e-07 | 0.0055691 | 0.0055694 | 0.0055694 | 0.9903 | -0.18595 | 0.99013 | -0.18927 | 1.53
54 | -0.0054037 | -0.0013539 | 0.0054042 | 0.0013539 | 4.82e-07 | 5.7597e-08 | 0.0081193 | 0.0081192 | 0.0081193 | 0.9903 | -0.18595 | 0.9904 | -0.18408 | 2.2306
55 | 0.031772 | 0.0079945 | -0.031755 | -0.0079835 | 1.7583e-05 | 1.0989e-05 | 0.047747 | 0.047747 | 0.047747 | 0.9904 | -0.18408 | 0.9898 | -0.19566 | 13.1173
56 | -0.037176 | -0.0093484 | 0.037206 | 0.0093672 | 2.9893e-05 | 1.8803e-05 | 0.055866 | 0.055866 | 0.055866 | 0.9904 | -0.18408 | 0.99127 | -0.16725 | 15.3478
57 | 0.00051347 | 0.00012856 | -0.00051346 | -0.00012869 | 2.1637e-09 | -1.2308e-07 | 0.00077187 | 0.00077192 | 0.00077192 | 0.9898 | -0.19566 | 0.9898 | -0.19575 | 0.21207
58 | 0.031241 | 0.0078549 | -0.031227 | -0.0078459 | 1.442e-05 | 9.005e-06 | 0.046975 | 0.046975 | 0.046975 | 0.9898 | -0.19566 | 0.9893 | -0.20533 | 12.9053
59 | 0.00068027 | 0.00016939 | -0.00068025 | -0.00017009 | 2.1787e-08 | -7.0465e-07 | 0.0010208 | 0.001021 | 0.001021 | 0.99127 | -0.16725 | 0.99124 | -0.16793 | 0.2805
60 | 0.029822 | 0.007494 | -0.029807 | -0.0074841 | 1.5833e-05 | 9.8641e-06 | 0.044863 | 0.044863 | 0.044863 | 0.9893 | -0.20533 | 0.98873 | -0.21646 | 12.3251
61 | 0.00068025 | 0.00017009 | -0.00068024 | -0.00017048 | 1.2144e-08 | -3.9257e-07 | 0.001021 | 0.0010212 | 0.0010212 | 0.99124 | -0.16793 | 0.99122 | -0.1683 | 0.28054
62 | -0.063707 | -0.016068 | 0.063724 | 0.016079 | 1.6783e-05 | 1.0679e-05 | 0.095982 | 0.095982 | 0.095982 | 0.98803 | -0.22906 | 0.98831 | -0.22356 | 26.3688
63 | 0.013309 | 0.0033366 | -0.013307 | -0.0033354 | 2.0701e-06 | 1.1497e-06 | 0.020067 | 0.020067 | 0.020067 | 0.98694 | -0.2512 | 0.98678 | -0.25447 | 5.5129
64 | -0.015696 | -0.0039346 | 0.015699 | 0.0039366 | 3.4792e-06 | 2.0149e-06 | 0.023665 | 0.023665 | 0.023665 | 0.98694 | -0.2512 | 0.98718 | -0.24655 | 6.5013
65 | 0.011599 | 0.0029072 | -0.011597 | -0.0029065 | 1.3347e-06 | 7.0561e-07 | 0.01749 | 0.017491 | 0.017491 | 0.98678 | -0.25447 | 0.98665 | -0.25689 | 4.8051
66 | -0.018436 | -0.0046225 | 0.01844 | 0.0046252 | 4.5788e-06 | 2.7282e-06 | 0.027789 | 0.027789 | 0.027789 | 0.98718 | -0.24655 | 0.98745 | -0.24134 | 7.6345
67 | 0.010039 | 0.0025158 | -0.010038 | -0.0025154 | 7.3586e-07 | 3.6162e-07 | 0.01514 | 0.01514 | 0.01514 | 0.98665 | -0.25689 | 0.98657 | -0.25842 | 4.1592
68 | -0.021214 | -0.0053205 | 0.021219 | 0.0053235 | 5.0139e-06 | 3.0415e-06 | 0.03197 | 0.03197 | 0.03197 | 0.98745 | -0.24134 | 0.9877 | -0.23639 | 8.7829
69 | 0.0090904 | 0.002278 | -0.0090892 | -0.0022775 | 1.232e-06 | 5.6536e-07 | 0.013711 | 0.013711 | 0.013711 | 0.98657 | -0.25842 | 0.98643 | -0.26127 | 3.7667
70 | -0.023414 | -0.0058735 | 0.023426 | 0.0058811 | 1.2463e-05 | 7.634e-06 | 0.035276 | 0.035275 | 0.035276 | 0.9877 | -0.23639 | 0.98828 | -0.22523 | 9.6911
71 | 0.0025942 | 0.00064996 | -0.0025941 | -0.00065015 | 1.1999e-07 | -1.8955e-07 | 0.0039146 | 0.0039147 | 0.0039147 | 0.98609 | -0.26786 | 0.98604 | -0.26883 | 1.0755
72 | -0.0047993 | -0.0012026 | 0.0047996 | 0.0012026 | 2.5225e-07 | -2.1809e-09 | 0.0072421 | 0.0072421 | 0.0072421 | 0.98609 | -0.26786 | 0.98615 | -0.26675 | 1.9896
73 | 0.0023543 | 0.00058951 | -0.0023542 | -0.00058969 | 8.614e-08 | -1.7711e-07 | 0.0035522 | 0.0035523 | 0.0035523 | 0.98615 | -0.26675 | 0.98611 | -0.26752 | 0.97591
74 | -0.0071538 | -0.0017921 | 0.0071542 | 0.0017922 | 3.8527e-07 | 1.3407e-07 | 0.010794 | 0.010794 | 0.010794 | 0.98615 | -0.26675 | 0.9862 | -0.26562 | 2.9655
75 | 0.0016637 | 0.00041664 | -0.0016637 | -0.00041678 | 3.1015e-08 | -1.4757e-07 | 0.0025104 | 0.0025104 | 0.0025104 | 0.98611 | -0.26752 | 0.98609 | -0.26791 | 0.68968
76 | -0.0080194 | -0.0020091 | 0.008021 | 0.0020097 | 1.6627e-06 | 6.7759e-07 | 0.0121 | 0.012099 | 0.0121 | 0.9862 | -0.26562 | 0.98643 | -0.26127 | 3.3241
77 | 0.0010995 | 0.00027539 | -0.0010995 | -0.00027556 | 1.4278e-08 | -1.6731e-07 | 0.0016591 | 0.0016592 | 0.0016592 | 0.98609 | -0.26791 | 0.98607 | -0.26819 | 0.45581
78 | -0.0020454 | -0.00051215 | 0.0020455 | 0.00051203 | 4.2078e-08 | -1.2143e-07 | 0.0030963 | 0.0030963 | 0.0030963 | 0.98294 | -0.32805 | 0.98296 | -0.32762 | 0.85063
79 | 0.0016742 | 0.00041911 | -0.0016742 | -0.00041926 | 3.0906e-08 | -1.4286e-07 | 0.0025343 | 0.0025344 | 0.0025344 | 0.98294 | -0.32805 | 0.98292 | -0.32844 | 0.69626
80 | -0.0046897 | -0.0011747 | 0.0046898 | 0.0011747 | 6.5409e-08 | -2.011e-09 | 0.0070991 | 0.0070991 | 0.0070991 | 0.98296 | -0.32762 | 0.98298 | -0.32733 | 1.9503
81 | 0.0012031 | 0.00030118 | -0.0012031 | -0.00030124 | 5.3139e-09 | -5.0752e-08 | 0.0018212 | 0.0018212 | 0.0018212 | 0.98292 | -0.32844 | 0.98292 | -0.32853 | 0.50033
82 | -0.0051745 | -0.0012962 | 0.005175 | 0.0012963 | 4.7133e-07 | 4.1938e-08 | 0.0078329 | 0.0078328 | 0.0078329 | 0.98298 | -0.32733 | 0.98308 | -0.32541 | 2.1519
83 | 0.0007256 | 0.00018157 | -0.00072559 | -0.00018185 | 1.0121e-08 | -2.7704e-07 | 0.0010984 | 0.0010985 | 0.0010985 | 0.98292 | -0.32853 | 0.9829 | -0.32882 | 0.30178
84 | -0.0058022 | -0.001453 | 0.0058026 | 0.001453 | 3.8279e-07 | 7.7157e-08 | 0.008782 | 0.0087819 | 0.008782 | 0.98308 | -0.32541 | 0.98315 | -0.32403 | 2.4126
85 | 0.00062719 | 0.00015668 | -0.00062717 | -0.00015718 | 1.3652e-08 | -5.035e-07 | 0.00094915 | 0.00094934 | 0.00094934 | 0.98308 | -0.32541 | 0.98305 | -0.32587 | 0.26081
86 | -0.0024837 | -0.00062109 | 0.0024838 | 0.00062089 | 1.1191e-07 | -2.0425e-07 | 0.0037312 | 0.0037311 | 0.0037312 | 0.9904 | -0.18482 | 0.99045 | -0.18387 | 1.025
87 | 0.0012088 | 0.00030157 | -0.0012088 | -0.0003019 | 3.3874e-08 | -3.3088e-07 | 0.0018157 | 0.0018158 | 0.0018158 | 0.9904 | -0.18482 | 0.99037 | -0.18541 | 0.49885
88 | 0.00018162 | 4.5503e-05 | -0.00018162 | -4.5517e-05 | 3.0741e-11 | -1.4164e-08 | 0.00027285 | 0.00027285 | 0.00027285 | 0.99045 | -0.18387 | 0.99045 | -0.18388 | 0.07496
89 | -0.0026654 | -0.00066639 | 0.0026656 | 0.00066623 | 1.0629e-07 | -1.5953e-07 | 0.0040039 | 0.0040038 | 0.0040039 | 0.99045 | -0.18387 | 0.99049 | -0.18303 | 1.1
90 | 0.0004045 | 0.00010101 | -0.0004045 | -0.00010109 | 8.3325e-10 | -7.6905e-08 | 0.00060763 | 0.00060766 | 0.00060766 | 0.99037 | -0.18541 | 0.99037 | -0.18545 | 0.16694
91 | 0.00080428 | 0.00020089 | -0.00080427 | -0.00020126 | 1.6021e-08 | -3.6631e-07 | 0.0012082 | 0.0012083 | 0.0012083 | 0.99037 | -0.18541 | 0.99035 | -0.18583 | 0.33196
92 | 0.00018592 | 4.6465e-05 | -0.00018592 | -4.6597e-05 | 2.9949e-10 | -1.3152e-07 | 0.0002793 | 0.00027935 | 0.00027935 | 0.99037 | -0.18545 | 0.99036 | -0.18549 | 0.076744
93 | 0.00021858 | 5.4622e-05 | -0.00021858 | -5.4781e-05 | 5.0219e-10 | -1.5947e-07 | 0.00032836 | 0.00032842 | 0.00032842 | 0.99037 | -0.18545 | 0.99036 | -0.1855 | 0.090224
94 | 0.00080427 | 0.00020126 | -0.00080425 | -0.00020157 | 1.3459e-08 | -3.0766e-07 | 0.0012083 | 0.0012084 | 0.0012084 | 0.99035 | -0.18583 | 0.99033 | -0.18618 | 0.33199
95 | -0.0001482 | -3.7143e-05 | 0.0001482 | 3.6887e-05 | 3.8562e-10 | -2.5619e-07 | 0.00022493 | 0.00022483 | 0.00022493 | 0.98045 | -0.37685 | 0.98045 | -0.37679 | 0.061793
96 | 0.013494 | 0.0033847 | -0.013489 | -0.003382 | 4.8186e-06 | 2.6977e-06 | 0.020481 | 0.020481 | 0.020481 | 0.98045 | -0.37679 | 0.98007 | -0.38429 | 5.6267
97 | 0.013299 | 0.0033343 | -0.013298 | -0.0033338 | 8.5298e-07 | 4.7561e-07 | 0.020192 | 0.020192 | 0.020192 | 0.98007 | -0.38429 | 0.98 | -0.38563 | 5.5472
98 | 0.01279 | 0.0032066 | -0.012788 | -0.0032056 | 1.8117e-06 | 9.9814e-07 | 0.019421 | 0.019421 | 0.019421 | 0.98 | -0.38563 | 0.97985 | -0.38861 | 5.3354
99 | 0.0032622 | 0.00081706 | -0.003262 | -0.0008172 | 1.8725e-07 | -1.3955e-07 | 0.0049389 | 0.004939 | 0.004939 | 0.98281 | -0.3307 | 0.98274 | -0.33191 | 1.3569
100 | 0.00088848 | 0.00022235 | -0.00088847 | -0.00022267 | 1.7917e-08 | -3.2306e-07 | 0.0013452 | 0.0013453 | 0.0013453 | 0.98274 | -0.33191 | 0.98272 | -0.33233 | 0.36959
101 | 0.0096294 | 0.0024117 | -0.0096277 | -0.0024108 | 1.7727e-06 | 8.4441e-07 | 0.014473 | 0.014473 | 0.014473 | 0.99001 | -0.19216 | 0.98982 | -0.19603 | 3.976
102 | 0.0032883 | 0.00082343 | -0.0032877 | -0.00082386 | 5.6048e-07 | -4.2733e-07 | 0.0049431 | 0.0049434 | 0.0049434 | 0.98982 | -0.19603 | 0.98963 | -0.19961 | 1.3581
103 | 0.0063394 | 0.0015874 | -0.0063378 | -0.0015869 | 1.6418e-06 | 4.3128e-07 | 0.0095297 | 0.0095299 | 0.0095299 | 0.98982 | -0.19603 | 0.98954 | -0.20147 | 2.6181
104 | 0.0011382 | 0.00028513 | -0.0011382 | -0.00028525 | 1.0414e-08 | -1.1517e-07 | 0.0017113 | 0.0017114 | 0.0017114 | 0.98963 | -0.19961 | 0.98962 | -0.1998 | 0.47015
105 | 0.0018488 | 0.0004619 | -0.0018486 | -0.00046269 | 2.0826e-07 | -7.8989e-07 | 0.0027796 | 0.0027799 | 0.0027799 | 0.98954 | -0.20147 | 0.98941 | -0.20384 | 0.76372
106 | 0.0010835 | 0.00027096 | -0.0010835 | -0.00027155 | 4.8448e-08 | -5.9387e-07 | 0.0016294 | 0.0016296 | 0.0016296 | 0.98941 | -0.20384 | 0.98937 | -0.20477 | 0.44769
107 | 0.02695 | 0.0067683 | -0.026948 | -0.006767 | 2.0453e-06 | 1.2665e-06 | 0.040565 | 0.040565 | 0.040565 | 0.98873 | -0.21646 | 0.98865 | -0.21805 | 11.1441
108 | 0.025327 | 0.0063607 | -0.025319 | -0.0063554 | 8.6672e-06 | 5.3432e-06 | 0.038125 | 0.038125 | 0.038125 | 0.98865 | -0.21805 | 0.98828 | -0.22523 | 10.4739
109 | 0.0093105 | 0.0023338 | -0.0093091 | -0.0023332 | 1.3375e-06 | 6.3138e-07 | 0.01414 | 0.01414 | 0.01414 | 0.97981 | -0.38936 | 0.97965 | -0.39237 | 3.8846
110 | -0.010105 | -0.0025329 | 0.010105 | 0.0025331 | 3.6146e-07 | 1.7979e-07 | 0.015346 | 0.015346 | 0.015346 | 0.97981 | -0.38936 | 0.97985 | -0.38861 | 4.216
111 | 0.0083051 | 0.0020815 | -0.0083046 | -0.0020813 | 4.9548e-07 | 2.1257e-07 | 0.012615 | 0.012615 | 0.012615 | 0.97965 | -0.39237 | 0.97959 | -0.39362 | 3.4656
112 | -0.023044 | -0.0057827 | 0.023051 | 0.005787 | 7.028e-06 | 4.3034e-06 | 0.03492 | 0.03492 | 0.03492 | 0.98204 | -0.34572 | 0.98236 | -0.33933 | 9.5933
113 | -0.024367 | -0.0061167 | 0.024371 | 0.0061196 | 4.6025e-06 | 2.8315e-06 | 0.036912 | 0.036912 | 0.036912 | 0.98236 | -0.33933 | 0.98256 | -0.33537 | 10.1408
114 | -0.0062943 | -0.0015763 | 0.0062949 | 0.0015764 | 6.3296e-07 | 1.692e-07 | 0.0095261 | 0.009526 | 0.0095261 | 0.98315 | -0.32403 | 0.98325 | -0.32192 | 2.6171
115 | 0.00065394 | 0.00016345 | -0.00065393 | -0.00016389 | 1.2463e-08 | -4.3505e-07 | 0.0009824 | 0.00098256 | 0.00098256 | 0.99035 | -0.18575 | 0.99033 | -0.18615 | 0.26993
116 | -0.00091221 | -0.00022818 | 0.00091222 | 0.00022804 | 8.1716e-09 | -1.4407e-07 | 0.0013705 | 0.0013704 | 0.0013705 | 0.99035 | -0.18575 | 0.99036 | -0.18556 | 0.3765
117 | -0.0014256 | -0.0003567 | 0.0014256 | 0.00035666 | 6.4394e-09 | -4.4049e-08 | 0.0021418 | 0.0021417 | 0.0021418 | 0.99036 | -0.18556 | 0.99036 | -0.18547 | 0.58839
118 | -0.00058086 | -0.00014558 | 0.00058087 | 0.00014521 | 8.6746e-09 | -3.6813e-07 | 0.0008826 | 0.00088247 | 0.0008826 | 0.9793 | -0.3995 | 0.97931 | -0.39918 | 0.24247
119 | 0.0011322 | 0.00028189 | -0.0011322 | -0.00028269 | 7.478e-08 | -8.0034e-07 | 0.0017197 | 0.00172 | 0.00172 | 0.97931 | -0.39918 | 0.97924 | -0.40058 | 0.47253
120 | 0.00082639 | 0.00020671 | -0.00082637 | -0.00020711 | 1.9429e-08 | -4.0083e-07 | 0.0012557 | 0.0012558 | 0.0012558 | 0.97918 | -0.40168 | 0.97916 | -0.40218 | 0.34501
121 | -0.0011321 | -0.00028332 | 0.0011322 | 0.00028269 | 5.9487e-08 | -6.3637e-07 | 0.0017202 | 0.00172 | 0.0017202 | 0.97918 | -0.40168 | 0.97924 | -0.40058 | 0.47259
122 | -0.00072158 | -0.00018074 | 0.00072158 | 0.0001807 | 1.4645e-09 | -3.9958e-08 | 0.0010963 | 0.0010963 | 0.0010963 | 0.9794 | -0.39737 | 0.97941 | -0.39732 | 0.30117
123 | 0.0002221 | 5.5561e-05 | -0.0002221 | -5.5664e-05 | 3.5014e-10 | -1.0298e-07 | 0.0003374 | 0.00033744 | 0.00033744 | 0.9794 | -0.39737 | 0.9794 | -0.3974 | 0.092703

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.14931 | 0.037627

## res_load
| p_mw | q_mvar
0 | 0.00065206 | 0.00016342
1 | 0.0037552 | 0.00094115
2 | 0.00028562 | 7.1583e-05
3 | 0.00089773 | 0.00022499
4 | 0.00075214 | 0.0001885
5 | 0.00022227 | 5.5705e-05
6 | 0.012385 | 0.003104
7 | 0.0018949 | 0.00047492
8 | 0.0017106 | 0.00042871
9 | 0.0031495 | 0.00078934
10 | 0.0016469 | 0.00041276
11 | 0.0003733 | 9.3557e-05
12 | 0.0050466 | 0.0012648
13 | 0.00084919 | 0.00021283
14 | 0.00072856 | 0.0001826
15 | 0.0010027 | 0.0002513
16 | 0.003061 | 0.00076716
17 | 0.00052067 | 0.00013049
18 | 0.0012836 | 0.0003217
19 | 0.0036274 | 0.00090912
20 | 0.0013876 | 0.00034776
21 | 0.0016837 | 0.00042198
22 | 0.00077472 | 0.00019416
23 | 0.0012043 | 0.00030183
24 | 0.00029736 | 7.4525e-05
25 | 9.8057e-05 | 2.4575e-05
26 | 0.00087438 | 0.00021914
27 | 0.00070464 | 0.0001766
28 | 0.0013841 | 0.00034689
29 | 0.0016972 | 0.00042536
30 | 0.0037059 | 0.00092878
31 | 0.00051346 | 0.00012869
32 | 0.0014042 | 0.00035193
33 | 0.00068024 | 0.00017048
34 | 0.0048304 | 0.0012106
35 | 0.0029943 | 0.00075043
36 | 0.0023862 | 0.00059805
37 | 0.0017086 | 0.00042822
38 | 0.0027365 | 0.00068584
39 | 0.0015589 | 0.00039068
40 | 0.0027742 | 0.00069528
41 | 0.00094736 | 0.00023743
42 | 0.0021943 | 0.00054994
43 | 0.0022051 | 0.00055265
44 | 0.0025941 | 0.00065015
45 | 0.0006905 | 0.00017305
46 | 0.00086512 | 0.00021682
47 | 0.00056417 | 0.00014139
48 | 0.0010682 | 0.00026771
49 | 0.00037124 | 9.304e-05
50 | 0.0026442 | 0.0006627
51 | 0.00047111 | 0.00011807
52 | 0.00048478 | 0.0001215
53 | 0.00047746 | 0.00011966
54 | 0.00072559 | 0.00018185
55 | 0.0012749 | 0.00031952
56 | 0.00018162 | 4.5517e-05
57 | 0.00018592 | 4.6597e-05
58 | 0.00021858 | 5.4781e-05
59 | 0.00080425 | 0.00020157
60 | 0.00093287 | 0.0002338
61 | 0.0001482 | 3.7143e-05
62 | 0.00019054 | 4.7755e-05
63 | 0.00050764 | 0.00012723
64 | 0.0023735 | 0.00059485
65 | 0.00097079 | 0.0002433
66 | 0.00050399 | 0.00012631
67 | 0.0021495 | 0.00053873
68 | 0.004489 | 0.001125
69 | 0.0011382 | 0.00028525
70 | 0.00076504 | 0.00019174
71 | 0.0028563 | 0.00071586
72 | 0.001621 | 0.00040626
73 | 0.0018925 | 0.0004743
74 | 0.0007944 | 0.00019909
75 | 0.001004 | 0.00025163
76 | 0.0026833 | 0.00067249
77 | 0.0083046 | 0.0020813
78 | 0.00088847 | 0.00022267
79 | 0.00090916 | 0.00022786
80 | 0.0013157 | 0.00032974
81 | 0.002525 | 0.00063282
82 | 0.00053803 | 0.00013484
83 | 0.0004917 | 0.00012323
84 | 0.00062717 | 0.00015718
85 | 0.0010995 | 0.00027556
86 | 0.00025827 | 6.4729e-05
87 | 0.00065393 | 0.00016389
88 | 0.00051338 | 0.00012866
89 | 0.0010835 | 0.00027155
90 | 0.00037288 | 9.3453e-05
91 | 0.00058086 | 0.00014558
92 | 0.0003057 | 7.6616e-05
93 | 0.00082637 | 0.00020711
94 | 0.00049948 | 0.00012518
95 | 0.00068417 | 0.00017147
96 | 0.0002221 | 5.5664e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1