## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1037-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1037-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1037-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1037-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1037-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1037-3_0_4_node_57 | 0.4 | n |  | TRUE
6 | bus_LV_1037-3_0_4_node_97 | 0.4 | n |  | TRUE
7 | bus_LV_1037-3_0_4_node_94 | 0.4 | n |  | TRUE
8 | bus_LV_1037-3_0_4_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_1037-3_0_4_node_108 | 0.4 | n |  | TRUE
10 | bus_LV_1037-3_0_4_node_141 | 0.4 | n |  | TRUE
11 | bus_LV_1037-3_0_4_node_95 | 0.4 | n |  | TRUE
12 | bus_LV_1037-3_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1037-3_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1037-3_0_4_node_131 | 0.4 | n |  | TRUE
15 | bus_LV_1037-3_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1037-3_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1037-3_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1037-3_0_4_node_128 | 0.4 | n |  | TRUE
19 | bus_LV_1037-3_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1037-3_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1037-3_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1037-3_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1037-3_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1037-3_0_4_node_107 | 0.4 | n |  | TRUE
25 | bus_LV_1037-3_0_4_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_1037-3_0_4_node_121 | 0.4 | n |  | TRUE
27 | bus_LV_1037-3_0_4_node_96 | 0.4 | n |  | TRUE
28 | bus_LV_1037-3_0_4_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_1037-3_0_4_node_129 | 0.4 | n |  | TRUE
30 | bus_LV_1037-3_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1037-3_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1037-3_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1037-3_0_4_node_117 | 0.4 | n |  | TRUE
34 | bus_LV_1037-3_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1037-3_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1037-3_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1037-3_0_4_node_118 | 0.4 | n |  | TRUE
38 | bus_LV_1037-3_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1037-3_0_4_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1037-3_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1037-3_0_4_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1037-3_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1037-3_0_4_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_1037-3_0_4_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_1037-3_0_4_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_1037-3_0_4_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_1037-3_0_4_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_1037-3_0_4_node_90 | 0.4 | n |  | TRUE
49 | bus_LV_1037-3_0_4_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1037-3_0_4_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_1037-3_0_4_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_1037-3_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_1037-3_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1037-3_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_1037-3_0_4_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_1037-3_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_1037-3_0_4_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_1037-3_0_4_node_119 | 0.4 | n |  | TRUE
59 | bus_LV_1037-3_0_4_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_1037-3_0_4_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_1037-3_0_4_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_1037-3_0_4_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_1037-3_0_4_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_1037-3_0_4_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_1037-3_0_4_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_1037-3_0_4_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_1037-3_0_4_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_1037-3_0_4_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_1037-3_0_4_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_1037-3_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_1037-3_0_4_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_1037-3_0_4_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_1037-3_0_4_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_1037-3_0_4_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_1037-3_0_4_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_1037-3_0_4_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_1037-3_0_4_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_1037-3_0_4_node_49 | 0.4 | n |  | TRUE
79 | bus_LV_1037-3_0_4_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_1037-3_0_4_node_134 | 0.4 | n |  | TRUE
81 | bus_LV_1037-3_0_4_node_124 | 0.4 | n |  | TRUE
82 | bus_LV_1037-3_0_4_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_1037-3_0_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1037-3_0_4_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_1037-3_0_4_node_133 | 0.4 | n |  | TRUE
86 | bus_LV_1037-3_0_4_node_125 | 0.4 | n |  | TRUE
87 | bus_LV_1037-3_0_4_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_1037-3_0_4_node_50 | 0.4 | n |  | TRUE
89 | bus_LV_1037-3_0_4_node_52 | 0.4 | n |  | TRUE
90 | bus_LV_1037-3_0_4_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_1037-3_0_4_node_150 | 0.4 | n |  | TRUE
92 | bus_LV_1037-3_0_4_node_122 | 0.4 | n |  | TRUE
93 | bus_LV_1037-3_0_4_node_151 | 0.4 | n |  | TRUE
94 | bus_LV_1037-3_0_4_node_123 | 0.4 | n |  | TRUE
95 | bus_LV_1037-3_0_4_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_1037-3_0_4_node_92 | 0.4 | n |  | TRUE
97 | bus_LV_1037-3_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1037-3_0_4_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_1037-3_0_4_node_63 | 0.4 | n |  | TRUE
100 | bus_LV_1037-3_0_4_node_64 | 0.4 | n |  | TRUE
101 | bus_LV_1037-3_0_4_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_1037-3_0_4_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_1037-3_0_4_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_1037-3_0_4_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_1037-3_0_4_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_1037-3_0_4_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_1037-3_0_4_node_70 | 0.4 | n |  | TRUE
108 | bus_LV_1037-3_0_4_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_1037-3_0_4_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_1037-3_0_4_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_1037-3_0_4_node_75 | 0.4 | n |  | TRUE
112 | bus_LV_1037-3_0_4_node_139 | 0.4 | n |  | TRUE
113 | bus_LV_1037-3_0_4_node_140 | 0.4 | n |  | TRUE
114 | bus_LV_1037-3_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_1037-3_0_4_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_1037-3_0_4_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_1037-3_0_4_node_78 | 0.4 | n |  | TRUE
118 | bus_LV_1037-3_0_4_node_80 | 0.4 | n |  | TRUE
119 | bus_LV_1037-3_0_4_node_81 | 0.4 | n |  | TRUE
120 | bus_LV_1037-3_0_4_node_143 | 0.4 | n |  | TRUE
121 | bus_LV_1037-3_0_4_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_1037-3_0_4_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_1037-3_0_4_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_1037-3_0_4_node_84 | 0.4 | n |  | TRUE
125 | bus_LV_1037-3_0_4_node_86 | 0.4 | n |  | TRUE
126 | bus_LV_1037-3_0_4_node_149 | 0.4 | n |  | TRUE
127 | bus_LV_1037-3_0_4_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_1037-3_0_4_node_91 | 0.4 | n |  | TRUE
129 | bus_LV_1037-3_0_4_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_1037-3_0_4_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_1037-3_0_4_node_127 | 0.4 | n |  | TRUE
132 | bus_LV_1037-3_0_4_node_114 | 0.4 | n |  | TRUE
133 | bus_LV_1037-3_0_4_node_103 | 0.4 | n |  | TRUE
134 | bus_LV_1037-3_0_4_node_105 | 0.4 | n |  | TRUE
135 | bus_LV_1037-3_0_4_node_147 | 0.4 | n |  | TRUE
136 | bus_LV_1037-3_0_4_node_148 | 0.4 | n |  | TRUE
137 | bus_LV_1037-3_0_4_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_1037-3_0_4_node_136 | 0.4 | n |  | TRUE
139 | bus_LV_1037-3_0_4_node_112 | 0.4 | n |  | TRUE
140 | bus_LV_1037-3_0_4_node_110 | 0.4 | n |  | TRUE
141 | bus_LV_1037-3_0_4_node_111 | 0.4 | n |  | TRUE
142 | bus_LV_1037-3_0_4_node_113 | 0.4 | n |  | TRUE
143 | bus_LV_1037-3_0_4_node_144 | 0.4 | n |  | TRUE
144 | bus_LV_1037-3_0_4_node_145 | 0.4 | n |  | TRUE
145 | bus_LV_1037-3_0_4_node_135 | 0.4 | n |  | TRUE
146 | bus_LV_1037-3_0_4_node_137 | 0.4 | n |  | TRUE
147 | bus_LV_1037-3_0_4_node_138 | 0.4 | n |  | TRUE
148 | bus_LV_1037-3_0_4_node_142 | 0.4 | n |  | TRUE
149 | bus_MV_354_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1037-3_0_4_load_0 | 0 | 0.031063 | 0.007785 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1037-3_0_4_load_57 | 5 | 0.017801 | 0.0044614 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1037-3_0_4_load_94 | 7 | 0.0024857 | 0.00062296 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1037-3_0_4_load_141 | 10 | 0.0019341 | 0.00048473 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1037-3_0_4_load_95 | 11 | 0.0026177 | 0.00065605 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1037-3_0_4_load_5 | 12 | 0.003674 | 0.0009208 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1037-3_0_4_load_6 | 13 | 0.0011159 | 0.00027968 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1037-3_0_4_load_131 | 14 | 0.002701 | 0.00067693 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1037-3_0_4_load_13 | 16 | 0.00053792 | 0.00013481 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1037-3_0_4_load_14 | 17 | 0.00047553 | 0.00011918 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1037-3_0_4_load_128 | 18 | 0.0008278 | 0.00020747 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1037-3_0_4_load_8 | 19 | 0.012435 | 0.0031164 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1037-3_0_4_load_9 | 20 | 0.0032597 | 0.00081695 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1037-3_0_4_load_10 | 21 | 0.0035793 | 0.00089705 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1037-3_0_4_load_11 | 22 | 0.0036856 | 0.00092371 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1037-3_0_4_load_41 | 25 | 0.0017125 | 0.0004292 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1037-3_0_4_load_121 | 26 | 0.0038403 | 0.00096246 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1037-3_0_4_load_39 | 28 | 0.0015868 | 0.00039769 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1037-3_0_4_load_15 | 30 | 0.00213 | 0.00053383 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1037-3_0_4_load_16 | 31 | 0.0036535 | 0.00091565 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1037-3_0_4_load_18 | 32 | 0.0034713 | 0.00086998 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1037-3_0_4_load_117 | 33 | 0.002349 | 0.00058871 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1037-3_0_4_load_30 | 36 | 0.0029587 | 0.00074153 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1037-3_0_4_load_24 | 38 | 0.0021797 | 0.00054629 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1037-3_0_4_load_20 | 39 | 0.0022435 | 0.00056228 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1037-3_0_4_load_31 | 40 | 0.0036656 | 0.00091869 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1037-3_0_4_load_21 | 41 | 0.0022445 | 0.00056252 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1037-3_0_4_load_58 | 43 | 0.0019788 | 0.00049594 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1037-3_0_4_load_59 | 44 | 0.0025258 | 0.00063304 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1037-3_0_4_load_60 | 45 | 0.0034158 | 0.00085608 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1037-3_0_4_load_53 | 46 | 0.00067792 | 0.0001699 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1037-3_0_4_load_100 | 47 | 0.0026269 | 0.00065836 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1037-3_0_4_load_51 | 49 | 0.00078029 | 0.00019556 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1037-3_0_4_load_25 | 50 | 0.0016029 | 0.00040172 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1037-3_0_4_load_26 | 51 | 0.0047511 | 0.0011907 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1037-3_0_4_load_27 | 52 | 0.0034704 | 0.00086977 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1037-3_0_4_load_28 | 53 | 0.001795 | 0.00044986 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1037-3_0_4_load_61 | 55 | 0.003774 | 0.00094586 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1037-3_0_4_load_32 | 56 | 0.0056283 | 0.0014106 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1037-3_0_4_load_62 | 57 | 0.0017512 | 0.00043889 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1037-3_0_4_load_119 | 58 | 0.0037543 | 0.00094092 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1037-3_0_4_load_33 | 59 | 0.0023257 | 0.00058287 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1037-3_0_4_load_34 | 60 | 0.0022386 | 0.00056104 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1037-3_0_4_load_35 | 61 | 0.0020563 | 0.00051536 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1037-3_0_4_load_36 | 62 | 0.004751 | 0.0011907 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1037-3_0_4_load_37 | 63 | 0.0024478 | 0.00061348 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1037-3_0_4_load_115 | 66 | 0.0021239 | 0.0005323 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1037-3_0_4_load_38 | 67 | 0.001544 | 0.00038697 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1037-3_0_4_load_43 | 69 | 0.0015082 | 0.00037798 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1037-3_0_4_load_55 | 70 | 0.017803 | 0.0044618 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1037-3_0_4_load_68 | 71 | 0.0013683 | 0.00034292 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1037-3_0_4_load_44 | 73 | 0.0019451 | 0.00048749 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1037-3_0_4_load_45 | 74 | 0.0024573 | 0.00061587 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1037-3_0_4_load_48 | 77 | 0.0027731 | 0.00069501 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1037-3_0_4_load_49 | 78 | 0.0017307 | 0.00043376 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1037-3_0_4_load_134 | 80 | 0.0031877 | 0.00079891 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1037-3_0_4_load_124 | 81 | 0.0035778 | 0.00089668 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1037-3_0_4_load_76 | 82 | 0.0021565 | 0.00054047 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1037-3_0_4_load_82 | 83 | 0.0042465 | 0.0010643 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1037-3_0_4_load_77 | 84 | 0.0042889 | 0.0010749 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1037-3_0_4_load_133 | 85 | 0.0030678 | 0.00076887 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1037-3_0_4_load_125 | 86 | 0.0049692 | 0.0012454 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1037-3_0_4_load_50 | 88 | 0.00070777 | 0.00017738 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1037-3_0_4_load_52 | 89 | 0.0010543 | 0.00026423 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1037-3_0_4_load_54 | 90 | 0.00068607 | 0.00017194 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1037-3_0_4_load_150 | 91 | 0.00068255 | 0.00017106 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1037-3_0_4_load_122 | 92 | 0.00078976 | 0.00019793 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1037-3_0_4_load_151 | 93 | 0.002965 | 0.00074309 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1037-3_0_4_load_123 | 94 | 0.0010174 | 0.00025498 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1037-3_0_4_load_101 | 95 | 0.0027011 | 0.00067697 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1037-3_0_4_load_92 | 96 | 0.0046275 | 0.0011598 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1037-3_0_4_load_88 | 97 | 0.0023146 | 0.0005801 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1037-3_0_4_load_87 | 98 | 0.0045968 | 0.0011521 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1037-3_0_4_load_63 | 99 | 0.0037725 | 0.00094548 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1037-3_0_4_load_64 | 100 | 0.0030408 | 0.00076209 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1037-3_0_4_load_65 | 101 | 0.006266 | 0.0015704 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1037-3_0_4_load_67 | 103 | 0.0029342 | 0.00073538 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1037-3_0_4_load_98 | 104 | 0.006409 | 0.0016063 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1037-3_0_4_load_99 | 105 | 0.002876 | 0.00072079 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1037-3_0_4_load_120 | 106 | 0.0020357 | 0.0005102 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1037-3_0_4_load_70 | 107 | 0.0013179 | 0.00033029 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1037-3_0_4_load_71 | 108 | 0.0024982 | 0.00062612 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1037-3_0_4_load_72 | 109 | 0.0026643 | 0.00066774 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1037-3_0_4_load_75 | 111 | 0.0017538 | 0.00043955 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1037-3_0_4_load_139 | 112 | 0.0034942 | 0.00087574 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1037-3_0_4_load_140 | 113 | 0.00061667 | 0.00015455 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1037-3_0_4_load_106 | 115 | 0.0020774 | 0.00052065 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1037-3_0_4_load_102 | 116 | 0.0017588 | 0.00044081 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1037-3_0_4_load_80 | 118 | 0.011544 | 0.0028931 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1037-3_0_4_load_143 | 120 | 0.00386 | 0.0009674 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1037-3_0_4_load_109 | 122 | 0.0024005 | 0.00060163 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1037-3_0_4_load_83 | 123 | 0.0020509 | 0.000514 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1037-3_0_4_load_84 | 124 | 0.0020495 | 0.00051365 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1037-3_0_4_load_149 | 126 | 0.0025657 | 0.00064303 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1037-3_0_4_load_89 | 127 | 0.0025462 | 0.00063813 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1037-3_0_4_load_91 | 128 | 0.0028327 | 0.00070995 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1037-3_0_4_load_126 | 129 | 0.0027823 | 0.00069731 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1037-3_0_4_load_132 | 130 | 0.002804 | 0.00070274 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1037-3_0_4_load_127 | 131 | 0.0027823 | 0.00069731 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1037-3_0_4_load_114 | 132 | 0.0049352 | 0.0012369 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1037-3_0_4_load_103 | 133 | 0.0038252 | 0.00095869 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1037-3_0_4_load_147 | 135 | 0.0020352 | 0.00051007 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1037-3_0_4_load_148 | 136 | 0.0023786 | 0.00059615 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1037-3_0_4_load_130 | 137 | 0.0024506 | 0.00061417 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1037-3_0_4_load_136 | 138 | 0.0004589 | 0.00011501 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1037-3_0_4_load_112 | 139 | 0.0022013 | 0.0005517 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1037-3_0_4_load_110 | 140 | 0.0020901 | 0.00052383 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1037-3_0_4_load_113 | 142 | 0.0022013 | 0.0005517 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1037-3_0_4_load_145 | 144 | 0.0020923 | 0.00052439 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1037-3_0_4_load_135 | 145 | 0.0032912 | 0.00082485 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1037-3_0_4_load_137 | 146 | 0.0014355 | 0.00035978 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1037-3_0_4_load_142 | 148 | 0.0012953 | 0.00032464 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 55 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1037-3_0_4_line_0 |  | 0 | 1 | 0.026477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1037-3_0_4_line_1 |  | 0 | 2 | 0.033686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1037-3_0_4_line_2 |  | 1 | 3 | 0.028453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1037-3_0_4_line_3 |  | 2 | 4 | 0.027545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1037-3_0_4_line_4 |  | 3 | 5 | 0.011767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1037-3_0_4_line_5 |  | 4 | 6 | 0.030346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1037-3_0_4_line_6 |  | 4 | 7 | 0.0036706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1037-3_0_4_line_7 |  | 5 | 8 | 0.018577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1037-3_0_4_line_8 |  | 6 | 9 | 0.004746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1037-3_0_4_line_9 |  | 6 | 10 | 0.037573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1037-3_0_4_line_10 |  | 7 | 11 | 0.022771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1037-3_0_4_line_11 |  | 8 | 70 | 0.017077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1037-3_0_4_line_12 |  | 9 | 122 | 0.031942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1037-3_0_4_line_13 |  | 9 | 118 | 0.020889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1037-3_0_4_line_14 |  | 11 | 27 | 0.027233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1037-3_0_4_line_15 |  | 12 | 13 | 0.045883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1037-3_0_4_line_16 |  | 12 | 14 | 0.19863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1037-3_0_4_line_17 |  | 13 | 15 | 0.018654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1037-3_0_4_line_18 |  | 15 | 16 | 0.033194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1037-3_0_4_line_19 |  | 15 | 17 | 0.042184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1037-3_0_4_line_20 |  | 17 | 18 | 0.00078975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1037-3_0_4_line_21 |  | 18 | 29 | 0.037697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1037-3_0_4_line_22 |  | 19 | 20 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1037-3_0_4_line_23 |  | 19 | 21 | 0.0058487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1037-3_0_4_line_24 |  | 20 | 22 | 0.023068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1037-3_0_4_line_25 |  | 21 | 23 | 0.011928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1037-3_0_4_line_26 |  | 23 | 24 | 0.029685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1037-3_0_4_line_27 |  | 23 | 25 | 0.012273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1037-3_0_4_line_28 |  | 24 | 26 | 0.0081453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1037-3_0_4_line_29 |  | 24 | 27 | 0.030443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1037-3_0_4_line_30 |  | 25 | 28 | 0.005809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1037-3_0_4_line_31 |  | 26 | 106 | 0.034371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1037-3_0_4_line_32 |  | 28 | 67 | 0.01797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1037-3_0_4_line_33 |  | 29 | 103 | 0.047834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1037-3_0_4_line_34 |  | 30 | 31 | 0.026819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1037-3_0_4_line_35 |  | 31 | 32 | 0.019949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1037-3_0_4_line_36 |  | 32 | 33 | 0.029093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1037-3_0_4_line_37 |  | 33 | 37 | 0.024785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1037-3_0_4_line_38 |  | 34 | 35 | 0.04777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1037-3_0_4_line_39 |  | 34 | 36 | 0.048373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1037-3_0_4_line_40 |  | 35 | 38 | 0.023584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1037-3_0_4_line_41 |  | 35 | 39 | 0.013339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1037-3_0_4_line_42 |  | 36 | 40 | 0.029961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1037-3_0_4_line_43 |  | 37 | 58 | 0.015534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1037-3_0_4_line_44 |  | 37 | 54 | 0.004421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1037-3_0_4_line_45 |  | 38 | 46 | 0.0066921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1037-3_0_4_line_46 |  | 39 | 41 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1037-3_0_4_line_47 |  | 40 | 56 | 0.038341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1037-3_0_4_line_48 |  | 41 | 42 | 0.024318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1037-3_0_4_line_49 |  | 42 | 43 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1037-3_0_4_line_50 |  | 42 | 44 | 0.01344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1037-3_0_4_line_51 |  | 42 | 45 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1037-3_0_4_line_52 |  | 44 | 47 | 0.014414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1037-3_0_4_line_53 |  | 45 | 48 | 0.018746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1037-3_0_4_line_54 |  | 46 | 49 | 0.01677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1037-3_0_4_line_55 |  | 47 | 95 | 0.013878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1037-3_0_4_line_56 |  | 48 | 96 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1037-3_0_4_line_57 |  | 48 | 97 | 0.0041613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1037-3_0_4_line_58 |  | 49 | 88 | 0.0056084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1037-3_0_4_line_59 |  | 50 | 51 | 0.011409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1037-3_0_4_line_60 |  | 50 | 52 | 0.0026603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1037-3_0_4_line_61 |  | 51 | 53 | 0.011667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1037-3_0_4_line_62 |  | 52 | 54 | 0.016056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1037-3_0_4_line_63 |  | 53 | 55 | 0.012121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1037-3_0_4_line_64 |  | 54 | 56 | 0.050894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1037-3_0_4_line_65 |  | 55 | 57 | 0.014479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1037-3_0_4_line_66 |  | 57 | 98 | 0.0093601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1037-3_0_4_line_67 |  | 58 | 122 | 0.034172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1037-3_0_4_line_68 |  | 59 | 60 | 0.00024831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1037-3_0_4_line_69 |  | 59 | 61 | 0.024853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1037-3_0_4_line_70 |  | 60 | 62 | 0.032294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1037-3_0_4_line_71 |  | 61 | 63 | 0.00091449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1037-3_0_4_line_72 |  | 62 | 64 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1037-3_0_4_line_73 |  | 64 | 65 | 0.02666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1037-3_0_4_line_74 |  | 64 | 66 | 0.010079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1037-3_0_4_line_75 |  | 65 | 130 | 0.021704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1037-3_0_4_line_76 |  | 65 | 128 | 0.012139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1037-3_0_4_line_77 |  | 66 | 132 | 0.010623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1037-3_0_4_line_78 |  | 67 | 68 | 0.0023416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1037-3_0_4_line_79 |  | 68 | 69 | 0.0028376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1037-3_0_4_line_80 |  | 69 | 71 | 0.020378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1037-3_0_4_line_81 |  | 71 | 72 | 0.013868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1037-3_0_4_line_82 |  | 72 | 107 | 0.0054264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1037-3_0_4_line_83 |  | 73 | 74 | 0.029438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1037-3_0_4_line_84 |  | 73 | 75 | 0.0056821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1037-3_0_4_line_85 |  | 74 | 76 | 0.014053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1037-3_0_4_line_86 |  | 75 | 77 | 0.01509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1037-3_0_4_line_87 |  | 75 | 78 | 0.02014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1037-3_0_4_line_88 |  | 76 | 79 | 0.037074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1037-3_0_4_line_89 |  | 76 | 80 | 0.015743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1037-3_0_4_line_90 |  | 77 | 81 | 0.0024464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1037-3_0_4_line_91 |  | 78 | 82 | 0.027347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1037-3_0_4_line_92 |  | 79 | 83 | 0.014369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1037-3_0_4_line_93 |  | 79 | 84 | 0.014107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1037-3_0_4_line_94 |  | 80 | 85 | 0.0011422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1037-3_0_4_line_95 |  | 81 | 86 | 0.023434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1037-3_0_4_line_96 |  | 82 | 87 | 0.004107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1037-3_0_4_line_97 |  | 83 | 121 | 0.0039646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1037-3_0_4_line_98 |  | 84 | 117 | 0.045826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1037-3_0_4_line_99 |  | 85 | 145 | 0.033797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1037-3_0_4_line_100 |  | 87 | 111 | 0.033465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1037-3_0_4_line_101 |  | 87 | 108 | 0.014909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1037-3_0_4_line_102 |  | 88 | 89 | 0.019745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1037-3_0_4_line_103 |  | 89 | 90 | 0.0045871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1037-3_0_4_line_104 |  | 89 | 91 | 0.057879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1037-3_0_4_line_105 |  | 90 | 92 | 0.014266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1037-3_0_4_line_106 |  | 91 | 93 | 0.017023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1037-3_0_4_line_107 |  | 92 | 94 | 0.016011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1037-3_0_4_line_108 |  | 96 | 129 | 0.019702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1037-3_0_4_line_109 |  | 97 | 127 | 0.013111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1037-3_0_4_line_110 |  | 99 | 100 | 0.0037691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1037-3_0_4_line_111 |  | 99 | 101 | 0.028077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1037-3_0_4_line_112 |  | 100 | 102 | 0.014892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1037-3_0_4_line_113 |  | 101 | 103 | 0.071807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1037-3_0_4_line_114 |  | 102 | 104 | 0.032608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1037-3_0_4_line_115 |  | 102 | 105 | 0.010894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1037-3_0_4_line_116 |  | 105 | 106 | 0.0096813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1037-3_0_4_line_117 |  | 108 | 109 | 0.0021677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1037-3_0_4_line_118 |  | 109 | 110 | 0.023467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1037-3_0_4_line_119 |  | 110 | 112 | 0.015319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1037-3_0_4_line_120 |  | 110 | 113 | 0.016226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1037-3_0_4_line_121 |  | 111 | 114 | 0.01041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1037-3_0_4_line_122 |  | 114 | 115 | 0.0093945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1037-3_0_4_line_123 |  | 114 | 116 | 0.016654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1037-3_0_4_line_124 |  | 115 | 137 | 0.026541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1037-3_0_4_line_125 |  | 116 | 133 | 0.0008359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1037-3_0_4_line_126 |  | 117 | 118 | 0.035624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1037-3_0_4_line_127 |  | 117 | 119 | 0.022932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1037-3_0_4_line_128 |  | 119 | 120 | 0.018268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1037-3_0_4_line_129 |  | 121 | 123 | 0.0081185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1037-3_0_4_line_130 |  | 123 | 124 | 0.0084981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1037-3_0_4_line_131 |  | 124 | 125 | 0.014892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1037-3_0_4_line_132 |  | 125 | 126 | 0.016933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1037-3_0_4_line_133 |  | 127 | 128 | 0.0050034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1037-3_0_4_line_134 |  | 129 | 131 | 0.012007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1037-3_0_4_line_135 |  | 133 | 134 | 0.018426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1037-3_0_4_line_136 |  | 134 | 135 | 0.017609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1037-3_0_4_line_137 |  | 134 | 136 | 0.018208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1037-3_0_4_line_138 |  | 136 | 138 | 0.18357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1037-3_0_4_line_139 |  | 137 | 139 | 0.0024312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1037-3_0_4_line_140 |  | 138 | 146 | 0.028267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1037-3_0_4_line_141 |  | 139 | 141 | 0.02117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1037-3_0_4_line_142 |  | 140 | 141 | 0.0045002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1037-3_0_4_line_143 |  | 141 | 142 | 0.012929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1037-3_0_4_line_144 |  | 142 | 143 | 0.020917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1037-3_0_4_line_145 |  | 143 | 144 | 0.01883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1037-3_0_4_line_146 |  | 146 | 147 | 0.056286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1037-3_0_4_line_147 |  | 147 | 148 | 0.044494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1037-3_0_4_trafo_61 | 0.63 MVA 20/0.4 kV | 149 | 55 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2661562.3887 | 1219894.4458 | 2661537.1039 | 1219886.5908
1 | 2661504.9343 | 1219876.5969 | 2661537.1039 | 1219886.5908
2 | 2661562.3887 | 1219894.4458 | 2661559.0594 | 1219903.8061 | 2661556.8462 | 1219909.4424 | 2661548.7277 | 1219918.92
3 | 2661504.9343 | 1219876.5969 | 2661478.6064 | 1219868.2534
4 | 2661548.7277 | 1219918.92 | 2661537.582 | 1219915.147
5 | 2661478.6064 | 1219868.2534 | 2661482.673 | 1219852.8746 | 2661488.7854 | 1219841.4639 | 2661489.2781 | 1219840.0459
6 | 2661478.6064 | 1219868.2534 | 2661477.6328 | 1219871.7925
7 | 2661532.5863 | 1219933.0399 | 2661537.582 | 1219915.147
8 | 2661490.8269 | 1219835.559 | 2661489.2781 | 1219840.0459
9 | 2661489.2781 | 1219840.0459 | 2661453.4194 | 1219828.8266
10 | 2661477.6328 | 1219871.7925 | 2661471.5923 | 1219893.7479
11 | 2661532.5863 | 1219933.0399 | 2661527.8134 | 1219949.436
12 | 2661490.8269 | 1219835.559 | 2661460.3375 | 1219826.0355
13 | 2661490.8269 | 1219835.559 | 2661499.0944 | 1219838.1015 | 2661510.6904 | 1219842.0167
14 | 2661464.3683 | 1219920.0056 | 2661471.5923 | 1219893.7479
15 | 2661252.4385 | 1220122.554 | 2661248.6575 | 1220120.6212 | 2661221.8665 | 1220088.7482
16 | 2661252.4385 | 1220122.554 | 2661377.4808 | 1220276.887
17 | 2661216.1914 | 1220070.9788 | 2661221.8665 | 1220088.7482
18 | 2661216.1914 | 1220070.9788 | 2661190.7061 | 1220049.7104
19 | 2661216.1914 | 1220070.9788 | 2661226.3314 | 1220073.6735 | 2661238.8869 | 1220071.6791 | 2661254.7434 | 1220061.2498
20 | 2661255.4032 | 1220060.8158 | 2661254.7434 | 1220061.2498
21 | 2661291.565 | 1220052.8978 | 2661288.9457 | 1220054.5163 | 2661270.7324 | 1220055.5074 | 2661258.6426 | 1220058.6851 | 2661255.4032 | 1220060.8158
22 | 2661485.4412 | 1219977.2241 | 2661483.6276 | 1219993.9616
23 | 2661485.4412 | 1219977.2241 | 2661486.0712 | 1219971.4094
24 | 2661481.1426 | 1220016.8954 | 2661483.6276 | 1219993.9616
25 | 2661486.1621 | 1219959.5885 | 2661486.8923 | 1219963.832 | 2661486.0712 | 1219971.4094
26 | 2661458.5586 | 1219949.8866 | 2661484.1989 | 1219957.1889 | 2661486.1621 | 1219959.5885
27 | 2661486.1621 | 1219959.5885 | 2661489.3505 | 1219947.7366
28 | 2661458.5586 | 1219949.8866 | 2661456.4158 | 1219957.7449
29 | 2661464.3683 | 1219920.0056 | 2661458.5586 | 1219949.8866
30 | 2661490.8595 | 1219942.127 | 2661489.3505 | 1219947.7366
31 | 2661435.5904 | 1219977.2751 | 2661439.1185 | 1219976.3471 | 2661445.7941 | 1219977.2498 | 2661449.818 | 1219976.2907 | 2661452.5334 | 1219971.9827 | 2661456.4158 | 1219957.7449
32 | 2661495.5278 | 1219924.7739 | 2661490.8595 | 1219942.127
33 | 2661291.565 | 1220052.8978 | 2661292.5764 | 1220046.7821 | 2661294.1162 | 1220012.9212 | 2661298.1666 | 1220008.6491 | 2661299.9744 | 1220008.247
34 | 2661338.9271 | 1219806.8123 | 2661334.1087 | 1219806.9262 | 2661324.4998 | 1219807.1496 | 2661316.4353 | 1219807.7226 | 2661312.1613 | 1219808.222
35 | 2661338.9271 | 1219806.8123 | 2661348.5221 | 1219806.5854 | 2661358.4497 | 1219807.0991 | 2661358.8595 | 1219807.1235
36 | 2661358.8595 | 1219807.1235 | 2661368.3764 | 1219807.6905 | 2661380.8189 | 1219808.6304 | 2661387.8443 | 1219809.516
37 | 2661412.3538 | 1219813.1803 | 2661396.1877 | 1219810.5677 | 2661387.8443 | 1219809.516
38 | 2661245.4841 | 1219825.6375 | 2661254.8233 | 1219862.7011 | 2661256.2522 | 1219868.3749 | 2661258.2309 | 1219871.4972
39 | 2661245.4841 | 1219825.6375 | 2661259.0977 | 1219821.8973 | 2661276.7508 | 1219817.9097 | 2661292.7034 | 1219815.3456
40 | 2661258.2309 | 1219871.4972 | 2661252.3305 | 1219882.2655 | 2661255.0342 | 1219893.2425
41 | 2661258.2309 | 1219871.4972 | 2661263.5125 | 1219872.9413 | 2661271.1769 | 1219871.1818
42 | 2661322.4373 | 1219811.8276 | 2661305.5498 | 1219813.2807 | 2661292.7034 | 1219815.3456
43 | 2661412.3538 | 1219813.1803 | 2661427.4807 | 1219816.7128
44 | 2661412.3538 | 1219813.1803 | 2661411.2928 | 1219817.4721
45 | 2661255.0342 | 1219893.2425 | 2661256.6347 | 1219899.7404
46 | 2661286.535 | 1219867.6561 | 2661271.1769 | 1219871.1818
47 | 2661322.4373 | 1219811.8276 | 2661323.899 | 1219811.7019 | 2661350.6366 | 1219811.2546 | 2661360.757 | 1219811.7429
48 | 2661310.2364 | 1219862.2151 | 2661286.535 | 1219867.6561
49 | 2661310.2364 | 1219862.2151 | 2661307.6117 | 1219851.5178
50 | 2661310.2364 | 1219862.2151 | 2661323.3338 | 1219859.2
51 | 2661310.2364 | 1219862.2151 | 2661313.7086 | 1219875.0878
52 | 2661337.3805 | 1219855.9663 | 2661323.3338 | 1219859.2
53 | 2661318.5906 | 1219893.1871 | 2661313.7086 | 1219875.0878
54 | 2661256.6347 | 1219899.7404 | 2661260.6454 | 1219916.0239
55 | 2661337.3805 | 1219855.9663 | 2661350.9048 | 1219852.8529
56 | 2661318.5906 | 1219893.1871 | 2661333.0715 | 1219888.542
57 | 2661318.5906 | 1219893.1871 | 2661319.4001 | 1219897.2689
58 | 2661261.9867 | 1219921.4695 | 2661260.6454 | 1219916.0239
59 | 2661406.7886 | 1219835.6383 | 2661404.0431 | 1219846.7116
60 | 2661407.4288 | 1219833.0562 | 2661406.7886 | 1219835.6383
61 | 2661401.2354 | 1219858.0356 | 2661404.0431 | 1219846.7116
62 | 2661411.2928 | 1219817.4721 | 2661407.4288 | 1219833.0562
63 | 2661401.2354 | 1219858.0356 | 2661398.3184 | 1219869.8003
64 | 2661411.2928 | 1219817.4721 | 2661395.2322 | 1219814.9272 | 2661369.6809 | 1219812.1734 | 2661360.757 | 1219811.7429
65 | 2661398.3184 | 1219869.8003 | 2661394.8339 | 1219883.8541
66 | 2661392.5813 | 1219892.9391 | 2661394.8339 | 1219883.8541
67 | 2661460.3375 | 1219826.0355 | 2661457.9549 | 1219825.2913 | 2661438.205 | 1219819.2172 | 2661427.4807 | 1219816.7128
68 | 2661388.9673 | 1219934.086 | 2661388.7256 | 1219934.1429
69 | 2661413.1591 | 1219928.3916 | 2661388.9673 | 1219934.086
70 | 2661388.7256 | 1219934.1429 | 2661357.2904 | 1219941.5423
71 | 2661414.0493 | 1219928.1821 | 2661413.1591 | 1219928.3916
72 | 2661339.5693 | 1219945.7136 | 2661357.2904 | 1219941.5423
73 | 2661333.0975 | 1219919.853 | 2661333.9814 | 1219923.9202 | 2661339.5693 | 1219945.7136
74 | 2661339.5693 | 1219945.7136 | 2661329.6979 | 1219947.7504
75 | 2661353.9306 | 1219913.5635 | 2661333.0975 | 1219919.853
76 | 2661333.0975 | 1219919.853 | 2661329.022 | 1219919.9222 | 2661325.4048 | 1219918.2284 | 2661322.9692 | 1219915.2681 | 2661322.9234 | 1219915.0373
77 | 2661319.2941 | 1219949.8971 | 2661329.6979 | 1219947.7504
78 | 2661496.1361 | 1219922.5126 | 2661495.5278 | 1219924.7739
79 | 2661496.1361 | 1219922.5126 | 2661496.889 | 1219919.7767
80 | 2661496.889 | 1219919.7767 | 2661502.2957 | 1219900.1293
81 | 2661505.9752 | 1219886.7585 | 2661502.2957 | 1219900.1293
82 | 2661505.9752 | 1219886.7585 | 2661500.8957 | 1219884.8493
83 | 2661493.9148 | 1219763.9934 | 2661521.5482 | 1219774.143
84 | 2661488.5811 | 1219762.0344 | 2661493.9148 | 1219763.9934
85 | 2661534.7395 | 1219778.988 | 2661521.5482 | 1219774.143
86 | 2661488.5811 | 1219762.0344 | 2661493.2235 | 1219747.6763
87 | 2661488.5811 | 1219762.0344 | 2661469.3846 | 1219755.9426
88 | 2661534.7395 | 1219778.988 | 2661550.1429 | 1219784.1837 | 2661556.1088 | 1219786.9693 | 2661563.5816 | 1219794.4623 | 2661565.6514 | 1219797.5634
89 | 2661534.7395 | 1219778.988 | 2661539.7527 | 1219764.0641
90 | 2661493.2235 | 1219747.6763 | 2661493.9761 | 1219745.3485
91 | 2661469.3846 | 1219755.9426 | 2661443.3182 | 1219747.6708
92 | 2661565.6514 | 1219797.5634 | 2661573.739 | 1219794.7674 | 2661579.5316 | 1219794.2919
93 | 2661565.6514 | 1219797.5634 | 2661560.9519 | 1219805.1418 | 2661559.2724 | 1219810.0522
94 | 2661540.1165 | 1219762.9813 | 2661539.7527 | 1219764.0641
95 | 2661501.1855 | 1219723.0512 | 2661493.9761 | 1219745.3485
96 | 2661439.4036 | 1219746.4285 | 2661443.3182 | 1219747.6708
97 | 2661583.4828 | 1219793.9676 | 2661579.5316 | 1219794.2919
98 | 2661544.4421 | 1219853.4125 | 2661559.2724 | 1219810.0522
99 | 2661558.7288 | 1219744.1807 | 2661549.0744 | 1219741.4571 | 2661546.7649 | 1219743.1898 | 2661540.1165 | 1219762.9813
100 | 2661439.4036 | 1219746.4285 | 2661425.1353 | 1219742.9904 | 2661410.8066 | 1219740.9859 | 2661406.4879 | 1219740.8697
101 | 2661439.4036 | 1219746.4285 | 2661444.2732 | 1219732.3369
102 | 2661261.9867 | 1219921.4695 | 2661266.7088 | 1219940.6411
103 | 2661267.8059 | 1219945.095 | 2661266.7088 | 1219940.6411
104 | 2661266.7088 | 1219940.6411 | 2661211.0833 | 1219956.6334
105 | 2661277.0918 | 1219955.0826 | 2661273.3391 | 1219953.3259 | 2661268.4132 | 1219947.5605 | 2661267.8059 | 1219945.095
106 | 2661214.6461 | 1219973.2796 | 2661211.0833 | 1219956.6334
107 | 2661277.0918 | 1219955.0826 | 2661282.0083 | 1219957.3842 | 2661292.3631 | 1219955.202
108 | 2661333.0715 | 1219888.542 | 2661351.8315 | 1219882.5242
109 | 2661319.4001 | 1219897.2689 | 2661321.9502 | 1219910.1294
110 | 2661397.4761 | 1219986.5609 | 2661401.1553 | 1219985.7426
111 | 2661397.4761 | 1219986.5609 | 2661370.0689 | 1219992.6568
112 | 2661415.6917 | 1219982.5095 | 2661401.1553 | 1219985.7426
113 | 2661299.9744 | 1220008.247 | 2661370.0689 | 1219992.6568
114 | 2661415.6917 | 1219982.5095 | 2661423.1571 | 1220014.2507
115 | 2661415.6917 | 1219982.5095 | 2661426.2276 | 1219979.738
116 | 2661435.5904 | 1219977.2751 | 2661426.2276 | 1219979.738
117 | 2661444.2732 | 1219732.3369 | 2661444.9812 | 1219730.288
118 | 2661452.6458 | 1219708.1078 | 2661444.9812 | 1219730.288
119 | 2661452.6458 | 1219708.1078 | 2661467.3046 | 1219712.6951
120 | 2661437.1172 | 1219703.2557 | 2661452.6458 | 1219708.1078
121 | 2661396.0819 | 1219740.5895 | 2661406.4879 | 1219740.8697
122 | 2661396.0819 | 1219740.5895 | 2661386.6877 | 1219740.6682
123 | 2661396.0819 | 1219740.5895 | 2661395.5885 | 1219723.9427
124 | 2661360.1473 | 1219740.8903 | 2661386.6877 | 1219740.6682
125 | 2661395.5885 | 1219723.9427 | 2661395.5637 | 1219723.1072
126 | 2661544.4421 | 1219853.4125 | 2661510.6904 | 1219842.0167
127 | 2661566.5412 | 1219859.767 | 2661544.4421 | 1219853.4125
128 | 2661566.5412 | 1219859.767 | 2661581.3932 | 1219863.2337 | 2661584.3571 | 1219863.7963
129 | 2661583.4828 | 1219793.9676 | 2661585.3309 | 1219789.8952 | 2661588.3023 | 1219787.7817
130 | 2661595.2272 | 1219782.8559 | 2661588.3023 | 1219787.7817
131 | 2661607.3621 | 1219774.2243 | 2661595.2272 | 1219782.8559
132 | 2661607.3621 | 1219774.2243 | 2661599.5958 | 1219759.1679
133 | 2661321.9502 | 1219910.1294 | 2661322.9234 | 1219915.0373
134 | 2661363.2651 | 1219878.8566 | 2661351.8315 | 1219882.5242
135 | 2661395.0178 | 1219704.6895 | 2661395.5637 | 1219723.1072
136 | 2661395.0178 | 1219704.6895 | 2661382.161 | 1219704.9127 | 2661377.8963 | 1219702.7119
137 | 2661409.3537 | 1219697.1769 | 2661406.707 | 1219702.9088 | 2661404.58 | 1219703.8652 | 2661395.0178 | 1219704.6895
138 | 2661409.3537 | 1219697.1769 | 2661395.2813 | 1219514.1421
139 | 2661357.7162 | 1219740.9107 | 2661360.1473 | 1219740.8903
140 | 2661395.2813 | 1219514.1421 | 2661419.6629 | 1219499.84
141 | 2661336.5472 | 1219741.0879 | 2661357.7162 | 1219740.9107
142 | 2661336.5472 | 1219741.0879 | 2661332.0474 | 1219741.1474
143 | 2661336.5472 | 1219741.0879 | 2661335.7206 | 1219728.1856
144 | 2661334.3833 | 1219707.3112 | 2661335.7206 | 1219728.1856
145 | 2661353.255 | 1219706.605 | 2661334.3833 | 1219707.3112
146 | 2661468.1422 | 1219471.2419 | 2661457.5892 | 1219477.5925 | 2661419.6629 | 1219499.84
147 | 2661468.1422 | 1219471.2419 | 2661496.4969 | 1219494.3933 | 2661501.8129 | 1219500.2219

## bus_geodata
| x | y | coords
0 | 2661537.1039 | 1219886.5908
1 | 2661562.3887 | 1219894.4458
2 | 2661504.9343 | 1219876.5969
3 | 2661548.7277 | 1219918.92
4 | 2661478.6064 | 1219868.2534
5 | 2661537.582 | 1219915.147
6 | 2661489.2781 | 1219840.0459
7 | 2661477.6328 | 1219871.7925
8 | 2661532.5863 | 1219933.0399
9 | 2661490.8269 | 1219835.559
10 | 2661453.4194 | 1219828.8266
11 | 2661471.5923 | 1219893.7479
12 | 2661252.4385 | 1220122.554
13 | 2661221.8665 | 1220088.7482
14 | 2661377.4808 | 1220276.887
15 | 2661216.1914 | 1220070.9788
16 | 2661190.7061 | 1220049.7104
17 | 2661254.7434 | 1220061.2498
18 | 2661255.4032 | 1220060.8158
19 | 2661485.4412 | 1219977.2241
20 | 2661483.6276 | 1219993.9616
21 | 2661486.0712 | 1219971.4094
22 | 2661481.1426 | 1220016.8954
23 | 2661486.1621 | 1219959.5885
24 | 2661458.5586 | 1219949.8866
25 | 2661489.3505 | 1219947.7366
26 | 2661456.4158 | 1219957.7449
27 | 2661464.3683 | 1219920.0056
28 | 2661490.8595 | 1219942.127
29 | 2661291.565 | 1220052.8978
30 | 2661312.1613 | 1219808.222
31 | 2661338.9271 | 1219806.8123
32 | 2661358.8595 | 1219807.1235
33 | 2661387.8443 | 1219809.516
34 | 2661245.4841 | 1219825.6375
35 | 2661258.2309 | 1219871.4972
36 | 2661292.7034 | 1219815.3456
37 | 2661412.3538 | 1219813.1803
38 | 2661255.0342 | 1219893.2425
39 | 2661271.1769 | 1219871.1818
40 | 2661322.4373 | 1219811.8276
41 | 2661286.535 | 1219867.6561
42 | 2661310.2364 | 1219862.2151
43 | 2661307.6117 | 1219851.5178
44 | 2661323.3338 | 1219859.2
45 | 2661313.7086 | 1219875.0878
46 | 2661256.6347 | 1219899.7404
47 | 2661337.3805 | 1219855.9663
48 | 2661318.5906 | 1219893.1871
49 | 2661260.6454 | 1219916.0239
50 | 2661406.7886 | 1219835.6383
51 | 2661404.0431 | 1219846.7116
52 | 2661407.4288 | 1219833.0562
53 | 2661401.2354 | 1219858.0356
54 | 2661411.2928 | 1219817.4721
55 | 2661398.3184 | 1219869.8003
56 | 2661360.757 | 1219811.7429
57 | 2661394.8339 | 1219883.8541
58 | 2661427.4807 | 1219816.7128
59 | 2661388.9673 | 1219934.086
60 | 2661388.7256 | 1219934.1429
61 | 2661413.1591 | 1219928.3916
62 | 2661357.2904 | 1219941.5423
63 | 2661414.0493 | 1219928.1821
64 | 2661339.5693 | 1219945.7136
65 | 2661333.0975 | 1219919.853
66 | 2661329.6979 | 1219947.7504
67 | 2661495.5278 | 1219924.7739
68 | 2661496.1361 | 1219922.5126
69 | 2661496.889 | 1219919.7767
70 | 2661527.8134 | 1219949.436
71 | 2661502.2957 | 1219900.1293
72 | 2661505.9752 | 1219886.7585
73 | 2661493.9148 | 1219763.9934
74 | 2661521.5482 | 1219774.143
75 | 2661488.5811 | 1219762.0344
76 | 2661534.7395 | 1219778.988
77 | 2661493.2235 | 1219747.6763
78 | 2661469.3846 | 1219755.9426
79 | 2661565.6514 | 1219797.5634
80 | 2661539.7527 | 1219764.0641
81 | 2661493.9761 | 1219745.3485
82 | 2661443.3182 | 1219747.6708
83 | 2661579.5316 | 1219794.2919
84 | 2661559.2724 | 1219810.0522
85 | 2661540.1165 | 1219762.9813
86 | 2661501.1855 | 1219723.0512
87 | 2661439.4036 | 1219746.4285
88 | 2661261.9867 | 1219921.4695
89 | 2661266.7088 | 1219940.6411
90 | 2661267.8059 | 1219945.095
91 | 2661211.0833 | 1219956.6334
92 | 2661277.0918 | 1219955.0826
93 | 2661214.6461 | 1219973.2796
94 | 2661292.3631 | 1219955.202
95 | 2661350.9048 | 1219852.8529
96 | 2661333.0715 | 1219888.542
97 | 2661319.4001 | 1219897.2689
98 | 2661392.5813 | 1219892.9391
99 | 2661397.4761 | 1219986.5609
100 | 2661401.1553 | 1219985.7426
101 | 2661370.0689 | 1219992.6568
102 | 2661415.6917 | 1219982.5095
103 | 2661299.9744 | 1220008.247
104 | 2661423.1571 | 1220014.2507
105 | 2661426.2276 | 1219979.738
106 | 2661435.5904 | 1219977.2751
107 | 2661500.8957 | 1219884.8493
108 | 2661444.2732 | 1219732.3369
109 | 2661444.9812 | 1219730.288
110 | 2661452.6458 | 1219708.1078
111 | 2661406.4879 | 1219740.8697
112 | 2661467.3046 | 1219712.6951
113 | 2661437.1172 | 1219703.2557
114 | 2661396.0819 | 1219740.5895
115 | 2661386.6877 | 1219740.6682
116 | 2661395.5885 | 1219723.9427
117 | 2661544.4421 | 1219853.4125
118 | 2661510.6904 | 1219842.0167
119 | 2661566.5412 | 1219859.767
120 | 2661584.3571 | 1219863.7963
121 | 2661583.4828 | 1219793.9676
122 | 2661460.3376 | 1219826.0355
123 | 2661588.3023 | 1219787.7817
124 | 2661595.2272 | 1219782.8559
125 | 2661607.3621 | 1219774.2243
126 | 2661599.5958 | 1219759.1679
127 | 2661321.9502 | 1219910.1294
128 | 2661322.9234 | 1219915.0373
129 | 2661351.8315 | 1219882.5242
130 | 2661353.9306 | 1219913.5635
131 | 2661363.2651 | 1219878.8566
132 | 2661319.2941 | 1219949.8971
133 | 2661395.5637 | 1219723.1072
134 | 2661395.0178 | 1219704.6895
135 | 2661377.8963 | 1219702.7119
136 | 2661409.3537 | 1219697.1769
137 | 2661360.1473 | 1219740.8903
138 | 2661395.2813 | 1219514.1421
139 | 2661357.7162 | 1219740.9107
140 | 2661332.0474 | 1219741.1474
141 | 2661336.5472 | 1219741.0879
142 | 2661335.7206 | 1219728.1856
143 | 2661334.3833 | 1219707.3112
144 | 2661353.255 | 1219706.605
145 | 2661558.7288 | 1219744.1807
146 | 2661419.6629 | 1219499.84
147 | 2661468.1422 | 1219471.2419
148 | 2661501.8129 | 1219500.2219
149 | 2661391.8558 | 1219895.8653

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98158 | -0.35274 | 0.031063 | 0.007785
1 | 0.98071 | -0.36981 | 0 | 0
2 | 0.98366 | -0.3122 | 0 | 0
3 | 0.97977 | -0.38819 | 0 | 0
4 | 0.98536 | -0.27918 | 0 | 0
5 | 0.97938 | -0.3958 | 0.017801 | 0.0044614
6 | 0.98739 | -0.23995 | 0 | 0
7 | 0.98509 | -0.28429 | 0.0024857 | 0.00062296
8 | 0.97908 | -0.40181 | 0 | 0
9 | 0.9876 | -0.23581 | 0 | 0
10 | 0.98732 | -0.24125 | 0.0019341 | 0.00048473
11 | 0.98351 | -0.31508 | 0.0026177 | 0.00065605
12 | 0.97432 | -0.49511 | 0.003674 | 0.0009208
13 | 0.97459 | -0.48974 | 0.0011159 | 0.00027968
14 | 0.97382 | -0.50498 | 0.002701 | 0.00067693
15 | 0.97472 | -0.48717 | 0 | 0
16 | 0.97471 | -0.4875 | 0.00053792 | 0.00013481
17 | 0.97504 | -0.48095 | 0.00047553 | 0.00011918
18 | 0.97504 | -0.48083 | 0.0008278 | 0.00020747
19 | 0.97839 | -0.41507 | 0.012435 | 0.0031164
20 | 0.97828 | -0.4172 | 0.0032597 | 0.00081695
21 | 0.97849 | -0.41301 | 0.0035793 | 0.00089705
22 | 0.9782 | -0.41875 | 0.0036856 | 0.00092371
23 | 0.97875 | -0.40802 | 0 | 0
24 | 0.97963 | -0.39075 | 0 | 0
25 | 0.97864 | -0.41004 | 0.0017125 | 0.0004292
26 | 0.97932 | -0.39675 | 0.0038403 | 0.00096246
27 | 0.98168 | -0.35074 | 0 | 0
28 | 0.9786 | -0.41082 | 0.0015868 | 0.00039769
29 | 0.97537 | -0.47437 | 0 | 0
30 | 0.99314 | -0.13002 | 0.00213 | 0.00053383
31 | 0.99319 | -0.12901 | 0.0036535 | 0.00091565
32 | 0.9933 | -0.12697 | 0.0034713 | 0.00086998
33 | 0.99354 | -0.12222 | 0.002349 | 0.00058871
34 | 0.98222 | -0.33956 | 0 | 0
35 | 0.97908 | -0.40091 | 0 | 0
36 | 0.98541 | -0.27783 | 0.0029587 | 0.00074153
37 | 0.9938 | -0.11714 | 0 | 0
38 | 0.97882 | -0.40586 | 0.0021797 | 0.00054629
39 | 0.97834 | -0.41531 | 0.0022435 | 0.00056228
40 | 0.98747 | -0.23821 | 0.0036656 | 0.00091869
41 | 0.9775 | -0.4317 | 0.0022445 | 0.00056252
42 | 0.97626 | -0.45605 | 0 | 0
43 | 0.97624 | -0.45645 | 0.0019788 | 0.00049594
44 | 0.97616 | -0.45798 | 0.0025258 | 0.00063304
45 | 0.9757 | -0.46702 | 0.0034158 | 0.00085608
46 | 0.97877 | -0.407 | 0.00067792 | 0.0001699
47 | 0.97609 | -0.45938 | 0.0026269 | 0.00065836
48 | 0.97498 | -0.4813 | 0 | 0
49 | 0.97863 | -0.40965 | 0.00078029 | 0.00019556
50 | 0.99616 | -0.072496 | 0.0016029 | 0.00040172
51 | 0.99739 | -0.049191 | 0.0047511 | 0.0011907
52 | 0.99587 | -0.077914 | 0.0034704 | 0.00086977
53 | 0.99867 | -0.025095 | 0.001795 | 0.00044986
54 | 0.99416 | -0.11035 | 0 | 0
55 | 1 | 0 | -0.37074 | -0.095168
56 | 0.99023 | -0.18525 | 0.0056283 | 0.0014106
57 | 0.99992 | -0.0016023 | 0.0017512 | 0.00043889
58 | 0.9926 | -0.13997 | 0.0037543 | 0.00094092
59 | 0.97308 | -0.51868 | 0.0023257 | 0.00058287
60 | 0.97309 | -0.51865 | 0.0022386 | 0.00056104
61 | 0.97298 | -0.52075 | 0.0020563 | 0.00051536
62 | 0.97336 | -0.51326 | 0.004751 | 0.0011907
63 | 0.97298 | -0.52079 | 0.0024478 | 0.00061348
64 | 0.97359 | -0.50864 | 0 | 0
65 | 0.97411 | -0.4984 | 0 | 0
66 | 0.97353 | -0.50994 | 0.0021239 | 0.0005323
67 | 0.97851 | -0.41269 | 0.001544 | 0.00038697
68 | 0.9785 | -0.41287 | 0 | 0
69 | 0.97849 | -0.41309 | 0.0015082 | 0.00037798
70 | 0.9788 | -0.40734 | 0.017803 | 0.0044618
71 | 0.97844 | -0.41409 | 0.0013683 | 0.00034292
72 | 0.97842 | -0.41442 | 0 | 0
73 | 0.97478 | -0.48513 | 0.0019451 | 0.00048749
74 | 0.97627 | -0.45575 | 0.0024573 | 0.00061587
75 | 0.9745 | -0.49061 | 0 | 0
76 | 0.97702 | -0.44112 | 0 | 0
77 | 0.97434 | -0.49375 | 0.0027731 | 0.00069501
78 | 0.97373 | -0.50587 | 0.0017307 | 0.00043376
79 | 0.97932 | -0.3962 | 0 | 0
80 | 0.97688 | -0.44386 | 0.0031877 | 0.00079891
81 | 0.97432 | -0.49413 | 0.0035778 | 0.00089668
82 | 0.97272 | -0.52575 | 0.0021565 | 0.00054047
83 | 0.97917 | -0.39905 | 0.0042465 | 0.0010643
84 | 0.98034 | -0.37637 | 0.0042889 | 0.0010749
85 | 0.97687 | -0.444 | 0.0030678 | 0.00076887
86 | 0.97421 | -0.49627 | 0.0049692 | 0.0012454
87 | 0.97257 | -0.52857 | 0 | 0
88 | 0.97859 | -0.41046 | 0.00070777 | 0.00017738
89 | 0.97846 | -0.41305 | 0.0010543 | 0.00026423
90 | 0.97845 | -0.41325 | 0.00068607 | 0.00017194
91 | 0.97826 | -0.41689 | 0.00068255 | 0.00017106
92 | 0.97842 | -0.41372 | 0.00078976 | 0.00019793
93 | 0.97822 | -0.41781 | 0.002965 | 0.00074309
94 | 0.97841 | -0.41402 | 0.0010174 | 0.00025498
95 | 0.97606 | -0.46007 | 0.0027011 | 0.00067697
96 | 0.97483 | -0.48415 | 0.0046275 | 0.0011598
97 | 0.97486 | -0.4837 | 0.0023146 | 0.0005801
98 | 0.99988 | -0.0023524 | 0.0045968 | 0.0011521
99 | 0.97709 | -0.44055 | 0.0037725 | 0.00094548
100 | 0.97717 | -0.43901 | 0.0030408 | 0.00076209
101 | 0.97661 | -0.45006 | 0.006266 | 0.0015704
102 | 0.97752 | -0.43212 | 0 | 0
103 | 0.97579 | -0.46619 | 0.0029342 | 0.00073538
104 | 0.97732 | -0.43593 | 0.006409 | 0.0016063
105 | 0.97784 | -0.42581 | 0.002876 | 0.00072079
106 | 0.97815 | -0.41969 | 0.0020357 | 0.0005102
107 | 0.97842 | -0.41455 | 0.0013179 | 0.00033029
108 | 0.97245 | -0.53112 | 0.0024982 | 0.00062612
109 | 0.97243 | -0.53139 | 0.0026643 | 0.00066774
110 | 0.97234 | -0.53317 | 0 | 0
111 | 0.9717 | -0.5459 | 0.0017538 | 0.00043955
112 | 0.97229 | -0.53416 | 0.0034942 | 0.00087574
113 | 0.97233 | -0.53336 | 0.00061667 | 0.00015455
114 | 0.97144 | -0.55096 | 0 | 0
115 | 0.97133 | -0.55323 | 0.0020774 | 0.00052065
116 | 0.97124 | -0.55502 | 0.0017588 | 0.00044081
117 | 0.98382 | -0.3087 | 0 | 0
118 | 0.98666 | -0.25396 | 0.011544 | 0.0028931
119 | 0.98374 | -0.31029 | 0 | 0
120 | 0.98367 | -0.31156 | 0.00386 | 0.0009674
121 | 0.97915 | -0.39953 | 0 | 0
122 | 0.99001 | -0.18962 | 0.0024005 | 0.00060163
123 | 0.9791 | -0.40052 | 0.0020509 | 0.000514
124 | 0.97906 | -0.40123 | 0.0020495 | 0.00051365
125 | 0.97903 | -0.40192 | 0 | 0
126 | 0.97899 | -0.40272 | 0.0025657 | 0.00064303
127 | 0.9745 | -0.49069 | 0.0025462 | 0.00063813
128 | 0.97438 | -0.49312 | 0.0028327 | 0.00070995
129 | 0.97473 | -0.48616 | 0.0027823 | 0.00069731
130 | 0.97405 | -0.49952 | 0.002804 | 0.00070274
131 | 0.9747 | -0.48677 | 0.0027823 | 0.00069731
132 | 0.97348 | -0.51091 | 0.0049352 | 0.0012369
133 | 0.97123 | -0.55519 | 0.0038252 | 0.00095869
134 | 0.9711 | -0.55779 | 0 | 0
135 | 0.97106 | -0.55845 | 0.0020352 | 0.00051007
136 | 0.971 | -0.55966 | 0.0023786 | 0.00059615
137 | 0.97105 | -0.55865 | 0.0024506 | 0.00061417
138 | 0.97046 | -0.57052 | 0.0004589 | 0.00011501
139 | 0.97103 | -0.55903 | 0.0022013 | 0.0005517
140 | 0.9709 | -0.56171 | 0.0020901 | 0.00052383
141 | 0.97091 | -0.56153 | 0 | 0
142 | 0.97086 | -0.56256 | 0.0022013 | 0.0005517
143 | 0.97082 | -0.56337 | 0 | 0
144 | 0.97078 | -0.5641 | 0.0020923 | 0.00052439
145 | 0.97677 | -0.44603 | 0.0032912 | 0.00082485
146 | 0.97038 | -0.57195 | 0.0014355 | 0.00035978
147 | 0.97032 | -0.5733 | 0 | 0
148 | 0.97026 | -0.57437 | 0.0012953 | 0.00032464
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035687 | 0.0089751 | -0.035658 | -0.0089568 | 2.9071e-05 | 1.8271e-05 | 0.05411 | 0.05411 | 0.05411 | 0.98158 | -0.35274 | 0.98071 | -0.36981 | 14.8655
1 | -0.06675 | -0.01676 | 0.066879 | 0.016842 | 0.00012937 | 8.2371e-05 | 0.1012 | 0.1012 | 0.1012 | 0.98158 | -0.35274 | 0.98366 | -0.3122 | 27.802
2 | 0.035658 | 0.0089568 | -0.035627 | -0.0089371 | 3.1241e-05 | 1.9635e-05 | 0.05411 | 0.054111 | 0.054111 | 0.98071 | -0.36981 | 0.97977 | -0.38819 | 14.8656
3 | -0.066879 | -0.016842 | 0.066985 | 0.01691 | 0.00010579 | 6.7353e-05 | 0.1012 | 0.1012 | 0.1012 | 0.98366 | -0.3122 | 0.98536 | -0.27918 | 27.802
4 | 0.035627 | 0.0089371 | -0.035614 | -0.008929 | 1.292e-05 | 8.1207e-06 | 0.054111 | 0.054111 | 0.054111 | 0.97977 | -0.38819 | 0.97938 | -0.3958 | 14.8656
5 | -0.14514 | -0.036697 | 0.14541 | 0.036871 | 0.00027361 | 0.00017434 | 0.21929 | 0.21929 | 0.21929 | 0.98536 | -0.27918 | 0.98739 | -0.23995 | 30.1221
6 | 0.078151 | 0.019787 | -0.078132 | -0.019775 | 1.9195e-05 | 1.2238e-05 | 0.11809 | 0.11809 | 0.11809 | 0.98536 | -0.27918 | 0.98509 | -0.28429 | 32.4423
7 | 0.017813 | 0.0044677 | -0.017808 | -0.0044646 | 5.103e-06 | 3.0322e-06 | 0.027065 | 0.027065 | 0.027065 | 0.97938 | -0.3958 | 0.97908 | -0.40181 | 7.4354
8 | -0.14734 | -0.037356 | 0.14737 | 0.037374 | 2.9291e-05 | 1.8564e-05 | 0.2222 | 0.2222 | 0.2222 | 0.98739 | -0.23995 | 0.9876 | -0.23581 | 20.3483
9 | 0.0019342 | 0.00048433 | -0.0019341 | -0.00048473 | 1.1971e-07 | -4.0393e-07 | 0.0029147 | 0.0029149 | 0.0029149 | 0.98739 | -0.23995 | 0.98732 | -0.24125 | 0.8008
10 | 0.075646 | 0.019152 | -0.075535 | -0.019081 | 0.00011163 | 7.1153e-05 | 0.11434 | 0.11434 | 0.11434 | 0.98509 | -0.28429 | 0.98351 | -0.31508 | 31.4109
11 | 0.017808 | 0.0044646 | -0.017803 | -0.0044618 | 4.6908e-06 | 2.7874e-06 | 0.027065 | 0.027065 | 0.027065 | 0.97908 | -0.40181 | 0.9788 | -0.40734 | 7.4354
12 | -0.24551 | -0.062367 | 0.24606 | 0.062716 | 0.00054724 | 0.00034901 | 0.37021 | 0.37021 | 0.37021 | 0.9876 | -0.23581 | 0.99001 | -0.18962 | 33.9024
13 | 0.098141 | 0.024992 | -0.098056 | -0.024938 | 8.5803e-05 | 5.438e-05 | 0.14801 | 0.14801 | 0.14801 | 0.9876 | -0.23581 | 0.98666 | -0.25396 | 20.3312
14 | 0.072917 | 0.018425 | -0.072793 | -0.018346 | 0.00012442 | 7.9281e-05 | 0.11038 | 0.11038 | 0.11038 | 0.98351 | -0.31508 | 0.98168 | -0.35074 | 30.3229
15 | -0.0063763 | -0.0015961 | 0.0063779 | 0.0015965 | 1.6314e-06 | 4.7251e-07 | 0.0097374 | 0.0097372 | 0.0097374 | 0.97432 | -0.49511 | 0.97459 | -0.48974 | 2.6751
16 | 0.0027023 | 0.00067527 | -0.002701 | -0.00067693 | 1.2685e-06 | -1.6607e-06 | 0.0041263 | 0.0041272 | 0.0041272 | 0.97432 | -0.49511 | 0.97382 | -0.50498 | 1.1338
17 | -0.0074939 | -0.0018762 | 0.0074948 | 0.0018766 | 9.1564e-07 | 3.5353e-07 | 0.011441 | 0.011441 | 0.011441 | 0.97459 | -0.48974 | 0.97472 | -0.48717 | 3.1431
18 | 0.00053793 | 0.00013441 | -0.00053792 | -0.00013481 | 8.3929e-09 | -4.0837e-07 | 0.00082105 | 0.0008212 | 0.0008212 | 0.97472 | -0.48717 | 0.97471 | -0.4875 | 0.2256
19 | -0.0080327 | -0.002011 | 0.0080351 | 0.002012 | 2.3784e-06 | 9.9624e-07 | 0.012262 | 0.012262 | 0.012262 | 0.97472 | -0.48717 | 0.97504 | -0.48095 | 3.3687
20 | -0.0085106 | -0.0021312 | 0.0085107 | 0.0021312 | 4.9955e-08 | 2.2121e-08 | 0.012988 | 0.012988 | 0.012988 | 0.97504 | -0.48095 | 0.97504 | -0.48083 | 3.568
21 | -0.0093385 | -0.0023387 | 0.0093414 | 0.00234 | 2.8709e-06 | 1.367e-06 | 0.014251 | 0.014251 | 0.014251 | 0.97504 | -0.48083 | 0.97537 | -0.47437 | 3.9151
22 | 0.0069463 | 0.0017408 | -0.0069456 | -0.0017405 | 7.0461e-07 | 2.3955e-07 | 0.010564 | 0.010565 | 0.010565 | 0.97839 | -0.41507 | 0.97828 | -0.4172 | 2.9023
23 | -0.019381 | -0.0048572 | 0.019383 | 0.0048583 | 1.9056e-06 | 1.1461e-06 | 0.029476 | 0.029476 | 0.029476 | 0.97839 | -0.41507 | 0.97849 | -0.41301 | 8.0978
24 | 0.0036859 | 0.00092359 | -0.0036856 | -0.00092371 | 2.7191e-07 | -1.1559e-07 | 0.0056064 | 0.0056065 | 0.0056065 | 0.97828 | -0.4172 | 0.9782 | -0.41875 | 1.5402
25 | -0.022962 | -0.0057554 | 0.022968 | 0.0057587 | 5.454e-06 | 3.3407e-06 | 0.034919 | 0.034919 | 0.034919 | 0.97849 | -0.41301 | 0.97875 | -0.40802 | 9.5932
26 | -0.032007 | -0.008024 | 0.032033 | 0.0080405 | 2.636e-05 | 1.6497e-05 | 0.048662 | 0.048662 | 0.048662 | 0.97875 | -0.40802 | 0.97963 | -0.39075 | 13.3687
27 | 0.0090395 | 0.0022652 | -0.0090387 | -0.0022648 | 8.6927e-07 | 4.021e-07 | 0.013743 | 0.013743 | 0.013743 | 0.97875 | -0.40802 | 0.97864 | -0.41004 | 3.7756
28 | 0.04062 | 0.010217 | -0.040609 | -0.010209 | 1.1633e-05 | 7.3427e-06 | 0.061713 | 0.061713 | 0.061713 | 0.97963 | -0.39075 | 0.97932 | -0.39675 | 16.9542
29 | -0.072654 | -0.018257 | 0.072793 | 0.018346 | 0.00013908 | 8.8627e-05 | 0.11038 | 0.11038 | 0.11038 | 0.97963 | -0.39075 | 0.98168 | -0.35074 | 30.3229
30 | 0.0073261 | 0.0018356 | -0.0073259 | -0.0018355 | 2.703e-07 | 1e-07 | 0.011139 | 0.011139 | 0.011139 | 0.97864 | -0.41004 | 0.9786 | -0.41082 | 3.0602
31 | 0.036768 | 0.0092467 | -0.036728 | -0.0092214 | 4.0245e-05 | 2.5325e-05 | 0.055878 | 0.055879 | 0.055879 | 0.97932 | -0.39675 | 0.97815 | -0.41969 | 15.3512
32 | 0.0057391 | 0.0014379 | -0.0057386 | -0.0014377 | 5.1316e-07 | 1.0267e-07 | 0.0087264 | 0.0087265 | 0.0087265 | 0.9786 | -0.41082 | 0.97851 | -0.41269 | 2.3974
33 | -0.0093414 | -0.00234 | 0.009345 | 0.0023418 | 3.6427e-06 | 1.7341e-06 | 0.014251 | 0.01425 | 0.014251 | 0.97537 | -0.47437 | 0.97579 | -0.46619 | 3.915
34 | -0.00213 | -0.00053383 | 0.0021301 | 0.00053354 | 1.0243e-07 | -2.815e-07 | 0.0031914 | 0.0031912 | 0.0031914 | 0.99314 | -0.13002 | 0.99319 | -0.12901 | 0.87675
35 | -0.0057836 | -0.0014492 | 0.0057841 | 0.0014493 | 5.6167e-07 | 1.0128e-07 | 0.0086649 | 0.0086648 | 0.0086649 | 0.99319 | -0.12901 | 0.9933 | -0.12697 | 2.3805
36 | -0.0092554 | -0.0023193 | 0.0092575 | 0.0023202 | 2.0973e-06 | 9.6558e-07 | 0.013865 | 0.013865 | 0.013865 | 0.9933 | -0.12697 | 0.99354 | -0.12222 | 3.8091
37 | -0.011606 | -0.0029089 | 0.011609 | 0.0029104 | 2.8085e-06 | 1.4764e-06 | 0.017383 | 0.017383 | 0.017383 | 0.99354 | -0.12222 | 0.9938 | -0.11714 | 4.7755
38 | 0.071305 | 0.018042 | -0.071096 | -0.017909 | 0.00020927 | 0.00013333 | 0.10808 | 0.10808 | 0.10808 | 0.98222 | -0.33956 | 0.97908 | -0.40091 | 29.6937
39 | -0.071305 | -0.018042 | 0.071517 | 0.018177 | 0.00021192 | 0.00013501 | 0.10808 | 0.10808 | 0.10808 | 0.98222 | -0.33956 | 0.98541 | -0.27783 | 29.6936
40 | 0.011547 | 0.0028942 | -0.011544 | -0.0028927 | 2.7238e-06 | 1.4467e-06 | 0.01755 | 0.01755 | 0.01755 | 0.97908 | -0.40091 | 0.97882 | -0.40586 | 4.8213
41 | 0.059549 | 0.015015 | -0.059508 | -0.014989 | 4.1001e-05 | 2.6073e-05 | 0.090535 | 0.090536 | 0.090536 | 0.97908 | -0.40091 | 0.97834 | -0.41531 | 24.8724
42 | -0.074476 | -0.018919 | 0.074618 | 0.01901 | 0.00014233 | 9.0709e-05 | 0.11255 | 0.11255 | 0.11255 | 0.98541 | -0.27783 | 0.98747 | -0.23821 | 30.921
43 | 0.25309 | 0.064817 | -0.25281 | -0.064639 | 0.00027958 | 0.00017832 | 0.37945 | 0.37945 | 0.37945 | 0.9938 | -0.11714 | 0.9926 | -0.13997 | 34.7481
44 | -0.2647 | -0.067728 | 0.26479 | 0.067783 | 8.7025e-05 | 5.5524e-05 | 0.39683 | 0.39683 | 0.39683 | 0.9938 | -0.11714 | 0.99416 | -0.11035 | 36.3399
45 | 0.0093647 | 0.0023464 | -0.0093642 | -0.0023462 | 5.086e-07 | 2.4139e-07 | 0.014236 | 0.014236 | 0.014236 | 0.97882 | -0.40586 | 0.97877 | -0.407 | 3.911
46 | 0.057264 | 0.014426 | -0.057219 | -0.014398 | 4.4853e-05 | 2.8508e-05 | 0.087123 | 0.087123 | 0.087123 | 0.97834 | -0.41531 | 0.9775 | -0.4317 | 23.935
47 | -0.078284 | -0.019928 | 0.078484 | 0.020056 | 0.00020045 | 0.0001278 | 0.11808 | 0.11808 | 0.11808 | 0.98747 | -0.23821 | 0.99023 | -0.18525 | 32.4384
48 | 0.054975 | 0.013835 | -0.054911 | -0.013795 | 6.3897e-05 | 4.0589e-05 | 0.083707 | 0.083707 | 0.083707 | 0.9775 | -0.4317 | 0.97626 | -0.45605 | 22.9963
49 | 0.0019789 | 0.00049582 | -0.0019788 | -0.00049594 | 3.7575e-08 | -1.1367e-07 | 0.0030161 | 0.0030162 | 0.0030162 | 0.97626 | -0.45605 | 0.97624 | -0.45645 | 0.82862
50 | 0.007855 | 0.0019686 | -0.0078543 | -0.0019683 | 7.2245e-07 | 2.9433e-07 | 0.011973 | 0.011973 | 0.011973 | 0.97626 | -0.45605 | 0.97616 | -0.45798 | 3.2892
51 | 0.045077 | 0.01133 | -0.045053 | -0.011315 | 2.361e-05 | 1.4944e-05 | 0.068718 | 0.068718 | 0.068718 | 0.97626 | -0.45605 | 0.9757 | -0.46702 | 18.8786
52 | 0.0053285 | 0.0013353 | -0.0053281 | -0.0013352 | 3.566e-07 | 4.8045e-08 | 0.0081224 | 0.0081224 | 0.0081224 | 0.97616 | -0.45798 | 0.97609 | -0.45938 | 2.2314
53 | 0.041638 | 0.010459 | -0.041609 | -0.010441 | 2.8354e-05 | 1.7913e-05 | 0.063509 | 0.063509 | 0.063509 | 0.9757 | -0.46702 | 0.97498 | -0.4813 | 17.4475
54 | 0.0086862 | 0.0021763 | -0.0086851 | -0.0021758 | 1.0967e-06 | 4.9113e-07 | 0.013205 | 0.013206 | 0.013206 | 0.97877 | -0.407 | 0.97863 | -0.40965 | 3.6279
55 | 0.0027012 | 0.00067685 | -0.0027011 | -0.00067697 | 8.825e-08 | -1.1698e-07 | 0.0041179 | 0.0041179 | 0.0041179 | 0.97609 | -0.45938 | 0.97606 | -0.46007 | 1.1313
56 | 0.010194 | 0.0025551 | -0.010193 | -0.0025544 | 1.3805e-06 | 6.9387e-07 | 0.015558 | 0.015558 | 0.015558 | 0.97498 | -0.4813 | 0.97483 | -0.48415 | 4.2743
57 | 0.031415 | 0.0078864 | -0.031411 | -0.0078841 | 3.588e-06 | 2.2444e-06 | 0.04795 | 0.04795 | 0.04795 | 0.97498 | -0.4813 | 0.97486 | -0.4837 | 13.1732
58 | 0.0079049 | 0.0019803 | -0.0079046 | -0.0019801 | 3.0382e-07 | 1.2398e-07 | 0.012019 | 0.012019 | 0.012019 | 0.97863 | -0.40965 | 0.97859 | -0.41046 | 3.302
59 | -0.35492 | -0.091127 | 0.35533 | 0.091384 | 0.00040201 | 0.00025684 | 0.53094 | 0.53094 | 0.53094 | 0.99616 | -0.072496 | 0.99739 | -0.049191 | 48.6213
60 | 0.35332 | 0.090725 | -0.35323 | -0.090666 | 9.2899e-05 | 5.9352e-05 | 0.52855 | 0.52855 | 0.52855 | 0.99616 | -0.072496 | 0.99587 | -0.077914 | 48.402
61 | -0.36008 | -0.092574 | 0.3605 | 0.092844 | 0.00042216 | 0.00026973 | 0.53803 | 0.53803 | 0.53803 | 0.99739 | -0.049191 | 0.99867 | -0.025095 | 49.2703
62 | 0.34976 | 0.089796 | -0.34921 | -0.089445 | 0.00054974 | 0.00035121 | 0.52336 | 0.52336 | 0.52336 | 0.99587 | -0.077914 | 0.99416 | -0.11035 | 47.9272
63 | -0.36229 | -0.093294 | 0.36274 | 0.093577 | 0.00044297 | 0.00028302 | 0.54071 | 0.54071 | 0.54071 | 0.99867 | -0.025095 | 1 | 0 | 49.5152
64 | 0.084418 | 0.021662 | -0.084112 | -0.021467 | 0.00030557 | 0.00019491 | 0.12653 | 0.12653 | 0.12653 | 0.99416 | -0.11035 | 0.99023 | -0.18525 | 34.7619
65 | 0.0063486 | 0.001591 | -0.0063481 | -0.0015909 | 4.8456e-07 | 1.2018e-07 | 0.0094468 | 0.0094469 | 0.0094469 | 1 | 0 | 0.99992 | -0.0016023 | 2.5953
66 | 0.0045969 | 0.001152 | -0.0045968 | -0.0011521 | 1.6426e-07 | -1.7645e-08 | 0.0068409 | 0.0068409 | 0.0068409 | 0.99992 | -0.0016023 | 0.99988 | -0.0023524 | 1.8794
67 | 0.24906 | 0.063698 | -0.24846 | -0.063317 | 0.00059691 | 0.0003807 | 0.37382 | 0.37382 | 0.37382 | 0.9926 | -0.13997 | 0.99001 | -0.18962 | 34.2328
68 | -0.0068303 | -0.0017117 | 0.0068303 | 0.0017117 | 1.0158e-08 | 3.4168e-09 | 0.010445 | 0.010445 | 0.010445 | 0.97308 | -0.51868 | 0.97309 | -0.51865 | 2.8694
69 | 0.0045046 | 0.0011288 | -0.0045041 | -0.0011288 | 4.4221e-07 | -2.5688e-08 | 0.0068882 | 0.0068883 | 0.0068883 | 0.97308 | -0.51868 | 0.97298 | -0.52075 | 1.8924
70 | -0.0090688 | -0.0022727 | 0.0090712 | 0.0022738 | 2.329e-06 | 1.0893e-06 | 0.013868 | 0.013868 | 0.013868 | 0.97309 | -0.51865 | 0.97336 | -0.51326 | 3.8098
71 | 0.0024478 | 0.00061347 | -0.0024478 | -0.00061348 | 4.806e-09 | -8.2822e-09 | 0.0037435 | 0.0037435 | 0.0037435 | 0.97298 | -0.52075 | 0.97298 | -0.52079 | 1.0284
72 | -0.013822 | -0.0034645 | 0.013825 | 0.0034662 | 3.0483e-06 | 1.7246e-06 | 0.021131 | 0.021131 | 0.021131 | 0.97336 | -0.51326 | 0.97359 | -0.50864 | 5.8051
73 | -0.020885 | -0.0052356 | 0.020895 | 0.0052418 | 1.0187e-05 | 6.1877e-06 | 0.03192 | 0.03192 | 0.03192 | 0.97359 | -0.50864 | 0.97411 | -0.4984 | 8.7694
74 | 0.0070597 | 0.0017693 | -0.0070593 | -0.0017692 | 4.4005e-07 | 1.563e-07 | 0.01079 | 0.01079 | 0.01079 | 0.97359 | -0.50864 | 0.97353 | -0.50994 | 2.9643
75 | 0.0028041 | 0.00070256 | -0.002804 | -0.00070274 | 1.4933e-07 | -1.746e-07 | 0.0042834 | 0.0042835 | 0.0042835 | 0.97411 | -0.4984 | 0.97405 | -0.49952 | 1.1768
76 | -0.023699 | -0.0059443 | 0.023705 | 0.005948 | 5.9665e-06 | 3.6674e-06 | 0.036204 | 0.036204 | 0.036204 | 0.97411 | -0.4984 | 0.97438 | -0.49312 | 9.9461
77 | 0.0049354 | 0.0012369 | -0.0049352 | -0.0012369 | 2.267e-07 | 1.3008e-08 | 0.0075437 | 0.0075437 | 0.0075437 | 0.97353 | -0.50994 | 0.97348 | -0.51091 | 2.0725
78 | 0.0041945 | 0.0010508 | -0.0041945 | -0.0010508 | 3.5726e-08 | -6.5497e-09 | 0.0063784 | 0.0063785 | 0.0063785 | 0.97851 | -0.41269 | 0.9785 | -0.41287 | 1.7523
79 | 0.0041945 | 0.0010508 | -0.0041945 | -0.0010508 | 4.3293e-08 | -7.9361e-09 | 0.0063785 | 0.0063785 | 0.0063785 | 0.9785 | -0.41287 | 0.97849 | -0.41309 | 1.7523
80 | 0.0026863 | 0.00067281 | -0.0026862 | -0.00067298 | 1.2752e-07 | -1.7434e-07 | 0.004085 | 0.004085 | 0.004085 | 0.97849 | -0.41309 | 0.97844 | -0.41409 | 1.1223
81 | 0.0013179 | 0.00033006 | -0.0013179 | -0.00033022 | 2.0889e-08 | -1.608e-07 | 0.0020042 | 0.0020042 | 0.0020042 | 0.97844 | -0.41409 | 0.97842 | -0.41442 | 0.55061
82 | 0.0013179 | 0.00033022 | -0.0013179 | -0.00033029 | 8.1742e-09 | -6.2919e-08 | 0.0020042 | 0.0020043 | 0.0020043 | 0.97842 | -0.41442 | 0.97842 | -0.41455 | 0.55062
83 | -0.054612 | -0.01373 | 0.054689 | 0.013778 | 7.6752e-05 | 4.8754e-05 | 0.083382 | 0.083382 | 0.083382 | 0.97478 | -0.48513 | 0.97627 | -0.45575 | 22.9071
84 | 0.052667 | 0.013242 | -0.052653 | -0.013233 | 1.3778e-05 | 8.7471e-06 | 0.080412 | 0.080412 | 0.080412 | 0.97478 | -0.48513 | 0.9745 | -0.49061 | 22.0913
85 | -0.057146 | -0.014394 | 0.057186 | 0.01442 | 4.0004e-05 | 2.5427e-05 | 0.087127 | 0.087127 | 0.087127 | 0.97627 | -0.45575 | 0.97702 | -0.44112 | 23.936
86 | 0.011322 | 0.0028381 | -0.011321 | -0.0028372 | 1.6915e-06 | 8.9456e-07 | 0.017289 | 0.017289 | 0.017289 | 0.9745 | -0.49061 | 0.97434 | -0.49375 | 4.7498
87 | 0.041331 | 0.010395 | -0.041301 | -0.010376 | 3.0093e-05 | 1.9009e-05 | 0.063123 | 0.063124 | 0.063124 | 0.9745 | -0.49061 | 0.97373 | -0.50587 | 17.3416
88 | -0.066735 | -0.016813 | 0.066878 | 0.016904 | 0.00014371 | 9.1507e-05 | 0.10167 | 0.10167 | 0.10167 | 0.97702 | -0.44112 | 0.97932 | -0.3962 | 27.9311
89 | 0.0095483 | 0.002393 | -0.009547 | -0.0023924 | 1.2485e-06 | 6.0192e-07 | 0.014542 | 0.014542 | 0.014542 | 0.97702 | -0.44112 | 0.97688 | -0.44386 | 3.9951
90 | 0.0085476 | 0.0021422 | -0.0085475 | -0.0021421 | 1.5633e-07 | 6.9583e-08 | 0.013054 | 0.013054 | 0.013054 | 0.97434 | -0.49375 | 0.97432 | -0.49413 | 3.5863
91 | 0.03957 | 0.0099424 | -0.039532 | -0.0099188 | 3.7511e-05 | 2.3667e-05 | 0.060479 | 0.060479 | 0.060479 | 0.97373 | -0.50587 | 0.97272 | -0.52575 | 16.6151
92 | 0.010915 | 0.0027356 | -0.010913 | -0.0027348 | 1.4821e-06 | 7.6777e-07 | 0.016585 | 0.016585 | 0.016585 | 0.97932 | -0.3962 | 0.97917 | -0.39905 | 4.5562
93 | -0.077793 | -0.01964 | 0.077867 | 0.019687 | 7.3976e-05 | 4.7167e-05 | 0.11825 | 0.11825 | 0.11825 | 0.97932 | -0.3962 | 0.98034 | -0.37637 | 32.4872
94 | 0.0063594 | 0.0015935 | -0.0063593 | -0.0015935 | 4.0192e-08 | 1.1422e-08 | 0.0096867 | 0.0096867 | 0.0096867 | 0.97688 | -0.44386 | 0.97687 | -0.444 | 2.6612
95 | 0.0049697 | 0.0012454 | -0.0049692 | -0.0012454 | 5.0623e-07 | 3.2171e-08 | 0.0075899 | 0.00759 | 0.00759 | 0.97432 | -0.49413 | 0.97421 | -0.49627 | 2.0852
96 | 0.037376 | 0.0093783 | -0.037371 | -0.0093751 | 5.0355e-06 | 3.1717e-06 | 0.05718 | 0.05718 | 0.05718 | 0.97272 | -0.52575 | 0.97257 | -0.52857 | 15.7088
97 | 0.0066669 | 0.0016705 | -0.0066668 | -0.0016705 | 1.526e-07 | 4.7798e-08 | 0.010131 | 0.010131 | 0.010131 | 0.97917 | -0.39905 | 0.97915 | -0.39953 | 2.7833
98 | -0.082156 | -0.020762 | 0.082424 | 0.020932 | 0.0002675 | 0.00017062 | 0.12476 | 0.12476 | 0.12476 | 0.98034 | -0.37637 | 0.98382 | -0.3087 | 34.2757
99 | 0.0032915 | 0.00082463 | -0.0032912 | -0.00082485 | 3.1859e-07 | -2.1918e-07 | 0.0050137 | 0.0050138 | 0.0050138 | 0.97687 | -0.444 | 0.97677 | -0.44603 | 1.3774
100 | 0.028096 | 0.0070508 | -0.028073 | -0.0070364 | 2.3192e-05 | 1.4428e-05 | 0.042989 | 0.042989 | 0.042989 | 0.97257 | -0.52857 | 0.9717 | -0.5459 | 11.8103
101 | 0.0092752 | 0.0023244 | -0.0092741 | -0.0023238 | 1.1259e-06 | 5.3558e-07 | 0.014191 | 0.014191 | 0.014191 | 0.97257 | -0.52857 | 0.97245 | -0.53112 | 3.8986
102 | 0.0071968 | 0.0018027 | -0.0071959 | -0.0018024 | 8.8664e-07 | 3.1942e-07 | 0.010943 | 0.010943 | 0.010943 | 0.97859 | -0.41046 | 0.97846 | -0.41305 | 3.0063
103 | 0.0024933 | 0.00062447 | -0.0024933 | -0.00062452 | 2.473e-08 | -4.1787e-08 | 0.0037916 | 0.0037916 | 0.0037916 | 0.97846 | -0.41305 | 0.97845 | -0.41325 | 1.0417
104 | 0.0036483 | 0.00091372 | -0.0036476 | -0.00091402 | 6.6812e-07 | -2.9923e-07 | 0.0055481 | 0.0055483 | 0.0055483 | 0.97846 | -0.41305 | 0.97826 | -0.41689 | 1.5243
105 | 0.0018072 | 0.00045257 | -0.0018072 | -0.00045273 | 4.0407e-08 | -1.5331e-07 | 0.0027483 | 0.0027483 | 0.0027483 | 0.97845 | -0.41325 | 0.97842 | -0.41372 | 0.75504
106 | 0.0029651 | 0.00074296 | -0.002965 | -0.00074309 | 1.2985e-07 | -1.3061e-07 | 0.0045101 | 0.0045102 | 0.0045102 | 0.97826 | -0.41689 | 0.97822 | -0.41781 | 1.2391
107 | 0.0010174 | 0.00025479 | -0.0010174 | -0.00025498 | 1.4374e-08 | -1.9188e-07 | 0.0015472 | 0.0015473 | 0.0015473 | 0.97842 | -0.41372 | 0.97841 | -0.41402 | 0.42509
108 | 0.0055652 | 0.0013946 | -0.0055647 | -0.0013945 | 5.3315e-07 | 9.5616e-08 | 0.0084949 | 0.0084949 | 0.0084949 | 0.97483 | -0.48415 | 0.97473 | -0.48616 | 2.3338
109 | 0.029097 | 0.007304 | -0.029087 | -0.007298 | 9.7e-06 | 6.0446e-06 | 0.044417 | 0.044418 | 0.044418 | 0.97486 | -0.4837 | 0.9745 | -0.49069 | 12.2026
110 | -0.022336 | -0.0056032 | 0.022337 | 0.0056042 | 1.6355e-06 | 9.9953e-07 | 0.034017 | 0.034017 | 0.034017 | 0.97709 | -0.44055 | 0.97717 | -0.43901 | 9.3453
111 | 0.018563 | 0.0046577 | -0.018555 | -0.0046527 | 8.4157e-06 | 5.0346e-06 | 0.028272 | 0.028272 | 0.028272 | 0.97709 | -0.44055 | 0.97661 | -0.45006 | 7.767
112 | -0.025378 | -0.0063663 | 0.025386 | 0.0063715 | 8.3409e-06 | 5.1516e-06 | 0.038647 | 0.038647 | 0.038647 | 0.97717 | -0.43901 | 0.97752 | -0.43212 | 10.6174
113 | 0.012289 | 0.0030823 | -0.012279 | -0.0030771 | 9.4414e-06 | 5.1447e-06 | 0.018725 | 0.018725 | 0.018725 | 0.97661 | -0.45006 | 0.97579 | -0.46619 | 5.1442
114 | 0.0064102 | 0.0016066 | -0.006409 | -0.0016063 | 1.1643e-06 | 3.3647e-07 | 0.0097579 | 0.009758 | 0.009758 | 0.97752 | -0.43212 | 0.97732 | -0.43593 | 2.6808
115 | -0.031797 | -0.007978 | 0.031806 | 0.007984 | 9.5723e-06 | 5.9896e-06 | 0.048405 | 0.048405 | 0.048405 | 0.97752 | -0.43212 | 0.97784 | -0.42581 | 13.2981
116 | -0.034682 | -0.0087048 | 0.034692 | 0.0087112 | 1.0114e-05 | 6.3516e-06 | 0.052782 | 0.052782 | 0.052782 | 0.97784 | -0.42581 | 0.97815 | -0.41969 | 14.5005
117 | 0.0067758 | 0.0016977 | -0.0067757 | -0.0016977 | 8.7384e-08 | 2.9033e-08 | 0.010368 | 0.010368 | 0.010368 | 0.97245 | -0.53112 | 0.97243 | -0.53139 | 2.8484
118 | 0.0041114 | 0.0010299 | -0.0041111 | -0.00103 | 3.4831e-07 | -6.819e-08 | 0.0062911 | 0.0062913 | 0.0062913 | 0.97243 | -0.53139 | 0.97234 | -0.53317 | 1.7284
119 | 0.0034944 | 0.00087566 | -0.0034942 | -0.00087574 | 1.6428e-07 | -8.4862e-08 | 0.0053476 | 0.0053477 | 0.0053477 | 0.97234 | -0.53317 | 0.97229 | -0.53416 | 1.4691
120 | 0.00061667 | 0.00015435 | -0.00061667 | -0.00015455 | 5.4187e-09 | -1.9779e-07 | 0.00094365 | 0.00094372 | 0.00094372 | 0.97234 | -0.53317 | 0.97233 | -0.53336 | 0.25926
121 | 0.026319 | 0.0065968 | -0.026312 | -0.0065929 | 6.341e-06 | 3.9293e-06 | 0.040304 | 0.040304 | 0.040304 | 0.9717 | -0.5459 | 0.97144 | -0.55096 | 11.0725
122 | 0.013119 | 0.0032886 | -0.013117 | -0.0032878 | 1.4226e-06 | 7.9416e-07 | 0.020095 | 0.020095 | 0.020095 | 0.97144 | -0.55096 | 0.97133 | -0.55323 | 5.5206
123 | 0.013194 | 0.0033043 | -0.013191 | -0.0033029 | 2.5506e-06 | 1.4262e-06 | 0.020209 | 0.020209 | 0.020209 | 0.97144 | -0.55096 | 0.97124 | -0.55502 | 5.5519
124 | 0.01104 | 0.0027671 | -0.011037 | -0.0027656 | 2.8469e-06 | 1.4936e-06 | 0.016912 | 0.016913 | 0.016913 | 0.97133 | -0.55323 | 0.97105 | -0.55865 | 4.6463
125 | 0.011432 | 0.0028621 | -0.011432 | -0.002862 | 9.6154e-08 | 5.1194e-08 | 0.017514 | 0.017514 | 0.017514 | 0.97124 | -0.55502 | 0.97123 | -0.55519 | 4.8116
126 | -0.086284 | -0.0219 | 0.086512 | 0.022045 | 0.00022786 | 0.00014538 | 0.1306 | 0.1306 | 0.1306 | 0.98382 | -0.3087 | 0.98666 | -0.25396 | 35.8797
127 | 0.0038605 | 0.00096721 | -0.0038602 | -0.00096731 | 2.9318e-07 | -1.0354e-07 | 0.0058388 | 0.0058389 | 0.0058389 | 0.98382 | -0.3087 | 0.98374 | -0.31029 | 1.6041
128 | 0.0038602 | 0.00096731 | -0.00386 | -0.0009674 | 2.3356e-07 | -8.2441e-08 | 0.0058389 | 0.005839 | 0.005839 | 0.98374 | -0.31029 | 0.98367 | -0.31156 | 1.6041
129 | 0.0066668 | 0.0016705 | -0.0066664 | -0.0016704 | 3.125e-07 | 9.7889e-08 | 0.010131 | 0.010131 | 0.010131 | 0.97915 | -0.39953 | 0.9791 | -0.40052 | 2.7834
130 | 0.0046156 | 0.0011564 | -0.0046154 | -0.0011564 | 1.568e-07 | -6.5204e-09 | 0.0070145 | 0.0070145 | 0.0070145 | 0.9791 | -0.40052 | 0.97906 | -0.40123 | 1.9271
131 | 0.0025659 | 0.00064275 | -0.0025658 | -0.00064288 | 8.4924e-08 | -1.3291e-07 | 0.0038996 | 0.0038997 | 0.0038997 | 0.97906 | -0.40123 | 0.97903 | -0.40192 | 1.0713
132 | 0.0025658 | 0.00064288 | -0.0025657 | -0.00064303 | 9.6569e-08 | -1.5112e-07 | 0.0038997 | 0.0038998 | 0.0038998 | 0.97903 | -0.40192 | 0.97899 | -0.40272 | 1.0714
133 | 0.026541 | 0.0066598 | -0.026538 | -0.0066579 | 3.082e-06 | 1.9102e-06 | 0.04053 | 0.04053 | 0.04053 | 0.9745 | -0.49069 | 0.97438 | -0.49312 | 11.1345
134 | 0.0027824 | 0.00069721 | -0.0027823 | -0.00069731 | 8.1238e-08 | -9.7672e-08 | 0.0042475 | 0.0042476 | 0.0042476 | 0.97473 | -0.48616 | 0.9747 | -0.48677 | 1.1669
135 | 0.0076071 | 0.0019033 | -0.0076061 | -0.001903 | 9.3839e-07 | 3.7258e-07 | 0.011654 | 0.011654 | 0.011654 | 0.97123 | -0.55519 | 0.9711 | -0.55779 | 3.2016
136 | 0.0020353 | 0.00050989 | -0.0020352 | -0.00051007 | 6.4223e-08 | -1.7675e-07 | 0.0031186 | 0.0031187 | 0.0031187 | 0.9711 | -0.55779 | 0.97106 | -0.55845 | 0.85678
137 | 0.0055709 | 0.0013931 | -0.0055704 | -0.001393 | 4.9741e-07 | 9.31e-08 | 0.0085351 | 0.0085352 | 0.0085352 | 0.9711 | -0.55779 | 0.971 | -0.55966 | 2.3448
138 | 0.0031917 | 0.00079683 | -0.0031901 | -0.00079804 | 1.6464e-06 | -1.2157e-06 | 0.00489 | 0.0048909 | 0.0048909 | 0.971 | -0.55966 | 0.97046 | -0.57052 | 1.3436
139 | 0.0085864 | 0.0021515 | -0.0085862 | -0.0021514 | 1.5783e-07 | 7.0936e-08 | 0.013157 | 0.013157 | 0.013157 | 0.97105 | -0.55865 | 0.97103 | -0.55903 | 3.6147
140 | 0.0027312 | 0.00068303 | -0.002731 | -0.00068326 | 1.8585e-07 | -2.3028e-07 | 0.0041872 | 0.0041874 | 0.0041874 | 0.97046 | -0.57052 | 0.97038 | -0.57195 | 1.1504
141 | 0.0063849 | 0.0015997 | -0.0063842 | -0.0015995 | 7.5996e-07 | 2.2453e-07 | 0.0097841 | 0.0097842 | 0.0097842 | 0.97103 | -0.55903 | 0.97091 | -0.56153 | 2.688
142 | -0.0020901 | -0.00052383 | 0.0020901 | 0.00052379 | 1.7317e-08 | -4.4571e-08 | 0.0032033 | 0.0032033 | 0.0032033 | 0.9709 | -0.56171 | 0.97091 | -0.56153 | 0.88004
143 | 0.004294 | 0.0010757 | -0.0042938 | -0.0010757 | 2.0997e-07 | -2.5502e-08 | 0.0065809 | 0.0065809 | 0.0065809 | 0.97091 | -0.56153 | 0.97086 | -0.56256 | 1.8079
144 | 0.0020925 | 0.000524 | -0.0020924 | -0.0005242 | 8.0675e-08 | -2.0701e-07 | 0.003207 | 0.0032071 | 0.0032071 | 0.97086 | -0.56256 | 0.97082 | -0.56337 | 0.88107
145 | 0.0020924 | 0.0005242 | -0.0020923 | -0.00052439 | 7.2629e-08 | -1.8634e-07 | 0.0032071 | 0.0032072 | 0.0032072 | 0.97082 | -0.56337 | 0.97078 | -0.5641 | 0.88109
146 | 0.0012955 | 0.00032349 | -0.0012954 | -0.00032413 | 8.3269e-08 | -6.4201e-07 | 0.0019861 | 0.0019863 | 0.0019863 | 0.97038 | -0.57195 | 0.97032 | -0.5733 | 0.54569
147 | 0.0012954 | 0.00032413 | -0.0012953 | -0.00032464 | 6.5839e-08 | -5.0743e-07 | 0.0019863 | 0.0019865 | 0.0019865 | 0.97032 | -0.5733 | 0.97026 | -0.57437 | 0.54575

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37451 | 0.096114

## res_load
| p_mw | q_mvar
0 | 0.031063 | 0.007785
1 | 0.017801 | 0.0044614
2 | 0.0024857 | 0.00062296
3 | 0.0019341 | 0.00048473
4 | 0.0026177 | 0.00065605
5 | 0.003674 | 0.0009208
6 | 0.0011159 | 0.00027968
7 | 0.002701 | 0.00067693
8 | 0.00053792 | 0.00013481
9 | 0.00047553 | 0.00011918
10 | 0.0008278 | 0.00020747
11 | 0.012435 | 0.0031164
12 | 0.0032597 | 0.00081695
13 | 0.0035793 | 0.00089705
14 | 0.0036856 | 0.00092371
15 | 0.0017125 | 0.0004292
16 | 0.0038403 | 0.00096246
17 | 0.0015868 | 0.00039769
18 | 0.00213 | 0.00053383
19 | 0.0036535 | 0.00091565
20 | 0.0034713 | 0.00086998
21 | 0.002349 | 0.00058871
22 | 0.0029587 | 0.00074153
23 | 0.0021797 | 0.00054629
24 | 0.0022435 | 0.00056228
25 | 0.0036656 | 0.00091869
26 | 0.0022445 | 0.00056252
27 | 0.0019788 | 0.00049594
28 | 0.0025258 | 0.00063304
29 | 0.0034158 | 0.00085608
30 | 0.00067792 | 0.0001699
31 | 0.0026269 | 0.00065836
32 | 0.00078029 | 0.00019556
33 | 0.0016029 | 0.00040172
34 | 0.0047511 | 0.0011907
35 | 0.0034704 | 0.00086977
36 | 0.001795 | 0.00044986
37 | 0.003774 | 0.00094586
38 | 0.0056283 | 0.0014106
39 | 0.0017512 | 0.00043889
40 | 0.0037543 | 0.00094092
41 | 0.0023257 | 0.00058287
42 | 0.0022386 | 0.00056104
43 | 0.0020563 | 0.00051536
44 | 0.004751 | 0.0011907
45 | 0.0024478 | 0.00061348
46 | 0.0021239 | 0.0005323
47 | 0.001544 | 0.00038697
48 | 0.0015082 | 0.00037798
49 | 0.017803 | 0.0044618
50 | 0.0013683 | 0.00034292
51 | 0.0019451 | 0.00048749
52 | 0.0024573 | 0.00061587
53 | 0.0027731 | 0.00069501
54 | 0.0017307 | 0.00043376
55 | 0.0031877 | 0.00079891
56 | 0.0035778 | 0.00089668
57 | 0.0021565 | 0.00054047
58 | 0.0042465 | 0.0010643
59 | 0.0042889 | 0.0010749
60 | 0.0030678 | 0.00076887
61 | 0.0049692 | 0.0012454
62 | 0.00070777 | 0.00017738
63 | 0.0010543 | 0.00026423
64 | 0.00068607 | 0.00017194
65 | 0.00068255 | 0.00017106
66 | 0.00078976 | 0.00019793
67 | 0.002965 | 0.00074309
68 | 0.0010174 | 0.00025498
69 | 0.0027011 | 0.00067697
70 | 0.0046275 | 0.0011598
71 | 0.0023146 | 0.0005801
72 | 0.0045968 | 0.0011521
73 | 0.0037725 | 0.00094548
74 | 0.0030408 | 0.00076209
75 | 0.006266 | 0.0015704
76 | 0.0029342 | 0.00073538
77 | 0.006409 | 0.0016063
78 | 0.002876 | 0.00072079
79 | 0.0020357 | 0.0005102
80 | 0.0013179 | 0.00033029
81 | 0.0024982 | 0.00062612
82 | 0.0026643 | 0.00066774
83 | 0.0017538 | 0.00043955
84 | 0.0034942 | 0.00087574
85 | 0.00061667 | 0.00015455
86 | 0.0020774 | 0.00052065
87 | 0.0017588 | 0.00044081
88 | 0.011544 | 0.0028931
89 | 0.00386 | 0.0009674
90 | 0.0024005 | 0.00060163
91 | 0.0020509 | 0.000514
92 | 0.0020495 | 0.00051365
93 | 0.0025657 | 0.00064303
94 | 0.0025462 | 0.00063813
95 | 0.0028327 | 0.00070995
96 | 0.0027823 | 0.00069731
97 | 0.002804 | 0.00070274
98 | 0.0027823 | 0.00069731
99 | 0.0049352 | 0.0012369
100 | 0.0038252 | 0.00095869
101 | 0.0020352 | 0.00051007
102 | 0.0023786 | 0.00059615
103 | 0.0024506 | 0.00061417
104 | 0.0004589 | 0.00011501
105 | 0.0022013 | 0.0005517
106 | 0.0020901 | 0.00052383
107 | 0.0022013 | 0.0005517
108 | 0.0020923 | 0.00052439
109 | 0.0032912 | 0.00082485
110 | 0.0014355 | 0.00035978
111 | 0.0012953 | 0.00032464

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1