## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1088-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1088-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1088-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1088-3_0_5_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_1088-3_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1088-3_0_5_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_1088-3_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1088-3_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1088-3_0_5_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1088-3_0_5_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1088-3_0_5_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1088-3_0_5_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1088-3_0_5_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_1088-3_0_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1088-3_0_5_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_1088-3_0_5_node_49 | 0.4 | n |  | TRUE
16 | bus_LV_1088-3_0_5_node_116 | 0.4 | n |  | TRUE
17 | bus_LV_1088-3_0_5_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_1088-3_0_5_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1088-3_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1088-3_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1088-3_0_5_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1088-3_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1088-3_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1088-3_0_5_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1088-3_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1088-3_0_5_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1088-3_0_5_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1088-3_0_5_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1088-3_0_5_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1088-3_0_5_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1088-3_0_5_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1088-3_0_5_node_74 | 0.4 | n |  | TRUE
33 | bus_LV_1088-3_0_5_node_71 | 0.4 | n |  | TRUE
34 | bus_LV_1088-3_0_5_node_147 | 0.4 | n |  | TRUE
35 | bus_LV_1088-3_0_5_node_78 | 0.4 | n |  | TRUE
36 | bus_LV_1088-3_0_5_node_72 | 0.4 | n |  | TRUE
37 | bus_LV_1088-3_0_5_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1088-3_0_5_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1088-3_0_5_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1088-3_0_5_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_1088-3_0_5_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1088-3_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1088-3_0_5_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1088-3_0_5_node_75 | 0.4 | n |  | TRUE
45 | bus_LV_1088-3_0_5_node_80 | 0.4 | n |  | TRUE
46 | bus_LV_1088-3_0_5_node_76 | 0.4 | n |  | TRUE
47 | bus_LV_1088-3_0_5_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_1088-3_0_5_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_1088-3_0_5_node_85 | 0.4 | n |  | TRUE
50 | bus_LV_1088-3_0_5_node_79 | 0.4 | n |  | TRUE
51 | bus_LV_1088-3_0_5_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_1088-3_0_5_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1088-3_0_5_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_1088-3_0_5_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1088-3_0_5_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_1088-3_0_5_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1088-3_0_5_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_1088-3_0_5_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_1088-3_0_5_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_1088-3_0_5_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_1088-3_0_5_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_1088-3_0_5_node_89 | 0.4 | n |  | TRUE
63 | bus_LV_1088-3_0_5_node_119 | 0.4 | n |  | TRUE
64 | bus_LV_1088-3_0_5_node_90 | 0.4 | n |  | TRUE
65 | bus_LV_1088-3_0_5_node_117 | 0.4 | n |  | TRUE
66 | bus_LV_1088-3_0_5_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_1088-3_0_5_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_1088-3_0_5_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_1088-3_0_5_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_1088-3_0_5_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_1088-3_0_5_node_77 | 0.4 | n |  | TRUE
72 | bus_LV_1088-3_0_5_node_92 | 0.4 | n |  | TRUE
73 | bus_LV_1088-3_0_5_node_93 | 0.4 | n |  | TRUE
74 | bus_LV_1088-3_0_5_node_94 | 0.4 | n |  | TRUE
75 | bus_LV_1088-3_0_5_node_95 | 0.4 | n |  | TRUE
76 | bus_LV_1088-3_0_5_node_120 | 0.4 | n |  | TRUE
77 | bus_LV_1088-3_0_5_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_1088-3_0_5_node_121 | 0.4 | n |  | TRUE
79 | bus_LV_1088-3_0_5_node_129 | 0.4 | n |  | TRUE
80 | bus_LV_1088-3_0_5_node_131 | 0.4 | n |  | TRUE
81 | bus_LV_1088-3_0_5_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_1088-3_0_5_node_81 | 0.4 | n |  | TRUE
83 | bus_LV_1088-3_0_5_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1088-3_0_5_node_103 | 0.4 | n |  | TRUE
85 | bus_LV_1088-3_0_5_node_101 | 0.4 | n |  | TRUE
86 | bus_LV_1088-3_0_5_node_136 | 0.4 | n |  | TRUE
87 | bus_LV_1088-3_0_5_node_134 | 0.4 | n |  | TRUE
88 | bus_LV_1088-3_0_5_node_104 | 0.4 | n |  | TRUE
89 | bus_LV_1088-3_0_5_node_105 | 0.4 | n |  | TRUE
90 | bus_LV_1088-3_0_5_node_99 | 0.4 | n |  | TRUE
91 | bus_LV_1088-3_0_5_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_1088-3_0_5_node_124 | 0.4 | n |  | TRUE
93 | bus_LV_1088-3_0_5_node_125 | 0.4 | n |  | TRUE
94 | bus_LV_1088-3_0_5_node_126 | 0.4 | n |  | TRUE
95 | bus_LV_1088-3_0_5_node_141 | 0.4 | n |  | TRUE
96 | bus_LV_1088-3_0_5_node_128 | 0.4 | n |  | TRUE
97 | bus_LV_1088-3_0_5_node_130 | 0.4 | n |  | TRUE
98 | bus_LV_1088-3_0_5_node_132 | 0.4 | n |  | TRUE
99 | bus_LV_1088-3_0_5_node_133 | 0.4 | n |  | TRUE
100 | bus_LV_1088-3_0_5_node_135 | 0.4 | n |  | TRUE
101 | bus_LV_1088-3_0_5_node_143 | 0.4 | n |  | TRUE
102 | bus_LV_1088-3_0_5_node_140 | 0.4 | n |  | TRUE
103 | bus_LV_1088-3_0_5_node_145 | 0.4 | n |  | TRUE
104 | bus_LV_1088-3_0_5_node_84 | 0.4 | n |  | TRUE
105 | bus_LV_1088-3_0_5_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_1088-3_0_5_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_1088-3_0_5_node_110 | 0.4 | n |  | TRUE
108 | bus_LV_1088-3_0_5_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_1088-3_0_5_node_137 | 0.4 | n |  | TRUE
110 | bus_LV_1088-3_0_5_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_1088-3_0_5_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_1088-3_0_5_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_1088-3_0_5_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_1088-3_0_5_node_146 | 0.4 | n |  | TRUE
115 | bus_LV_1088-3_0_5_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_1088-3_0_5_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_1088-3_0_5_node_144 | 0.4 | n |  | TRUE
118 | bus_LV_1088-3_0_5_node_138 | 0.4 | n |  | TRUE
119 | bus_LV_1088-3_0_5_node_142 | 0.4 | n |  | TRUE
120 | bus_LV_1088-3_0_5_node_139 | 0.4 | n |  | TRUE
121 | bus_LV_1088-3_0_5_node_91 | 0.4 | n |  | TRUE
122 | bus_LV_1088-3_0_5_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_1088-3_0_5_node_97 | 0.4 | n |  | TRUE
124 | bus_LV_1088-3_0_5_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_1088-3_0_5_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_1088-3_0_5_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_1088-3_0_5_node_118 | 0.4 | n |  | TRUE
128 | bus_MV_354_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1088-3_0_5_load_0 | 0 | 0.0016145 | 0.00040463 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1088-3_0_5_load_1 | 1 | 0.0015501 | 0.0003885 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1088-3_0_5_load_2 | 2 | 0.0029257 | 0.00073324 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1088-3_0_5_load_24 | 3 | 0.0015068 | 0.00037764 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1088-3_0_5_load_3 | 4 | 0.0042152 | 0.0010564 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1088-3_0_5_load_6 | 6 | 0.0069873 | 0.0017512 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1088-3_0_5_load_8 | 7 | 0.0034695 | 0.00086953 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1088-3_0_5_load_12 | 10 | 0.00325 | 0.00081453 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1088-3_0_5_load_17 | 11 | 0.0046924 | 0.001176 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1088-3_0_5_load_38 | 12 | 0.0018232 | 0.00045693 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1088-3_0_5_load_15 | 13 | 0.0046943 | 0.0011765 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1088-3_0_5_load_37 | 14 | 0.0021536 | 0.00053974 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1088-3_0_5_load_116 | 16 | 0.0026343 | 0.00066021 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1088-3_0_5_load_13 | 19 | 0.0067928 | 0.0017024 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1088-3_0_5_load_14 | 20 | 0.015219 | 0.0038142 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1088-3_0_5_load_16 | 21 | 0.0038553 | 0.00096623 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1088-3_0_5_load_18 | 22 | 0.0035136 | 0.0008806 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1088-3_0_5_load_19 | 23 | 0.0051212 | 0.0012835 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1088-3_0_5_load_20 | 24 | 0.0035113 | 0.00088002 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1088-3_0_5_load_21 | 25 | 0.0028743 | 0.00072036 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1088-3_0_5_load_22 | 26 | 0.0031794 | 0.00079684 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1088-3_0_5_load_27 | 27 | 0.0027832 | 0.00069753 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1088-3_0_5_load_25 | 28 | 0.0013469 | 0.00033756 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1088-3_0_5_load_26 | 29 | 0.0018027 | 0.0004518 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1088-3_0_5_load_71 | 33 | 0.0026704 | 0.00066928 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1088-3_0_5_load_147 | 34 | 0.0042994 | 0.0010775 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1088-3_0_5_load_78 | 35 | 0.0042189 | 0.0010574 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1088-3_0_5_load_72 | 36 | 0.0032997 | 0.00082699 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1088-3_0_5_load_30 | 37 | 0.0042962 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1088-3_0_5_load_31 | 38 | 0.0042189 | 0.0010574 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1088-3_0_5_load_32 | 39 | 0.0081125 | 0.0020332 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1088-3_0_5_load_33 | 40 | 0.012728 | 0.0031901 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1088-3_0_5_load_75 | 44 | 0.0098144 | 0.0024597 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1088-3_0_5_load_80 | 45 | 0.0069725 | 0.0017475 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1088-3_0_5_load_76 | 46 | 0.0098018 | 0.0024566 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1088-3_0_5_load_88 | 48 | 0.0066526 | 0.0016673 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1088-3_0_5_load_85 | 49 | 0.0018293 | 0.00045848 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1088-3_0_5_load_79 | 50 | 0.0098862 | 0.0024777 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1088-3_0_5_load_39 | 51 | 0.0018294 | 0.00045849 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1088-3_0_5_load_40 | 52 | 0.0022709 | 0.00056915 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1088-3_0_5_load_42 | 54 | 0.002201 | 0.00055162 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1088-3_0_5_load_43 | 55 | 0.0018083 | 0.00045319 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1088-3_0_5_load_44 | 56 | 0.0021417 | 0.00053677 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1088-3_0_5_load_46 | 57 | 0.0022341 | 0.00055992 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1088-3_0_5_load_45 | 58 | 0.0021446 | 0.00053749 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1088-3_0_5_load_56 | 59 | 0.0025829 | 0.00064734 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1088-3_0_5_load_119 | 63 | 0.0012138 | 0.00030422 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1088-3_0_5_load_90 | 64 | 0.0018914 | 0.00047403 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1088-3_0_5_load_117 | 65 | 0.0015303 | 0.00038352 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1088-3_0_5_load_51 | 66 | 0.0023975 | 0.00060087 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1088-3_0_5_load_52 | 67 | 0.0026926 | 0.00067483 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1088-3_0_5_load_53 | 68 | 0.010445 | 0.0026177 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1088-3_0_5_load_55 | 69 | 0.0021005 | 0.00052644 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1088-3_0_5_load_73 | 70 | 0.0031531 | 0.00079025 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1088-3_0_5_load_77 | 71 | 0.024471 | 0.0061331 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1088-3_0_5_load_92 | 72 | 0.0037788 | 0.00094706 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1088-3_0_5_load_93 | 73 | 0.011248 | 0.0028191 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1088-3_0_5_load_120 | 76 | 0.0051869 | 0.0012999 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1088-3_0_5_load_121 | 78 | 0.0024037 | 0.00060243 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1088-3_0_5_load_129 | 79 | 0.00029178 | 7.3127e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1088-3_0_5_load_131 | 80 | 0.0028757 | 0.00072072 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1088-3_0_5_load_127 | 81 | 0.0016513 | 0.00041384 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1088-3_0_5_load_81 | 82 | 0.013195 | 0.003307 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1088-3_0_5_load_82 | 83 | 0.010654 | 0.0026701 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1088-3_0_5_load_103 | 84 | 0.0087947 | 0.0022042 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1088-3_0_5_load_136 | 86 | 0.0014479 | 0.00036289 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1088-3_0_5_load_134 | 87 | 0.0014479 | 0.00036289 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1088-3_0_5_load_104 | 88 | 0.0041421 | 0.0010381 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1088-3_0_5_load_105 | 89 | 0.0061006 | 0.0015289 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1088-3_0_5_load_106 | 91 | 0.010567 | 0.0026484 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1088-3_0_5_load_124 | 92 | 0.00059643 | 0.00014948 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1088-3_0_5_load_125 | 93 | 0.00096713 | 0.00024238 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1088-3_0_5_load_126 | 94 | 0.00046629 | 0.00011686 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1088-3_0_5_load_128 | 96 | 0.0015084 | 0.00037805 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1088-3_0_5_load_130 | 97 | 0.0015079 | 0.00037792 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1088-3_0_5_load_132 | 98 | 0.0014677 | 0.00036784 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1088-3_0_5_load_133 | 99 | 0.0014698 | 0.00036838 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1088-3_0_5_load_135 | 100 | 0.0053636 | 0.0013442 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1088-3_0_5_load_145 | 103 | 0.00075957 | 0.00019037 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1088-3_0_5_load_84 | 104 | 0.004983 | 0.0012489 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1088-3_0_5_load_86 | 105 | 0.0084915 | 0.0021282 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1088-3_0_5_load_87 | 106 | 0.0057693 | 0.0014459 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1088-3_0_5_load_110 | 107 | 0.0094196 | 0.0023608 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1088-3_0_5_load_115 | 112 | 0.0035272 | 0.000884 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1088-3_0_5_load_107 | 113 | 0.0025398 | 0.00063653 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1088-3_0_5_load_146 | 114 | 0.0035912 | 0.00090005 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1088-3_0_5_load_108 | 115 | 0.0057183 | 0.0014331 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1088-3_0_5_load_109 | 116 | 0.0026125 | 0.00065475 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1088-3_0_5_load_144 | 117 | 0.0092672 | 0.0023226 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1088-3_0_5_load_139 | 120 | 0.0036889 | 0.00092453 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1088-3_0_5_load_91 | 121 | 0.007575 | 0.0018985 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1088-3_0_5_load_111 | 122 | 0.0022972 | 0.00057574 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1088-3_0_5_load_114 | 124 | 0.0038174 | 0.00095674 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1088-3_0_5_load_112 | 125 | 0.0065118 | 0.001632 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1088-3_0_5_load_113 | 126 | 0.002267 | 0.00056816 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1088-3_0_5_load_118 | 127 | 0.0020504 | 0.00051388 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1088-3_0_5_line_0 |  | 0 | 1 | 0.0011432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1088-3_0_5_line_1 |  | 0 | 2 | 0.032073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1088-3_0_5_line_2 |  | 1 | 3 | 0.2521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1088-3_0_5_line_3 |  | 2 | 4 | 0.01105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1088-3_0_5_line_4 |  | 3 | 5 | 0.016442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1088-3_0_5_line_5 |  | 4 | 6 | 0.041095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1088-3_0_5_line_6 |  | 5 | 27 | 0.020369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1088-3_0_5_line_7 |  | 5 | 26 | 0.016085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1088-3_0_5_line_8 |  | 7 | 8 | 0.037043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1088-3_0_5_line_9 |  | 8 | 9 | 0.005675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1088-3_0_5_line_10 |  | 8 | 10 | 0.05386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1088-3_0_5_line_11 |  | 9 | 11 | 0.03089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1088-3_0_5_line_12 |  | 9 | 12 | 0.010859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1088-3_0_5_line_13 |  | 11 | 13 | 0.012007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1088-3_0_5_line_14 |  | 12 | 14 | 0.0085175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1088-3_0_5_line_15 |  | 13 | 19 | 0.01544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1088-3_0_5_line_16 |  | 14 | 51 | 0.0067555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1088-3_0_5_line_17 |  | 15 | 16 | 0.024978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1088-3_0_5_line_18 |  | 15 | 17 | 0.1416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1088-3_0_5_line_19 |  | 15 | 18 | 0.011941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1088-3_0_5_line_20 |  | 16 | 65 | 0.010839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1088-3_0_5_line_21 |  | 17 | 63 | 0.12664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1088-3_0_5_line_22 |  | 18 | 61 | 0.006381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1088-3_0_5_line_23 |  | 18 | 57 | 0.030838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1088-3_0_5_line_24 |  | 19 | 20 | 0.014699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1088-3_0_5_line_25 |  | 20 | 21 | 0.012997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1088-3_0_5_line_26 |  | 21 | 22 | 0.01957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1088-3_0_5_line_27 |  | 22 | 23 | 0.0074173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1088-3_0_5_line_28 |  | 23 | 24 | 0.00038703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1088-3_0_5_line_29 |  | 24 | 25 | 0.024883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1088-3_0_5_line_30 |  | 25 | 26 | 0.0023633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1088-3_0_5_line_31 |  | 28 | 29 | 0.010022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1088-3_0_5_line_32 |  | 29 | 30 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1088-3_0_5_line_33 |  | 30 | 31 | 0.017744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1088-3_0_5_line_34 |  | 31 | 32 | 0.009691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1088-3_0_5_line_35 |  | 31 | 33 | 0.015233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1088-3_0_5_line_36 |  | 32 | 34 | 0.080787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1088-3_0_5_line_37 |  | 32 | 35 | 0.037866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1088-3_0_5_line_38 |  | 33 | 36 | 0.00030047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1088-3_0_5_line_39 |  | 35 | 42 | 0.0061876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1088-3_0_5_line_40 |  | 36 | 70 | 0.026363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1088-3_0_5_line_41 |  | 37 | 38 | 0.023153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1088-3_0_5_line_42 |  | 37 | 39 | 0.030963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1088-3_0_5_line_43 |  | 38 | 40 | 0.0024927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1088-3_0_5_line_44 |  | 40 | 41 | 0.019007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1088-3_0_5_line_45 |  | 41 | 42 | 0.021233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1088-3_0_5_line_46 |  | 41 | 43 | 0.03255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1088-3_0_5_line_47 |  | 42 | 44 | 0.016144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1088-3_0_5_line_48 |  | 43 | 45 | 0.017118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1088-3_0_5_line_49 |  | 44 | 46 | 0.0019564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1088-3_0_5_line_50 |  | 45 | 50 | 0.00011079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1088-3_0_5_line_51 |  | 46 | 71 | 0.025206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1088-3_0_5_line_52 |  | 47 | 48 | 0.044741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1088-3_0_5_line_53 |  | 47 | 49 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1088-3_0_5_line_54 |  | 48 | 61 | 0.016641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1088-3_0_5_line_55 |  | 49 | 104 | 0.0021728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1088-3_0_5_line_56 |  | 50 | 82 | 0.026569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1088-3_0_5_line_57 |  | 51 | 52 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1088-3_0_5_line_58 |  | 52 | 53 | 0.023781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1088-3_0_5_line_59 |  | 53 | 54 | 0.0084245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1088-3_0_5_line_60 |  | 53 | 55 | 0.031559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1088-3_0_5_line_61 |  | 54 | 56 | 0.009362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1088-3_0_5_line_62 |  | 55 | 57 | 0.0081893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1088-3_0_5_line_63 |  | 56 | 58 | 0.00050679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1088-3_0_5_line_64 |  | 58 | 59 | 0.010704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1088-3_0_5_line_65 |  | 59 | 60 | 0.0031488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1088-3_0_5_line_66 |  | 60 | 69 | 0.037227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1088-3_0_5_line_67 |  | 60 | 67 | 0.010921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1088-3_0_5_line_68 |  | 61 | 62 | 0.007475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1088-3_0_5_line_69 |  | 62 | 64 | 0.029052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1088-3_0_5_line_70 |  | 64 | 121 | 0.0045379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1088-3_0_5_line_71 |  | 65 | 127 | 0.010124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1088-3_0_5_line_72 |  | 66 | 67 | 0.011456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1088-3_0_5_line_73 |  | 66 | 68 | 0.0071084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1088-3_0_5_line_74 |  | 72 | 73 | 0.0080075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1088-3_0_5_line_75 |  | 72 | 74 | 0.018872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1088-3_0_5_line_76 |  | 74 | 75 | 0.003821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1088-3_0_5_line_77 |  | 75 | 76 | 0.032441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1088-3_0_5_line_78 |  | 76 | 77 | 0.033286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1088-3_0_5_line_79 |  | 77 | 78 | 0.063558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1088-3_0_5_line_80 |  | 77 | 85 | 0.019895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1088-3_0_5_line_81 |  | 79 | 80 | 0.0058751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1088-3_0_5_line_82 |  | 79 | 81 | 0.01045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1088-3_0_5_line_83 |  | 81 | 96 | 0.0072824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1088-3_0_5_line_84 |  | 82 | 83 | 0.0021519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1088-3_0_5_line_85 |  | 83 | 84 | 0.050524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1088-3_0_5_line_86 |  | 84 | 88 | 0.023014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1088-3_0_5_line_87 |  | 84 | 89 | 0.025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1088-3_0_5_line_88 |  | 85 | 86 | 0.0018572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1088-3_0_5_line_89 |  | 85 | 87 | 0.0085802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1088-3_0_5_line_90 |  | 86 | 99 | 0.019999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1088-3_0_5_line_91 |  | 87 | 100 | 0.03507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1088-3_0_5_line_92 |  | 88 | 90 | 0.0097623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_1088-3_0_5_line_93 |  | 89 | 91 | 0.00067819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1088-3_0_5_line_94 |  | 90 | 113 | 0.015286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_1088-3_0_5_line_95 |  | 92 | 93 | 0.050922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1088-3_0_5_line_96 |  | 93 | 94 | 0.011969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1088-3_0_5_line_97 |  | 94 | 95 | 0.03191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1088-3_0_5_line_98 |  | 95 | 101 | 0.032556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1088-3_0_5_line_99 |  | 95 | 102 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1088-3_0_5_line_100 |  | 96 | 97 | 0.0098167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1088-3_0_5_line_101 |  | 97 | 98 | 0.0073019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1088-3_0_5_line_102 |  | 98 | 99 | 0.0042802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1088-3_0_5_line_103 |  | 100 | 108 | 0.01851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1088-3_0_5_line_104 |  | 101 | 103 | 0.048392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1088-3_0_5_line_105 |  | 102 | 120 | 0.051699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1088-3_0_5_line_106 |  | 104 | 105 | 0.011936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_1088-3_0_5_line_107 |  | 105 | 106 | 0.0083399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_1088-3_0_5_line_108 |  | 106 | 107 | 0.053691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_1088-3_0_5_line_109 |  | 107 | 116 | 0.01421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_1088-3_0_5_line_110 |  | 108 | 109 | 0.004631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1088-3_0_5_line_111 |  | 109 | 117 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1088-3_0_5_line_112 |  | 109 | 111 | 0.003932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1088-3_0_5_line_113 |  | 110 | 111 | 0.0087977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1088-3_0_5_line_114 |  | 110 | 112 | 0.037424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1088-3_0_5_line_115 |  | 111 | 114 | 0.032501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1088-3_0_5_line_116 |  | 112 | 124 | 0.012128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1088-3_0_5_line_117 |  | 113 | 115 | 0.010521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_1088-3_0_5_line_118 |  | 115 | 116 | 0.00076377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_1088-3_0_5_line_119 |  | 117 | 119 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1088-3_0_5_line_120 |  | 118 | 119 | 0.002371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1088-3_0_5_line_121 |  | 118 | 120 | 0.01261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1088-3_0_5_line_122 |  | 121 | 122 | 0.045608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_1088-3_0_5_line_123 |  | 122 | 125 | 0.017459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_1088-3_0_5_line_124 |  | 122 | 126 | 0.0037549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1088-3_0_5_line_125 |  | 123 | 124 | 0.013959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_1088-3_0_5_line_126 |  | 123 | 125 | 0.042858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1088-3_0_5_trafo_80 | 0.63 MVA 20/0.4 kV | 128 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2659305.0472 | 1223050.3278 | 2659304.115 | 1223049.6661
1 | 2659305.0472 | 1223050.3278 | 2659318.9765 | 1223060.2164 | 2659327.2057 | 1223064.7123 | 2659332.4135 | 1223066.8065
2 | 2659350.5454 | 1222801.8797 | 2659304.115 | 1223049.6661
3 | 2659342.9824 | 1223069.9551 | 2659335.7111 | 1223068.1325 | 2659332.4135 | 1223066.8065
4 | 2659366.5916 | 1222798.2929 | 2659350.5454 | 1222801.8797
5 | 2659342.9824 | 1223069.9551 | 2659346.1509 | 1223070.7493 | 2659355.9033 | 1223072.3252 | 2659383.8059 | 1223073.951
6 | 2659366.5916 | 1222798.2929 | 2659360.7111 | 1222778.7888
7 | 2659366.5916 | 1222798.2929 | 2659372.3333 | 1222799.0062 | 2659382.4752 | 1222797.2137
8 | 2659526.0554 | 1222782.6856 | 2659511.7359 | 1222803.1999 | 2659506.0118 | 1222813.7756
9 | 2659526.0554 | 1222782.6856 | 2659520.7206 | 1222780.7089
10 | 2659526.0554 | 1222782.6856 | 2659532.4342 | 1222773.5436 | 2659560.557 | 1222741.3959
11 | 2659520.7206 | 1222780.7089 | 2659514.6604 | 1222778.4691 | 2659500.8864 | 1222776.2857 | 2659490.5634 | 1222778.1102
12 | 2659520.7206 | 1222780.7089 | 2659526.495 | 1222771.5123
13 | 2659478.7397 | 1222780.1999 | 2659490.5634 | 1222778.1102
14 | 2659531.0242 | 1222764.2988 | 2659526.495 | 1222771.5123
15 | 2659478.7397 | 1222780.1999 | 2659463.5357 | 1222782.8871
16 | 2659531.0242 | 1222764.2988 | 2659532.2504 | 1222762.3459 | 2659535.239 | 1222759.0495
17 | 2659614.4538 | 1222695.2481 | 2659617.907 | 1222700.3192 | 2659622.5925 | 1222718.5706
18 | 2659614.4538 | 1222695.2481 | 2659618.7011 | 1222692.2109 | 2659649.8706 | 1222673.5334 | 2659683.4675 | 1222656.348 | 2659712.9891 | 1222641.7014 | 2659722.1034 | 1222659.3149 | 2659729.5832 | 1222665.2047
19 | 2659613.6794 | 1222687.7467 | 2659618.7011 | 1222692.2109 | 2659614.4538 | 1222695.2481
20 | 2659622.5925 | 1222718.5706 | 2659625.2878 | 1222729.0696
21 | 2659729.5832 | 1222665.2047 | 2659725.0504 | 1222677.7894 | 2659717.9865 | 1222686.3795 | 2659707.8064 | 1222693.3708 | 2659684.4254 | 1222696.972 | 2659647.9828 | 1222696.1732 | 2659643.8445 | 1222697.4103 | 2659642.5202 | 1222701.6553 | 2659644.6085 | 1222705.9344 | 2659660.2611 | 1222709.9542
22 | 2659613.6794 | 1222687.7467 | 2659608.9059 | 1222683.4963
23 | 2659613.6794 | 1222687.7467 | 2659605.1437 | 1222694.132 | 2659589.1146 | 1222706.3889
24 | 2659449.061 | 1222785.4453 | 2659463.5357 | 1222782.8871
25 | 2659449.061 | 1222785.4453 | 2659436.2624 | 1222787.7074
26 | 2659416.9911 | 1222791.1134 | 2659436.2624 | 1222787.7074
27 | 2659416.9911 | 1222791.1134 | 2659409.6869 | 1222792.4043
28 | 2659409.6869 | 1222792.4043 | 2659409.3058 | 1222792.4717
29 | 2659409.3058 | 1222792.4717 | 2659384.8024 | 1222796.8024
30 | 2659382.4752 | 1222797.2137 | 2659384.8024 | 1222796.8024
31 | 2659358.7043 | 1222731.6792 | 2659357.2034 | 1222741.5878
32 | 2659359.9439 | 1222714.2517 | 2659360.6896 | 1222718.573 | 2659358.7043 | 1222731.6792
33 | 2659359.9439 | 1222714.2517 | 2659377.0793 | 1222709.4639
34 | 2659386.7023 | 1222708.1034 | 2659377.0793 | 1222709.4639
35 | 2659377.0793 | 1222709.4639 | 2659374.5101 | 1222694.4493
36 | 2659386.7023 | 1222708.1034 | 2659397.8849 | 1222767.0631 | 2659418.4632 | 1222763.8218
37 | 2659386.7023 | 1222708.1034 | 2659402.2919 | 1222706.9693 | 2659424.2613 | 1222703.5442
38 | 2659374.4594 | 1222694.1531 | 2659374.5101 | 1222694.4493
39 | 2659430.3751 | 1222702.5911 | 2659424.2613 | 1222703.5442
40 | 2659370.0129 | 1222668.1676 | 2659374.4594 | 1222694.1531
41 | 2659457.1805 | 1222743.4986 | 2659453.6518 | 1222727.6391 | 2659453.1083 | 1222720.7545
42 | 2659457.1805 | 1222743.4986 | 2659460.5764 | 1222758.7611 | 2659475.7797 | 1222756.8157
43 | 2659453.1083 | 1222720.7545 | 2659452.9122 | 1222718.2695
44 | 2659451.4165 | 1222699.3212 | 2659452.9122 | 1222718.2695
45 | 2659451.4165 | 1222699.3212 | 2659430.3751 | 1222702.5911
46 | 2659451.4165 | 1222699.3212 | 2659483.7342 | 1222694.7187
47 | 2659430.3751 | 1222702.5911 | 2659428.491 | 1222686.5571
48 | 2659483.7342 | 1222694.7187 | 2659482.6703 | 1222677.634
49 | 2659428.491 | 1222686.5571 | 2659428.2626 | 1222684.6141
50 | 2659482.6634 | 1222677.5235 | 2659482.6703 | 1222677.634
51 | 2659425.3209 | 1222659.5803 | 2659428.2626 | 1222684.6141
52 | 2659548.7456 | 1222685.8294 | 2659592.9344 | 1222678.8224
53 | 2659548.7456 | 1222685.8294 | 2659547.7019 | 1222671.9212
54 | 2659608.9059 | 1222683.4963 | 2659592.9344 | 1222678.8224
55 | 2659547.5392 | 1222669.7544 | 2659547.7019 | 1222671.9212
56 | 2659482.6634 | 1222677.5235 | 2659481.012 | 1222651.0057
57 | 2659543.2385 | 1222750.226 | 2659535.239 | 1222759.0495
58 | 2659559.5976 | 1222732.9675 | 2659546.645 | 1222746.4687 | 2659543.2385 | 1222750.226
59 | 2659559.5976 | 1222732.9675 | 2659551.902 | 1222729.5397
60 | 2659559.5976 | 1222732.9675 | 2659582.6733 | 1222711.4391
61 | 2659551.902 | 1222729.5397 | 2659543.3499 | 1222725.7305
62 | 2659582.6733 | 1222711.4391 | 2659583.4149 | 1222710.7473 | 2659589.1146 | 1222706.3889
63 | 2659543.3499 | 1222725.7305 | 2659542.887 | 1222725.5243
64 | 2659533.1091 | 1222721.1691 | 2659542.887 | 1222725.5243
65 | 2659530.2328 | 1222719.8879 | 2659533.1091 | 1222721.1691
66 | 2659530.2328 | 1222719.8879 | 2659519.0363 | 1222740.5668 | 2659510.1776 | 1222742.1015 | 2659507.4913 | 1222746.0327
67 | 2659530.2328 | 1222719.8879 | 2659519.4058 | 1222721.3199
68 | 2659613.2144 | 1222677.38 | 2659608.9059 | 1222683.4963
69 | 2659613.2144 | 1222677.38 | 2659612.3638 | 1222648.3406
70 | 2659612.2309 | 1222643.8046 | 2659612.3638 | 1222648.3406
71 | 2659627.8052 | 1222738.8758 | 2659625.2878 | 1222729.0696
72 | 2659508.0489 | 1222722.8219 | 2659519.4058 | 1222721.3199
73 | 2659501.0019 | 1222723.7539 | 2659508.0489 | 1222722.8219
74 | 2659400.4029 | 1222599.0827 | 2659399.0355 | 1222591.1928
75 | 2659395.813 | 1222572.5981 | 2659399.0355 | 1222591.1928
76 | 2659395.1604 | 1222568.8337 | 2659395.813 | 1222572.5981
77 | 2659395.1604 | 1222568.8337 | 2659427.2451 | 1222564.0396
78 | 2659460.1661 | 1222559.1206 | 2659427.2451 | 1222564.0396
79 | 2659460.1661 | 1222559.1206 | 2659458.1984 | 1222551.863 | 2659453.4322 | 1222544.5776 | 2659412.9392 | 1222520.069
80 | 2659460.1661 | 1222559.1206 | 2659477.0944 | 1222558.4113 | 2659476.9418 | 1222555.4635
81 | 2659420.3005 | 1222522.2358 | 2659425.3318 | 1222525.2693
82 | 2659434.2809 | 1222530.6651 | 2659425.3318 | 1222525.2693
83 | 2659434.2809 | 1222530.6651 | 2659435.0147 | 1222531.1075 | 2659440.5924 | 1222534.2976
84 | 2659481.012 | 1222651.0057 | 2659480.8783 | 1222648.858
85 | 2659480.8783 | 1222648.858 | 2659483.3565 | 1222598.3952
86 | 2659483.3565 | 1222598.3952 | 2659505.9621 | 1222594.0803
87 | 2659483.3565 | 1222598.3952 | 2659482.0091 | 1222598.6523 | 2659458.2835 | 1222600.9774
88 | 2659476.9418 | 1222555.4635 | 2659475.0906 | 1222555.316
89 | 2659476.9418 | 1222555.4635 | 2659479.4124 | 1222555.6661 | 2659485.5108 | 1222555.4748
90 | 2659458.9084 | 1222545.3216 | 2659463.5226 | 1222551.1157 | 2659465.7344 | 1222552.9278 | 2659468.7701 | 1222554.259 | 2659473.2738 | 1222555.1712 | 2659475.0906 | 1222555.316
91 | 2659485.5108 | 1222555.4748 | 2659512.2033 | 1222554.6374 | 2659520.5578 | 1222554.2338
92 | 2659515.5513 | 1222592.25 | 2659505.9621 | 1222594.0803
93 | 2659457.6086 | 1222601.0436 | 2659458.2835 | 1222600.9774
94 | 2659515.5513 | 1222592.25 | 2659521.673 | 1222596.7028 | 2659528.1344 | 1222596.7675 | 2659529.3746 | 1222596.5814
95 | 2659418.9408 | 1222455.3891 | 2659469.6926 | 1222451.2256
96 | 2659469.6926 | 1222451.2256 | 2659481.6219 | 1222450.247
97 | 2659513.4246 | 1222447.638 | 2659481.6219 | 1222450.247
98 | 2659506.8032 | 1222415.763 | 2659510.1537 | 1222431.8955 | 2659513.4246 | 1222447.638
99 | 2659515.5883 | 1222458.055 | 2659513.4246 | 1222447.638
100 | 2659449.1138 | 1222539.1714 | 2659440.5924 | 1222534.2976
101 | 2659449.1138 | 1222539.1714 | 2659455.4523 | 1222542.7966 | 2659455.4523 | 1222542.7966
102 | 2659458.9084 | 1222545.3216 | 2659458.9084 | 1222545.3216 | 2659455.4523 | 1222542.7966
103 | 2659538.8511 | 1222552.0465 | 2659532.6081 | 1222553.6518 | 2659520.5578 | 1222554.2338
104 | 2659506.8032 | 1222415.763 | 2659458.541 | 1222419.3078
105 | 2659515.5883 | 1222458.055 | 2659517.81 | 1222468.7395 | 2659525.562 | 1222483.1038 | 2659530.1915 | 1222507.1256
106 | 2659547.5392 | 1222669.7544 | 2659546.6459 | 1222657.8514
107 | 2659546.0218 | 1222649.5349 | 2659546.6459 | 1222657.8514
108 | 2659546.0218 | 1222649.5349 | 2659553.9782 | 1222596.4367
109 | 2659553.9782 | 1222596.4367 | 2659551.3595 | 1222594.3647 | 2659544.6023 | 1222594.2972 | 2659540.535 | 1222594.9073
110 | 2659538.8511 | 1222552.0465 | 2659543.3452 | 1222550.8796
111 | 2659543.3452 | 1222550.8796 | 2659541.635 | 1222548.2164 | 2659540.199 | 1222544.6776 | 2659538.5228 | 1222536.568
112 | 2659547.2836 | 1222550.6855 | 2659543.3452 | 1222550.8796
113 | 2659547.2836 | 1222550.6855 | 2659547.6 | 1222555.4472 | 2659547.8708 | 1222559.4635
114 | 2659547.8708 | 1222559.4635 | 2659551.7416 | 1222559.2021 | 2659566.0652 | 1222557.2885 | 2659584.8742 | 1222554.0029
115 | 2659547.2836 | 1222550.6855 | 2659551.3965 | 1222550.482 | 2659570.6113 | 1222547.9059 | 2659579.4704 | 1222546.3383
116 | 2659584.8742 | 1222554.0029 | 2659587.1949 | 1222553.5975 | 2659596.8246 | 1222551.9359
117 | 2659529.3746 | 1222596.5814 | 2659539.7797 | 1222595.0206
118 | 2659539.7797 | 1222595.0206 | 2659540.535 | 1222594.9073
119 | 2659534.9395 | 1222519.2312 | 2659538.5228 | 1222536.568
120 | 2659532.5779 | 1222519.5078 | 2659534.9395 | 1222519.2312
121 | 2659532.5779 | 1222519.5078 | 2659530.1915 | 1222507.1256
122 | 2659612.2309 | 1222643.8046 | 2659629.6726 | 1222601.6639
123 | 2659629.6726 | 1222601.6639 | 2659625.7609 | 1222601.469 | 2659621.9615 | 1222599.9078 | 2659619.145 | 1222597.1445 | 2659618.1726 | 1222591.742
124 | 2659629.6726 | 1222601.6639 | 2659629.6726 | 1222601.6639 | 2659633.3805 | 1222601.0717
125 | 2659610.5807 | 1222549.5623 | 2659596.8246 | 1222551.9359
126 | 2659610.5807 | 1222549.5623 | 2659618.1726 | 1222591.742

## bus_geodata
| x | y | coords
0 | 2659305.0472 | 1223050.3278
1 | 2659304.115 | 1223049.6661
2 | 2659332.4135 | 1223066.8065
3 | 2659350.5454 | 1222801.8797
4 | 2659342.9824 | 1223069.9551
5 | 2659366.5916 | 1222798.2929
6 | 2659383.8059 | 1223073.951
7 | 2659506.0118 | 1222813.7756
8 | 2659526.0554 | 1222782.6856
9 | 2659520.7206 | 1222780.7089
10 | 2659560.557 | 1222741.3959
11 | 2659490.5634 | 1222778.1102
12 | 2659526.495 | 1222771.5123
13 | 2659478.7397 | 1222780.1999
14 | 2659531.0242 | 1222764.2988
15 | 2659614.4538 | 1222695.2481
16 | 2659622.5925 | 1222718.5706
17 | 2659729.5832 | 1222665.2047
18 | 2659613.6794 | 1222687.7467
19 | 2659463.5357 | 1222782.8871
20 | 2659449.061 | 1222785.4453
21 | 2659436.2624 | 1222787.7074
22 | 2659416.9911 | 1222791.1134
23 | 2659409.6869 | 1222792.4043
24 | 2659409.3058 | 1222792.4717
25 | 2659384.8024 | 1222796.8024
26 | 2659382.4752 | 1222797.2137
27 | 2659360.7111 | 1222778.7888
28 | 2659357.2034 | 1222741.5878
29 | 2659358.7043 | 1222731.6792
30 | 2659359.9439 | 1222714.2517
31 | 2659377.0793 | 1222709.4639
32 | 2659386.7023 | 1222708.1034
33 | 2659374.5101 | 1222694.4493
34 | 2659418.4632 | 1222763.8218
35 | 2659424.2613 | 1222703.5442
36 | 2659374.4594 | 1222694.1531
37 | 2659457.1805 | 1222743.4986
38 | 2659453.1083 | 1222720.7545
39 | 2659475.7797 | 1222756.8157
40 | 2659452.9122 | 1222718.2695
41 | 2659451.4165 | 1222699.3212
42 | 2659430.3751 | 1222702.5911
43 | 2659483.7342 | 1222694.7187
44 | 2659428.491 | 1222686.5571
45 | 2659482.6703 | 1222677.634
46 | 2659428.2626 | 1222684.6141
47 | 2659548.7456 | 1222685.8294
48 | 2659592.9344 | 1222678.8224
49 | 2659547.7019 | 1222671.9212
50 | 2659482.6634 | 1222677.5235
51 | 2659535.239 | 1222759.0495
52 | 2659543.2385 | 1222750.226
53 | 2659559.5976 | 1222732.9675
54 | 2659551.902 | 1222729.5397
55 | 2659582.6733 | 1222711.4391
56 | 2659543.3499 | 1222725.7305
57 | 2659589.1146 | 1222706.3889
58 | 2659542.887 | 1222725.5243
59 | 2659533.1091 | 1222721.1691
60 | 2659530.2328 | 1222719.8879
61 | 2659608.9059 | 1222683.4963
62 | 2659613.2144 | 1222677.38
63 | 2659660.2611 | 1222709.9542
64 | 2659612.3638 | 1222648.3406
65 | 2659625.2878 | 1222729.0696
66 | 2659508.0489 | 1222722.8219
67 | 2659519.4058 | 1222721.3199
68 | 2659501.0019 | 1222723.7539
69 | 2659507.4913 | 1222746.0327
70 | 2659370.0129 | 1222668.1676
71 | 2659425.3209 | 1222659.5803
72 | 2659399.0355 | 1222591.1928
73 | 2659400.4029 | 1222599.0827
74 | 2659395.813 | 1222572.5981
75 | 2659395.1604 | 1222568.8337
76 | 2659427.2451 | 1222564.0396
77 | 2659460.1661 | 1222559.1206
78 | 2659412.9392 | 1222520.069
79 | 2659425.3318 | 1222525.2693
80 | 2659420.3005 | 1222522.2358
81 | 2659434.2809 | 1222530.6651
82 | 2659481.012 | 1222651.0057
83 | 2659480.8783 | 1222648.858
84 | 2659483.3565 | 1222598.3952
85 | 2659476.9418 | 1222555.4635
86 | 2659475.0906 | 1222555.316
87 | 2659485.5108 | 1222555.4748
88 | 2659505.9621 | 1222594.0803
89 | 2659458.2835 | 1222600.9774
90 | 2659515.5513 | 1222592.25
91 | 2659457.6086 | 1222601.0436
92 | 2659418.9408 | 1222455.3891
93 | 2659469.6926 | 1222451.2256
94 | 2659481.6219 | 1222450.247
95 | 2659513.4246 | 1222447.638
96 | 2659440.5924 | 1222534.2976
97 | 2659449.1138 | 1222539.1714
98 | 2659455.4523 | 1222542.7966
99 | 2659458.9084 | 1222545.3216
100 | 2659520.5578 | 1222554.2338
101 | 2659506.8032 | 1222415.763
102 | 2659515.5883 | 1222458.055
103 | 2659458.541 | 1222419.3078
104 | 2659547.5392 | 1222669.7544
105 | 2659546.6459 | 1222657.8514
106 | 2659546.0218 | 1222649.5349
107 | 2659553.9782 | 1222596.4367
108 | 2659538.8511 | 1222552.0465
109 | 2659543.3452 | 1222550.8796
110 | 2659547.8708 | 1222559.4635
111 | 2659547.2836 | 1222550.6855
112 | 2659584.8742 | 1222554.0029
113 | 2659529.3746 | 1222596.5814
114 | 2659579.4704 | 1222546.3383
115 | 2659539.7797 | 1222595.0206
116 | 2659540.535 | 1222594.9073
117 | 2659538.5228 | 1222536.568
118 | 2659532.5779 | 1222519.5078
119 | 2659534.9395 | 1222519.2312
120 | 2659530.1915 | 1222507.1256
121 | 2659612.2309 | 1222643.8046
122 | 2659629.6726 | 1222601.6639
123 | 2659610.5807 | 1222549.5623
124 | 2659596.8246 | 1222551.9359
125 | 2659618.1726 | 1222591.742
126 | 2659633.3805 | 1222601.0717
127 | 2659627.8052 | 1222738.8758
128 | 2659483.7342 | 1222694.7187

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97108 | -0.55872 | 0.0016145 | 0.00040463
1 | 0.97109 | -0.55839 | 0.0015501 | 0.0003885
2 | 0.97065 | -0.5671 | 0.0029257 | 0.00073324
3 | 0.97517 | -0.47812 | 0.0015068 | 0.00037764
4 | 0.97054 | -0.56939 | 0.0042152 | 0.0010564
5 | 0.97546 | -0.47245 | 0 | 0
6 | 0.97027 | -0.5747 | 0.0069873 | 0.0017512
7 | 0.97825 | -0.41765 | 0.0034695 | 0.00086953
8 | 0.97837 | -0.41531 | 0 | 0
9 | 0.9784 | -0.41461 | 0 | 0
10 | 0.97821 | -0.4185 | 0.00325 | 0.00081453
11 | 0.97787 | -0.42517 | 0.0046924 | 0.001176
12 | 0.97861 | -0.41057 | 0.0018232 | 0.00045693
13 | 0.97767 | -0.42902 | 0.0046943 | 0.0011765
14 | 0.97878 | -0.40733 | 0.0021536 | 0.00053974
15 | 0.98151 | -0.35393 | 0 | 0
16 | 0.98137 | -0.35674 | 0.0026343 | 0.00066021
17 | 0.98135 | -0.35706 | 0 | 0
18 | 0.98159 | -0.35232 | 0 | 0
19 | 0.97743 | -0.43365 | 0.0067928 | 0.0017024
20 | 0.97723 | -0.43759 | 0.015219 | 0.0038142
21 | 0.9771 | -0.44018 | 0.0038553 | 0.00096623
22 | 0.97674 | -0.44729 | 0.0035136 | 0.0008806
23 | 0.97649 | -0.45221 | 0.0051212 | 0.0012835
24 | 0.97648 | -0.45243 | 0.0035113 | 0.00088002
25 | 0.97583 | -0.46502 | 0.0028743 | 0.00072036
26 | 0.97578 | -0.46609 | 0.0031794 | 0.00079684
27 | 0.9754 | -0.47349 | 0.0027832 | 0.00069753
28 | 0.99356 | -0.12384 | 0.0013469 | 0.00033756
29 | 0.99357 | -0.1236 | 0.0018027 | 0.0004518
30 | 0.99362 | -0.12262 | 0 | 0
31 | 0.99367 | -0.12163 | 0 | 0
32 | 0.99378 | -0.11953 | 0 | 0
33 | 0.99355 | -0.12408 | 0.0026704 | 0.00066928
34 | 0.99347 | -0.12566 | 0.0042994 | 0.0010775
35 | 0.99436 | -0.10846 | 0.0042189 | 0.0010574
36 | 0.99355 | -0.12412 | 0.0032997 | 0.00082699
37 | 0.99492 | -0.09754 | 0.0042962 | 0.0010767
38 | 0.99518 | -0.092482 | 0.0042189 | 0.0010574
39 | 0.99469 | -0.10196 | 0.0081125 | 0.0020332
40 | 0.99522 | -0.091753 | 0.012728 | 0.0031901
41 | 0.99573 | -0.081938 | 0 | 0
42 | 0.99447 | -0.10619 | 0 | 0
43 | 0.99853 | -0.028161 | 0 | 0
44 | 0.99382 | -0.11874 | 0.0098144 | 0.0024597
45 | 1 | 0 | -0.43029 | -0.10977
46 | 0.99376 | -0.11992 | 0.0098018 | 0.0024566
47 | 0.98494 | -0.28727 | 0 | 0
48 | 0.98262 | -0.33232 | 0.0066526 | 0.0016673
49 | 0.98567 | -0.27327 | 0.0018293 | 0.00045848
50 | 0.99999 | -0.00015852 | 0.0098862 | 0.0024777
51 | 0.97891 | -0.4047 | 0.0018294 | 0.00045849
52 | 0.97915 | -0.39995 | 0.0022709 | 0.00056915
53 | 0.97965 | -0.39025 | 0 | 0
54 | 0.97944 | -0.39433 | 0.002201 | 0.00055162
55 | 0.9805 | -0.37356 | 0.0018083 | 0.00045319
56 | 0.97923 | -0.3985 | 0.0021417 | 0.00053677
57 | 0.98073 | -0.36916 | 0.0022341 | 0.00055992
58 | 0.97922 | -0.39871 | 0.0021446 | 0.00053749
59 | 0.97902 | -0.40264 | 0.0025829 | 0.00064734
60 | 0.97897 | -0.40365 | 0 | 0
61 | 0.98178 | -0.34863 | 0 | 0
62 | 0.98163 | -0.35163 | 0 | 0
63 | 0.98121 | -0.35985 | 0.0012138 | 0.00030422
64 | 0.98102 | -0.36332 | 0.0018914 | 0.00047403
65 | 0.98133 | -0.35744 | 0.0015303 | 0.00038352
66 | 0.97867 | -0.40942 | 0.0023975 | 0.00060087
67 | 0.97881 | -0.40674 | 0.0026926 | 0.00067483
68 | 0.9786 | -0.41077 | 0.010445 | 0.0026177
69 | 0.97889 | -0.40508 | 0.0021005 | 0.00052644
70 | 0.99347 | -0.12559 | 0.0031531 | 0.00079025
71 | 0.9932 | -0.13082 | 0.024471 | 0.0061331
72 | 0.97021 | -0.57554 | 0.0037788 | 0.00094706
73 | 0.97013 | -0.57721 | 0.011248 | 0.0028191
74 | 0.97048 | -0.57029 | 0 | 0
75 | 0.97053 | -0.56923 | 0 | 0
76 | 0.97099 | -0.56021 | 0.0051869 | 0.0012999
77 | 0.97162 | -0.54778 | 0 | 0
78 | 0.97147 | -0.5506 | 0.0024037 | 0.00060243
79 | 0.9716 | -0.54806 | 0.00029178 | 7.3127e-05
80 | 0.97159 | -0.54837 | 0.0028757 | 0.00072072
81 | 0.97163 | -0.54745 | 0.0016513 | 0.00041384
82 | 0.99803 | -0.037104 | 0.013195 | 0.003307
83 | 0.99788 | -0.039978 | 0.010654 | 0.0026701
84 | 0.99443 | -0.10534 | 0.0087947 | 0.0022042
85 | 0.97204 | -0.53947 | 0 | 0
86 | 0.97202 | -0.53989 | 0.0014479 | 0.00036289
87 | 0.97232 | -0.53396 | 0.0014479 | 0.00036289
88 | 0.993 | -0.13268 | 0.0041421 | 0.0010381
89 | 0.99405 | -0.11275 | 0.0061006 | 0.0015289
90 | 0.9924 | -0.14412 | 0 | 0
91 | 0.99404 | -0.11288 | 0.010567 | 0.0026484
92 | 0.97372 | -0.50641 | 0.00059643 | 0.00014948
93 | 0.97374 | -0.50585 | 0.00096713 | 0.00024238
94 | 0.97376 | -0.50551 | 0.00046629 | 0.00011686
95 | 0.97382 | -0.50432 | 0 | 0
96 | 0.97167 | -0.5468 | 0.0015084 | 0.00037805
97 | 0.97173 | -0.54566 | 0.0015079 | 0.00037792
98 | 0.97178 | -0.5446 | 0.0014677 | 0.00036784
99 | 0.97182 | -0.54386 | 0.0014698 | 0.00036838
100 | 0.97351 | -0.51052 | 0.0053636 | 0.0013442
101 | 0.9738 | -0.50477 | 0 | 0
102 | 0.97385 | -0.50377 | 0 | 0
103 | 0.97377 | -0.50545 | 0.00075957 | 0.00019037
104 | 0.98578 | -0.27107 | 0.004983 | 0.0012489
105 | 0.98642 | -0.25875 | 0.0084915 | 0.0021282
106 | 0.98688 | -0.24983 | 0.0057693 | 0.0014459
107 | 0.98993 | -0.19122 | 0.0094196 | 0.0023608
108 | 0.97423 | -0.49635 | 0 | 0
109 | 0.97441 | -0.4928 | 0 | 0
110 | 0.97512 | -0.47882 | 0 | 0
111 | 0.97462 | -0.48866 | 0 | 0
112 | 0.97725 | -0.43706 | 0.0035272 | 0.000884
113 | 0.99146 | -0.16206 | 0.0025398 | 0.00063653
114 | 0.97451 | -0.4908 | 0.0035912 | 0.00090005
115 | 0.99082 | -0.17431 | 0.0057183 | 0.0014331
116 | 0.99077 | -0.17518 | 0.0026125 | 0.00065475
117 | 0.97418 | -0.49722 | 0.0092672 | 0.0023226
118 | 0.97406 | -0.49961 | 0 | 0
119 | 0.97407 | -0.49933 | 0 | 0
120 | 0.97398 | -0.50111 | 0.0036889 | 0.00092453
121 | 0.98093 | -0.36511 | 0.007575 | 0.0018985
122 | 0.98009 | -0.38153 | 0.0022972 | 0.00057574
123 | 0.97842 | -0.41409 | 0 | 0
124 | 0.97797 | -0.42278 | 0.0038174 | 0.00095674
125 | 0.97979 | -0.38746 | 0.0065118 | 0.001632
126 | 0.98008 | -0.38169 | 0.002267 | 0.00056816
127 | 0.98131 | -0.35782 | 0.0020504 | 0.00051388
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015751 | -0.00395 | 0.015752 | 0.0039501 | 2.4977e-07 | 1.4571e-07 | 0.024137 | 0.024137 | 0.024137 | 0.97108 | -0.55872 | 0.97109 | -0.55839 | 6.6311
1 | 0.014137 | 0.0035453 | -0.014131 | -0.0035421 | 5.6444e-06 | 3.2158e-06 | 0.021663 | 0.021663 | 0.021663 | 0.97108 | -0.55872 | 0.97065 | -0.5671 | 5.9515
2 | -0.017302 | -0.0043386 | 0.017368 | 0.004378 | 6.6448e-05 | 3.9395e-05 | 0.026512 | 0.026511 | 0.026512 | 0.97109 | -0.55839 | 0.97517 | -0.47812 | 7.2836
3 | 0.011206 | 0.0028089 | -0.011204 | -0.0028082 | 1.2228e-06 | 6.4605e-07 | 0.017178 | 0.017178 | 0.017178 | 0.97065 | -0.5671 | 0.97054 | -0.56939 | 4.7193
4 | -0.018875 | -0.0047557 | 0.01888 | 0.0047587 | 5.1179e-06 | 3.0703e-06 | 0.028811 | 0.02881 | 0.028811 | 0.97517 | -0.47812 | 0.97546 | -0.47245 | 7.915
5 | 0.0069891 | 0.0017518 | -0.0069873 | -0.0017512 | 1.7696e-06 | 6.2483e-07 | 0.010716 | 0.010716 | 0.010716 | 0.97054 | -0.56939 | 0.97027 | -0.5747 | 2.9439
6 | 0.0027833 | 0.00069737 | -0.0027832 | -0.00069753 | 1.377e-07 | -1.6613e-07 | 0.0042458 | 0.0042459 | 0.0042459 | 0.97546 | -0.47245 | 0.9754 | -0.47349 | 1.1664
7 | -0.021663 | -0.0054561 | 0.02167 | 0.0054601 | 6.591e-06 | 4.0174e-06 | 0.033056 | 0.033056 | 0.033056 | 0.97546 | -0.47245 | 0.97578 | -0.46609 | 9.0814
8 | -0.0034695 | -0.00086953 | 0.0034699 | 0.00086931 | 3.8687e-07 | -2.1753e-07 | 0.0052774 | 0.0052772 | 0.0052774 | 0.97825 | -0.41765 | 0.97837 | -0.41531 | 1.4498
9 | -0.0067204 | -0.0016835 | 0.0067206 | 0.0016836 | 2.2231e-07 | 7.1013e-08 | 0.010221 | 0.010221 | 0.010221 | 0.97837 | -0.41531 | 0.9784 | -0.41461 | 2.8079
10 | 0.0032505 | 0.00081417 | -0.00325 | -0.00081453 | 4.9363e-07 | -3.6033e-07 | 0.0049436 | 0.0049438 | 0.0049438 | 0.97837 | -0.41531 | 0.97821 | -0.4185 | 1.3582
11 | 0.075246 | 0.01893 | -0.075208 | -0.018907 | 3.7942e-05 | 2.2732e-05 | 0.11446 | 0.11446 | 0.11446 | 0.9784 | -0.41461 | 0.97787 | -0.42517 | 7.8616
12 | -0.081966 | -0.020613 | 0.081982 | 0.020623 | 1.5827e-05 | 9.5835e-06 | 0.12468 | 0.12468 | 0.12468 | 0.9784 | -0.41461 | 0.97861 | -0.41057 | 8.5635
13 | 0.070515 | 0.017731 | -0.070502 | -0.017723 | 1.2966e-05 | 7.6958e-06 | 0.10732 | 0.10732 | 0.10732 | 0.97787 | -0.42517 | 0.97767 | -0.42902 | 7.3712
14 | -0.083805 | -0.02108 | 0.083818 | 0.021088 | 1.2972e-05 | 7.874e-06 | 0.12746 | 0.12746 | 0.12746 | 0.97861 | -0.41057 | 0.97878 | -0.40733 | 8.7539
15 | 0.065808 | 0.016547 | -0.065794 | -0.016538 | 1.4527e-05 | 8.5228e-06 | 0.10018 | 0.10018 | 0.10018 | 0.97767 | -0.42902 | 0.97743 | -0.43365 | 6.8805
16 | -0.085972 | -0.021628 | 0.085983 | 0.021634 | 1.0824e-05 | 6.5876e-06 | 0.13073 | 0.13073 | 0.13073 | 0.97878 | -0.40733 | 0.97891 | -0.4047 | 8.9788
17 | 0.0062159 | 0.0015577 | -0.0062151 | -0.0015575 | 8.3183e-07 | 2.1673e-07 | 0.0094236 | 0.0094237 | 0.0094237 | 0.98151 | -0.35393 | 0.98137 | -0.35674 | 2.5889
18 | 0.0012142 | 0.00030105 | -0.001214 | -0.00030272 | 1.7977e-07 | -1.6743e-06 | 0.0018396 | 0.0018402 | 0.0018402 | 0.98151 | -0.35393 | 0.98135 | -0.35706 | 0.50556
19 | -0.0074301 | -0.0018587 | 0.0074307 | 0.0018589 | 5.6804e-07 | 2.1262e-07 | 0.011263 | 0.011263 | 0.011263 | 0.98151 | -0.35393 | 0.98159 | -0.35232 | 3.0943
20 | 0.0035809 | 0.00089724 | -0.0035807 | -0.0008973 | 1.1983e-07 | -6.026e-08 | 0.0054295 | 0.0054295 | 0.0054295 | 0.98137 | -0.35674 | 0.98133 | -0.35744 | 1.4916
21 | 0.001214 | 0.00030272 | -0.0012138 | -0.00030422 | 1.6088e-07 | -1.4969e-06 | 0.0018402 | 0.0018408 | 0.0018408 | 0.98135 | -0.35706 | 0.98121 | -0.35985 | 0.50572
22 | -0.12856 | -0.03241 | 0.12858 | 0.032425 | 2.2736e-05 | 1.4229e-05 | 0.19495 | 0.19495 | 0.19495 | 0.98159 | -0.35232 | 0.98178 | -0.34863 | 13.3897
23 | 0.12113 | 0.030552 | -0.12103 | -0.030491 | 9.7551e-05 | 6.0875e-05 | 0.18369 | 0.18369 | 0.18369 | 0.98159 | -0.35232 | 0.98073 | -0.36916 | 12.6162
24 | 0.059001 | 0.014836 | -0.05899 | -0.01483 | 1.1122e-05 | 6.3814e-06 | 0.089839 | 0.089839 | 0.089839 | 0.97743 | -0.43365 | 0.97723 | -0.43759 | 6.1703
25 | 0.043771 | 0.011015 | -0.043766 | -0.011013 | 5.4153e-06 | 2.8145e-06 | 0.066666 | 0.066666 | 0.066666 | 0.97723 | -0.43759 | 0.9771 | -0.44018 | 4.5787
26 | 0.03991 | 0.010046 | -0.039897 | -0.010038 | 1.3562e-05 | 8.1897e-06 | 0.060795 | 0.060795 | 0.060795 | 0.9771 | -0.44018 | 0.97674 | -0.44729 | 8.351
27 | 0.036383 | 0.0091576 | -0.036375 | -0.0091522 | 8.5499e-06 | 5.3791e-06 | 0.055442 | 0.055442 | 0.055442 | 0.97674 | -0.44729 | 0.97649 | -0.45221 | 15.2314
28 | 0.031253 | 0.0078687 | -0.031253 | -0.0078685 | 3.2937e-07 | 2.0595e-07 | 0.047638 | 0.047638 | 0.047638 | 0.97649 | -0.45221 | 0.97648 | -0.45243 | 13.0874
29 | 0.027742 | 0.0069885 | -0.027725 | -0.0069781 | 1.6686e-05 | 1.0368e-05 | 0.042287 | 0.042287 | 0.042287 | 0.97648 | -0.45243 | 0.97583 | -0.46502 | 11.6174
30 | 0.024851 | 0.0062577 | -0.024849 | -0.0062569 | 1.2733e-06 | 7.8538e-07 | 0.037905 | 0.037905 | 0.037905 | 0.97583 | -0.46502 | 0.97578 | -0.46609 | 10.4134
31 | -0.0013469 | -0.00033756 | 0.0013469 | 0.00033744 | 1.5291e-08 | -1.2e-07 | 0.0020172 | 0.0020171 | 0.0020172 | 0.99356 | -0.12384 | 0.99357 | -0.1236 | 0.55416
32 | -0.0031496 | -0.00078924 | 0.0031498 | 0.00078911 | 1.4719e-07 | -1.3428e-07 | 0.0047169 | 0.0047169 | 0.0047169 | 0.99357 | -0.1236 | 0.99362 | -0.12262 | 1.2959
33 | -0.0031498 | -0.00078911 | 0.0031499 | 0.00078897 | 1.4804e-07 | -1.3509e-07 | 0.0047169 | 0.0047168 | 0.0047169 | 0.99362 | -0.12262 | 0.99367 | -0.12163 | 1.2958
34 | -0.012274 | -0.0030758 | 0.012276 | 0.0030764 | 1.2278e-06 | 6.6024e-07 | 0.018381 | 0.018381 | 0.018381 | 0.99367 | -0.12163 | 0.99378 | -0.11953 | 5.0496
35 | 0.0091246 | 0.0022868 | -0.0091235 | -0.0022863 | 1.0665e-06 | 4.8527e-07 | 0.013664 | 0.013664 | 0.013664 | 0.99367 | -0.12163 | 0.99355 | -0.12408 | 3.7538
36 | 0.0043007 | 0.0010773 | -0.0042994 | -0.0010775 | 1.2562e-06 | -2.424e-07 | 0.0064393 | 0.0064397 | 0.0064397 | 0.99378 | -0.11953 | 0.99347 | -0.12566 | 1.7691
37 | -0.016576 | -0.0041537 | 0.016585 | 0.0041588 | 8.7473e-06 | 5.1074e-06 | 0.02482 | 0.02482 | 0.02482 | 0.99378 | -0.11953 | 0.99436 | -0.10846 | 6.8187
38 | 0.0064531 | 0.001617 | -0.0064531 | -0.001617 | 1.0525e-08 | 2.8442e-09 | 0.0096645 | 0.0096645 | 0.0096645 | 0.99355 | -0.12408 | 0.99355 | -0.12412 | 2.6551
39 | -0.020804 | -0.0052162 | 0.020806 | 0.0052175 | 2.2491e-06 | 1.3591e-06 | 0.031133 | 0.031133 | 0.031133 | 0.99436 | -0.10846 | 0.99447 | -0.10619 | 8.5531
40 | 0.0031533 | 0.00079005 | -0.0031531 | -0.00079025 | 2.205e-07 | -2.0027e-07 | 0.0047226 | 0.0047227 | 0.0047227 | 0.99355 | -0.12412 | 0.99347 | -0.12559 | 1.2975
41 | -0.01241 | -0.0031106 | 0.012413 | 0.0031122 | 2.9913e-06 | 1.6137e-06 | 0.018561 | 0.018561 | 0.018561 | 0.99492 | -0.09754 | 0.99518 | -0.092482 | 5.0993
42 | 0.0081142 | 0.0020339 | -0.0081125 | -0.0020332 | 1.7101e-06 | 6.9245e-07 | 0.012136 | 0.012136 | 0.012136 | 0.99492 | -0.09754 | 0.99469 | -0.10196 | 3.3341
43 | -0.016632 | -0.0041696 | 0.016633 | 0.0041699 | 5.7815e-07 | 3.3763e-07 | 0.024869 | 0.024869 | 0.024869 | 0.99518 | -0.092482 | 0.99522 | -0.091753 | 6.8323
44 | -0.029361 | -0.00736 | 0.029375 | 0.0073685 | 1.3737e-05 | 8.5445e-06 | 0.043901 | 0.0439 | 0.043901 | 0.99522 | -0.091753 | 0.99573 | -0.081938 | 12.0606
45 | 0.06501 | 0.01634 | -0.064935 | -0.016293 | 7.5177e-05 | 4.7838e-05 | 0.097168 | 0.097168 | 0.097168 | 0.99573 | -0.081938 | 0.99447 | -0.10619 | 26.6944
46 | -0.094385 | -0.023709 | 0.094628 | 0.023864 | 0.00024291 | 0.00015504 | 0.14107 | 0.14107 | 0.14107 | 0.99573 | -0.081938 | 0.99853 | -0.028161 | 38.755
47 | 0.044129 | 0.011075 | -0.044102 | -0.011058 | 2.6399e-05 | 1.6686e-05 | 0.066035 | 0.066035 | 0.066035 | 0.99447 | -0.10619 | 0.99382 | -0.11874 | 18.1414
48 | -0.094628 | -0.023864 | 0.094756 | 0.023946 | 0.00012774 | 8.1531e-05 | 0.14107 | 0.14107 | 0.14107 | 0.99853 | -0.028161 | 1 | 0 | 38.7549
49 | 0.034288 | 0.0085987 | -0.034286 | -0.0085975 | 1.9337e-06 | 1.2122e-06 | 0.05134 | 0.05134 | 0.05134 | 0.99382 | -0.11874 | 0.99376 | -0.11992 | 14.1044
50 | 0.33388 | 0.08582 | -0.33388 | -0.085818 | 2.5715e-06 | 1.6399e-06 | 0.49758 | 0.49758 | 0.49758 | 1 | 0 | 0.99999 | -0.00015852 | 34.1744
51 | 0.024484 | 0.0061409 | -0.024471 | -0.0061331 | 1.2706e-05 | 7.8052e-06 | 0.036663 | 0.036663 | 0.036663 | 0.99376 | -0.11992 | 0.9932 | -0.13082 | 10.0723
52 | 0.22537 | 0.057156 | -0.22488 | -0.056846 | 0.00048694 | 0.00030937 | 0.34072 | 0.34072 | 0.34072 | 0.98494 | -0.28727 | 0.98262 | -0.33232 | 23.4014
53 | -0.22537 | -0.057156 | 0.22552 | 0.057252 | 0.0001518 | 9.644e-05 | 0.34072 | 0.34072 | 0.34072 | 0.98494 | -0.28727 | 0.98567 | -0.27327 | 23.4013
54 | 0.21823 | 0.055179 | -0.21806 | -0.055071 | 0.00017057 | 0.00010832 | 0.33065 | 0.33065 | 0.33065 | 0.98262 | -0.33232 | 0.98178 | -0.34863 | 22.7095
55 | -0.22735 | -0.057711 | 0.22738 | 0.057726 | 2.4033e-05 | 1.527e-05 | 0.34348 | 0.34348 | 0.34348 | 0.98567 | -0.27327 | 0.98578 | -0.27107 | 23.591
56 | 0.32399 | 0.08334 | -0.32341 | -0.08297 | 0.00058077 | 0.0003703 | 0.48287 | 0.48287 | 0.48287 | 0.99999 | -0.00015852 | 0.99803 | -0.037104 | 33.1641
57 | -0.087812 | -0.022093 | 0.087832 | 0.022105 | 1.9903e-05 | 1.2139e-05 | 0.13351 | 0.13351 | 0.13351 | 0.97891 | -0.4047 | 0.97915 | -0.39995 | 9.1697
58 | -0.090103 | -0.022674 | 0.090145 | 0.022699 | 4.1822e-05 | 2.5569e-05 | 0.13696 | 0.13696 | 0.13696 | 0.97915 | -0.39995 | 0.97965 | -0.39025 | 9.4067
59 | 0.026725 | 0.0067044 | -0.02672 | -0.0067012 | 5.2065e-06 | 3.2261e-06 | 0.040596 | 0.040596 | 0.040596 | 0.97965 | -0.39025 | 0.97944 | -0.39433 | 11.1528
60 | -0.11687 | -0.029404 | 0.11696 | 0.029462 | 9.3276e-05 | 5.8106e-05 | 0.17756 | 0.17756 | 0.17756 | 0.97965 | -0.39025 | 0.9805 | -0.37356 | 12.1949
61 | 0.024519 | 0.0061496 | -0.024514 | -0.0061466 | 4.872e-06 | 3.0003e-06 | 0.037252 | 0.037252 | 0.037252 | 0.97944 | -0.39433 | 0.97923 | -0.3985 | 10.2342
62 | -0.11877 | -0.029915 | 0.1188 | 0.029931 | 2.4959e-05 | 1.556e-05 | 0.1803 | 0.1803 | 0.1803 | 0.9805 | -0.37356 | 0.98073 | -0.36916 | 12.3834
63 | 0.022373 | 0.0056098 | -0.022372 | -0.0056097 | 2.1967e-07 | 1.3421e-07 | 0.033998 | 0.033998 | 0.033998 | 0.97923 | -0.3985 | 0.97922 | -0.39871 | 9.3401
64 | 0.020228 | 0.0050722 | -0.020224 | -0.0050699 | 3.7927e-06 | 2.2927e-06 | 0.030739 | 0.030739 | 0.030739 | 0.97922 | -0.39871 | 0.97902 | -0.40264 | 8.4448
65 | 0.017641 | 0.0044226 | -0.01764 | -0.0044221 | 8.4893e-07 | 5.0372e-07 | 0.026813 | 0.026813 | 0.026813 | 0.97902 | -0.40264 | 0.97897 | -0.40365 | 7.3663
66 | 0.0021007 | 0.00052607 | -0.0021005 | -0.00052644 | 1.4232e-07 | -3.7694e-07 | 0.0031929 | 0.003193 | 0.003193 | 0.97897 | -0.40365 | 0.97889 | -0.40508 | 0.8772
67 | 0.01554 | 0.003896 | -0.015537 | -0.0038947 | 2.285e-06 | 1.3251e-06 | 0.02362 | 0.02362 | 0.02362 | 0.97897 | -0.40365 | 0.97881 | -0.40674 | 6.4891
68 | 0.089479 | 0.022646 | -0.089466 | -0.022638 | 1.2904e-05 | 7.8804e-06 | 0.1357 | 0.1357 | 0.1357 | 0.98178 | -0.34863 | 0.98163 | -0.35163 | 9.3198
69 | 0.089466 | 0.022638 | -0.089416 | -0.022607 | 5.0152e-05 | 3.0629e-05 | 0.1357 | 0.1357 | 0.1357 | 0.98163 | -0.35163 | 0.98102 | -0.36332 | 9.3199
70 | 0.087525 | 0.022133 | -0.087517 | -0.022129 | 7.5059e-06 | 4.5746e-06 | 0.13283 | 0.13283 | 0.13283 | 0.98102 | -0.36332 | 0.98093 | -0.36511 | 9.1228
71 | 0.0020505 | 0.00051378 | -0.0020504 | -0.00051388 | 3.6701e-08 | -1.0442e-07 | 0.0031091 | 0.0031092 | 0.0031092 | 0.98133 | -0.35744 | 0.98131 | -0.35782 | 0.85417
72 | -0.012843 | -0.0032189 | 0.012845 | 0.0032198 | 1.6381e-06 | 9.0439e-07 | 0.019527 | 0.019527 | 0.019527 | 0.97867 | -0.40942 | 0.97881 | -0.40674 | 5.3646
73 | 0.010446 | 0.0026181 | -0.010445 | -0.0026177 | 6.7237e-07 | 3.41e-07 | 0.015882 | 0.015882 | 0.015882 | 0.97867 | -0.40942 | 0.9786 | -0.41077 | 4.3632
74 | 0.011249 | 0.0028196 | -0.011248 | -0.0028191 | 8.9384e-07 | 4.7318e-07 | 0.017253 | 0.017253 | 0.017253 | 0.97021 | -0.57554 | 0.97013 | -0.57721 | 4.7398
75 | -0.015028 | -0.0037666 | 0.015032 | 0.0037688 | 3.7595e-06 | 2.173e-06 | 0.023049 | 0.023048 | 0.023049 | 0.97021 | -0.57554 | 0.97048 | -0.57029 | 6.332
76 | -0.015032 | -0.0037688 | 0.015033 | 0.0037692 | 7.6119e-07 | 4.3995e-07 | 0.023048 | 0.023048 | 0.023048 | 0.97048 | -0.57029 | 0.97053 | -0.56923 | 6.332
77 | -0.015033 | -0.0037692 | 0.015039 | 0.003773 | 6.4626e-06 | 3.735e-06 | 0.023048 | 0.023048 | 0.023048 | 0.97053 | -0.56923 | 0.97099 | -0.56021 | 6.332
78 | -0.020226 | -0.0050729 | 0.020238 | 0.0050802 | 1.1993e-05 | 7.2637e-06 | 0.030997 | 0.030997 | 0.030997 | 0.97099 | -0.56021 | 0.97162 | -0.54778 | 8.5157
79 | 0.0024041 | 0.00060185 | -0.0024037 | -0.00060243 | 3.2307e-07 | -5.8029e-07 | 0.0036815 | 0.0036818 | 0.0036818 | 0.97162 | -0.54778 | 0.97147 | -0.5506 | 1.0115
80 | -0.022642 | -0.005682 | 0.022651 | 0.0056875 | 8.972e-06 | 5.4956e-06 | 0.034678 | 0.034678 | 0.034678 | 0.97162 | -0.54778 | 0.97204 | -0.53947 | 9.527
81 | 0.0028757 | 0.00072067 | -0.0028757 | -0.00072072 | 4.2734e-08 | -4.541e-08 | 0.0044042 | 0.0044042 | 0.0044042 | 0.9716 | -0.54806 | 0.97159 | -0.54837 | 1.2099
82 | -0.0031675 | -0.0007938 | 0.0031676 | 0.00079373 | 9.2217e-08 | -7.0405e-08 | 0.004851 | 0.004851 | 0.004851 | 0.9716 | -0.54806 | 0.97163 | -0.54745 | 1.3327
83 | -0.0048189 | -0.0012076 | 0.004819 | 0.0012076 | 1.4873e-07 | 4.9871e-09 | 0.0073798 | 0.0073798 | 0.0073798 | 0.97163 | -0.54745 | 0.97167 | -0.5468 | 2.0274
84 | 0.31022 | 0.079663 | -0.31017 | -0.079635 | 4.3283e-05 | 2.7589e-05 | 0.4632 | 0.4632 | 0.4632 | 0.99803 | -0.037104 | 0.99788 | -0.039978 | 31.8129
85 | 0.29952 | 0.076965 | -0.29857 | -0.076361 | 0.00094773 | 0.00060392 | 0.44731 | 0.44731 | 0.44731 | 0.99788 | -0.039978 | 0.99443 | -0.10534 | 30.7219
86 | 0.2731 | 0.069976 | -0.27274 | -0.069746 | 0.00036127 | 0.00023002 | 0.4092 | 0.4092 | 0.4092 | 0.99443 | -0.10534 | 0.993 | -0.13268 | 28.1045
87 | 0.016674 | 0.0041809 | -0.016668 | -0.0041774 | 5.8855e-06 | 3.4398e-06 | 0.024951 | 0.024951 | 0.024951 | 0.99443 | -0.10534 | 0.99405 | -0.11275 | 6.8546
88 | 0.012224 | 0.0030643 | -0.012224 | -0.0030641 | 2.4388e-07 | 1.3306e-07 | 0.018713 | 0.018713 | 0.018713 | 0.97204 | -0.53947 | 0.97202 | -0.53989 | 5.141
89 | -0.034875 | -0.0087518 | 0.034884 | 0.0087576 | 9.1722e-06 | 5.7638e-06 | 0.053392 | 0.053392 | 0.053392 | 0.97204 | -0.53947 | 0.97232 | -0.53396 | 14.668
90 | 0.010776 | 0.0027012 | -0.010774 | -0.0027002 | 2.0409e-06 | 1.0584e-06 | 0.016497 | 0.016497 | 0.016497 | 0.97202 | -0.53989 | 0.97182 | -0.54386 | 4.5321
91 | -0.036332 | -0.0091204 | 0.036373 | 0.009146 | 4.0666e-05 | 2.5591e-05 | 0.055607 | 0.055607 | 0.055607 | 0.97232 | -0.53396 | 0.97351 | -0.51052 | 15.2768
92 | 0.2686 | 0.068708 | -0.26845 | -0.068614 | 0.00014864 | 9.4622e-05 | 0.40299 | 0.40299 | 0.40299 | 0.993 | -0.13268 | 0.9924 | -0.14412 | 27.6782
93 | 0.010567 | 0.0026485 | -0.010567 | -0.0026484 | 6.3639e-08 | 3.1937e-08 | 0.015819 | 0.015819 | 0.015819 | 0.99405 | -0.11275 | 0.99404 | -0.11288 | 4.3458
94 | 0.26845 | 0.068614 | -0.26822 | -0.068465 | 0.00023273 | 0.00014816 | 0.40299 | 0.40299 | 0.40299 | 0.9924 | -0.14412 | 0.99146 | -0.16206 | 27.6782
95 | -0.00059643 | -0.00014948 | 0.00059644 | 0.00014886 | 1.586e-08 | -6.2328e-07 | 0.00091145 | 0.00091122 | 0.00091145 | 0.97372 | -0.50641 | 0.97374 | -0.50585 | 0.2504
96 | -0.0015636 | -0.00039124 | 0.0015636 | 0.00039111 | 2.5619e-08 | -1.325e-07 | 0.0023891 | 0.0023891 | 0.0023891 | 0.97374 | -0.50585 | 0.97376 | -0.50551 | 0.65635
97 | -0.0020299 | -0.00050797 | 0.00203 | 0.00050765 | 1.1511e-07 | -3.2331e-07 | 0.0031016 | 0.0031015 | 0.0031016 | 0.97376 | -0.50551 | 0.97382 | -0.50432 | 0.85209
98 | 0.00075961 | 0.00018939 | -0.0007596 | -0.00018978 | 1.6439e-08 | -3.9451e-07 | 0.0011603 | 0.0011605 | 0.0011605 | 0.97382 | -0.50432 | 0.9738 | -0.50477 | 0.31882
99 | -0.0027896 | -0.00069703 | 0.0027897 | 0.00069695 | 7.247e-08 | -8.6e-08 | 0.0042618 | 0.0042618 | 0.0042618 | 0.97382 | -0.50432 | 0.97385 | -0.50377 | 1.1708
100 | -0.0063275 | -0.0015856 | 0.0063278 | 0.0015857 | 3.4564e-07 | 9.961e-08 | 0.0096898 | 0.0096898 | 0.0096898 | 0.97167 | -0.5468 | 0.97173 | -0.54566 | 2.662
101 | -0.0078357 | -0.0019636 | 0.0078361 | 0.0019638 | 3.9423e-07 | 1.6185e-07 | 0.011999 | 0.011999 | 0.011999 | 0.97173 | -0.54566 | 0.97178 | -0.5446 | 3.2964
102 | -0.0093038 | -0.0023316 | 0.0093041 | 0.0023318 | 3.2576e-07 | 1.5545e-07 | 0.014246 | 0.014246 | 0.014246 | 0.97178 | -0.5446 | 0.97182 | -0.54386 | 3.9138
103 | -0.041736 | -0.01049 | 0.041765 | 0.010508 | 2.826e-05 | 1.7856e-05 | 0.063806 | 0.063806 | 0.063806 | 0.97351 | -0.51052 | 0.97423 | -0.49635 | 17.529
104 | 0.0007596 | 0.00018978 | -0.00075957 | -0.00019037 | 2.4444e-08 | -5.8637e-07 | 0.0011605 | 0.0011607 | 0.0011607 | 0.9738 | -0.50477 | 0.97377 | -0.50545 | 0.31888
105 | -0.0027897 | -0.00069695 | 0.00279 | 0.00069653 | 3.521e-07 | -4.1799e-07 | 0.0042618 | 0.0042615 | 0.0042618 | 0.97385 | -0.50377 | 0.97398 | -0.50111 | 1.1708
106 | -0.23236 | -0.058975 | 0.2325 | 0.059062 | 0.00013787 | 8.7629e-05 | 0.35101 | 0.35101 | 0.35101 | 0.98578 | -0.27107 | 0.98642 | -0.25875 | 24.1076
107 | -0.24099 | -0.061191 | 0.24109 | 0.061256 | 0.00010349 | 6.5807e-05 | 0.36382 | 0.36382 | 0.36382 | 0.98642 | -0.25875 | 0.98688 | -0.24983 | 24.9873
108 | -0.24686 | -0.062702 | 0.24756 | 0.063147 | 0.00069849 | 0.00044428 | 0.37251 | 0.37251 | 0.37251 | 0.98688 | -0.24983 | 0.98993 | -0.19122 | 25.5848
109 | -0.25698 | -0.065507 | 0.25718 | 0.065634 | 0.00019918 | 0.00012674 | 0.38667 | 0.38667 | 0.38667 | 0.98993 | -0.19122 | 0.99077 | -0.17518 | 26.5572
110 | -0.041765 | -0.010508 | 0.041772 | 0.010513 | 7.0701e-06 | 4.4672e-06 | 0.063806 | 0.063806 | 0.063806 | 0.97423 | -0.49635 | 0.97441 | -0.4928 | 17.529
111 | 0.015751 | 0.0039459 | -0.015747 | -0.003944 | 3.3117e-06 | 1.9294e-06 | 0.024052 | 0.024052 | 0.024052 | 0.97441 | -0.4928 | 0.97418 | -0.49722 | 6.6078
112 | -0.057522 | -0.014459 | 0.057534 | 0.014466 | 1.1382e-05 | 7.2353e-06 | 0.087858 | 0.087858 | 0.087858 | 0.97441 | -0.4928 | 0.97462 | -0.48866 | 24.1368
113 | 0.061154 | 0.015384 | -0.061125 | -0.015366 | 2.8744e-05 | 1.8286e-05 | 0.093341 | 0.093341 | 0.093341 | 0.97512 | -0.47882 | 0.97462 | -0.48866 | 25.6432
114 | -0.061154 | -0.015384 | 0.061276 | 0.015462 | 0.00012227 | 7.7787e-05 | 0.093341 | 0.093341 | 0.093341 | 0.97512 | -0.47882 | 0.97725 | -0.43706 | 25.6432
115 | 0.0035916 | 0.00089988 | -0.0035912 | -0.00090005 | 3.6648e-07 | -1.7043e-07 | 0.0054835 | 0.0054836 | 0.0054836 | 0.97462 | -0.48866 | 0.97451 | -0.4908 | 1.5065
116 | -0.064804 | -0.016346 | 0.064848 | 0.016374 | 4.4315e-05 | 2.821e-05 | 0.098712 | 0.098712 | 0.098712 | 0.97725 | -0.43706 | 0.97797 | -0.42278 | 27.1186
117 | 0.26568 | 0.067829 | -0.26552 | -0.067729 | 0.00015718 | 0.00010005 | 0.39918 | 0.39918 | 0.39918 | 0.99146 | -0.16206 | 0.99082 | -0.17431 | 27.4164
118 | 0.2598 | 0.066296 | -0.25979 | -0.066289 | 1.0924e-05 | 6.9521e-06 | 0.3906 | 0.3906 | 0.3906 | 0.99082 | -0.17431 | 0.99077 | -0.17518 | 26.8266
119 | 0.0064801 | 0.0016214 | -0.0064795 | -0.0016212 | 6.5029e-07 | 1.9579e-07 | 0.0098972 | 0.0098972 | 0.0098972 | 0.97418 | -0.49722 | 0.97407 | -0.49933 | 2.719
120 | -0.0064794 | -0.0016212 | 0.0064795 | 0.0016212 | 8.7095e-08 | 2.6227e-08 | 0.0098972 | 0.0098972 | 0.0098972 | 0.97406 | -0.49961 | 0.97407 | -0.49933 | 2.719
121 | 0.0064794 | 0.0016212 | -0.0064789 | -0.0016211 | 4.6321e-07 | 1.395e-07 | 0.0098972 | 0.0098973 | 0.0098973 | 0.97406 | -0.49961 | 0.97398 | -0.50111 | 2.719
122 | 0.079942 | 0.02023 | -0.079879 | -0.020192 | 6.2951e-05 | 3.7988e-05 | 0.12134 | 0.12134 | 0.12134 | 0.98093 | -0.36511 | 0.98009 | -0.38153 | 8.3337
123 | 0.075315 | 0.019049 | -0.075294 | -0.019036 | 2.1425e-05 | 1.2832e-05 | 0.11441 | 0.11441 | 0.11441 | 0.98009 | -0.38153 | 0.97979 | -0.38746 | 7.8578
124 | 0.002267 | 0.00056812 | -0.002267 | -0.00056816 | 1.6681e-08 | -3.6643e-08 | 0.0034418 | 0.0034419 | 0.0034419 | 0.98009 | -0.38153 | 0.98008 | -0.38169 | 0.94557
125 | 0.068694 | 0.017349 | -0.068665 | -0.017331 | 2.8593e-05 | 1.7949e-05 | 0.10452 | 0.10452 | 0.10452 | 0.97842 | -0.41409 | 0.97797 | -0.42278 | 14.3572
126 | -0.068694 | -0.017349 | 0.068782 | 0.017404 | 8.7786e-05 | 5.5105e-05 | 0.10452 | 0.10452 | 0.10452 | 0.97842 | -0.41409 | 0.97979 | -0.38746 | 14.3571

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43726 | 0.11151

## res_load
| p_mw | q_mvar
0 | 0.0016145 | 0.00040463
1 | 0.0015501 | 0.0003885
2 | 0.0029257 | 0.00073324
3 | 0.0015068 | 0.00037764
4 | 0.0042152 | 0.0010564
5 | 0.0069873 | 0.0017512
6 | 0.0034695 | 0.00086953
7 | 0.00325 | 0.00081453
8 | 0.0046924 | 0.001176
9 | 0.0018232 | 0.00045693
10 | 0.0046943 | 0.0011765
11 | 0.0021536 | 0.00053974
12 | 0.0026343 | 0.00066021
13 | 0.0067928 | 0.0017024
14 | 0.015219 | 0.0038142
15 | 0.0038553 | 0.00096623
16 | 0.0035136 | 0.0008806
17 | 0.0051212 | 0.0012835
18 | 0.0035113 | 0.00088002
19 | 0.0028743 | 0.00072036
20 | 0.0031794 | 0.00079684
21 | 0.0027832 | 0.00069753
22 | 0.0013469 | 0.00033756
23 | 0.0018027 | 0.0004518
24 | 0.0026704 | 0.00066928
25 | 0.0042994 | 0.0010775
26 | 0.0042189 | 0.0010574
27 | 0.0032997 | 0.00082699
28 | 0.0042962 | 0.0010767
29 | 0.0042189 | 0.0010574
30 | 0.0081125 | 0.0020332
31 | 0.012728 | 0.0031901
32 | 0.0098144 | 0.0024597
33 | 0.0069725 | 0.0017475
34 | 0.0098018 | 0.0024566
35 | 0.0066526 | 0.0016673
36 | 0.0018293 | 0.00045848
37 | 0.0098862 | 0.0024777
38 | 0.0018294 | 0.00045849
39 | 0.0022709 | 0.00056915
40 | 0.002201 | 0.00055162
41 | 0.0018083 | 0.00045319
42 | 0.0021417 | 0.00053677
43 | 0.0022341 | 0.00055992
44 | 0.0021446 | 0.00053749
45 | 0.0025829 | 0.00064734
46 | 0.0012138 | 0.00030422
47 | 0.0018914 | 0.00047403
48 | 0.0015303 | 0.00038352
49 | 0.0023975 | 0.00060087
50 | 0.0026926 | 0.00067483
51 | 0.010445 | 0.0026177
52 | 0.0021005 | 0.00052644
53 | 0.0031531 | 0.00079025
54 | 0.024471 | 0.0061331
55 | 0.0037788 | 0.00094706
56 | 0.011248 | 0.0028191
57 | 0.0051869 | 0.0012999
58 | 0.0024037 | 0.00060243
59 | 0.00029178 | 7.3127e-05
60 | 0.0028757 | 0.00072072
61 | 0.0016513 | 0.00041384
62 | 0.013195 | 0.003307
63 | 0.010654 | 0.0026701
64 | 0.0087947 | 0.0022042
65 | 0.0014479 | 0.00036289
66 | 0.0014479 | 0.00036289
67 | 0.0041421 | 0.0010381
68 | 0.0061006 | 0.0015289
69 | 0.010567 | 0.0026484
70 | 0.00059643 | 0.00014948
71 | 0.00096713 | 0.00024238
72 | 0.00046629 | 0.00011686
73 | 0.0015084 | 0.00037805
74 | 0.0015079 | 0.00037792
75 | 0.0014677 | 0.00036784
76 | 0.0014698 | 0.00036838
77 | 0.0053636 | 0.0013442
78 | 0.00075957 | 0.00019037
79 | 0.004983 | 0.0012489
80 | 0.0084915 | 0.0021282
81 | 0.0057693 | 0.0014459
82 | 0.0094196 | 0.0023608
83 | 0.0035272 | 0.000884
84 | 0.0025398 | 0.00063653
85 | 0.0035912 | 0.00090005
86 | 0.0057183 | 0.0014331
87 | 0.0026125 | 0.00065475
88 | 0.0092672 | 0.0023226
89 | 0.0036889 | 0.00092453
90 | 0.007575 | 0.0018985
91 | 0.0022972 | 0.00057574
92 | 0.0038174 | 0.00095674
93 | 0.0065118 | 0.001632
94 | 0.002267 | 0.00056816
95 | 0.0020504 | 0.00051388

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1