## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1093-10_1_3_node_26 | 0.4 | n |  | TRUE
1 | bus_LV_1093-10_1_3_node_51 | 0.4 | n |  | TRUE
2 | bus_LV_1093-10_1_3_node_30 | 0.4 | n |  | TRUE
3 | bus_LV_1093-10_1_3_node_49 | 0.4 | n |  | TRUE
4 | bus_LV_1093-10_1_3_node_48 | 0.4 | n |  | TRUE
5 | bus_LV_1093-10_1_3_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_1093-10_1_3_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_1093-10_1_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_1093-10_1_3_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_1093-10_1_3_node_90 | 0.4 | n |  | TRUE
10 | bus_LV_1093-10_1_3_node_88 | 0.4 | n |  | TRUE
11 | bus_LV_1093-10_1_3_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_1093-10_1_3_node_214 | 0.4 | n |  | TRUE
13 | bus_LV_1093-10_1_3_node_55 | 0.4 | n |  | TRUE
14 | bus_LV_1093-10_1_3_node_212 | 0.4 | n |  | TRUE
15 | bus_LV_1093-10_1_3_node_210 | 0.4 | n |  | TRUE
16 | bus_LV_1093-10_1_3_node_203 | 0.4 | n |  | TRUE
17 | bus_LV_1093-10_1_3_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_1093-10_1_3_node_253 | 0.4 | n |  | TRUE
19 | bus_LV_1093-10_1_3_node_252 | 0.4 | n |  | TRUE
20 | bus_LV_1093-10_1_3_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1093-10_1_3_node_266 | 0.4 | n |  | TRUE
22 | bus_LV_1093-10_1_3_node_89 | 0.4 | n |  | TRUE
23 | bus_LV_1093-10_1_3_node_54 | 0.4 | n |  | TRUE
24 | bus_LV_1093-10_1_3_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_1093-10_1_3_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_1093-10_1_3_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_1093-10_1_3_node_208 | 0.4 | n |  | TRUE
28 | bus_LV_1093-10_1_3_node_216 | 0.4 | n |  | TRUE
29 | bus_LV_1093-10_1_3_node_207 | 0.4 | n |  | TRUE
30 | bus_LV_1093-10_1_3_node_204 | 0.4 | n |  | TRUE
31 | bus_LV_1093-10_1_3_node_60 | 0.4 | n |  | TRUE
32 | bus_LV_1093-10_1_3_node_61 | 0.4 | n |  | TRUE
33 | bus_LV_1093-10_1_3_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_1093-10_1_3_node_63 | 0.4 | n |  | TRUE
35 | bus_LV_1093-10_1_3_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1093-10_1_3_node_80 | 0.4 | n |  | TRUE
37 | bus_LV_1093-10_1_3_node_115 | 0.4 | n |  | TRUE
38 | bus_LV_1093-10_1_3_node_81 | 0.4 | n |  | TRUE
39 | bus_LV_1093-10_1_3_node_150 | 0.4 | n |  | TRUE
40 | bus_LV_1093-10_1_3_node_72 | 0.4 | n |  | TRUE
41 | bus_LV_1093-10_1_3_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_1093-10_1_3_node_74 | 0.4 | n |  | TRUE
43 | bus_LV_1093-10_1_3_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_1093-10_1_3_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_1093-10_1_3_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_1093-10_1_3_node_155 | 0.4 | n |  | TRUE
47 | bus_LV_1093-10_1_3_node_157 | 0.4 | n |  | TRUE
48 | bus_LV_1093-10_1_3_node_158 | 0.4 | n |  | TRUE
49 | bus_LV_1093-10_1_3_node_153 | 0.4 | n |  | TRUE
50 | bus_LV_1093-10_1_3_node_159 | 0.4 | n |  | TRUE
51 | bus_LV_1093-10_1_3_node_77 | 0.4 | n |  | TRUE
52 | bus_LV_1093-10_1_3_node_156 | 0.4 | n |  | TRUE
53 | bus_LV_1093-10_1_3_node_79 | 0.4 | n |  | TRUE
54 | bus_LV_1093-10_1_3_node_177 | 0.4 | n |  | TRUE
55 | bus_LV_1093-10_1_3_node_251 | 0.4 | n |  | TRUE
56 | bus_LV_1093-10_1_3_node_178 | 0.4 | n |  | TRUE
57 | bus_LV_1093-10_1_3_node_176 | 0.4 | n |  | TRUE
58 | bus_LV_1093-10_1_3_node_249 | 0.4 | n |  | TRUE
59 | bus_LV_1093-10_1_3_node_133 | 0.4 | n |  | TRUE
60 | bus_LV_1093-10_1_3_node_222 | 0.4 | n |  | TRUE
61 | bus_LV_1093-10_1_3_node_223 | 0.4 | n |  | TRUE
62 | bus_LV_1093-10_1_3_node_194 | 0.4 | n |  | TRUE
63 | bus_LV_1093-10_1_3_node_196 | 0.4 | n |  | TRUE
64 | bus_LV_1093-10_1_3_node_134 | 0.4 | n |  | TRUE
65 | bus_LV_1093-10_1_3_node_135 | 0.4 | n |  | TRUE
66 | bus_LV_1093-10_1_3_node_136 | 0.4 | n |  | TRUE
67 | bus_LV_1093-10_1_3_node_144 | 0.4 | n |  | TRUE
68 | bus_LV_1093-10_1_3_node_145 | 0.4 | n |  | TRUE
69 | bus_LV_1093-10_1_3_node_146 | 0.4 | n |  | TRUE
70 | bus_LV_1093-10_1_3_node_147 | 0.4 | n |  | TRUE
71 | bus_LV_1093-10_1_3_node_148 | 0.4 | n |  | TRUE
72 | bus_LV_1093-10_1_3_node_149 | 0.4 | n |  | TRUE
73 | bus_LV_1093-10_1_3_node_154 | 0.4 | n |  | TRUE
74 | bus_LV_1093-10_1_3_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_1093-10_1_3_node_152 | 0.4 | n |  | TRUE
76 | bus_LV_1093-10_1_3_node_192 | 0.4 | n |  | TRUE
77 | bus_LV_1093-10_1_3_node_193 | 0.4 | n |  | TRUE
78 | bus_LV_1093-10_1_3_node_197 | 0.4 | n |  | TRUE
79 | bus_LV_1093-10_1_3_node_221 | 0.4 | n |  | TRUE
80 | bus_LV_1093-10_1_3_node_219 | 0.4 | n |  | TRUE
81 | bus_LV_1093-10_1_3_node_218 | 0.4 | n |  | TRUE
82 | bus_LV_1093-10_1_3_node_195 | 0.4 | n |  | TRUE
83 | bus_LV_1093-10_1_3_node_243 | 0.4 | n |  | TRUE
84 | bus_LV_1093-10_1_3_node_213 | 0.4 | n |  | TRUE
85 | bus_LV_1093-10_1_3_node_220 | 0.4 | n |  | TRUE
86 | bus_LV_1093-10_1_3_node_231 | 0.4 | n |  | TRUE
87 | bus_LV_1093-10_1_3_node_235 | 0.4 | n |  | TRUE
88 | bus_LV_1093-10_1_3_node_234 | 0.4 | n |  | TRUE
89 | bus_LV_1093-10_1_3_node_236 | 0.4 | n |  | TRUE
90 | bus_LV_1093-10_1_3_node_217 | 0.4 | n |  | TRUE
91 | bus_LV_1093-10_1_3_node_215 | 0.4 | n |  | TRUE
92 | bus_LV_1093-10_1_3_node_211 | 0.4 | n |  | TRUE
93 | bus_LV_1093-10_1_3_node_228 | 0.4 | n |  | TRUE
94 | bus_LV_1093-10_1_3_node_248 | 0.4 | n |  | TRUE
95 | bus_LV_1093-10_1_3_node_233 | 0.4 | n |  | TRUE
96 | bus_LV_1093-10_1_3_node_200 | 0.4 | n |  | TRUE
97 | bus_LV_1093-10_1_3_node_201 | 0.4 | n |  | TRUE
98 | bus_LV_1093-10_1_3_node_202 | 0.4 | n |  | TRUE
99 | bus_LV_1093-10_1_3_node_205 | 0.4 | n |  | TRUE
100 | bus_LV_1093-10_1_3_node_206 | 0.4 | n |  | TRUE
101 | bus_LV_1093-10_1_3_node_225 | 0.4 | n |  | TRUE
102 | bus_LV_1093-10_1_3_node_267 | 0.4 | n |  | TRUE
103 | bus_LV_1093-10_1_3_node_268 | 0.4 | n |  | TRUE
104 | bus_LV_1093-10_1_3_node_209 | 0.4 | n |  | TRUE
105 | bus_LV_1093-10_1_3_node_238 | 0.4 | n |  | TRUE
106 | bus_LV_1093-10_1_3_node_237 | 0.4 | n |  | TRUE
107 | bus_LV_1093-10_1_3_node_224 | 0.4 | n |  | TRUE
108 | bus_LV_1093-10_1_3_node_226 | 0.4 | n |  | TRUE
109 | bus_LV_1093-10_1_3_node_227 | 0.4 | n |  | TRUE
110 | bus_LV_1093-10_1_3_node_229 | 0.4 | n |  | TRUE
111 | bus_LV_1093-10_1_3_node_230 | 0.4 | n |  | TRUE
112 | bus_LV_1093-10_1_3_node_247 | 0.4 | n |  | TRUE
113 | bus_LV_1093-10_1_3_node_258 | 0.4 | n |  | TRUE
114 | bus_LV_1093-10_1_3_node_232 | 0.4 | n |  | TRUE
115 | bus_LV_1093-10_1_3_node_240 | 0.4 | n |  | TRUE
116 | bus_LV_1093-10_1_3_node_242 | 0.4 | n |  | TRUE
117 | bus_LV_1093-10_1_3_node_239 | 0.4 | n |  | TRUE
118 | bus_LV_1093-10_1_3_node_241 | 0.4 | n |  | TRUE
119 | bus_LV_1093-10_1_3_node_245 | 0.4 | n |  | TRUE
120 | bus_LV_1093-10_1_3_node_244 | 0.4 | n |  | TRUE
121 | bus_LV_1093-10_1_3_node_246 | 0.4 | n |  | TRUE
122 | bus_LV_1093-10_1_3_node_257 | 0.4 | n |  | TRUE
123 | bus_LV_1093-10_1_3_node_250 | 0.4 | n |  | TRUE
124 | bus_LV_1093-10_1_3_node_265 | 0.4 | n |  | TRUE
125 | bus_LV_1093-10_1_3_node_263 | 0.4 | n |  | TRUE
126 | bus_LV_1093-10_1_3_node_254 | 0.4 | n |  | TRUE
127 | bus_LV_1093-10_1_3_node_255 | 0.4 | n |  | TRUE
128 | bus_LV_1093-10_1_3_node_256 | 0.4 | n |  | TRUE
129 | bus_LV_1093-10_1_3_node_259 | 0.4 | n |  | TRUE
130 | bus_LV_1093-10_1_3_node_260 | 0.4 | n |  | TRUE
131 | bus_LV_1093-10_1_3_node_261 | 0.4 | n |  | TRUE
132 | bus_LV_1093-10_1_3_node_262 | 0.4 | n |  | TRUE
133 | bus_LV_1093-10_1_3_node_264 | 0.4 | n |  | TRUE
134 | bus_MV_3_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1093-10_1_3_load_51 | 1 | 0.017471 | 0.0043788 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1093-10_1_3_load_49 | 3 | 0.0063701 | 0.0015965 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1093-10_1_3_load_48 | 4 | 0.0075623 | 0.0018953 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1093-10_1_3_load_47 | 5 | 0.01368 | 0.0034286 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1093-10_1_3_load_90 | 9 | 0.012005 | 0.0030088 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1093-10_1_3_load_88 | 10 | 0.0083873 | 0.0021021 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1093-10_1_3_load_55 | 13 | 0.004501 | 0.0011281 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1093-10_1_3_load_212 | 14 | 0.0052577 | 0.0013177 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1093-10_1_3_load_210 | 15 | 0.0057644 | 0.0014447 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1093-10_1_3_load_203 | 16 | 0.004866 | 0.0012195 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1093-10_1_3_load_52 | 17 | 0.0087678 | 0.0021974 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1093-10_1_3_load_253 | 18 | 0.0015997 | 0.00040093 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1093-10_1_3_load_252 | 19 | 0.017471 | 0.0043788 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1093-10_1_3_load_266 | 21 | 0.0016006 | 0.00040116 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1093-10_1_3_load_89 | 22 | 0.0094883 | 0.002378 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1093-10_1_3_load_54 | 23 | 0.0049808 | 0.0012483 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1093-10_1_3_load_58 | 25 | 0.0040711 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1093-10_1_3_load_59 | 26 | 0.0010495 | 0.00026304 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1093-10_1_3_load_208 | 27 | 0.0043931 | 0.001101 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1093-10_1_3_load_216 | 28 | 0.00040706 | 0.00010202 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1093-10_1_3_load_207 | 29 | 0.0054242 | 0.0013594 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1093-10_1_3_load_204 | 30 | 0.00068388 | 0.0001714 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1093-10_1_3_load_60 | 31 | 0.00069255 | 0.00017357 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1093-10_1_3_load_61 | 32 | 0.00011835 | 2.9661e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1093-10_1_3_load_62 | 33 | 0.00010728 | 2.6888e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1093-10_1_3_load_63 | 34 | 0.00012087 | 3.0292e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1093-10_1_3_load_115 | 37 | 8.6645e-05 | 2.1715e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1093-10_1_3_load_150 | 39 | 0.00010378 | 2.601e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1093-10_1_3_load_72 | 40 | 8.424e-05 | 2.1113e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1093-10_1_3_load_73 | 41 | 3.8178e-05 | 9.5683e-06 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1093-10_1_3_load_75 | 43 | 0.00010548 | 2.6437e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1093-10_1_3_load_155 | 46 | 5.2247e-05 | 1.3094e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1093-10_1_3_load_157 | 47 | 0.00017437 | 4.3702e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1093-10_1_3_load_159 | 50 | 0.00010673 | 2.6748e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1093-10_1_3_load_77 | 51 | 0.00028522 | 7.1483e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1093-10_1_3_load_156 | 52 | 0.00012984 | 3.2542e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1093-10_1_3_load_79 | 53 | 9.6387e-05 | 2.4157e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1093-10_1_3_load_251 | 55 | 0.00057111 | 0.00014313 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1093-10_1_3_load_178 | 56 | 0.00060419 | 0.00015142 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1093-10_1_3_load_176 | 57 | 0.0019682 | 0.00049329 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1093-10_1_3_load_133 | 59 | 0.0008898 | 0.000223 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1093-10_1_3_load_223 | 61 | 0.0021521 | 0.00053936 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1093-10_1_3_load_134 | 64 | 0.0028432 | 0.00071258 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1093-10_1_3_load_135 | 65 | 0.00088303 | 0.00022131 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1093-10_1_3_load_136 | 66 | 0.00044592 | 0.00011176 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1093-10_1_3_load_144 | 67 | 0.00013744 | 3.4445e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1093-10_1_3_load_145 | 68 | 0.00010439 | 2.6162e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1093-10_1_3_load_147 | 70 | 0.00028394 | 7.1162e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1093-10_1_3_load_148 | 71 | 9.9706e-05 | 2.4989e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1093-10_1_3_load_149 | 72 | 0.00015824 | 3.966e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1093-10_1_3_load_154 | 73 | 8.8722e-05 | 2.2236e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1093-10_1_3_load_151 | 74 | 0.0002195 | 5.5011e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1093-10_1_3_load_152 | 75 | 6.0901e-05 | 1.5263e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1093-10_1_3_load_221 | 79 | 0.002066 | 0.00051778 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1093-10_1_3_load_219 | 80 | 0.0034808 | 0.00087238 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1093-10_1_3_load_218 | 81 | 0.0017849 | 0.00044734 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1093-10_1_3_load_243 | 83 | 0.0085793 | 0.0021502 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1093-10_1_3_load_220 | 85 | 0.010727 | 0.0026884 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1093-10_1_3_load_231 | 86 | 0.0028275 | 0.00070865 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1093-10_1_3_load_235 | 87 | 0.0016114 | 0.00040385 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1093-10_1_3_load_234 | 88 | 0.0021632 | 0.00054216 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1093-10_1_3_load_236 | 89 | 0.0044844 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1093-10_1_3_load_217 | 90 | 0.0013707 | 0.00034354 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1093-10_1_3_load_215 | 91 | 0.00095589 | 0.00023957 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1093-10_1_3_load_211 | 92 | 0.0017694 | 0.00044345 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1093-10_1_3_load_248 | 94 | 0.00093724 | 0.00023489 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1093-10_1_3_load_233 | 95 | 0.0019032 | 0.00047699 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1093-10_1_3_load_200 | 96 | 0.00038619 | 9.6789e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1093-10_1_3_load_201 | 97 | 0.00055921 | 0.00014015 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1093-10_1_3_load_205 | 99 | 0.0017637 | 0.00044203 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1093-10_1_3_load_225 | 101 | 0.0024561 | 0.00061555 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1093-10_1_3_load_268 | 103 | 0.0015999 | 0.00040097 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1093-10_1_3_load_209 | 104 | 0.0051846 | 0.0012994 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1093-10_1_3_load_238 | 105 | 0.001709 | 0.00042833 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1093-10_1_3_load_237 | 106 | 0.0036672 | 0.00091909 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1093-10_1_3_load_224 | 107 | 0.001931 | 0.00048396 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1093-10_1_3_load_226 | 108 | 0.0041422 | 0.0010381 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1093-10_1_3_load_227 | 109 | 0.0031278 | 0.00078391 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1093-10_1_3_load_229 | 110 | 0.0019344 | 0.00048481 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1093-10_1_3_load_230 | 111 | 0.0016415 | 0.0004114 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1093-10_1_3_load_247 | 112 | 0.002348 | 0.00058846 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1093-10_1_3_load_258 | 113 | 0.0012835 | 0.00032168 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1093-10_1_3_load_232 | 114 | 0.0018796 | 0.00047107 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1093-10_1_3_load_242 | 116 | 0.0042188 | 0.0010573 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1093-10_1_3_load_239 | 117 | 0.0055799 | 0.0013985 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1093-10_1_3_load_241 | 118 | 0.00062169 | 0.00015581 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1093-10_1_3_load_245 | 119 | 0.0048385 | 0.0012126 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1093-10_1_3_load_244 | 120 | 0.0051857 | 0.0012997 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1093-10_1_3_load_246 | 121 | 0.0034446 | 0.00086329 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1093-10_1_3_load_257 | 122 | 0.001084 | 0.00027167 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1093-10_1_3_load_250 | 123 | 0.0006624 | 0.00016601 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1093-10_1_3_load_265 | 124 | 0.00055597 | 0.00013934 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1093-10_1_3_load_254 | 126 | 0.0010559 | 0.00026463 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1093-10_1_3_load_255 | 127 | 0.0010824 | 0.00027129 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1093-10_1_3_load_256 | 128 | 0.0010559 | 0.00026463 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1093-10_1_3_load_259 | 129 | 0.0026139 | 0.0006551 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1093-10_1_3_load_260 | 130 | 0.0024398 | 0.00061147 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1093-10_1_3_load_261 | 131 | 0.0007086 | 0.00017759 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1093-10_1_3_load_262 | 132 | 0.00078341 | 0.00019634 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1093-10_1_3_load_264 | 133 | 0.00069234 | 0.00017352 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1093-10_1_3_line_0 |  | 0 | 1 | 0.031919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1093-10_1_3_line_1 |  | 0 | 2 | 0.031222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1093-10_1_3_line_2 |  | 0 | 3 | 0.00825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1093-10_1_3_line_3 |  | 2 | 4 | 0.01066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1093-10_1_3_line_4 |  | 2 | 5 | 0.021587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1093-10_1_3_line_5 |  | 3 | 6 | 0.050666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1093-10_1_3_line_6 |  | 4 | 17 | 0.019567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1093-10_1_3_line_7 |  | 6 | 7 | 0.003872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1093-10_1_3_line_8 |  | 7 | 18 | 0.073596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1093-10_1_3_line_9 |  | 7 | 19 | 0.025326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1093-10_1_3_line_10 |  | 8 | 9 | 0.028729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1093-10_1_3_line_11 |  | 8 | 10 | 0.0091836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1093-10_1_3_line_12 |  | 10 | 20 | 0.012314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1093-10_1_3_line_13 |  | 11 | 12 | 0.069732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1093-10_1_3_line_14 |  | 11 | 13 | 0.0094227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1093-10_1_3_line_15 |  | 12 | 14 | 0.058171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1093-10_1_3_line_16 |  | 13 | 23 | 0.0021902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1093-10_1_3_line_17 |  | 15 | 16 | 0.023788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1093-10_1_3_line_18 |  | 16 | 97 | 0.021749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1093-10_1_3_line_19 |  | 17 | 20 | 0.0050115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1093-10_1_3_line_20 |  | 18 | 21 | 0.030874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1093-10_1_3_line_21 |  | 20 | 22 | 0.015463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1093-10_1_3_line_22 |  | 21 | 102 | 0.026428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1093-10_1_3_line_23 |  | 23 | 24 | 0.01558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1093-10_1_3_line_24 |  | 24 | 25 | 0.014285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1093-10_1_3_line_25 |  | 24 | 26 | 0.06775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1093-10_1_3_line_26 |  | 25 | 27 | 0.036221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1093-10_1_3_line_27 |  | 26 | 28 | 0.0036561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1093-10_1_3_line_28 |  | 27 | 29 | 0.0098027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1093-10_1_3_line_29 |  | 28 | 30 | 0.0041998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1093-10_1_3_line_30 |  | 29 | 104 | 0.015768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1093-10_1_3_line_31 |  | 30 | 98 | 0.025555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1093-10_1_3_line_32 |  | 31 | 32 | 0.029776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1093-10_1_3_line_33 |  | 31 | 33 | 0.029466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1093-10_1_3_line_34 |  | 32 | 34 | 0.0072814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1093-10_1_3_line_35 |  | 33 | 35 | 0.13927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1093-10_1_3_line_36 |  | 34 | 36 | 0.10356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1093-10_1_3_line_37 |  | 35 | 37 | 0.021171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1093-10_1_3_line_38 |  | 36 | 38 | 0.34144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1093-10_1_3_line_39 |  | 37 | 39 | 0.043562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1093-10_1_3_line_40 |  | 38 | 54 | 0.004362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1093-10_1_3_line_41 |  | 38 | 55 | 0.055571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1093-10_1_3_line_42 |  | 38 | 45 | 0.52672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1093-10_1_3_line_43 |  | 40 | 41 | 0.054741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1093-10_1_3_line_44 |  | 40 | 42 | 0.016314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1093-10_1_3_line_45 |  | 41 | 43 | 0.017355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1093-10_1_3_line_46 |  | 42 | 44 | 0.1477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1093-10_1_3_line_47 |  | 44 | 45 | 0.10043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1093-10_1_3_line_48 |  | 44 | 46 | 0.075985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1093-10_1_3_line_49 |  | 45 | 51 | 0.056361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1093-10_1_3_line_50 |  | 46 | 52 | 0.02506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1093-10_1_3_line_51 |  | 47 | 48 | 0.033981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1093-10_1_3_line_52 |  | 47 | 49 | 0.41852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1093-10_1_3_line_53 |  | 48 | 50 | 0.021787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1093-10_1_3_line_54 |  | 49 | 75 | 0.23937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1093-10_1_3_line_55 |  | 51 | 53 | 0.024847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1093-10_1_3_line_56 |  | 52 | 72 | 0.034471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1093-10_1_3_line_57 |  | 54 | 56 | 0.027176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1093-10_1_3_line_58 |  | 54 | 57 | 0.029643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1093-10_1_3_line_59 |  | 55 | 58 | 0.01226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1093-10_1_3_line_60 |  | 57 | 66 | 0.023513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1093-10_1_3_line_61 |  | 58 | 123 | 0.036043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1093-10_1_3_line_62 |  | 58 | 94 | 0.026107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1093-10_1_3_line_63 |  | 59 | 60 | 0.0203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1093-10_1_3_line_64 |  | 60 | 61 | 0.04095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1093-10_1_3_line_65 |  | 60 | 62 | 0.004368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1093-10_1_3_line_66 |  | 60 | 63 | 0.00714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1093-10_1_3_line_67 |  | 61 | 107 | 0.030114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1093-10_1_3_line_68 |  | 62 | 81 | 0.0492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1093-10_1_3_line_69 |  | 63 | 78 | 0.022944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1093-10_1_3_line_70 |  | 63 | 86 | 0.01777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1093-10_1_3_line_71 |  | 64 | 65 | 0.16001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1093-10_1_3_line_72 |  | 65 | 66 | 0.0071019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1093-10_1_3_line_73 |  | 67 | 68 | 0.028369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1093-10_1_3_line_74 |  | 67 | 69 | 0.042102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1093-10_1_3_line_75 |  | 68 | 70 | 0.01077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1093-10_1_3_line_76 |  | 69 | 71 | 0.051647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1093-10_1_3_line_77 |  | 69 | 72 | 0.11994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1093-10_1_3_line_78 |  | 70 | 73 | 0.030204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1093-10_1_3_line_79 |  | 73 | 74 | 0.33312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1093-10_1_3_line_80 |  | 74 | 75 | 0.024056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1093-10_1_3_line_81 |  | 76 | 77 | 0.006266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1093-10_1_3_line_82 |  | 76 | 78 | 0.030133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1093-10_1_3_line_83 |  | 77 | 79 | 0.025043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1093-10_1_3_line_84 |  | 77 | 80 | 0.01671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1093-10_1_3_line_85 |  | 78 | 87 | 0.041892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1093-10_1_3_line_86 |  | 78 | 88 | 0.021031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1093-10_1_3_line_87 |  | 79 | 89 | 0.013119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1093-10_1_3_line_88 |  | 80 | 85 | 0.026413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1093-10_1_3_line_89 |  | 81 | 90 | 0.030027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1093-10_1_3_line_90 |  | 82 | 83 | 0.036557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1093-10_1_3_line_91 |  | 82 | 84 | 0.018867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1093-10_1_3_line_92 |  | 82 | 85 | 0.015287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1093-10_1_3_line_93 |  | 84 | 91 | 0.0053609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1093-10_1_3_line_94 |  | 84 | 92 | 0.037171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1093-10_1_3_line_95 |  | 86 | 93 | 0.030725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1093-10_1_3_line_96 |  | 87 | 94 | 0.02585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1093-10_1_3_line_97 |  | 88 | 95 | 0.029235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1093-10_1_3_line_98 |  | 89 | 106 | 0.007362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1093-10_1_3_line_99 |  | 90 | 99 | 0.031383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1093-10_1_3_line_100 |  | 91 | 105 | 0.0013627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1093-10_1_3_line_101 |  | 93 | 111 | 0.020821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1093-10_1_3_line_102 |  | 93 | 108 | 0.014378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1093-10_1_3_line_103 |  | 95 | 114 | 0.020641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1093-10_1_3_line_104 |  | 96 | 97 | 0.031204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1093-10_1_3_line_105 |  | 96 | 98 | 0.052906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1093-10_1_3_line_106 |  | 98 | 99 | 0.022114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1093-10_1_3_line_107 |  | 98 | 100 | 0.003955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1093-10_1_3_line_108 |  | 100 | 101 | 0.0097552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1093-10_1_3_line_109 |  | 100 | 102 | 0.038934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1093-10_1_3_line_110 |  | 102 | 103 | 0.028567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1093-10_1_3_line_111 |  | 106 | 115 | 0.025167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1093-10_1_3_line_112 |  | 108 | 109 | 0.0020702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1093-10_1_3_line_113 |  | 109 | 110 | 0.035978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1093-10_1_3_line_114 |  | 110 | 112 | 0.031528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1093-10_1_3_line_115 |  | 112 | 113 | 0.053541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1093-10_1_3_line_116 |  | 113 | 122 | 0.019353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1093-10_1_3_line_117 |  | 115 | 116 | 0.0084051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1093-10_1_3_line_118 |  | 115 | 117 | 0.014867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1093-10_1_3_line_119 |  | 116 | 119 | 0.0087848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1093-10_1_3_line_120 |  | 117 | 118 | 0.0012084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1093-10_1_3_line_121 |  | 119 | 120 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1093-10_1_3_line_122 |  | 120 | 121 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1093-10_1_3_line_123 |  | 122 | 127 | 0.0069298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1093-10_1_3_line_124 |  | 123 | 124 | 0.020528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1093-10_1_3_line_125 |  | 124 | 125 | 0.012924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1093-10_1_3_line_126 |  | 125 | 133 | 0.020573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1093-10_1_3_line_127 |  | 125 | 132 | 0.010302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1093-10_1_3_line_128 |  | 126 | 127 | 0.017816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1093-10_1_3_line_129 |  | 126 | 128 | 0.007017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1093-10_1_3_line_130 |  | 129 | 130 | 0.0013495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1093-10_1_3_line_131 |  | 130 | 131 | 0.020294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1093-10_1_3_line_132 |  | 131 | 132 | 0.0059776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1093-10_1_3_trafo_204 | 0.63 MVA 20/0.4 kV | 134 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2657917.5014 | 1216767.36 | 2657931.8766 | 1216738.8613
1 | 2657917.5014 | 1216767.36 | 2657928.7536 | 1216771.9499 | 2657943.6355 | 1216778.0093 | 2657944.6802 | 1216775.1955
2 | 2657917.5014 | 1216767.36 | 2657909.815 | 1216764.3629
3 | 2657944.6802 | 1216775.1955 | 2657948.3848 | 1216765.1996
4 | 2657944.6802 | 1216775.1955 | 2657948.1748 | 1216776.5191 | 2657964.6823 | 1216783.3117
5 | 2657864.9004 | 1216741.9782 | 2657870.9591 | 1216747.4181 | 2657878.1118 | 1216752.0014 | 2657909.815 | 1216764.3629
6 | 2657948.3848 | 1216765.1996 | 2657949.3893 | 1216762.489 | 2657957.2555 | 1216747.7846
7 | 2657864.9004 | 1216741.9782 | 2657864.7938 | 1216738.1081
8 | 2657864.7938 | 1216738.1081 | 2657864.5632 | 1216732.1467 | 2657865.3657 | 1216723.7715 | 2657866.6304 | 1216719.4034 | 2657875.0442 | 1216709.0564 | 2657907.6575 | 1216683.6637
9 | 2657864.7938 | 1216738.1081 | 2657879.4672 | 1216734.3927 | 2657885.7802 | 1216734.7542 | 2657889.3703 | 1216736.1895
10 | 2657991.4035 | 1216730.4556 | 2657977.2969 | 1216755.5005
11 | 2657977.2969 | 1216755.5005 | 2657975.8016 | 1216753.9072 | 2657969.9376 | 1216750.0872
12 | 2657959.6194 | 1216743.3656 | 2657969.9376 | 1216750.0872
13 | 2657836.6843 | 1216665.7688 | 2657830.1844 | 1216673.7107 | 2657826.7031 | 1216681.1815 | 2657824.4056 | 1216690.2648 | 2657823.6214 | 1216692.8476 | 2657823.2036 | 1216694.4334 | 2657820.365 | 1216693.5721 | 2657806.8986 | 1216679.2883 | 2657798.263 | 1216667.1194
14 | 2657836.6843 | 1216665.7688 | 2657844.0807 | 1216659.931
15 | 2657798.263 | 1216667.1194 | 2657797.7216 | 1216649.3588 | 2657798.8344 | 1216639.5191 | 2657806.6003 | 1216626.2974 | 2657817.514 | 1216615.7661
16 | 2657844.0807 | 1216659.931 | 2657845.7999 | 1216658.574
17 | 2657895.0715 | 1216688.7242 | 2657880.9138 | 1216699.5743 | 2657876.3386 | 1216703.3794
18 | 2657911.9109 | 1216674.9714 | 2657902.1014 | 1216683.3367 | 2657895.0715 | 1216688.7242
19 | 2657959.6194 | 1216743.3656 | 2657957.2555 | 1216747.7846
20 | 2657907.6575 | 1216683.6637 | 2657913.4619 | 1216679.1444 | 2657922.1032 | 1216671.1679 | 2657926.3488 | 1216666.3173 | 2657929.4277 | 1216661.989
21 | 2657952.1996 | 1216730.3522 | 2657959.0265 | 1216738.757 | 2657959.6194 | 1216743.3656
22 | 2657940.2442 | 1216638.0016 | 2657937.7379 | 1216645.9043 | 2657935.2273 | 1216651.9058 | 2657929.4277 | 1216661.989
23 | 2657858.0297 | 1216648.9212 | 2657845.7999 | 1216658.574
24 | 2657858.0297 | 1216648.9212 | 2657850.0575 | 1216637.0677
25 | 2657858.0297 | 1216648.9212 | 2657910.8675 | 1216606.515
26 | 2657850.0575 | 1216637.0677 | 2657847.4548 | 1216633.1978 | 2657846.5065 | 1216626.0843 | 2657864.7505 | 1216609.9114
27 | 2657913.7188 | 1216604.2266 | 2657910.8675 | 1216606.515
28 | 2657872.086 | 1216603.4088 | 2657864.7505 | 1216609.9114
29 | 2657913.7188 | 1216604.2266 | 2657916.9942 | 1216601.5979
30 | 2657883.8854 | 1216592.9489 | 2657872.086 | 1216603.4088
31 | 2657941.8452 | 1216599.06 | 2657929.0509 | 1216597.657 | 2657916.9942 | 1216601.5979
32 | 2657700.6022 | 1215886.6363 | 2657702.5548 | 1215894.1975 | 2657702.7021 | 1215902.5151 | 2657698.514 | 1215915.5047
33 | 2657700.6022 | 1215886.6363 | 2657696.0412 | 1215868.9746 | 2657697.4635 | 1215857.8398
34 | 2657699.5757 | 1215922.7083 | 2657698.514 | 1215915.5047 | 2657698.514 | 1215915.5047
35 | 2657771.0299 | 1215748.3713 | 2657769.3975 | 1215778.1292 | 2657766.1532 | 1215788.5264 | 2657760.0346 | 1215798.551 | 2657738.1904 | 1215815.6611 | 2657714.2508 | 1215836.6755 | 2657702.5221 | 1215848.9473 | 2657697.5036 | 1215857.5262 | 2657697.4635 | 1215857.8398
36 | 2657765.4049 | 1216000.482 | 2657763.5825 | 1215993.4378 | 2657751.8228 | 1215974.4567 | 2657730.201 | 1215949.0763 | 2657704.4725 | 1215929.0484 | 2657699.5757 | 1215922.7083
37 | 2657771.0299 | 1215748.3713 | 2657772.187 | 1215727.2321
38 | 2657765.4049 | 1216000.482 | 2657765.9759 | 1216002.6777 | 2657766.9971 | 1216013.2496 | 2657762.9466 | 1216059.0495 | 2657763.7406 | 1216116.5813 | 2657767.796 | 1216139.9904 | 2657783.0581 | 1216193.1708 | 2657798.4909 | 1216229.4981 | 2657801.2635 | 1216245.0234 | 2657801.0151 | 1216270.6366 | 2657798.1939 | 1216291.4331 | 2657796.9578 | 1216297.5471 | 2657794.9762 | 1216303.0202 | 2657797.7136 | 1216305.7372 | 2657800.5811 | 1216308.3333 | 2657803.5822 | 1216310.4748 | 2657808.5701 | 1216312.8579 | 2657813.125 | 1216315.2702 | 2657821.5389 | 1216320.5995
39 | 2657782.8758 | 1215687.1862 | 2657778.6092 | 1215689.4977 | 2657775.0722 | 1215697.1792 | 2657773.3552 | 1215705.8901 | 2657772.187 | 1215727.2321
40 | 2657817.6102 | 1216322.5182 | 2657821.5389 | 1216320.5995
41 | 2657821.5389 | 1216320.5995 | 2657835.5349 | 1216331.2418 | 2657849.0046 | 1216342.1346 | 2657858.052 | 1216351.0278 | 2657863.3977 | 1216356.951
42 | 2657389.7294 | 1216072.41 | 2657505.4264 | 1216087.5893 | 2657529.1044 | 1216091.131 | 2657549.2605 | 1216094.5609 | 2657605.7872 | 1216108.0815 | 2657617.4719 | 1216111.2742 | 2657624.9306 | 1216114.148 | 2657631.5966 | 1216117.3366 | 2657637.0332 | 1216120.4577 | 2657642.3549 | 1216124.4671 | 2657647.0818 | 1216128.7376 | 2657656.0921 | 1216138.3973 | 2657754.0436 | 1216252.237 | 2657781.2886 | 1216284.0537 | 2657786.5819 | 1216290.9648 | 2657794.9762 | 1216303.0202 | 2657797.7136 | 1216305.7372 | 2657800.5811 | 1216308.3333 | 2657803.5822 | 1216310.4748 | 2657808.5701 | 1216312.8579 | 2657813.125 | 1216315.2702 | 2657821.5389 | 1216320.5995
43 | 2657252.4888 | 1215919.4018 | 2657235.5726 | 1215957.7807 | 2657230.0481 | 1215969.3269
44 | 2657259.0686 | 1215904.4738 | 2657252.4888 | 1215919.4018
45 | 2657216.8604 | 1215970.9009 | 2657222.4804 | 1215974.5987 | 2657224.6247 | 1215975.064 | 2657226.5039 | 1215974.6707 | 2657227.9202 | 1215973.4613 | 2657229.3506 | 1215970.7845 | 2657230.0481 | 1215969.3269
46 | 2657259.0686 | 1215904.4738 | 2657275.6967 | 1215906.1122 | 2657281.2766 | 1215907.0108 | 2657285.6146 | 1215908.3422 | 2657289.7212 | 1215910.0493 | 2657293.196 | 1215911.9172 | 2657296.3973 | 1215914.594 | 2657299.3675 | 1215917.6133 | 2657302.0358 | 1215922.0194 | 2657304.0719 | 1215926.6418 | 2657305.6788 | 1215931.6714 | 2657306.7645 | 1215936.418 | 2657315.554 | 1216013.3383 | 2657316.3744 | 1216019.6167
47 | 2657389.7294 | 1216072.41 | 2657365.6382 | 1216068.3868 | 2657357.1135 | 1216066.6038 | 2657349.6088 | 1216064.5414 | 2657344.3814 | 1216062.5455 | 2657338.254 | 1216059.3958 | 2657332.6885 | 1216055.4399 | 2657329.2788 | 1216052.3385 | 2657326.5573 | 1216048.7324 | 2657323.9584 | 1216044.2158 | 2657322.0156 | 1216040.1724 | 2657320.4062 | 1216036.1878 | 2657319.1072 | 1216032.3063 | 2657317.8258 | 1216027.391 | 2657316.3744 | 1216019.6167
48 | 2657316.3744 | 1216019.6167 | 2657320.5068 | 1216013.8863 | 2657321.8586 | 1216010.7084 | 2657333.5618 | 1215979.6575 | 2657346.4112 | 1215950.042
49 | 2657389.7294 | 1216072.41 | 2657387.7546 | 1216023.5945 | 2657383.8299 | 1216017.1973
50 | 2657346.4112 | 1215950.042 | 2657356.3859 | 1215927.0523
51 | 2656831.3437 | 1215559.1833 | 2656835.4827 | 1215556.7323 | 2656847.6811 | 1215548.4213 | 2656852.3258 | 1215544.7078 | 2656857.322 | 1215542.3428 | 2656860.2473 | 1215542.0982
52 | 2657075.9411 | 1215250.1753 | 2657065.3659 | 1215271.2758 | 2657054.6384 | 1215287.6721 | 2657045.1895 | 1215322.0248 | 2657038.5865 | 1215361.33 | 2657035.7815 | 1215371.1536 | 2657033.606 | 1215375.5133 | 2657024.5413 | 1215383.2202 | 2657018.5091 | 1215385.8975 | 2657003.2823 | 1215388.4424 | 2656999.623 | 1215388.3518 | 2656986.2125 | 1215382.0087 | 2656979.3054 | 1215376.1169 | 2656977.4717 | 1215375.6991 | 2656974.0867 | 1215377.1009 | 2656971.3639 | 1215375.9631 | 2656963.7661 | 1215374.0116 | 2656958.4433 | 1215373.9718 | 2656953.5574 | 1215377.4829 | 2656948.9741 | 1215387.4674 | 2656948.9489 | 1215399.6413 | 2656947.1628 | 1215406.1726 | 2656928.7778 | 1215429.3112 | 2656921.7105 | 1215439.4054 | 2656915.8574 | 1215450.3674 | 2656904.9944 | 1215478.6476 | 2656892.6369 | 1215500.4207 | 2656877.4629 | 1215524.524 | 2656872.1242 | 1215538.1036 | 2656869.8646 | 1215540.15 | 2656864.9596 | 1215541.7042 | 2656860.2473 | 1215542.0982
53 | 2656831.3437 | 1215559.1833 | 2656841.5924 | 1215561.827 | 2656852.4215 | 1215564.921
54 | 2657075.9411 | 1215250.1753 | 2657150.1334 | 1215299.2378 | 2657190.2081 | 1215324.3261 | 2657235.1644 | 1215368.4731 | 2657258.1926 | 1215390.9745 | 2657264.6177 | 1215395.6405
55 | 2657369.3255 | 1216000.0584 | 2657368.9439 | 1216006.5698 | 2657372.5804 | 1216009.7734 | 2657383.8299 | 1216017.1973
56 | 2657356.3859 | 1215927.0523 | 2657370.1061 | 1215895.4298
57 | 2657817.6102 | 1216322.5182 | 2657836.0621 | 1216336.3833 | 2657839.2102 | 1216339.0027
58 | 2657817.6102 | 1216322.5182 | 2657795.6177 | 1216332.3888 | 2657791.1758 | 1216335.6944
59 | 2657871.5185 | 1216366.1344 | 2657868.2152 | 1216362.2889 | 2657863.3977 | 1216356.951
60 | 2657777.1828 | 1216354.5122 | 2657790.0579 | 1216336.5263 | 2657791.1758 | 1216335.6944
61 | 2657871.5185 | 1216366.1344 | 2657903.9491 | 1216350.408
62 | 2657871.5185 | 1216366.1344 | 2657887.1695 | 1216387.0304
63 | 2657944.1057 | 1216466.5119 | 2657949.0192 | 1216465.6035 | 2657962.6116 | 1216470.0606 | 2657963.5985 | 1216470.2112
64 | 2657944.1057 | 1216466.5119 | 2657950.3965 | 1216481.6823 | 2657952.2078 | 1216488.2595 | 2657954.8011 | 1216505.7732
65 | 2657940.2216 | 1216468.5309 | 2657944.1057 | 1216466.5119
66 | 2657940.5444 | 1216460.3179 | 2657944.1057 | 1216466.5119
67 | 2657953.3166 | 1216535.8129 | 2657954.2514 | 1216527.1698 | 2657954.989 | 1216514.5582 | 2657954.8011 | 1216505.7732 | 2657954.8011 | 1216505.7732
68 | 2657940.2216 | 1216468.5309 | 2657943.274 | 1216474.7533 | 2657945.5543 | 1216480.7235 | 2657947.9191 | 1216488.9516 | 2657950.8833 | 1216508.9148 | 2657950.8949 | 1216516.05
69 | 2657927.6625 | 1216441.3367 | 2657933.5121 | 1216449.5764 | 2657940.5444 | 1216460.3179
70 | 2657940.5444 | 1216460.3179 | 2657956.3198 | 1216452.139
71 | 2657773.0489 | 1216360.287 | 2657773.0251 | 1216360.3203 | 2657698.041 | 1216446.6916 | 2657687.0096 | 1216458.4365 | 2657663.8735 | 1216476.6955
72 | 2657777.1828 | 1216354.5122 | 2657773.0489 | 1216360.287
73 | 2657436.6037 | 1215736.345 | 2657420.7551 | 1215753.8475 | 2657417.8394 | 1215757.6068
74 | 2657409.6454 | 1215798.0786 | 2657412.4593 | 1215790.5233 | 2657413.5064 | 1215766.163 | 2657416.2188 | 1215759.6963 | 2657417.8394 | 1215757.6068
75 | 2657436.6037 | 1215736.345 | 2657436.6037 | 1215736.345 | 2657438.0782 | 1215731.4784 | 2657436.2835 | 1215727.8145 | 2657435.0692 | 1215726.7642
76 | 2657409.6454 | 1215798.0786 | 2657426.9327 | 1215800.68 | 2657461.2439 | 1215800.1324
77 | 2657409.6454 | 1215798.0786 | 2657386.4645 | 1215804.2815 | 2657381.3329 | 1215808.09 | 2657377.5935 | 1215815.5586 | 2657376.2616 | 1215826.9194 | 2657377.8175 | 1215856.1745 | 2657377.0208 | 1215875.045 | 2657373.8554 | 1215886.7884 | 2657370.1061 | 1215895.4298
78 | 2657409.5647 | 1215718.3475 | 2657412.9642 | 1215716.8277 | 2657418.6839 | 1215715.0483 | 2657422.7512 | 1215716.1103 | 2657435.0692 | 1215726.7642
79 | 2657409.5647 | 1215718.3475 | 2657284.099 | 1215409.7531
80 | 2657284.099 | 1215409.7531 | 2657275.2278 | 1215403.3456 | 2657264.6177 | 1215395.6405
81 | 2657918.5156 | 1216458.336 | 2657914.0013 | 1216462.6949
82 | 2657918.5156 | 1216458.336 | 2657920.4072 | 1216460.5669 | 2657931.4836 | 1216451.2688 | 2657933.5121 | 1216449.5764 | 2657927.6625 | 1216441.3367
83 | 2657914.0013 | 1216462.6949 | 2657893.2358 | 1216448.6961
84 | 2657914.0013 | 1216462.6949 | 2657911.1885 | 1216465.4137 | 2657907.3947 | 1216469.0791 | 2657902.4329 | 1216474.7328
85 | 2657927.6625 | 1216441.3367 | 2657904.6773 | 1216410.4056 | 2657902.666 | 1216407.7202
86 | 2657927.6625 | 1216441.3367 | 2657937.8423 | 1216422.933
87 | 2657893.2358 | 1216448.6961 | 2657882.3574 | 1216441.3625
88 | 2657902.4329 | 1216474.7328 | 2657897.6522 | 1216480.1801 | 2657891.097 | 1216489.878 | 2657886.8994 | 1216496.0449
89 | 2657948.1146 | 1216545.9323 | 2657950.1026 | 1216529.0863 | 2657950.8975 | 1216517.6092 | 2657950.8949 | 1216516.05
90 | 2657880.3102 | 1216509.2296 | 2657847.596 | 1216492.7243
91 | 2657880.3102 | 1216509.2296 | 2657877.5974 | 1216514.9512 | 2657878.1278 | 1216522.8723 | 2657879.0635 | 1216527.373
92 | 2657880.3102 | 1216509.2296 | 2657880.0983 | 1216506.0367 | 2657886.8994 | 1216496.0449
93 | 2657879.0635 | 1216527.373 | 2657880.1591 | 1216532.6208
94 | 2657879.0635 | 1216527.373 | 2657870.531 | 1216532.7268 | 2657869.7593 | 1216559.8137
95 | 2657974.2221 | 1216427.7253 | 2657965.7951 | 1216442.508 | 2657962.4929 | 1216447.1454 | 2657958.5836 | 1216450.9653 | 2657956.3198 | 1216452.139
96 | 2657887.1695 | 1216387.0304 | 2657902.666 | 1216407.7202
97 | 2657937.8423 | 1216422.933 | 2657948.6678 | 1216403.362 | 2657942.7034 | 1216399.9532
98 | 2657882.3574 | 1216441.3625 | 2657876.253 | 1216437.2473
99 | 2657944.4368 | 1216577.0987 | 2657948.1146 | 1216545.9323
100 | 2657880.1591 | 1216532.6208 | 2657880.4375 | 1216533.9547
101 | 2657974.2221 | 1216427.7253 | 2657992.7835 | 1216437.1596
102 | 2657974.2221 | 1216427.7253 | 2657981.3431 | 1216415.2346
103 | 2657924.7827 | 1216389.7112 | 2657942.7034 | 1216399.9532
104 | 2657930.8887 | 1216650.4975 | 2657928.5756 | 1216655.1432 | 2657925.8307 | 1216659.4748 | 2657919.5185 | 1216667.6184 | 2657912.62 | 1216674.3667 | 2657911.9109 | 1216674.9714
105 | 2657941.8452 | 1216599.06 | 2657937.7276 | 1216629.7833 | 2657936.1906 | 1216637.1617 | 2657932.7569 | 1216646.7453 | 2657930.8887 | 1216650.4975
106 | 2657941.8452 | 1216599.06 | 2657944.4368 | 1216577.0987
107 | 2657941.8452 | 1216599.06 | 2657945.7889 | 1216599.4875
108 | 2657945.7889 | 1216599.4875 | 2657946.9577 | 1216589.8025
109 | 2657945.7889 | 1216599.4875 | 2657941.6685 | 1216631.2891 | 2657940.2442 | 1216638.0016
110 | 2657940.2442 | 1216638.0016 | 2657948.832 | 1216639.4526 | 2657957.4538 | 1216639.7366 | 2657964.0147 | 1216638.0438 | 2657967.8978 | 1216635.8586
111 | 2657855.3851 | 1216423.1795 | 2657876.253 | 1216437.2473
112 | 2657981.3431 | 1216415.2346 | 2657982.3684 | 1216413.4361
113 | 2657982.3684 | 1216413.4361 | 2658000.1874 | 1216382.1802
114 | 2658023.1693 | 1216381.0395 | 2658006.1928 | 1216371.6463 | 2658000.1874 | 1216382.1802
115 | 2658048.7274 | 1216416.0901 | 2658052.7736 | 1216408.9335 | 2658054.0363 | 1216404.7877 | 2658053.4795 | 1216399.6013 | 2658050.2496 | 1216396.0233 | 2658023.1693 | 1216381.0395
116 | 2658039.2024 | 1216432.9369 | 2658048.7274 | 1216416.0901
117 | 2657855.3851 | 1216423.1795 | 2657850.2976 | 1216429.8701
118 | 2657855.3851 | 1216423.1795 | 2657857.9918 | 1216408.5424
119 | 2657844.9803 | 1216436.8629 | 2657850.2976 | 1216429.8701
120 | 2657858.2036 | 1216407.3527 | 2657857.9918 | 1216408.5424
121 | 2657836.578 | 1216447.913 | 2657844.9803 | 1216436.8629
122 | 2657827.9684 | 1216459.2356 | 2657836.578 | 1216447.913
123 | 2658039.2024 | 1216432.9369 | 2658035.7918 | 1216438.9693
124 | 2657922.4197 | 1216341.451 | 2657903.9491 | 1216350.408
125 | 2657934.0485 | 1216335.8119 | 2657922.4197 | 1216341.451
126 | 2657934.0485 | 1216335.8119 | 2657945.6374 | 1216318.8134
127 | 2657934.0485 | 1216335.8119 | 2657943.0359 | 1216340.8484
128 | 2658027.0235 | 1216454.478 | 2658035.7918 | 1216438.9693
129 | 2658027.0235 | 1216454.478 | 2658023.5699 | 1216460.5864
130 | 2657967.1317 | 1216354.3515 | 2657965.9544 | 1216353.6917
131 | 2657948.2506 | 1216343.7706 | 2657965.9544 | 1216353.6917
132 | 2657948.2506 | 1216343.7706 | 2657943.0359 | 1216340.8484

## bus_geodata
| x | y | coords
0 | 2657917.5014 | 1216767.36
1 | 2657931.8766 | 1216738.8613
2 | 2657944.6802 | 1216775.1955
3 | 2657909.815 | 1216764.3629
4 | 2657948.3848 | 1216765.1996
5 | 2657964.6823 | 1216783.3117
6 | 2657864.9004 | 1216741.9782
7 | 2657864.7938 | 1216738.1081
8 | 2657977.2969 | 1216755.5005
9 | 2657991.4035 | 1216730.4556
10 | 2657969.9376 | 1216750.0872
11 | 2657836.6843 | 1216665.7688
12 | 2657798.263 | 1216667.1194
13 | 2657844.0807 | 1216659.931
14 | 2657817.514 | 1216615.7661
15 | 2657876.3386 | 1216703.3794
16 | 2657895.0715 | 1216688.7242
17 | 2657957.2555 | 1216747.7846
18 | 2657907.6575 | 1216683.6637
19 | 2657889.3703 | 1216736.1895
20 | 2657959.6194 | 1216743.3656
21 | 2657929.4277 | 1216661.989
22 | 2657952.1996 | 1216730.3522
23 | 2657845.7999 | 1216658.574
24 | 2657858.0297 | 1216648.9212
25 | 2657850.0575 | 1216637.0677
26 | 2657910.8675 | 1216606.515
27 | 2657864.7505 | 1216609.9114
28 | 2657913.7188 | 1216604.2266
29 | 2657872.086 | 1216603.4088
30 | 2657916.9942 | 1216601.5979
31 | 2657700.6022 | 1215886.6363
32 | 2657698.514 | 1215915.5047
33 | 2657697.4635 | 1215857.8398
34 | 2657699.5757 | 1215922.7083
35 | 2657771.0299 | 1215748.3713
36 | 2657765.4049 | 1216000.482
37 | 2657772.187 | 1215727.2321
38 | 2657821.5389 | 1216320.5995
39 | 2657782.8758 | 1215687.1862
40 | 2657252.4888 | 1215919.4018
41 | 2657230.0481 | 1215969.3269
42 | 2657259.0686 | 1215904.4738
43 | 2657216.8604 | 1215970.9009
44 | 2657316.3744 | 1216019.6167
45 | 2657389.7294 | 1216072.41
46 | 2657346.4112 | 1215950.042
47 | 2656860.2473 | 1215542.0982
48 | 2656831.3437 | 1215559.1833
49 | 2657075.9411 | 1215250.1753
50 | 2656852.4215 | 1215564.921
51 | 2657383.8299 | 1216017.1973
52 | 2657356.3859 | 1215927.0523
53 | 2657369.3255 | 1216000.0584
54 | 2657817.6102 | 1216322.5182
55 | 2657863.3977 | 1216356.951
56 | 2657839.2102 | 1216339.0027
57 | 2657791.1758 | 1216335.6944
58 | 2657871.5185 | 1216366.1344
59 | 2657963.5985 | 1216470.2112
60 | 2657944.1057 | 1216466.5119
61 | 2657954.8011 | 1216505.7732
62 | 2657940.2216 | 1216468.5309
63 | 2657940.5444 | 1216460.3179
64 | 2657663.8735 | 1216476.6955
65 | 2657773.0489 | 1216360.287
66 | 2657777.1828 | 1216354.5122
67 | 2657417.8394 | 1215757.6068
68 | 2657436.6037 | 1215736.345
69 | 2657409.6454 | 1215798.0786
70 | 2657435.0692 | 1215726.7642
71 | 2657461.2439 | 1215800.1324
72 | 2657370.1061 | 1215895.4298
73 | 2657409.5647 | 1215718.3475
74 | 2657284.099 | 1215409.7531
75 | 2657264.6177 | 1215395.6405
76 | 2657918.5156 | 1216458.336
77 | 2657914.0013 | 1216462.6949
78 | 2657927.6625 | 1216441.3367
79 | 2657893.2358 | 1216448.6961
80 | 2657902.4329 | 1216474.7328
81 | 2657950.8949 | 1216516.05
82 | 2657880.3102 | 1216509.2296
83 | 2657847.596 | 1216492.7243
84 | 2657879.0635 | 1216527.373
85 | 2657886.8994 | 1216496.0449
86 | 2657956.3198 | 1216452.139
87 | 2657902.666 | 1216407.7202
88 | 2657937.8423 | 1216422.933
89 | 2657882.3574 | 1216441.3625
90 | 2657948.1146 | 1216545.9323
91 | 2657880.1591 | 1216532.6208
92 | 2657869.7593 | 1216559.8137
93 | 2657974.2221 | 1216427.7253
94 | 2657887.1695 | 1216387.0304
95 | 2657942.7034 | 1216399.9532
96 | 2657930.8887 | 1216650.4975
97 | 2657911.9109 | 1216674.9714
98 | 2657941.8452 | 1216599.06
99 | 2657944.4368 | 1216577.0987
100 | 2657945.7889 | 1216599.4875
101 | 2657946.9577 | 1216589.8025
102 | 2657940.2442 | 1216638.0016
103 | 2657967.8978 | 1216635.8586
104 | 2657883.8854 | 1216592.9489
105 | 2657880.4375 | 1216533.9547
106 | 2657876.253 | 1216437.2473
107 | 2657953.3166 | 1216535.8129
108 | 2657981.3431 | 1216415.2346
109 | 2657982.3684 | 1216413.4361
110 | 2658000.1874 | 1216382.1802
111 | 2657992.7835 | 1216437.1596
112 | 2658023.1693 | 1216381.0395
113 | 2658048.7274 | 1216416.0901
114 | 2657924.7827 | 1216389.7112
115 | 2657855.3851 | 1216423.1795
116 | 2657850.2976 | 1216429.8701
117 | 2657857.9918 | 1216408.5424
118 | 2657858.2036 | 1216407.3527
119 | 2657844.9803 | 1216436.8629
120 | 2657836.578 | 1216447.913
121 | 2657827.9684 | 1216459.2356
122 | 2658039.2024 | 1216432.9369
123 | 2657903.9491 | 1216350.408
124 | 2657922.4197 | 1216341.451
125 | 2657934.0485 | 1216335.8119
126 | 2658027.0235 | 1216454.478
127 | 2658035.7918 | 1216438.9693
128 | 2658023.5699 | 1216460.5864
129 | 2657967.1317 | 1216354.3515
130 | 2657965.9544 | 1216353.6917
131 | 2657948.2506 | 1216343.7706
132 | 2657943.0359 | 1216340.8484
133 | 2657945.6374 | 1216318.8134
134 | 2657941.8452 | 1216599.06

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97559 | -0.46845 | 0 | 0
1 | 0.97507 | -0.47866 | 0.017471 | 0.0043788
2 | 0.97384 | -0.50275 | 0 | 0
3 | 0.97618 | -0.45676 | 0.0063701 | 0.0015965
4 | 0.97339 | -0.51181 | 0.0075623 | 0.0018953
5 | 0.97357 | -0.50818 | 0.01368 | 0.0034286
6 | 0.98014 | -0.37948 | 0 | 0
7 | 0.98044 | -0.3736 | 0 | 0
8 | 0.9722 | -0.53515 | 0 | 0
9 | 0.97188 | -0.54152 | 0.012005 | 0.0030088
10 | 0.97231 | -0.53312 | 0.0083873 | 0.0021021
11 | 0.99739 | -0.050114 | 0 | 0
12 | 0.99706 | -0.056544 | 0 | 0
13 | 0.99744 | -0.049245 | 0.004501 | 0.0011281
14 | 0.99678 | -0.061908 | 0.0052577 | 0.0013177
15 | 0.99593 | -0.077112 | 0.0057644 | 0.0014447
16 | 0.99606 | -0.074702 | 0.004866 | 0.0012195
17 | 0.97268 | -0.52573 | 0.0087678 | 0.0021974
18 | 0.98737 | -0.23948 | 0.0015997 | 0.00040093
19 | 0.98003 | -0.38162 | 0.017471 | 0.0043788
20 | 0.97254 | -0.52849 | 0 | 0
21 | 0.99033 | -0.1829 | 0.0016006 | 0.00040116
22 | 0.9724 | -0.5312 | 0.0094883 | 0.002378
23 | 0.99746 | -0.048871 | 0.0049808 | 0.0012483
24 | 0.99767 | -0.044847 | 0 | 0
25 | 0.99742 | -0.04962 | 0.0040711 | 0.0010203
26 | 0.99975 | -0.0048058 | 0.0010495 | 0.00026304
27 | 0.99692 | -0.059145 | 0.0043931 | 0.001101
28 | 0.99987 | -0.0025828 | 0.00040706 | 0.00010202
29 | 0.99683 | -0.06097 | 0.0054242 | 0.0013594
30 | 1 | 0 | -0.28257 | -0.072316
31 | 0.97657 | -0.45134 | 0.00069255 | 0.00017357
32 | 0.9766 | -0.45079 | 0.00011835 | 2.9661e-05
33 | 0.97657 | -0.4515 | 0.00010728 | 2.6888e-05
34 | 0.97661 | -0.45064 | 0.00012087 | 3.0292e-05
35 | 0.97654 | -0.452 | 0 | 0
36 | 0.97673 | -0.4483 | 0 | 0
37 | 0.97654 | -0.45207 | 8.6645e-05 | 2.1715e-05
38 | 0.97712 | -0.44052 | 0 | 0
39 | 0.97653 | -0.45215 | 0.00010378 | 2.601e-05
40 | 0.97583 | -0.46681 | 8.424e-05 | 2.1113e-05
41 | 0.97582 | -0.46695 | 3.8178e-05 | 9.5683e-06
42 | 0.97583 | -0.46674 | 0 | 0
43 | 0.97582 | -0.46699 | 0.00010548 | 2.6437e-05
44 | 0.97586 | -0.46611 | 0 | 0
45 | 0.97603 | -0.46261 | 0 | 0
46 | 0.97575 | -0.46842 | 5.2247e-05 | 1.3094e-05
47 | 0.97508 | -0.48235 | 0.00017437 | 4.3702e-05
48 | 0.97507 | -0.48242 | 0 | 0
49 | 0.97518 | -0.48013 | 0 | 0
50 | 0.97507 | -0.48246 | 0.00010673 | 2.6748e-05
51 | 0.97601 | -0.46301 | 0.00028522 | 7.1483e-05
52 | 0.97571 | -0.46916 | 0.00012984 | 3.2542e-05
53 | 0.97601 | -0.46305 | 9.6387e-05 | 2.4157e-05
54 | 0.97709 | -0.44106 | 0 | 0
55 | 0.97764 | -0.43007 | 0.00057111 | 0.00014313
56 | 0.97707 | -0.44136 | 0.00060419 | 0.00015142
57 | 0.97692 | -0.44439 | 0.0019682 | 0.00049329
58 | 0.97776 | -0.42764 | 0 | 0
59 | 0.98217 | -0.34115 | 0.0008898 | 0.000223
60 | 0.98219 | -0.34082 | 0 | 0
61 | 0.98203 | -0.34384 | 0.0021521 | 0.00053936
62 | 0.98266 | -0.33169 | 0 | 0
63 | 0.98145 | -0.35512 | 0 | 0
64 | 0.97638 | -0.45499 | 0.0028432 | 0.00071258
65 | 0.9768 | -0.44666 | 0.00088303 | 0.00022131
66 | 0.97683 | -0.44618 | 0.00044592 | 0.00011176
67 | 0.97548 | -0.47392 | 0.00013744 | 3.4445e-05
68 | 0.97545 | -0.47448 | 0.00010439 | 2.6162e-05
69 | 0.97553 | -0.47298 | 0 | 0
70 | 0.97544 | -0.47467 | 0.00028394 | 7.1162e-05
71 | 0.97552 | -0.47308 | 9.9706e-05 | 2.4989e-05
72 | 0.97567 | -0.47009 | 0.00015824 | 3.966e-05
73 | 0.97543 | -0.47505 | 8.8722e-05 | 2.2236e-05
74 | 0.97525 | -0.47865 | 0.0002195 | 5.5011e-05
75 | 0.97525 | -0.47881 | 6.0901e-05 | 1.5263e-05
76 | 0.97784 | -0.42585 | 0 | 0
77 | 0.97748 | -0.43286 | 0 | 0
78 | 0.97956 | -0.39222 | 0 | 0
79 | 0.97669 | -0.44845 | 0.002066 | 0.00051778
80 | 0.97706 | -0.44116 | 0.0034808 | 0.00087238
81 | 0.98794 | -0.22944 | 0.0017849 | 0.00044734
82 | 0.97629 | -0.45625 | 0 | 0
83 | 0.976 | -0.46199 | 0.0085793 | 0.0021502
84 | 0.97622 | -0.45778 | 0 | 0
85 | 0.97648 | -0.45262 | 0.010727 | 0.0026884
86 | 0.9811 | -0.36206 | 0.0028275 | 0.00070865
87 | 0.97871 | -0.40889 | 0.0016114 | 0.00040385
88 | 0.97944 | -0.39449 | 0.0021632 | 0.00054216
89 | 0.9763 | -0.45614 | 0.0044844 | 0.0011239
90 | 0.99121 | -0.16663 | 0.0013707 | 0.00034354
91 | 0.9762 | -0.45805 | 0.00095589 | 0.00023957
92 | 0.97615 | -0.45899 | 0.0017694 | 0.00044345
93 | 0.98057 | -0.37251 | 0 | 0
94 | 0.97823 | -0.41843 | 0.00093724 | 0.00023489
95 | 0.97934 | -0.3965 | 0.0019032 | 0.00047699
96 | 0.99659 | -0.064511 | 0.00038619 | 9.6789e-05
97 | 0.99627 | -0.070641 | 0.00055921 | 0.00014015
98 | 0.99714 | -0.053766 | 0 | 0
99 | 0.99467 | -0.10066 | 0.0017637 | 0.00044203
100 | 0.99674 | -0.06129 | 0 | 0
101 | 0.99672 | -0.06171 | 0.0024561 | 0.00061555
102 | 0.9929 | -0.13398 | 0 | 0
103 | 0.99286 | -0.13479 | 0.0015999 | 0.00040097
104 | 0.99676 | -0.062404 | 0.0051846 | 0.0012994
105 | 0.9762 | -0.45809 | 0.001709 | 0.00042833
106 | 0.97611 | -0.45985 | 0.0036672 | 0.00091909
107 | 0.98198 | -0.34489 | 0.001931 | 0.00048396
108 | 0.98034 | -0.37697 | 0.0041422 | 0.0010381
109 | 0.98031 | -0.37746 | 0.0031278 | 0.00078391
110 | 0.97999 | -0.38389 | 0.0019344 | 0.00048481
111 | 0.98053 | -0.37313 | 0.0016415 | 0.0004114
112 | 0.97976 | -0.38842 | 0.002348 | 0.00058846
113 | 0.97948 | -0.39383 | 0.0012835 | 0.00032168
114 | 0.9793 | -0.3972 | 0.0018796 | 0.00047107
115 | 0.97555 | -0.47085 | 0 | 0
116 | 0.97541 | -0.47358 | 0.0042188 | 0.0010573
117 | 0.97547 | -0.47254 | 0.0055799 | 0.0013985
118 | 0.97546 | -0.47255 | 0.00062169 | 0.00015581
119 | 0.9753 | -0.47574 | 0.0048385 | 0.0012126
120 | 0.97519 | -0.47794 | 0.0051857 | 0.0012997
121 | 0.97515 | -0.47884 | 0.0034446 | 0.00086329
122 | 0.9794 | -0.39533 | 0.001084 | 0.00027167
123 | 0.97748 | -0.4332 | 0.0006624 | 0.00016601
124 | 0.97733 | -0.43612 | 0.00055597 | 0.00013934
125 | 0.97724 | -0.43782 | 0 | 0
126 | 0.97935 | -0.39642 | 0.0010559 | 0.00026463
127 | 0.97938 | -0.39573 | 0.0010824 | 0.00027129
128 | 0.97934 | -0.39655 | 0.0010559 | 0.00026463
129 | 0.97705 | -0.44162 | 0.0026139 | 0.0006551
130 | 0.97706 | -0.44156 | 0.0024398 | 0.00061147
131 | 0.97715 | -0.43968 | 0.0007086 | 0.00017759
132 | 0.97718 | -0.43906 | 0.00078341 | 0.00019634
133 | 0.97723 | -0.43808 | 0.00069234 | 0.00017352
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01748 | 0.0043838 | -0.017471 | -0.0043788 | 8.5091e-06 | 5.0474e-06 | 0.026662 | 0.026663 | 0.026663 | 0.97559 | -0.46845 | 0.97507 | -0.47866 | 7.3249
1 | 0.060053 | 0.015112 | -0.059955 | -0.015049 | 9.8278e-05 | 6.2509e-05 | 0.091618 | 0.091618 | 0.091618 | 0.97559 | -0.46845 | 0.97384 | -0.50275 | 25.1698
2 | -0.077533 | -0.019496 | 0.077576 | 0.019523 | 4.3282e-05 | 2.7598e-05 | 0.11828 | 0.11828 | 0.11828 | 0.97559 | -0.46845 | 0.97618 | -0.45676 | 32.4946
3 | 0.046271 | 0.011619 | -0.046251 | -0.011606 | 1.9987e-05 | 1.2659e-05 | 0.070709 | 0.070709 | 0.070709 | 0.97384 | -0.50275 | 0.97339 | -0.51181 | 19.4255
4 | 0.013684 | 0.0034306 | -0.01368 | -0.0034286 | 3.5392e-06 | 1.9966e-06 | 0.020909 | 0.020909 | 0.020909 | 0.97384 | -0.50275 | 0.97357 | -0.50818 | 5.7443
5 | -0.083946 | -0.02112 | 0.084258 | 0.021318 | 0.00031124 | 0.00019856 | 0.12799 | 0.12799 | 0.12799 | 0.97618 | -0.45676 | 0.98014 | -0.37948 | 35.1622
6 | 0.038689 | 0.0097108 | -0.038663 | -0.0096946 | 2.5671e-05 | 1.6186e-05 | 0.059149 | 0.059149 | 0.059149 | 0.97339 | -0.51181 | 0.97268 | -0.52573 | 16.2496
7 | -0.084258 | -0.021318 | 0.084281 | 0.021333 | 2.3786e-05 | 1.5174e-05 | 0.12799 | 0.12799 | 0.12799 | 0.98014 | -0.37948 | 0.98044 | -0.3736 | 35.1621
8 | -0.10176 | -0.025716 | 0.10242 | 0.026137 | 0.00065893 | 0.00042078 | 0.15452 | 0.15452 | 0.15452 | 0.98044 | -0.3736 | 0.98737 | -0.23948 | 42.4499
9 | 0.017478 | 0.0043827 | -0.017471 | -0.0043788 | 6.6834e-06 | 3.9581e-06 | 0.026528 | 0.026528 | 0.026528 | 0.98044 | -0.3736 | 0.98003 | -0.38162 | 7.2878
10 | 0.012009 | 0.0030107 | -0.012005 | -0.0030088 | 3.6397e-06 | 1.9733e-06 | 0.01838 | 0.018381 | 0.018381 | 0.9722 | -0.53515 | 0.97188 | -0.54152 | 5.0496
11 | -0.012009 | -0.0030107 | 0.01201 | 0.0030114 | 1.1635e-06 | 6.3073e-07 | 0.01838 | 0.01838 | 0.01838 | 0.9722 | -0.53515 | 0.97231 | -0.53312 | 5.0496
12 | -0.020397 | -0.0051134 | 0.020402 | 0.0051161 | 4.4999e-06 | 2.7272e-06 | 0.031216 | 0.031216 | 0.031216 | 0.97231 | -0.53312 | 0.97254 | -0.52849 | 8.5759
13 | 0.0052606 | 0.0013179 | -0.005259 | -0.0013178 | 1.6107e-06 | 1.2109e-07 | 0.0078482 | 0.0078485 | 0.0078485 | 0.99739 | -0.050114 | 0.99706 | -0.056544 | 2.1562
14 | -0.0052606 | -0.0013179 | 0.0052608 | 0.0013179 | 2.1764e-07 | 1.6309e-08 | 0.0078482 | 0.0078481 | 0.0078482 | 0.99739 | -0.050114 | 0.99744 | -0.049245 | 2.1561
15 | 0.005259 | 0.0013178 | -0.0052577 | -0.0013177 | 1.3438e-06 | 1.0154e-07 | 0.0078485 | 0.0078487 | 0.0078487 | 0.99706 | -0.056544 | 0.99678 | -0.061908 | 2.1562
16 | -0.0097619 | -0.002446 | 0.009762 | 0.0024461 | 1.7419e-07 | 8.2892e-08 | 0.014563 | 0.014563 | 0.014563 | 0.99744 | -0.049245 | 0.99746 | -0.048871 | 4.0008
17 | -0.0057644 | -0.0014447 | 0.0057651 | 0.0014448 | 6.6168e-07 | 1.1389e-07 | 0.0086126 | 0.0086124 | 0.0086126 | 0.99593 | -0.077112 | 0.99606 | -0.074702 | 2.3661
18 | -0.010631 | -0.0026643 | 0.010633 | 0.0026654 | 2.0571e-06 | 1.0334e-06 | 0.015882 | 0.015882 | 0.015882 | 0.99606 | -0.074702 | 0.99627 | -0.070641 | 4.3631
19 | 0.029895 | 0.0074972 | -0.029891 | -0.0074947 | 3.9311e-06 | 2.4537e-06 | 0.045736 | 0.045736 | 0.045736 | 0.97268 | -0.52573 | 0.97254 | -0.52849 | 12.5647
20 | -0.10402 | -0.026538 | 0.1043 | 0.02672 | 0.00028512 | 0.00018208 | 0.15693 | 0.15693 | 0.15693 | 0.98737 | -0.23948 | 0.99033 | -0.1829 | 43.1121
21 | 0.0094895 | 0.0023786 | -0.0094883 | -0.002378 | 1.2224e-06 | 5.9051e-07 | 0.014519 | 0.014519 | 0.014519 | 0.97254 | -0.52849 | 0.9724 | -0.5312 | 3.9889
22 | -0.1059 | -0.027121 | 0.10616 | 0.027282 | 0.0002516 | 0.00016068 | 0.15933 | 0.15933 | 0.15933 | 0.99033 | -0.1829 | 0.9929 | -0.13398 | 43.7728
23 | -0.014743 | -0.0036944 | 0.014746 | 0.003696 | 2.8261e-06 | 1.6053e-06 | 0.021993 | 0.021993 | 0.021993 | 0.99746 | -0.048871 | 0.99767 | -0.044847 | 6.0421
24 | 0.019085 | 0.0047871 | -0.019081 | -0.0047845 | 4.3411e-06 | 2.5918e-06 | 0.028467 | 0.028467 | 0.028467 | 0.99767 | -0.044847 | 0.99742 | -0.04962 | 7.8207
25 | -0.033831 | -0.0084831 | 0.033896 | 0.0085236 | 6.4691e-05 | 4.0516e-05 | 0.05046 | 0.05046 | 0.05046 | 0.99767 | -0.044847 | 0.99975 | -0.0048058 | 13.8628
26 | 0.01501 | 0.0037642 | -0.015003 | -0.0037603 | 6.8115e-06 | 3.8869e-06 | 0.022394 | 0.022394 | 0.022394 | 0.99742 | -0.04962 | 0.99692 | -0.059145 | 6.1522
27 | -0.034945 | -0.0087867 | 0.034949 | 0.008789 | 3.7105e-06 | 2.3268e-06 | 0.052022 | 0.052022 | 0.052022 | 0.99975 | -0.0048058 | 0.99987 | -0.0025828 | 14.2918
28 | 0.01061 | 0.0026593 | -0.010609 | -0.0026588 | 9.2196e-07 | 4.6225e-07 | 0.015837 | 0.015837 | 0.015837 | 0.99692 | -0.059145 | 0.99683 | -0.06097 | 4.3508
29 | -0.035356 | -0.008891 | 0.03536 | 0.0088937 | 4.3621e-06 | 2.7366e-06 | 0.052628 | 0.052628 | 0.052628 | 0.99987 | -0.0025828 | 1 | 0 | 14.4583
30 | 0.0051849 | 0.0012994 | -0.0051846 | -0.0012994 | 3.5422e-07 | 2.1158e-08 | 0.0077398 | 0.0077398 | 0.0077398 | 0.99683 | -0.06097 | 0.99676 | -0.062404 | 2.1263
31 | 0.24556 | 0.063422 | -0.24492 | -0.063012 | 0.00064209 | 0.00041027 | 0.36606 | 0.36606 | 0.36606 | 1 | 0 | 0.99714 | -0.053766 | 50.2834
32 | -0.00099027 | -0.00024527 | 0.00099029 | 0.00024491 | 2.5385e-08 | -3.5632e-07 | 0.0015078 | 0.0015077 | 0.0015078 | 0.97657 | -0.45134 | 0.9766 | -0.45079 | 0.41424
33 | 0.00029772 | 7.1698e-05 | -0.00029772 | -7.2065e-05 | 2.2643e-09 | -3.6723e-07 | 0.00045261 | 0.00045274 | 0.00045274 | 0.97657 | -0.45134 | 0.97657 | -0.4515 | 0.12438
34 | -0.0011086 | -0.00027457 | 0.0011086 | 0.00027448 | 7.7803e-09 | -8.613e-08 | 0.001688 | 0.001688 | 0.001688 | 0.9766 | -0.45079 | 0.97661 | -0.45064 | 0.46374
35 | 0.00019043 | 4.5177e-05 | -0.00019043 | -4.6916e-05 | 4.3794e-09 | -1.7397e-06 | 0.00028927 | 0.00028988 | 0.00028988 | 0.97657 | -0.4515 | 0.97654 | -0.452 | 0.079637
36 | -0.0012295 | -0.00030478 | 0.0012297 | 0.00030357 | 1.3608e-07 | -1.2089e-06 | 0.0018722 | 0.0018717 | 0.0018722 | 0.97661 | -0.45064 | 0.97673 | -0.4483 | 0.51433
37 | 0.00019043 | 4.6916e-05 | -0.00019043 | -4.7181e-05 | 6.6734e-10 | -2.6444e-07 | 0.00028988 | 0.00028997 | 0.00028997 | 0.97654 | -0.452 | 0.97654 | -0.45207 | 0.079663
38 | -0.0012297 | -0.00030357 | 0.0012301 | 0.00029958 | 4.482e-07 | -3.9883e-06 | 0.0018717 | 0.0018702 | 0.0018717 | 0.97673 | -0.4483 | 0.97712 | -0.44052 | 0.5142
39 | 0.00010378 | 2.5466e-05 | -0.00010378 | -2.601e-05 | 4.0803e-10 | -5.4473e-07 | 0.00015795 | 0.00015814 | 0.00015814 | 0.97654 | -0.45207 | 0.97653 | -0.45215 | 0.043445
40 | 0.0067473 | 0.0016889 | -0.0067471 | -0.0016889 | 1.7268e-07 | 5.5879e-08 | 0.010275 | 0.010275 | 0.010275 | 0.97712 | -0.44052 | 0.97709 | -0.44106 | 2.8227
41 | -0.010206 | -0.002518 | 0.010211 | 0.0025205 | 5.0249e-06 | 2.5195e-06 | 0.015528 | 0.015528 | 0.015528 | 0.97712 | -0.44052 | 0.97764 | -0.43007 | 4.2661
42 | 0.0022288 | 0.00052947 | -0.0022265 | -0.00053461 | 2.2634e-06 | -5.1417e-06 | 0.003384 | 0.0033862 | 0.0033862 | 0.97712 | -0.44052 | 0.97603 | -0.46261 | 0.93028
43 | 0.00014366 | 3.5105e-05 | -0.00014366 | -3.5788e-05 | 9.8337e-10 | -6.8323e-07 | 0.00021875 | 0.00021899 | 0.00021899 | 0.97583 | -0.46681 | 0.97582 | -0.46695 | 0.060162
44 | -0.0002279 | -5.6218e-05 | 0.0002279 | 5.6014e-05 | 7.3733e-10 | -2.0333e-07 | 0.0003472 | 0.00034713 | 0.0003472 | 0.97583 | -0.46681 | 0.97583 | -0.46674 | 0.095385
45 | 0.00010548 | 2.622e-05 | -0.00010548 | -2.6437e-05 | 1.683e-10 | -2.167e-07 | 0.00016077 | 0.00016085 | 0.00016085 | 0.97582 | -0.46695 | 0.97582 | -0.46699 | 0.04419
46 | -0.0002279 | -5.6014e-05 | 0.00022791 | 5.4173e-05 | 6.6618e-09 | -1.841e-06 | 0.00034713 | 0.00034649 | 0.00034713 | 0.97583 | -0.46674 | 0.97586 | -0.46611 | 0.095366
47 | -0.0018446 | -0.00044104 | 0.0018449 | 0.00043998 | 2.9634e-07 | -1.0653e-06 | 0.0028053 | 0.0028048 | 0.0028053 | 0.97586 | -0.46611 | 0.97603 | -0.46261 | 0.77067
48 | 0.0016167 | 0.00038687 | -0.0016165 | -0.00038771 | 1.7229e-07 | -8.3895e-07 | 0.0024588 | 0.0024591 | 0.0024591 | 0.97586 | -0.46611 | 0.97575 | -0.46842 | 0.67557
49 | 0.00038162 | 9.463e-05 | -0.00038161 | -9.533e-05 | 7.1482e-09 | -6.998e-07 | 0.00058143 | 0.00058168 | 0.00058168 | 0.97603 | -0.46261 | 0.97601 | -0.46301 | 0.1598
50 | 0.0015643 | 0.00037461 | -0.0015642 | -0.00037489 | 5.3208e-08 | -2.7896e-07 | 0.0023794 | 0.0023795 | 0.0023795 | 0.97575 | -0.46842 | 0.97571 | -0.46916 | 0.65372
51 | 0.00010673 | 2.6053e-05 | -0.00010673 | -2.6476e-05 | 3.373e-10 | -4.2364e-07 | 0.00016262 | 0.00016277 | 0.00016277 | 0.97508 | -0.48235 | 0.97507 | -0.48242 | 0.044718
52 | -0.0002811 | -6.9755e-05 | 0.00028113 | 6.4553e-05 | 2.8724e-08 | -5.2026e-06 | 0.00042873 | 0.00042693 | 0.00042873 | 0.97508 | -0.48235 | 0.97518 | -0.48013 | 0.11778
53 | 0.00010673 | 2.6476e-05 | -0.00010673 | -2.6748e-05 | 2.166e-10 | -2.7162e-07 | 0.00016277 | 0.00016287 | 0.00016287 | 0.97507 | -0.48242 | 0.97507 | -0.48246 | 0.044744
54 | -0.00028113 | -6.4553e-05 | 0.00028115 | 6.1576e-05 | 1.6324e-08 | -2.9762e-06 | 0.00042693 | 0.00042596 | 0.00042693 | 0.97518 | -0.48013 | 0.97525 | -0.47881 | 0.11729
55 | 9.6388e-05 | 2.3847e-05 | -9.6387e-05 | -2.4157e-05 | 2.0107e-10 | -3.104e-07 | 0.00014684 | 0.00014695 | 0.00014695 | 0.97601 | -0.46301 | 0.97601 | -0.46305 | 0.040371
56 | 0.0014344 | 0.00034235 | -0.0014343 | -0.00034274 | 6.1522e-08 | -3.9114e-07 | 0.0021815 | 0.0021817 | 0.0021817 | 0.97571 | -0.46916 | 0.97567 | -0.47009 | 0.59936
57 | 0.0006042 | 0.00015109 | -0.00060419 | -0.00015142 | 8.6272e-09 | -3.3485e-07 | 0.00092002 | 0.00092014 | 0.00092014 | 0.97709 | -0.44106 | 0.97707 | -0.44136 | 0.25279
58 | 0.0061429 | 0.0015378 | -0.006142 | -0.0015375 | 9.7275e-07 | 2.5135e-07 | 0.0093545 | 0.0093546 | 0.0093546 | 0.97709 | -0.44106 | 0.97692 | -0.44439 | 2.57
59 | -0.010782 | -0.0026636 | 0.010784 | 0.0026643 | 1.2362e-06 | 6.3739e-07 | 0.016397 | 0.016397 | 0.016397 | 0.97764 | -0.43007 | 0.97776 | -0.42764 | 4.5048
60 | 0.0041737 | 0.0010443 | -0.0041734 | -0.0010443 | 3.5629e-07 | -6.6342e-08 | 0.0063567 | 0.0063568 | 0.0063568 | 0.97692 | -0.44439 | 0.97683 | -0.44618 | 1.7464
61 | 0.0084613 | 0.0021209 | -0.0084591 | -0.0021199 | 2.2412e-06 | 9.8246e-07 | 0.012877 | 0.012877 | 0.012877 | 0.97776 | -0.42764 | 0.97748 | -0.4332 | 3.5377
62 | -0.019245 | -0.0047852 | 0.019253 | 0.0047903 | 8.3902e-06 | 5.0421e-06 | 0.029274 | 0.029274 | 0.029274 | 0.97776 | -0.42764 | 0.97823 | -0.41843 | 8.0424
63 | -0.0008898 | -0.000223 | 0.00088981 | 0.00022276 | 1.3833e-08 | -2.4805e-07 | 0.0013481 | 0.001348 | 0.0013481 | 0.98217 | -0.34115 | 0.98219 | -0.34082 | 0.37035
64 | 0.0040838 | 0.0010229 | -0.0040832 | -0.001023 | 5.8779e-07 | -1.42e-07 | 0.0061867 | 0.0061869 | 0.0061869 | 0.98219 | -0.34082 | 0.98203 | -0.34384 | 1.6997
65 | -0.11613 | -0.029253 | 0.11618 | 0.029285 | 5.0733e-05 | 3.2414e-05 | 0.17599 | 0.17599 | 0.17599 | 0.98219 | -0.34082 | 0.98266 | -0.33169 | 48.3488
66 | 0.11116 | 0.028007 | -0.11108 | -0.027959 | 7.5979e-05 | 4.8537e-05 | 0.16845 | 0.16845 | 0.16845 | 0.98219 | -0.34082 | 0.98145 | -0.35512 | 46.2788
67 | 0.0019311 | 0.00048365 | -0.001931 | -0.00048396 | 9.6687e-08 | -3.191e-07 | 0.002926 | 0.0029262 | 0.0029262 | 0.98203 | -0.34384 | 0.98198 | -0.34489 | 0.80389
68 | -0.11618 | -0.029285 | 0.11675 | 0.02965 | 0.00057144 | 0.00036509 | 0.17599 | 0.17599 | 0.17599 | 0.98266 | -0.33169 | 0.98794 | -0.22944 | 48.3488
69 | 0.08947 | 0.022535 | -0.089311 | -0.022434 | 0.00015841 | 0.00010109 | 0.13569 | 0.13569 | 0.13569 | 0.98145 | -0.35512 | 0.97956 | -0.39222 | 37.277
70 | 0.02161 | 0.0054233 | -0.021603 | -0.005419 | 7.1544e-06 | 4.3543e-06 | 0.032767 | 0.032767 | 0.032767 | 0.98145 | -0.35512 | 0.9811 | -0.36206 | 9.0018
71 | -0.0028432 | -0.00071258 | 0.0028443 | 0.0007113 | 1.1264e-06 | -1.2812e-06 | 0.0043331 | 0.0043324 | 0.0043331 | 0.97638 | -0.45499 | 0.9768 | -0.44666 | 1.1904
72 | -0.0037274 | -0.00093261 | 0.0037275 | 0.00093257 | 8.5847e-08 | -3.396e-08 | 0.0056776 | 0.0056775 | 0.0056776 | 0.9768 | -0.44666 | 0.97683 | -0.44618 | 1.5598
73 | 0.0010387 | 0.00024618 | -0.0010387 | -0.00024651 | 2.6545e-08 | -3.3716e-07 | 0.0015795 | 0.0015797 | 0.0015797 | 0.97548 | -0.47392 | 0.97545 | -0.47448 | 0.43397
74 | -0.0011762 | -0.00028062 | 0.0011762 | 0.00028013 | 5.0536e-08 | -4.9327e-07 | 0.0017892 | 0.001789 | 0.0017892 | 0.97548 | -0.47392 | 0.97553 | -0.47298 | 0.49153
75 | 0.00093432 | 0.00022035 | -0.00093431 | -0.00022048 | 8.1493e-09 | -1.2923e-07 | 0.0014204 | 0.0014205 | 0.0014205 | 0.97545 | -0.47448 | 0.97544 | -0.47467 | 0.39024
76 | 9.9707e-05 | 2.4344e-05 | -9.9706e-05 | -2.4989e-05 | 4.4731e-10 | -6.4452e-07 | 0.00015186 | 0.00015209 | 0.00015209 | 0.97553 | -0.47298 | 0.97552 | -0.47308 | 0.041782
77 | -0.0012759 | -0.00030447 | 0.0012761 | 0.00030308 | 1.6939e-07 | -1.3893e-06 | 0.0019409 | 0.0019403 | 0.0019409 | 0.97553 | -0.47298 | 0.97567 | -0.47009 | 0.5332
78 | 0.00065037 | 0.00014932 | -0.00065036 | -0.00014969 | 1.1044e-08 | -3.6995e-07 | 0.0009874 | 0.00098752 | 0.00098752 | 0.97544 | -0.47467 | 0.97543 | -0.47505 | 0.2713
79 | 0.00056164 | 0.00012745 | -0.00056155 | -0.00013155 | 9.0872e-08 | -4.0993e-06 | 0.00085221 | 0.00085359 | 0.00085359 | 0.97543 | -0.47505 | 0.97525 | -0.47865 | 0.2345
80 | 0.00034205 | 7.6541e-05 | -0.00034205 | -7.684e-05 | 2.428e-09 | -2.9861e-07 | 0.00051875 | 0.00051885 | 0.00051885 | 0.97525 | -0.47865 | 0.97525 | -0.47881 | 0.14254
81 | 0.061437 | 0.015436 | -0.061416 | -0.015423 | 2.0544e-05 | 1.307e-05 | 0.093505 | 0.093505 | 0.093505 | 0.97784 | -0.42585 | 0.97748 | -0.43286 | 25.6882
82 | -0.061437 | -0.015436 | 0.061536 | 0.015499 | 9.8798e-05 | 6.2852e-05 | 0.093505 | 0.093505 | 0.093505 | 0.97784 | -0.42585 | 0.97956 | -0.39222 | 25.6882
83 | 0.034167 | 0.0085846 | -0.034141 | -0.0085686 | 2.5413e-05 | 1.5951e-05 | 0.052019 | 0.052019 | 0.052019 | 0.97748 | -0.43286 | 0.97669 | -0.44845 | 14.291
84 | 0.02725 | 0.0068387 | -0.027239 | -0.006832 | 1.0784e-05 | 6.6926e-06 | 0.041486 | 0.041486 | 0.041486 | 0.97748 | -0.43286 | 0.97706 | -0.44116 | 11.3972
85 | 0.021828 | 0.005445 | -0.021811 | -0.0054345 | 1.7263e-05 | 1.0521e-05 | 0.03315 | 0.03315 | 0.03315 | 0.97956 | -0.39222 | 0.97871 | -0.40889 | 9.1071
86 | 0.0059471 | 0.00149 | -0.0059465 | -0.0014899 | 6.4366e-07 | 1.4722e-07 | 0.0090339 | 0.009034 | 0.009034 | 0.97956 | -0.39222 | 0.97944 | -0.39449 | 2.4819
87 | 0.032075 | 0.0080508 | -0.032063 | -0.0080435 | 1.1751e-05 | 7.3563e-06 | 0.048872 | 0.048872 | 0.048872 | 0.97669 | -0.44845 | 0.9763 | -0.45614 | 13.4263
88 | 0.023758 | 0.0059597 | -0.023745 | -0.0059517 | 1.2969e-05 | 7.9694e-06 | 0.036185 | 0.036185 | 0.036185 | 0.97706 | -0.44116 | 0.97648 | -0.45262 | 9.9409
89 | -0.11854 | -0.030098 | 0.1189 | 0.030327 | 0.00035948 | 0.00022968 | 0.17868 | 0.17868 | 0.17868 | 0.98794 | -0.22944 | 0.99121 | -0.16663 | 49.0873
90 | 0.0085816 | 0.0021512 | -0.0085793 | -0.0021502 | 2.3454e-06 | 1.044e-06 | 0.01308 | 0.01308 | 0.01308 | 0.97629 | -0.45625 | 0.976 | -0.46199 | 3.5934
91 | 0.0044348 | 0.0011109 | -0.0044345 | -0.0011109 | 3.2323e-07 | -2.9038e-08 | 0.0067591 | 0.0067592 | 0.0067592 | 0.97629 | -0.45625 | 0.97622 | -0.45778 | 1.8569
92 | -0.013016 | -0.0032621 | 0.013019 | 0.0032633 | 2.2562e-06 | 1.2528e-06 | 0.019839 | 0.019839 | 0.019839 | 0.97629 | -0.45625 | 0.97648 | -0.45262 | 5.4503
93 | 0.002665 | 0.00066784 | -0.0026649 | -0.00066788 | 3.3172e-08 | -4.5794e-08 | 0.0040621 | 0.0040621 | 0.0040621 | 0.97622 | -0.45778 | 0.9762 | -0.45805 | 1.116
94 | 0.0017695 | 0.00044305 | -0.0017694 | -0.00044345 | 1.014e-07 | -3.9981e-07 | 0.002697 | 0.0026972 | 0.0026972 | 0.97622 | -0.45778 | 0.97615 | -0.45899 | 0.74099
95 | 0.018776 | 0.0047103 | -0.018766 | -0.0047047 | 9.3443e-06 | 5.5926e-06 | 0.028478 | 0.028478 | 0.028478 | 0.9811 | -0.36206 | 0.98057 | -0.37251 | 7.8237
96 | 0.0202 | 0.0050307 | -0.020191 | -0.0050251 | 9.1361e-06 | 5.5224e-06 | 0.0307 | 0.0307 | 0.0307 | 0.97871 | -0.40889 | 0.97823 | -0.41843 | 8.4341
97 | 0.0037832 | 0.0009477 | -0.0037829 | -0.00094784 | 3.6217e-07 | -1.3611e-07 | 0.0057475 | 0.0057476 | 0.0057476 | 0.97944 | -0.39449 | 0.97934 | -0.3965 | 1.579
98 | 0.027579 | 0.0069196 | -0.027574 | -0.0069166 | 4.8786e-06 | 3.0302e-06 | 0.042037 | 0.042037 | 0.042037 | 0.9763 | -0.45614 | 0.97611 | -0.45985 | 11.5486
99 | -0.12027 | -0.030671 | 0.12065 | 0.030917 | 0.00038442 | 0.00024562 | 0.18074 | 0.18074 | 0.18074 | 0.99121 | -0.16663 | 0.99467 | -0.10066 | 49.6525
100 | 0.0017091 | 0.00042831 | -0.001709 | -0.00042833 | 3.468e-09 | -1.4817e-08 | 0.0026051 | 0.0026051 | 0.0026051 | 0.9762 | -0.45805 | 0.9762 | -0.45809 | 0.71568
101 | 0.0016416 | 0.00041117 | -0.0016415 | -0.0004114 | 4.8451e-08 | -2.3163e-07 | 0.002491 | 0.0024911 | 0.0024911 | 0.98057 | -0.37251 | 0.98053 | -0.37313 | 0.68436
102 | 0.017125 | 0.0042936 | -0.017121 | -0.0042914 | 3.6413e-06 | 2.1491e-06 | 0.025987 | 0.025987 | 0.025987 | 0.98057 | -0.37251 | 0.98034 | -0.37697 | 7.1394
103 | 0.0018797 | 0.00047085 | -0.0018796 | -0.00047107 | 6.3133e-08 | -2.1931e-07 | 0.0028559 | 0.002856 | 0.002856 | 0.97934 | -0.3965 | 0.9793 | -0.3972 | 0.78461
104 | 0.011196 | 0.0028072 | -0.011192 | -0.0028055 | 3.27e-06 | 1.6863e-06 | 0.016717 | 0.016717 | 0.016717 | 0.99659 | -0.064511 | 0.99627 | -0.070641 | 4.5926
105 | -0.011582 | -0.002904 | 0.011588 | 0.0029071 | 5.9333e-06 | 3.1076e-06 | 0.017293 | 0.017293 | 0.017293 | 0.99659 | -0.064511 | 0.99714 | -0.053766 | 4.7509
106 | 0.12269 | 0.031537 | -0.12241 | -0.031359 | 0.00027885 | 0.00017817 | 0.18337 | 0.18337 | 0.18337 | 0.99714 | -0.053766 | 0.99467 | -0.10066 | 50.3774
107 | 0.11063 | 0.028568 | -0.11059 | -0.028542 | 4.0573e-05 | 2.5915e-05 | 0.1654 | 0.1654 | 0.1654 | 0.99714 | -0.053766 | 0.99674 | -0.06129 | 45.4387
108 | 0.0024561 | 0.00061545 | -0.0024561 | -0.00061555 | 4.9183e-08 | -9.567e-08 | 0.0036666 | 0.0036667 | 0.0036667 | 0.99674 | -0.06129 | 0.99672 | -0.06171 | 1.0073
109 | 0.10814 | 0.027926 | -0.10776 | -0.027682 | 0.00038189 | 0.00024391 | 0.16173 | 0.16173 | 0.16173 | 0.99674 | -0.06129 | 0.9929 | -0.13398 | 44.4314
110 | 0.0015999 | 0.00040064 | -0.0015999 | -0.00040097 | 6.1588e-08 | -3.3005e-07 | 0.0023976 | 0.0023978 | 0.0023978 | 0.9929 | -0.13398 | 0.99286 | -0.13479 | 0.65873
111 | 0.023907 | 0.0059975 | -0.023894 | -0.0059898 | 1.2537e-05 | 7.709e-06 | 0.036447 | 0.036447 | 0.036447 | 0.97611 | -0.45985 | 0.97555 | -0.47085 | 10.0128
112 | 0.012979 | 0.0032533 | -0.012979 | -0.0032531 | 3.0129e-07 | 1.6672e-07 | 0.0197 | 0.0197 | 0.0197 | 0.98034 | -0.37697 | 0.98031 | -0.37746 | 5.4121
113 | 0.0098507 | 0.0024692 | -0.0098476 | -0.0024677 | 3.0165e-06 | 1.4771e-06 | 0.014952 | 0.014953 | 0.014953 | 0.98031 | -0.37746 | 0.97999 | -0.38389 | 4.1079
114 | 0.0079132 | 0.0019829 | -0.0079115 | -0.0019822 | 1.7069e-06 | 6.9526e-07 | 0.012015 | 0.012016 | 0.012016 | 0.97999 | -0.38389 | 0.97976 | -0.38842 | 3.301
115 | 0.0055636 | 0.0013938 | -0.0055621 | -0.0013935 | 1.4335e-06 | 2.4335e-07 | 0.0084495 | 0.0084498 | 0.0084498 | 0.97976 | -0.38842 | 0.97948 | -0.39383 | 2.3214
116 | 0.0042786 | 0.0010718 | -0.0042783 | -0.0010719 | 3.0661e-07 | -4.7335e-08 | 0.0064998 | 0.0064999 | 0.0064999 | 0.97948 | -0.39383 | 0.9794 | -0.39533 | 1.7857
117 | 0.017692 | 0.0044354 | -0.01769 | -0.004434 | 2.2955e-06 | 1.3642e-06 | 0.026987 | 0.026987 | 0.026987 | 0.97555 | -0.47085 | 0.97541 | -0.47358 | 7.4139
118 | 0.0062021 | 0.0015544 | -0.0062016 | -0.0015542 | 4.9895e-07 | 1.3372e-07 | 0.0094601 | 0.0094601 | 0.0094601 | 0.97555 | -0.47085 | 0.97547 | -0.47254 | 2.5989
119 | 0.013471 | 0.0033767 | -0.01347 | -0.0033759 | 1.3913e-06 | 7.808e-07 | 0.020551 | 0.020551 | 0.020551 | 0.97541 | -0.47358 | 0.9753 | -0.47574 | 5.6459
120 | 0.00062169 | 0.0001558 | -0.00062169 | -0.00015581 | 4.0756e-10 | -1.4824e-08 | 0.00094835 | 0.00094835 | 0.00094835 | 0.97547 | -0.47254 | 0.97546 | -0.47255 | 0.26054
121 | 0.0086313 | 0.0021633 | -0.0086304 | -0.0021629 | 9.0276e-07 | 4.0455e-07 | 0.013169 | 0.013169 | 0.013169 | 0.9753 | -0.47574 | 0.97519 | -0.47794 | 3.6178
122 | 0.0034447 | 0.00086321 | -0.0034446 | -0.00086329 | 1.4737e-07 | -8.3144e-08 | 0.0052562 | 0.0052562 | 0.0052562 | 0.97519 | -0.47794 | 0.97515 | -0.47884 | 1.444
123 | 0.0031943 | 0.00080022 | -0.0031943 | -0.00080027 | 6.1204e-08 | -4.8035e-08 | 0.004853 | 0.0048531 | 0.0048531 | 0.9794 | -0.39533 | 0.97938 | -0.39573 | 1.3333
124 | 0.0077967 | 0.0019539 | -0.0077956 | -0.0019535 | 1.0844e-06 | 4.3675e-07 | 0.011869 | 0.011869 | 0.011869 | 0.97748 | -0.4332 | 0.97733 | -0.43612 | 3.2607
125 | 0.0072396 | 0.0018142 | -0.007239 | -0.0018139 | 5.8883e-07 | 2.1491e-07 | 0.011022 | 0.011023 | 0.011023 | 0.97733 | -0.43612 | 0.97724 | -0.43782 | 3.0282
126 | 0.00069235 | 0.00017326 | -0.00069234 | -0.00017352 | 8.5734e-09 | -2.5227e-07 | 0.0010541 | 0.0010542 | 0.0010542 | 0.97724 | -0.43782 | 0.97723 | -0.43808 | 0.28962
127 | 0.0065467 | 0.0016407 | -0.0065463 | -0.0016406 | 3.839e-07 | 1.1663e-07 | 0.0099684 | 0.0099684 | 0.0099684 | 0.97724 | -0.43782 | 0.97718 | -0.43906 | 2.7386
128 | -0.0021117 | -0.00052917 | 0.0021118 | 0.00052899 | 6.8777e-08 | -1.8017e-07 | 0.0032085 | 0.0032085 | 0.0032085 | 0.97935 | -0.39642 | 0.97938 | -0.39573 | 0.88147
129 | 0.0010559 | 0.00026454 | -0.0010559 | -0.00026463 | 6.7724e-09 | -8.396e-08 | 0.0016043 | 0.0016043 | 0.0016043 | 0.97935 | -0.39642 | 0.97934 | -0.39655 | 0.44074
130 | -0.0026139 | -0.0006551 | 0.0026139 | 0.00065509 | 8.02e-09 | -1.1769e-08 | 0.0039808 | 0.0039808 | 0.0039808 | 0.97705 | -0.44162 | 0.97706 | -0.44156 | 1.0936
131 | -0.0050537 | -0.0012666 | 0.0050541 | 0.0012666 | 4.5081e-07 | 3.4325e-08 | 0.0076966 | 0.0076965 | 0.0076966 | 0.97706 | -0.44156 | 0.97715 | -0.43968 | 2.1144
132 | -0.0057627 | -0.0014442 | 0.0057629 | 0.0014442 | 1.7262e-07 | 3.5599e-08 | 0.0087755 | 0.0087755 | 0.0087755 | 0.97715 | -0.43968 | 0.97718 | -0.43906 | 2.4109

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28325 | 0.072487

## res_load
| p_mw | q_mvar
0 | 0.017471 | 0.0043788
1 | 0.0063701 | 0.0015965
2 | 0.0075623 | 0.0018953
3 | 0.01368 | 0.0034286
4 | 0.012005 | 0.0030088
5 | 0.0083873 | 0.0021021
6 | 0.004501 | 0.0011281
7 | 0.0052577 | 0.0013177
8 | 0.0057644 | 0.0014447
9 | 0.004866 | 0.0012195
10 | 0.0087678 | 0.0021974
11 | 0.0015997 | 0.00040093
12 | 0.017471 | 0.0043788
13 | 0.0016006 | 0.00040116
14 | 0.0094883 | 0.002378
15 | 0.0049808 | 0.0012483
16 | 0.0040711 | 0.0010203
17 | 0.0010495 | 0.00026304
18 | 0.0043931 | 0.001101
19 | 0.00040706 | 0.00010202
20 | 0.0054242 | 0.0013594
21 | 0.00068388 | 0.0001714
22 | 0.00069255 | 0.00017357
23 | 0.00011835 | 2.9661e-05
24 | 0.00010728 | 2.6888e-05
25 | 0.00012087 | 3.0292e-05
26 | 8.6645e-05 | 2.1715e-05
27 | 0.00010378 | 2.601e-05
28 | 8.424e-05 | 2.1113e-05
29 | 3.8178e-05 | 9.5683e-06
30 | 0.00010548 | 2.6437e-05
31 | 5.2247e-05 | 1.3094e-05
32 | 0.00017437 | 4.3702e-05
33 | 0.00010673 | 2.6748e-05
34 | 0.00028522 | 7.1483e-05
35 | 0.00012984 | 3.2542e-05
36 | 9.6387e-05 | 2.4157e-05
37 | 0.00057111 | 0.00014313
38 | 0.00060419 | 0.00015142
39 | 0.0019682 | 0.00049329
40 | 0.0008898 | 0.000223
41 | 0.0021521 | 0.00053936
42 | 0.0028432 | 0.00071258
43 | 0.00088303 | 0.00022131
44 | 0.00044592 | 0.00011176
45 | 0.00013744 | 3.4445e-05
46 | 0.00010439 | 2.6162e-05
47 | 0.00028394 | 7.1162e-05
48 | 9.9706e-05 | 2.4989e-05
49 | 0.00015824 | 3.966e-05
50 | 8.8722e-05 | 2.2236e-05
51 | 0.0002195 | 5.5011e-05
52 | 6.0901e-05 | 1.5263e-05
53 | 0.002066 | 0.00051778
54 | 0.0034808 | 0.00087238
55 | 0.0017849 | 0.00044734
56 | 0.0085793 | 0.0021502
57 | 0.010727 | 0.0026884
58 | 0.0028275 | 0.00070865
59 | 0.0016114 | 0.00040385
60 | 0.0021632 | 0.00054216
61 | 0.0044844 | 0.0011239
62 | 0.0013707 | 0.00034354
63 | 0.00095589 | 0.00023957
64 | 0.0017694 | 0.00044345
65 | 0.00093724 | 0.00023489
66 | 0.0019032 | 0.00047699
67 | 0.00038619 | 9.6789e-05
68 | 0.00055921 | 0.00014015
69 | 0.0017637 | 0.00044203
70 | 0.0024561 | 0.00061555
71 | 0.0015999 | 0.00040097
72 | 0.0051846 | 0.0012994
73 | 0.001709 | 0.00042833
74 | 0.0036672 | 0.00091909
75 | 0.001931 | 0.00048396
76 | 0.0041422 | 0.0010381
77 | 0.0031278 | 0.00078391
78 | 0.0019344 | 0.00048481
79 | 0.0016415 | 0.0004114
80 | 0.002348 | 0.00058846
81 | 0.0012835 | 0.00032168
82 | 0.0018796 | 0.00047107
83 | 0.0042188 | 0.0010573
84 | 0.0055799 | 0.0013985
85 | 0.00062169 | 0.00015581
86 | 0.0048385 | 0.0012126
87 | 0.0051857 | 0.0012997
88 | 0.0034446 | 0.00086329
89 | 0.001084 | 0.00027167
90 | 0.0006624 | 0.00016601
91 | 0.00055597 | 0.00013934
92 | 0.0010559 | 0.00026463
93 | 0.0010824 | 0.00027129
94 | 0.0010559 | 0.00026463
95 | 0.0026139 | 0.0006551
96 | 0.0024398 | 0.00061147
97 | 0.0007086 | 0.00017759
98 | 0.00078341 | 0.00019634
99 | 0.00069234 | 0.00017352

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1