## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1093-9_1_5_node_14 | 0.4 | n |  | TRUE
1 | bus_LV_1093-9_1_5_node_15 | 0.4 | n |  | TRUE
2 | bus_LV_1093-9_1_5_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_1093-9_1_5_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_1093-9_1_5_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_1093-9_1_5_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1093-9_1_5_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1093-9_1_5_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_1093-9_1_5_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1093-9_1_5_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_1093-9_1_5_node_160 | 0.4 | n |  | TRUE
11 | bus_LV_1093-9_1_5_node_113 | 0.4 | n |  | TRUE
12 | bus_LV_1093-9_1_5_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1093-9_1_5_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_1093-9_1_5_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1093-9_1_5_node_114 | 0.4 | n |  | TRUE
16 | bus_LV_1093-9_1_5_node_103 | 0.4 | n |  | TRUE
17 | bus_LV_1093-9_1_5_node_85 | 0.4 | n |  | TRUE
18 | bus_LV_1093-9_1_5_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1093-9_1_5_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1093-9_1_5_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_1093-9_1_5_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1093-9_1_5_node_90 | 0.4 | n |  | TRUE
23 | bus_LV_1093-9_1_5_node_89 | 0.4 | n |  | TRUE
24 | bus_LV_1093-9_1_5_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_1093-9_1_5_node_91 | 0.4 | n |  | TRUE
26 | bus_LV_1093-9_1_5_node_99 | 0.4 | n |  | TRUE
27 | bus_LV_1093-9_1_5_node_100 | 0.4 | n |  | TRUE
28 | bus_LV_1093-9_1_5_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_1093-9_1_5_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_1093-9_1_5_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_1093-9_1_5_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_1093-9_1_5_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_1093-9_1_5_node_74 | 0.4 | n |  | TRUE
34 | bus_LV_1093-9_1_5_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_1093-9_1_5_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_1093-9_1_5_node_70 | 0.4 | n |  | TRUE
37 | bus_LV_1093-9_1_5_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_1093-9_1_5_node_72 | 0.4 | n |  | TRUE
39 | bus_LV_1093-9_1_5_node_73 | 0.4 | n |  | TRUE
40 | bus_LV_1093-9_1_5_node_78 | 0.4 | n |  | TRUE
41 | bus_LV_1093-9_1_5_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_1093-9_1_5_node_80 | 0.4 | n |  | TRUE
43 | bus_LV_1093-9_1_5_node_79 | 0.4 | n |  | TRUE
44 | bus_LV_1093-9_1_5_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_1093-9_1_5_node_82 | 0.4 | n |  | TRUE
46 | bus_LV_1093-9_1_5_node_84 | 0.4 | n |  | TRUE
47 | bus_LV_1093-9_1_5_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_1093-9_1_5_node_87 | 0.4 | n |  | TRUE
49 | bus_LV_1093-9_1_5_node_88 | 0.4 | n |  | TRUE
50 | bus_LV_1093-9_1_5_node_131 | 0.4 | n |  | TRUE
51 | bus_LV_1093-9_1_5_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_1093-9_1_5_node_93 | 0.4 | n |  | TRUE
53 | bus_LV_1093-9_1_5_node_94 | 0.4 | n |  | TRUE
54 | bus_LV_1093-9_1_5_node_95 | 0.4 | n |  | TRUE
55 | bus_LV_1093-9_1_5_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_1093-9_1_5_node_104 | 0.4 | n |  | TRUE
57 | bus_LV_1093-9_1_5_node_101 | 0.4 | n |  | TRUE
58 | bus_LV_1093-9_1_5_node_102 | 0.4 | n |  | TRUE
59 | bus_LV_1093-9_1_5_node_111 | 0.4 | n |  | TRUE
60 | bus_LV_1093-9_1_5_node_112 | 0.4 | n |  | TRUE
61 | bus_LV_1093-9_1_5_node_109 | 0.4 | n |  | TRUE
62 | bus_LV_1093-9_1_5_node_105 | 0.4 | n |  | TRUE
63 | bus_LV_1093-9_1_5_node_106 | 0.4 | n |  | TRUE
64 | bus_LV_1093-9_1_5_node_107 | 0.4 | n |  | TRUE
65 | bus_LV_1093-9_1_5_node_108 | 0.4 | n |  | TRUE
66 | bus_LV_1093-9_1_5_node_110 | 0.4 | n |  | TRUE
67 | bus_LV_1093-9_1_5_node_116 | 0.4 | n |  | TRUE
68 | bus_LV_1093-9_1_5_node_118 | 0.4 | n |  | TRUE
69 | bus_LV_1093-9_1_5_node_154 | 0.4 | n |  | TRUE
70 | bus_LV_1093-9_1_5_node_115 | 0.4 | n |  | TRUE
71 | bus_LV_1093-9_1_5_node_120 | 0.4 | n |  | TRUE
72 | bus_LV_1093-9_1_5_node_117 | 0.4 | n |  | TRUE
73 | bus_LV_1093-9_1_5_node_122 | 0.4 | n |  | TRUE
74 | bus_LV_1093-9_1_5_node_121 | 0.4 | n |  | TRUE
75 | bus_LV_1093-9_1_5_node_155 | 0.4 | n |  | TRUE
76 | bus_LV_1093-9_1_5_node_153 | 0.4 | n |  | TRUE
77 | bus_LV_1093-9_1_5_node_119 | 0.4 | n |  | TRUE
78 | bus_LV_1093-9_1_5_node_151 | 0.4 | n |  | TRUE
79 | bus_LV_1093-9_1_5_node_150 | 0.4 | n |  | TRUE
80 | bus_LV_1093-9_1_5_node_123 | 0.4 | n |  | TRUE
81 | bus_LV_1093-9_1_5_node_156 | 0.4 | n |  | TRUE
82 | bus_LV_1093-9_1_5_node_148 | 0.4 | n |  | TRUE
83 | bus_LV_1093-9_1_5_node_152 | 0.4 | n |  | TRUE
84 | bus_LV_1093-9_1_5_node_157 | 0.4 | n |  | TRUE
85 | bus_LV_1093-9_1_5_node_158 | 0.4 | n |  | TRUE
86 | bus_MV_354_0_node_236 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1093-9_1_5_load_14 | 0 | 0.09326 | 0.023373 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1093-9_1_5_load_21 | 6 | 0.040233 | 0.010083 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1093-9_1_5_load_23 | 7 | 0.024593 | 0.0061635 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1093-9_1_5_load_31 | 8 | 0.00064568 | 0.00016182 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1093-9_1_5_load_160 | 10 | 0.00075498 | 0.00018922 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1093-9_1_5_load_32 | 13 | 0.00035203 | 8.8226e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1093-9_1_5_load_114 | 15 | 0.00028831 | 7.2258e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1093-9_1_5_load_26 | 18 | 0.00038619 | 9.6788e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1093-9_1_5_load_30 | 21 | 0.00015329 | 3.8417e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1093-9_1_5_load_90 | 22 | 0.00021264 | 5.3292e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1093-9_1_5_load_89 | 23 | 0.0010492 | 0.00026294 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1093-9_1_5_load_91 | 25 | 0.00018594 | 4.6602e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1093-9_1_5_load_99 | 26 | 0.00030719 | 7.6988e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1093-9_1_5_load_100 | 27 | 0.0013408 | 0.00033605 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1093-9_1_5_load_86 | 28 | 0.0052122 | 0.0013063 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1093-9_1_5_load_63 | 30 | 0.0013813 | 0.00034619 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1093-9_1_5_load_67 | 31 | 0.0015123 | 0.00037903 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1093-9_1_5_load_68 | 32 | 0.00089792 | 0.00022504 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1093-9_1_5_load_74 | 33 | 0.0016868 | 0.00042276 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1093-9_1_5_load_75 | 34 | 0.0020271 | 0.00050805 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1093-9_1_5_load_69 | 35 | 0.00071494 | 0.00017918 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1093-9_1_5_load_71 | 37 | 0.0010016 | 0.00025102 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1093-9_1_5_load_73 | 39 | 0.00089103 | 0.00022331 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1093-9_1_5_load_77 | 41 | 0.095016 | 0.023813 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1093-9_1_5_load_80 | 42 | 0.0010468 | 0.00026235 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1093-9_1_5_load_79 | 43 | 0.001447 | 0.00036264 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1093-9_1_5_load_76 | 44 | 0.023771 | 0.0059576 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1093-9_1_5_load_82 | 45 | 0.00069403 | 0.00017394 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1093-9_1_5_load_84 | 46 | 0.0022759 | 0.00057039 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1093-9_1_5_load_83 | 47 | 0.0010867 | 0.00027236 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1093-9_1_5_load_88 | 49 | 0.00080137 | 0.00020084 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1093-9_1_5_load_131 | 50 | 0.00077887 | 0.0001952 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1093-9_1_5_load_92 | 51 | 0.00069181 | 0.00017338 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1093-9_1_5_load_93 | 52 | 0.00067547 | 0.00016929 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1093-9_1_5_load_94 | 53 | 0.0019648 | 0.00049243 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1093-9_1_5_load_96 | 55 | 0.001127 | 0.00028244 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1093-9_1_5_load_102 | 58 | 0.00031517 | 7.8989e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1093-9_1_5_load_111 | 59 | 0.00050151 | 0.00012569 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1093-9_1_5_load_112 | 60 | 0.00023622 | 5.9203e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1093-9_1_5_load_109 | 61 | 9.9306e-05 | 2.4888e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1093-9_1_5_load_106 | 63 | 0.0010373 | 0.00025998 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1093-9_1_5_load_107 | 64 | 0.00014258 | 3.5734e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1093-9_1_5_load_108 | 65 | 0.00017773 | 4.4543e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1093-9_1_5_load_154 | 69 | 9.3141e-05 | 2.3343e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1093-9_1_5_load_115 | 70 | 0.00047873 | 0.00011998 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1093-9_1_5_load_117 | 72 | 0.00051369 | 0.00012874 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1093-9_1_5_load_122 | 73 | 0.00072451 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1093-9_1_5_load_155 | 75 | 5.0932e-05 | 1.2765e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1093-9_1_5_load_153 | 76 | 0.00058505 | 0.00014663 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1093-9_1_5_load_119 | 77 | 0.00031564 | 7.9106e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1093-9_1_5_load_123 | 80 | 0.00019558 | 4.9016e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1093-9_1_5_load_148 | 82 | 0.00029211 | 7.3209e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1093-9_1_5_load_157 | 84 | 0.00069665 | 0.0001746 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1093-9_1_5_load_158 | 85 | 0.00012266 | 3.0742e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1093-9_1_5_line_0 |  | 0 | 1 | 0.045751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1093-9_1_5_line_1 |  | 0 | 2 | 0.058819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1093-9_1_5_line_2 |  | 1 | 3 | 0.092845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1093-9_1_5_line_3 |  | 2 | 4 | 0.046627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1093-9_1_5_line_4 |  | 3 | 5 | 0.079053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1093-9_1_5_line_5 |  | 3 | 6 | 0.023616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1093-9_1_5_line_6 |  | 4 | 8 | 0.11391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1093-9_1_5_line_7 |  | 5 | 7 | 0.043589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1093-9_1_5_line_8 |  | 8 | 12 | 0.036221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1093-9_1_5_line_9 |  | 9 | 10 | 0.014361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1093-9_1_5_line_10 |  | 9 | 11 | 0.029018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1093-9_1_5_line_11 |  | 11 | 15 | 0.02221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1093-9_1_5_line_12 |  | 11 | 16 | 0.031724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1093-9_1_5_line_13 |  | 12 | 13 | 0.0095413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1093-9_1_5_line_14 |  | 12 | 14 | 0.049729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1093-9_1_5_line_15 |  | 13 | 17 | 0.032354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1093-9_1_5_line_16 |  | 14 | 18 | 0.012223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1093-9_1_5_line_17 |  | 15 | 70 | 0.013846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1093-9_1_5_line_18 |  | 16 | 60 | 0.02745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1093-9_1_5_line_19 |  | 16 | 57 | 0.030284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1093-9_1_5_line_20 |  | 17 | 28 | 0.026086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1093-9_1_5_line_21 |  | 17 | 29 | 0.058001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1093-9_1_5_line_22 |  | 18 | 19 | 0.016633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1093-9_1_5_line_23 |  | 19 | 20 | 0.020394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1093-9_1_5_line_24 |  | 19 | 21 | 0.015212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1093-9_1_5_line_25 |  | 20 | 22 | 0.016128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1093-9_1_5_line_26 |  | 20 | 23 | 0.036467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1093-9_1_5_line_27 |  | 21 | 24 | 0.018718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1093-9_1_5_line_28 |  | 22 | 25 | 0.062572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1093-9_1_5_line_29 |  | 24 | 26 | 0.018817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1093-9_1_5_line_30 |  | 24 | 27 | 0.036698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1093-9_1_5_line_31 |  | 25 | 51 | 0.026315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1093-9_1_5_line_32 |  | 26 | 57 | 0.030768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1093-9_1_5_line_33 |  | 27 | 56 | 0.023436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1093-9_1_5_line_34 |  | 28 | 48 | 0.29438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1093-9_1_5_line_35 |  | 29 | 46 | 0.012636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1093-9_1_5_line_36 |  | 30 | 31 | 0.1252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1093-9_1_5_line_37 |  | 31 | 32 | 0.031764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1093-9_1_5_line_38 |  | 32 | 35 | 0.012842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1093-9_1_5_line_39 |  | 33 | 34 | 0.019454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1093-9_1_5_line_40 |  | 34 | 44 | 0.0096703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1093-9_1_5_line_41 |  | 35 | 36 | 0.18122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1093-9_1_5_line_42 |  | 36 | 37 | 0.028321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1093-9_1_5_line_43 |  | 36 | 38 | 0.03532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1093-9_1_5_line_44 |  | 37 | 39 | 0.14819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1093-9_1_5_line_45 |  | 38 | 40 | 0.11451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1093-9_1_5_line_46 |  | 38 | 41 | 0.01388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1093-9_1_5_line_47 |  | 40 | 42 | 0.033492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_1093-9_1_5_line_48 |  | 40 | 43 | 0.0096817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1093-9_1_5_line_49 |  | 41 | 44 | 0.009792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1093-9_1_5_line_50 |  | 42 | 45 | 0.028959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_1093-9_1_5_line_51 |  | 45 | 47 | 0.013387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_1093-9_1_5_line_52 |  | 46 | 47 | 0.040482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_1093-9_1_5_line_53 |  | 48 | 49 | 0.48069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1093-9_1_5_line_54 |  | 49 | 50 | 0.023733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1093-9_1_5_line_55 |  | 51 | 52 | 0.035708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1093-9_1_5_line_56 |  | 53 | 54 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1093-9_1_5_line_57 |  | 54 | 55 | 0.056425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1093-9_1_5_line_58 |  | 55 | 56 | 0.045607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1093-9_1_5_line_59 |  | 57 | 58 | 0.010898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1093-9_1_5_line_60 |  | 58 | 59 | 0.015839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1093-9_1_5_line_61 |  | 59 | 61 | 0.020598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1093-9_1_5_line_62 |  | 61 | 62 | 0.06719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1093-9_1_5_line_63 |  | 62 | 63 | 0.033733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1093-9_1_5_line_64 |  | 63 | 64 | 0.026549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1093-9_1_5_line_65 |  | 64 | 65 | 0.33489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1093-9_1_5_line_66 |  | 65 | 66 | 0.17981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1093-9_1_5_line_67 |  | 66 | 67 | 0.29252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1093-9_1_5_line_68 |  | 67 | 68 | 0.32542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1093-9_1_5_line_69 |  | 67 | 69 | 0.062127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1093-9_1_5_line_70 |  | 68 | 71 | 0.08327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1093-9_1_5_line_71 |  | 68 | 72 | 0.10001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1093-9_1_5_line_72 |  | 69 | 76 | 0.0092519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1093-9_1_5_line_73 |  | 71 | 73 | 0.046252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1093-9_1_5_line_74 |  | 73 | 80 | 0.0035545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1093-9_1_5_line_75 |  | 74 | 75 | 0.015313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1093-9_1_5_line_76 |  | 74 | 76 | 0.015618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1093-9_1_5_line_77 |  | 75 | 81 | 0.017469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1093-9_1_5_line_78 |  | 77 | 78 | 0.041102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1093-9_1_5_line_79 |  | 78 | 79 | 0.003243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1093-9_1_5_line_80 |  | 79 | 83 | 0.015049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1093-9_1_5_line_81 |  | 79 | 82 | 0.23034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1093-9_1_5_line_82 |  | 81 | 83 | 0.0073634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1093-9_1_5_line_83 |  | 83 | 84 | 0.054036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1093-9_1_5_line_84 |  | 84 | 85 | 0.011138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1093-9_1_5_trafo_16 | 0.63 MVA 20/0.4 kV | 86 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2658224.58 | 1218534.56 | 2658221.8138 | 1218525.6053 | 2658254.411 | 1218509.4542
1 | 2658268.737 | 1218467.7947 | 2658270.802 | 1218469.2936 | 2658275.9506 | 1218483.7529 | 2658279.5288 | 1218492.7156 | 2658276.8477 | 1218498.3373 | 2658254.411 | 1218509.4542
2 | 2658224.58 | 1218534.56 | 2658224.0908 | 1218542.6714 | 2658220.1528 | 1218550.3376 | 2658212.6178 | 1218556.39 | 2658182.9195 | 1218569.5971 | 2658176.0444 | 1218547.7276 | 2658170.1316 | 1218538.442
3 | 2658268.737 | 1218467.7947 | 2658274.6231 | 1218461.9598 | 2658306.0635 | 1218439.8758
4 | 2658141.6809 | 1218587.906 | 2658182.9195 | 1218569.5971 | 2658176.0444 | 1218547.7276 | 2658170.1316 | 1218538.442
5 | 2658170.1316 | 1218538.442 | 2658191.2188 | 1218527.8106
6 | 2658306.0635 | 1218439.8758 | 2658332.0854 | 1218427.0669 | 2658393.6544 | 1218396.8288 | 2658402.4269 | 1218393.1014 | 2658406.5164 | 1218390.9179 | 2658408.048 | 1218392.4272
7 | 2658141.6809 | 1218587.906 | 2658158.9803 | 1218627.9151
8 | 2658440.129 | 1218389.6687 | 2658430.3627 | 1218392.5748 | 2658414.4246 | 1218398.7113 | 2658408.048 | 1218392.4272
9 | 2658410.9655 | 1218553.3395 | 2658404.2365 | 1218540.6435
10 | 2658410.9655 | 1218553.3395 | 2658437.331 | 1218541.057
11 | 2658437.331 | 1218541.057 | 2658429.0154 | 1218526.0773 | 2658428.7316 | 1218521.0078
12 | 2658466.6639 | 1218528.8037 | 2658451.7908 | 1218535.4953 | 2658437.331 | 1218541.057
13 | 2658440.129 | 1218389.6687 | 2658434.691 | 1218381.8289
14 | 2658468.4323 | 1218430.5937 | 2658465.9128 | 1218427.4671 | 2658447.4738 | 1218400.7253 | 2658441.0639 | 1218391.0788 | 2658440.129 | 1218389.6687
15 | 2658416.1783 | 1218355.3128 | 2658424.6198 | 1218366.7692 | 2658427.2939 | 1218371.1648 | 2658434.691 | 1218381.8289
16 | 2658468.4323 | 1218430.5937 | 2658477.8023 | 1218438.4422
17 | 2658425.1192 | 1218507.7834 | 2658428.4923 | 1218516.7331 | 2658428.7316 | 1218521.0078
18 | 2658466.6639 | 1218528.8037 | 2658464.5639 | 1218533.9863 | 2658454.8787 | 1218545.6652 | 2658450.5933 | 1218550.7973
19 | 2658466.6639 | 1218528.8037 | 2658479.6539 | 1218523.7613 | 2658488.6613 | 1218516.9566 | 2658492.2267 | 1218513.2782
20 | 2658416.1783 | 1218355.3128 | 2658415.2316 | 1218349.6889 | 2658416.9083 | 1218343.5682 | 2658420.3135 | 1218339.9661 | 2658428.4454 | 1218335.9258
21 | 2658416.1783 | 1218355.3128 | 2658399.7627 | 1218362.9122 | 2658389.6497 | 1218367.894 | 2658375.8169 | 1218368.3032 | 2658361.9361 | 1218362.7639
22 | 2658492.1817 | 1218446.7367 | 2658479.2575 | 1218439.6611 | 2658477.8023 | 1218438.4422
23 | 2658494.521 | 1218426.4805 | 2658492.1817 | 1218446.7367
24 | 2658492.1817 | 1218446.7367 | 2658503.1904 | 1218452.5705 | 2658505.3509 | 1218454.2772
25 | 2658494.521 | 1218426.4805 | 2658510.432 | 1218423.8416
26 | 2658494.521 | 1218426.4805 | 2658498.1456 | 1218399.7662 | 2658499.2575 | 1218390.3233
27 | 2658514.5599 | 1218469.5704 | 2658511.5276 | 1218459.1564 | 2658505.3509 | 1218454.2772
28 | 2658563.7693 | 1218396.0406 | 2658560.2342 | 1218400.1761 | 2658543.8196 | 1218415.3909 | 2658535.0256 | 1218419.7628 | 2658510.432 | 1218423.8416
29 | 2658514.5599 | 1218469.5704 | 2658510.9211 | 1218483.043 | 2658508.5956 | 1218487.3123
30 | 2658514.5599 | 1218469.5704 | 2658544.766 | 1218474.3255 | 2658550.8838 | 1218474.1757
31 | 2658563.7693 | 1218396.0406 | 2658573.8246 | 1218384.2776 | 2658584.2218 | 1218381.212
32 | 2658492.2267 | 1218513.2782 | 2658495.8515 | 1218508.9556 | 2658503.6867 | 1218496.3247 | 2658508.5956 | 1218487.3123
33 | 2658573.8742 | 1218470.3201 | 2658559.023 | 1218473.9764 | 2658550.8838 | 1218474.1757
34 | 2658620.9722 | 1218132.1076 | 2658613.0962 | 1218141.8695 | 2658574.8317 | 1218218.5407 | 2658558.5551 | 1218257.4938 | 2658551.5388 | 1218267.8534 | 2658543.6535 | 1218276.2701 | 2658535.4343 | 1218282.3709 | 2658522.5709 | 1218289.1599 | 2658428.4454 | 1218335.9258
35 | 2658361.9361 | 1218362.7639 | 2658363.6071 | 1218350.2392
36 | 2657956.6978 | 1217988.6705 | 2657960.2587 | 1217999.6769 | 2657979.0909 | 1218026.1429 | 2657993.9632 | 1218052.3593 | 2658005.0557 | 1218084.7872 | 2658010.8236 | 1218100.495
37 | 2658010.8236 | 1218100.495 | 2658017.6258 | 1218119.0195 | 2658023.2298 | 1218129.6651
38 | 2658023.2298 | 1218129.6651 | 2658026.1736 | 1218135.2571 | 2658030.616 | 1218140.0323
39 | 2658131.0553 | 1218278.6129 | 2658148.1857 | 1218287.832
40 | 2658148.1857 | 1218287.832 | 2658156.7012 | 1218292.4148
41 | 2658164.2767 | 1218261.2472 | 2658145.5136 | 1218238.7503 | 2658122.0526 | 1218213.0835 | 2658093.4621 | 1218190.3686 | 2658051.7504 | 1218158.8429 | 2658036.5696 | 1218146.4318 | 2658030.616 | 1218140.0323
42 | 2658164.2767 | 1218261.2472 | 2658168.5003 | 1218246.8907 | 2658177.5221 | 1218237.0423
43 | 2658180.2108 | 1218291.2879 | 2658181.0709 | 1218286.371 | 2658177.8368 | 1218279.4574 | 2658168.6579 | 1218266.5043 | 2658164.2767 | 1218261.2472
44 | 2658177.5221 | 1218237.0423 | 2658189.9814 | 1218223.4414 | 2658242.4562 | 1218166.2964 | 2658255.0142 | 1218145.7176 | 2658263.1305 | 1218118.8628
45 | 2658283.9011 | 1218327.4008 | 2658276.8581 | 1218320.3721 | 2658261.9962 | 1218307.252 | 2658238.0763 | 1218296.0114 | 2658211.9553 | 1218290.9643 | 2658189.4431 | 1218289.4435 | 2658180.2108 | 1218291.2879
46 | 2658180.2108 | 1218291.2879 | 2658172.3018 | 1218292.8672 | 2658166.489 | 1218292.6986
47 | 2658283.9011 | 1218327.4008 | 2658296.6573 | 1218321.4552 | 2658309.8409 | 1218307.1989
48 | 2658283.9011 | 1218327.4008 | 2658275.2328 | 1218331.713
49 | 2658166.489 | 1218292.6986 | 2658156.7012 | 1218292.4148 | 2658156.7012 | 1218292.4148
50 | 2658309.8409 | 1218307.1989 | 2658316.679 | 1218299.8044 | 2658327.4785 | 1218299.9101 | 2658332.2601 | 1218306.4322
51 | 2658340.1749 | 1218317.2283 | 2658332.2601 | 1218306.4322
52 | 2658340.1749 | 1218317.2283 | 2658341.4023 | 1218318.9025 | 2658363.6071 | 1218350.2392
53 | 2658620.9722 | 1218132.1076 | 2658622.1162 | 1218125.3814 | 2658628.0933 | 1218114.2222 | 2658631.3838 | 1218102.2471 | 2658631.5445 | 1218089.7744 | 2658629.2916 | 1218074.9764 | 2658624.6434 | 1218064.4798 | 2658587.1597 | 1218016.9153 | 2658579.9343 | 1218006.0376 | 2658572.3708 | 1217994.0448 | 2658569.7272 | 1217988.0818 | 2658567.3968 | 1217981.9218 | 2658565.8691 | 1217976.7258 | 2658564.0349 | 1217966.4125 | 2658564.8753 | 1217948.8655 | 2658566.4378 | 1217934.3163 | 2658570.0844 | 1217905.4232 | 2658571.6241 | 1217898.5897 | 2658584.3015 | 1217862.1807 | 2658596.433 | 1217829.5799 | 2658616.5559 | 1217770.9193 | 2658625.7834 | 1217748.8298 | 2658638.5703 | 1217721.4053 | 2658644.1939 | 1217710.7207 | 2658655.6033 | 1217690.6205
54 | 2658670.747 | 1217672.3464 | 2658655.6033 | 1217690.6205 | 2658655.6033 | 1217690.6205
55 | 2658584.2218 | 1218381.212 | 2658596.4854 | 1218377.5961 | 2658618.324 | 1218370.6317
56 | 2658665.9859 | 1218426.9324 | 2658659.3949 | 1218400.1455
57 | 2658665.9859 | 1218426.9324 | 2658625.3353 | 1218443.0758 | 2658613.874 | 1218448.5141
58 | 2658573.8742 | 1218470.3201 | 2658582.6266 | 1218465.5476 | 2658598.7989 | 1218455.6671 | 2658613.874 | 1218448.5141
59 | 2658492.2267 | 1218513.2782 | 2658500.0266 | 1218520.8898
60 | 2658500.0266 | 1218520.8898 | 2658506.5554 | 1218527.2608 | 2658512.3946 | 1218530.5799
61 | 2658512.3946 | 1218530.5799 | 2658516.2087 | 1218532.7478 | 2658531.1051 | 1218539.1425
62 | 2658597.047 | 1218549.6746 | 2658573.0603 | 1218548.4714 | 2658557.5931 | 1218546.8629 | 2658544.2364 | 1218543.6631 | 2658531.1051 | 1218539.1425
63 | 2658597.047 | 1218549.6746 | 2658623.4413 | 1218549.9343 | 2658630.7321 | 1218549.1099
64 | 2658630.7321 | 1218549.1099 | 2658642.5278 | 1218547.7762 | 2658657.1388 | 1218546.3766
65 | 2658657.1388 | 1218546.3766 | 2658667.7873 | 1218545.3566 | 2658698.2159 | 1218544.4334 | 2658711.1278 | 1218545.7836 | 2658721.8502 | 1218548.2796 | 2658732.4128 | 1218551.5857 | 2658746.7955 | 1218556.1747 | 2658763.087 | 1218559.6041 | 2658770.9389 | 1218559.9484 | 2658779.1541 | 1218558.0949 | 2658791.0896 | 1218553.7877 | 2658801.7261 | 1218548.834 | 2658822.7717 | 1218536.5896 | 2658864.8328 | 1218511.3448 | 2658878.4009 | 1218505.4307 | 2658889.102 | 1218500.8669 | 2658901.9622 | 1218496.7136 | 2658911.7452 | 1218494.4311 | 2658921.4092 | 1218494.2043 | 2658929.4712 | 1218496.3297 | 2658940.6088 | 1218502.1212 | 2658967.7162 | 1218519.311 | 2658967.8774 | 1218519.4123
66 | 2659119.9932 | 1218614.4671 | 2659112.2574 | 1218607.7862 | 2659096.2556 | 1218599.6559 | 2659076.545 | 1218590.5104 | 2659065.8119 | 1218584.5225 | 2659025.9719 | 1218557.1443 | 2659000.0899 | 1218539.6439 | 2658967.8774 | 1218519.4123
67 | 2659119.9932 | 1218614.4671 | 2659110.3782 | 1218627.3686 | 2659079.404 | 1218671.0997 | 2659024.5023 | 1218746.0688 | 2658997.6864 | 1218782.3258 | 2658991.8849 | 1218792.6192 | 2658988.3059 | 1218804.5578 | 2658986.9432 | 1218819.5425 | 2658985.095 | 1218865.1747
68 | 2658705.9933 | 1218937.4085 | 2658705.9218 | 1218933.1051 | 2658795.7097 | 1218915.4014 | 2658872.1407 | 1218899.268 | 2658888.9946 | 1218896.3771 | 2658897.3173 | 1218895.8813 | 2658907.8469 | 1218895.5518 | 2658935.8118 | 1218897.2293 | 2658960.6901 | 1218900.2216 | 2658983.5765 | 1218904.3284 | 2658985.095 | 1218865.1747
69 | 2658985.095 | 1218865.1747 | 2659003.411 | 1218879.4203 | 2659014.9457 | 1218887.9398 | 2659029.1055 | 1218898.0752 | 2659034.8686 | 1218902.3409
70 | 2658705.9933 | 1218937.4085 | 2658705.9218 | 1218933.1051 | 2658684.9681 | 1218938.491 | 2658631.9035 | 1218960.1933
71 | 2658705.9933 | 1218937.4085 | 2658706.7583 | 1218982.2215 | 2658706.1166 | 1218988.041 | 2658704.0425 | 1218992.1231 | 2658699.7641 | 1218995.7832 | 2658695.8265 | 1218997.9792 | 2658689.493 | 1219000.7074 | 2658679.5746 | 1219005.2792 | 2658664.8626 | 1219011.1158 | 2658663.9036 | 1219011.2741
72 | 2659042.305 | 1218907.8453 | 2659034.8686 | 1218902.3409
73 | 2658631.9035 | 1218960.1933 | 2658616.1504 | 1218932.9993 | 2658613.109 | 1218918.4895
74 | 2658613.109 | 1218918.4895 | 2658612.3797 | 1218915.0106
75 | 2659031.3497 | 1218918.977 | 2659043.1914 | 1218928.686
76 | 2659031.3497 | 1218918.977 | 2659042.305 | 1218907.8453
77 | 2659057.3194 | 1218938.9355 | 2659055.1021 | 1218937.5349 | 2659046.8876 | 1218931.7166 | 2659043.1914 | 1218928.686
78 | 2659049.0503 | 1218956.231 | 2659045.8714 | 1218955.3767 | 2659047.3577 | 1218950.8998 | 2659049.9508 | 1218943.4875 | 2659049.6221 | 1218941.4275 | 2659048.0281 | 1218937.6204 | 2659033.4445 | 1218925.4004
79 | 2659049.0503 | 1218956.231 | 2659052.1915 | 1218957.0737
80 | 2659058.6545 | 1218943.5961 | 2659055.1846 | 1218949.1207 | 2659053.4806 | 1218952.5837 | 2659052.1915 | 1218957.0737
81 | 2659052.1915 | 1218957.0737 | 2659050.405 | 1218965.0387 | 2659049.7372 | 1218973.4484 | 2659051.0564 | 1219001.1453 | 2659059.721 | 1219139.1389 | 2659061.9998 | 1219166.4784 | 2659063.0008 | 1219172.6811 | 2659064.8673 | 1219177.3024 | 2659069.4426 | 1219185.109
82 | 2659058.6545 | 1218943.5961 | 2659055.4041 | 1218942.2853 | 2659057.3194 | 1218938.9355
83 | 2659058.6545 | 1218943.5961 | 2659067.5135 | 1218947.175 | 2659111.4411 | 1218954.1748
84 | 2659111.4411 | 1218954.1748 | 2659113.6435 | 1218954.5257 | 2659122.2379 | 1218956.8674

## bus_geodata
| x | y | coords
0 | 2658254.411 | 1218509.4542
1 | 2658224.58 | 1218534.56
2 | 2658268.737 | 1218467.7947
3 | 2658170.1316 | 1218538.442
4 | 2658306.0635 | 1218439.8758
5 | 2658141.6809 | 1218587.906
6 | 2658191.2188 | 1218527.8106
7 | 2658158.9803 | 1218627.9151
8 | 2658408.048 | 1218392.4272
9 | 2658410.9655 | 1218553.3395
10 | 2658404.2365 | 1218540.6435
11 | 2658437.331 | 1218541.057
12 | 2658440.129 | 1218389.6687
13 | 2658434.691 | 1218381.8289
14 | 2658468.4323 | 1218430.5937
15 | 2658428.7316 | 1218521.0078
16 | 2658466.6639 | 1218528.8037
17 | 2658416.1783 | 1218355.3128
18 | 2658477.8023 | 1218438.4422
19 | 2658492.1817 | 1218446.7367
20 | 2658494.521 | 1218426.4805
21 | 2658505.3508 | 1218454.2772
22 | 2658510.432 | 1218423.8416
23 | 2658499.2575 | 1218390.3233
24 | 2658514.5599 | 1218469.5704
25 | 2658563.7693 | 1218396.0406
26 | 2658508.5956 | 1218487.3123
27 | 2658550.8838 | 1218474.1757
28 | 2658428.4454 | 1218335.9258
29 | 2658361.9361 | 1218362.7639
30 | 2657956.6978 | 1217988.6705
31 | 2658010.8236 | 1218100.495
32 | 2658023.2298 | 1218129.6651
33 | 2658131.0553 | 1218278.6129
34 | 2658148.1857 | 1218287.832
35 | 2658030.616 | 1218140.0323
36 | 2658164.2767 | 1218261.2472
37 | 2658177.5221 | 1218237.0423
38 | 2658180.2108 | 1218291.2879
39 | 2658263.1305 | 1218118.8628
40 | 2658283.9011 | 1218327.4008
41 | 2658166.489 | 1218292.6986
42 | 2658309.8409 | 1218307.1989
43 | 2658275.2328 | 1218331.7131
44 | 2658156.7012 | 1218292.4148
45 | 2658332.2601 | 1218306.4322
46 | 2658363.6071 | 1218350.2392
47 | 2658340.1749 | 1218317.2283
48 | 2658620.9722 | 1218132.1076
49 | 2658655.6033 | 1217690.6205
50 | 2658670.747 | 1217672.3464
51 | 2658584.2218 | 1218381.212
52 | 2658618.324 | 1218370.6317
53 | 2658659.3949 | 1218400.1455
54 | 2658665.9859 | 1218426.9324
55 | 2658613.874 | 1218448.5141
56 | 2658573.8742 | 1218470.3201
57 | 2658492.2267 | 1218513.2782
58 | 2658500.0266 | 1218520.8898
59 | 2658512.3946 | 1218530.5799
60 | 2658450.5933 | 1218550.7973
61 | 2658531.1051 | 1218539.1425
62 | 2658597.047 | 1218549.6746
63 | 2658630.7321 | 1218549.1099
64 | 2658657.1388 | 1218546.3766
65 | 2658967.8774 | 1218519.4123
66 | 2659119.9932 | 1218614.4671
67 | 2658985.095 | 1218865.1747
68 | 2658705.9933 | 1218937.4085
69 | 2659034.8686 | 1218902.3409
70 | 2658425.1192 | 1218507.7834
71 | 2658631.9035 | 1218960.1933
72 | 2658663.9036 | 1219011.2741
73 | 2658613.109 | 1218918.4895
74 | 2659031.3497 | 1218918.977
75 | 2659043.1914 | 1218928.686
76 | 2659042.305 | 1218907.8453
77 | 2659033.4445 | 1218925.4004
78 | 2659049.0503 | 1218956.231
79 | 2659052.1915 | 1218957.0737
80 | 2658612.3797 | 1218915.0106
81 | 2659057.3194 | 1218938.9355
82 | 2659069.4426 | 1219185.109
83 | 2659058.6545 | 1218943.5961
84 | 2659111.4411 | 1218954.1748
85 | 2659122.2379 | 1218956.8674
86 | 2658256.229 | 1218470.9077

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99575 | -0.081385 | 0.09326 | 0.023373
1 | 0.99302 | -0.13367 | 0 | 0
2 | 1 | 0 | -0.32364 | -0.082549
3 | 0.98748 | -0.24066 | 0 | 0
4 | 0.9977 | -0.04321 | 0 | 0
5 | 0.98569 | -0.27548 | 0 | 0
6 | 0.98661 | -0.25766 | 0.040233 | 0.010083
7 | 0.9847 | -0.29473 | 0.024593 | 0.0061635
8 | 0.99207 | -0.14961 | 0.00064568 | 0.00016182
9 | 0.98831 | -0.22222 | 0 | 0
10 | 0.9883 | -0.22242 | 0.00075498 | 0.00018922
11 | 0.98833 | -0.22183 | 0 | 0
12 | 0.99029 | -0.18356 | 0 | 0
13 | 0.98987 | -0.19163 | 0.00035203 | 8.8226e-05
14 | 0.98958 | -0.19754 | 0 | 0
15 | 0.98832 | -0.22214 | 0.00028831 | 7.2258e-05
16 | 0.98838 | -0.22097 | 0 | 0
17 | 0.98844 | -0.21897 | 0 | 0
18 | 0.9894 | -0.20098 | 0.00038619 | 9.6788e-05
19 | 0.98917 | -0.20554 | 0 | 0
20 | 0.98911 | -0.20657 | 0 | 0
21 | 0.98899 | -0.20896 | 0.00015329 | 3.8417e-05
22 | 0.98909 | -0.20708 | 0.00021264 | 5.3292e-05
23 | 0.98908 | -0.20725 | 0.0010492 | 0.00026294
24 | 0.98878 | -0.21311 | 0 | 0
25 | 0.989 | -0.20881 | 0.00018594 | 4.6602e-05
26 | 0.98864 | -0.21579 | 0.00030719 | 7.6988e-05
27 | 0.98863 | -0.21601 | 0.0013408 | 0.00033605
28 | 0.98828 | -0.22214 | 0.0052122 | 0.0013063
29 | 0.98599 | -0.26582 | 0 | 0
30 | 0.97254 | -0.52796 | 0.0013813 | 0.00034619
31 | 0.9727 | -0.52477 | 0.0015123 | 0.00037903
32 | 0.97279 | -0.52307 | 0.00089792 | 0.00022504
33 | 0.97191 | -0.54049 | 0.0016868 | 0.00042276
34 | 0.97194 | -0.53988 | 0.0020271 | 0.00050805
35 | 0.97284 | -0.52217 | 0.00071494 | 0.00017918
36 | 0.9736 | -0.50712 | 0 | 0
37 | 0.97355 | -0.50811 | 0.0010016 | 0.00025102
38 | 0.97381 | -0.50295 | 0 | 0
39 | 0.97342 | -0.51054 | 0.00089103 | 0.00022331
40 | 0.98069 | -0.36823 | 0 | 0
41 | 0.97222 | -0.53425 | 0.095016 | 0.023813
42 | 0.98205 | -0.34189 | 0.0010468 | 0.00026235
43 | 0.98068 | -0.36849 | 0.001447 | 0.00036264
44 | 0.97197 | -0.53922 | 0.023771 | 0.0059576
45 | 0.98323 | -0.31899 | 0.00069403 | 0.00017394
46 | 0.98546 | -0.27605 | 0.0022759 | 0.00057039
47 | 0.98378 | -0.30837 | 0.0010867 | 0.00027236
48 | 0.98785 | -0.23056 | 0 | 0
49 | 0.98715 | -0.24421 | 0.00080137 | 0.00020084
50 | 0.98714 | -0.24454 | 0.00077887 | 0.0001952
51 | 0.98897 | -0.20946 | 0.00069181 | 0.00017338
52 | 0.98894 | -0.20989 | 0.00067547 | 0.00016929
53 | 0.98828 | -0.22277 | 0.0019648 | 0.00049243
54 | 0.98833 | -0.2218 | 0 | 0
55 | 0.98843 | -0.21983 | 0.001127 | 0.00028244
56 | 0.98856 | -0.21731 | 0 | 0
57 | 0.98843 | -0.22002 | 0 | 0
58 | 0.98837 | -0.22117 | 0.00031517 | 7.8989e-05
59 | 0.98829 | -0.22276 | 0.00050151 | 0.00012569
60 | 0.98837 | -0.22108 | 0.00023622 | 5.9203e-05
61 | 0.98819 | -0.22463 | 9.9306e-05 | 2.4888e-05
62 | 0.98789 | -0.23065 | 0 | 0
63 | 0.98773 | -0.23366 | 0.0010373 | 0.00025998
64 | 0.98764 | -0.23555 | 0.00014258 | 3.5734e-05
65 | 0.98648 | -0.25845 | 0.00017773 | 4.4543e-05
66 | 0.98589 | -0.27017 | 0 | 0
67 | 0.98492 | -0.28922 | 0 | 0
68 | 0.98449 | -0.29768 | 0 | 0
69 | 0.9848 | -0.29164 | 9.3141e-05 | 2.3343e-05
70 | 0.98831 | -0.22225 | 0.00047873 | 0.00011998
71 | 0.98442 | -0.29907 | 0 | 0
72 | 0.98445 | -0.29861 | 0.00051369 | 0.00012874
73 | 0.98438 | -0.29983 | 0.00072451 | 0.00018158
74 | 0.98476 | -0.29241 | 0 | 0
75 | 0.98474 | -0.29282 | 5.0932e-05 | 1.2765e-05
76 | 0.98478 | -0.29199 | 0.00058505 | 0.00014663
77 | 0.98469 | -0.29388 | 0.00031564 | 7.9106e-05
78 | 0.9847 | -0.29365 | 0 | 0
79 | 0.9847 | -0.29363 | 0 | 0
80 | 0.98438 | -0.29984 | 0.00019558 | 4.9016e-05
81 | 0.98472 | -0.29327 | 0 | 0
82 | 0.98464 | -0.29485 | 0.00029211 | 7.3209e-05
83 | 0.98471 | -0.29346 | 0 | 0
84 | 0.98467 | -0.29426 | 0.00069665 | 0.0001746
85 | 0.98467 | -0.29428 | 0.00012266 | 3.0742e-05
86 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.065419 | 0.016623 | -0.065255 | -0.016519 | 0.00016424 | 0.00010452 | 0.097841 | 0.097841 | 0.097841 | 0.99575 | -0.081385 | 0.99302 | -0.13367 | 26.8795
1 | -0.15868 | -0.039996 | 0.1593 | 0.040392 | 0.00062054 | 0.00039561 | 0.23721 | 0.23721 | 0.23721 | 0.99575 | -0.081385 | 1 | 0 | 32.5833
2 | 0.065255 | 0.016519 | -0.064922 | -0.016306 | 0.0003333 | 0.00021212 | 0.097841 | 0.097842 | 0.097842 | 0.99302 | -0.13367 | 0.98748 | -0.24066 | 26.8796
3 | 0.16269 | 0.042157 | -0.16235 | -0.041939 | 0.00034298 | 0.00021768 | 0.24258 | 0.24258 | 0.24258 | 1 | 0 | 0.9977 | -0.04321 | 22.2146
4 | 0.024656 | 0.0062026 | -0.024615 | -0.0061774 | 4.0941e-05 | 2.5193e-05 | 0.037162 | 0.037163 | 0.037163 | 0.98748 | -0.24066 | 0.98569 | -0.27548 | 10.2095
5 | 0.040265 | 0.010104 | -0.040233 | -0.010083 | 3.2608e-05 | 2.0567e-05 | 0.06068 | 0.06068 | 0.06068 | 0.98748 | -0.24066 | 0.98661 | -0.25766 | 16.6703
6 | 0.16235 | 0.041939 | -0.16151 | -0.041407 | 0.00083794 | 0.00053185 | 0.24258 | 0.24258 | 0.24258 | 0.9977 | -0.04321 | 0.99207 | -0.14961 | 22.2147
7 | 0.024615 | 0.0061774 | -0.024593 | -0.0061635 | 2.2575e-05 | 1.3893e-05 | 0.037163 | 0.037163 | 0.037163 | 0.98569 | -0.27548 | 0.9847 | -0.29473 | 10.2096
8 | 0.16087 | 0.041246 | -0.1606 | -0.041078 | 0.00026432 | 0.00016776 | 0.24162 | 0.24162 | 0.24162 | 0.99207 | -0.14961 | 0.99029 | -0.18356 | 22.1261
9 | 0.00075499 | 0.00018904 | -0.00075498 | -0.00018922 | 6.9582e-09 | -1.7957e-07 | 0.0011366 | 0.0011367 | 0.0011367 | 0.98831 | -0.22222 | 0.9883 | -0.22242 | 0.31228
10 | -0.00075499 | -0.00018904 | 0.000755 | 0.00018867 | 1.4057e-08 | -3.6286e-07 | 0.0011366 | 0.0011365 | 0.0011366 | 0.98831 | -0.22222 | 0.98833 | -0.22183 | 0.31227
11 | 0.00076705 | 0.00019179 | -0.00076704 | -0.00019206 | 1.1106e-08 | -2.7751e-07 | 0.0011547 | 0.0011548 | 0.0011548 | 0.98833 | -0.22183 | 0.98832 | -0.22214 | 0.31725
12 | -0.0015221 | -0.00038046 | 0.0015221 | 0.00038009 | 6.2449e-08 | -3.6659e-07 | 0.0022912 | 0.0022911 | 0.0022912 | 0.98833 | -0.22183 | 0.98838 | -0.22097 | 0.62946
13 | 0.14485 | 0.037149 | -0.14479 | -0.037113 | 5.6654e-05 | 3.589e-05 | 0.21795 | 0.21795 | 0.21795 | 0.99029 | -0.18356 | 0.98987 | -0.19163 | 19.9588
14 | 0.015755 | 0.003929 | -0.015745 | -0.003923 | 1.0446e-05 | 6.046e-06 | 0.023667 | 0.023667 | 0.023667 | 0.99029 | -0.18356 | 0.98958 | -0.19754 | 6.5021
15 | 0.14444 | 0.037025 | -0.14425 | -0.036904 | 0.00019118 | 0.00012111 | 0.21742 | 0.21742 | 0.21742 | 0.98987 | -0.19163 | 0.98844 | -0.21897 | 19.9104
16 | 0.015745 | 0.003923 | -0.015742 | -0.0039215 | 2.5675e-06 | 1.4862e-06 | 0.023667 | 0.023668 | 0.023668 | 0.98958 | -0.19754 | 0.9894 | -0.20098 | 6.5021
17 | 0.00047873 | 0.0001198 | -0.00047873 | -0.00011998 | 2.6971e-09 | -1.757e-07 | 0.00072071 | 0.00072077 | 0.00072077 | 0.98832 | -0.22214 | 0.98831 | -0.22225 | 0.19802
18 | 0.00023622 | 5.8852e-05 | -0.00023622 | -5.9203e-05 | 1.3015e-09 | -3.5097e-07 | 0.00035551 | 0.00035564 | 0.00035564 | 0.98838 | -0.22097 | 0.98837 | -0.22108 | 0.097703
19 | -0.0017583 | -0.00043894 | 0.0017584 | 0.00043861 | 7.9542e-08 | -3.3724e-07 | 0.0026466 | 0.0026464 | 0.0026466 | 0.98838 | -0.22097 | 0.98843 | -0.22002 | 0.72708
20 | 0.0067951 | 0.0016935 | -0.0067941 | -0.0016932 | 1.023e-06 | 3.204e-07 | 0.010226 | 0.010226 | 0.010226 | 0.98844 | -0.21897 | 0.98828 | -0.22214 | 2.8094
21 | 0.13745 | 0.03521 | -0.13714 | -0.035013 | 0.00031125 | 0.00019697 | 0.2072 | 0.2072 | 0.2072 | 0.98844 | -0.21897 | 0.98599 | -0.26582 | 18.974
22 | 0.015356 | 0.0038247 | -0.015353 | -0.0038228 | 3.3244e-06 | 1.9141e-06 | 0.023087 | 0.023087 | 0.023087 | 0.9894 | -0.20098 | 0.98917 | -0.20554 | 6.3425
23 | 0.0028154 | 0.00070323 | -0.0028153 | -0.0007034 | 1.3713e-07 | -1.7401e-07 | 0.0042344 | 0.0042345 | 0.0042345 | 0.98917 | -0.20554 | 0.98911 | -0.20657 | 1.1633
24 | 0.012538 | 0.0031196 | -0.012536 | -0.0031185 | 2.0275e-06 | 1.1023e-06 | 0.018852 | 0.018852 | 0.018852 | 0.98917 | -0.20554 | 0.98899 | -0.20896 | 5.1793
25 | 0.0017661 | 0.0004409 | -0.001766 | -0.00044108 | 4.2675e-08 | -1.7969e-07 | 0.0026563 | 0.0026563 | 0.0026563 | 0.98911 | -0.20657 | 0.98909 | -0.20708 | 0.72976
26 | 0.0010492 | 0.0002625 | -0.0010492 | -0.00026294 | 3.4066e-08 | -4.4624e-07 | 0.0015782 | 0.0015784 | 0.0015784 | 0.98911 | -0.20657 | 0.98908 | -0.20725 | 0.43363
27 | 0.012382 | 0.0030801 | -0.01238 | -0.0030787 | 2.4341e-06 | 1.3177e-06 | 0.018622 | 0.018622 | 0.018622 | 0.98899 | -0.20896 | 0.98878 | -0.21311 | 5.1159
28 | 0.0015534 | 0.00038779 | -0.0015533 | -0.00038851 | 1.2811e-07 | -7.2102e-07 | 0.0023364 | 0.0023367 | 0.0023367 | 0.98909 | -0.20708 | 0.989 | -0.20881 | 0.64196
29 | 0.0079457 | 0.0019693 | -0.0079447 | -0.0019689 | 1.0076e-06 | 4.0356e-07 | 0.01195 | 0.01195 | 0.01195 | 0.98878 | -0.21311 | 0.98864 | -0.21579 | 3.2829
30 | 0.0044341 | 0.0011094 | -0.0044335 | -0.0011095 | 6.1266e-07 | -7.8534e-08 | 0.0066722 | 0.0066723 | 0.0066723 | 0.98878 | -0.21311 | 0.98863 | -0.21601 | 1.8331
31 | 0.0013673 | 0.00034191 | -0.0013673 | -0.00034222 | 4.1755e-08 | -3.1094e-07 | 0.002057 | 0.0020571 | 0.0020571 | 0.989 | -0.20881 | 0.98897 | -0.20946 | 0.56513
32 | 0.0076375 | 0.0018919 | -0.007636 | -0.0018914 | 1.5226e-06 | 5.8001e-07 | 0.011487 | 0.011488 | 0.011488 | 0.98864 | -0.21579 | 0.98843 | -0.22002 | 3.1559
33 | 0.0030926 | 0.00077345 | -0.0030924 | -0.00077363 | 1.9038e-07 | -1.7865e-07 | 0.0046542 | 0.0046543 | 0.0046543 | 0.98863 | -0.21601 | 0.98856 | -0.21731 | 1.2787
34 | 0.0015819 | 0.00038688 | -0.0015813 | -0.00039025 | 6.2483e-07 | -3.3705e-06 | 0.0023784 | 0.0023798 | 0.0023798 | 0.98828 | -0.22214 | 0.98785 | -0.23056 | 0.65378
35 | 0.13714 | 0.035013 | -0.13707 | -0.03497 | 6.7807e-05 | 4.2913e-05 | 0.2072 | 0.2072 | 0.2072 | 0.98599 | -0.26582 | 0.98546 | -0.27605 | 18.9741
36 | -0.0013813 | -0.00034619 | 0.0013815 | 0.00034477 | 2.0965e-07 | -1.4196e-06 | 0.0021135 | 0.0021129 | 0.0021135 | 0.97254 | -0.52796 | 0.9727 | -0.52477 | 0.58062
37 | -0.0028939 | -0.0007238 | 0.0028941 | 0.00072356 | 2.3338e-07 | -2.4496e-07 | 0.0044264 | 0.0044263 | 0.0044264 | 0.9727 | -0.52477 | 0.97279 | -0.52307 | 1.2161
38 | -0.003792 | -0.0009486 | 0.0037922 | 0.00094854 | 1.6198e-07 | -5.5767e-08 | 0.0057998 | 0.0057997 | 0.0057998 | 0.97279 | -0.52307 | 0.97284 | -0.52217 | 1.5934
39 | -0.0016868 | -0.00042276 | 0.0016869 | 0.00042255 | 4.8656e-08 | -2.0995e-07 | 0.0025826 | 0.0025825 | 0.0025826 | 0.97191 | -0.54049 | 0.97194 | -0.53988 | 0.70951
40 | -0.003714 | -0.0009306 | 0.0037141 | 0.00093056 | 1.1724e-07 | -4.4816e-08 | 0.005686 | 0.005686 | 0.005686 | 0.97194 | -0.53988 | 0.97197 | -0.53922 | 1.5621
41 | -0.0045071 | -0.0011277 | 0.0045104 | 0.0011275 | 3.2288e-06 | -1.854e-07 | 0.0068933 | 0.0068925 | 0.0068933 | 0.97284 | -0.52217 | 0.9736 | -0.50712 | 1.8938
42 | 0.0018928 | 0.00047226 | -0.0018927 | -0.00047255 | 8.8836e-08 | -2.9532e-07 | 0.0028921 | 0.0028922 | 0.0028922 | 0.9736 | -0.50712 | 0.97355 | -0.50811 | 0.79457
43 | -0.0064032 | -0.0015998 | 0.0064044 | 0.0016002 | 1.268e-06 | 3.7222e-07 | 0.0097846 | 0.0097844 | 0.0097846 | 0.9736 | -0.50712 | 0.97381 | -0.50295 | 2.6881
44 | 0.00089113 | 0.00022154 | -0.00089103 | -0.00022331 | 1.0305e-07 | -1.7765e-06 | 0.0013614 | 0.0013621 | 0.0013621 | 0.97355 | -0.50811 | 0.97342 | -0.51054 | 0.37419
45 | -0.1291 | -0.032423 | 0.12993 | 0.032955 | 0.00083568 | 0.00053197 | 0.19729 | 0.19729 | 0.19729 | 0.97381 | -0.50295 | 0.98069 | -0.36823 | 27.0999
46 | 0.12269 | 0.030822 | -0.12251 | -0.030705 | 0.000183 | 0.00011695 | 0.1875 | 0.1875 | 0.1875 | 0.97381 | -0.50295 | 0.97222 | -0.53425 | 51.5118
47 | -0.13138 | -0.033317 | 0.13154 | 0.033422 | 0.00016659 | 0.00010535 | 0.19948 | 0.19948 | 0.19948 | 0.98069 | -0.36823 | 0.98205 | -0.34189 | 18.2676
48 | 0.001447 | 0.00036253 | -0.001447 | -0.00036264 | 1.75e-08 | -1.1096e-07 | 0.0021955 | 0.0021955 | 0.0021955 | 0.98069 | -0.36823 | 0.98068 | -0.36849 | 0.60316
49 | 0.027492 | 0.0068922 | -0.027485 | -0.0068881 | 6.5014e-06 | 4.0395e-06 | 0.042078 | 0.042078 | 0.042078 | 0.97222 | -0.53425 | 0.97197 | -0.53922 | 11.5598
50 | -0.13259 | -0.033685 | 0.13274 | 0.033777 | 0.00014634 | 9.2559e-05 | 0.20107 | 0.20107 | 0.20107 | 0.98205 | -0.34189 | 0.98323 | -0.31899 | 18.4128
51 | -0.13343 | -0.033951 | 0.1335 | 0.033995 | 6.8357e-05 | 4.3239e-05 | 0.20212 | 0.20212 | 0.20212 | 0.98323 | -0.31899 | 0.98378 | -0.30837 | 18.5089
52 | 0.1348 | 0.0344 | -0.13459 | -0.034267 | 0.00021009 | 0.00013292 | 0.20376 | 0.20376 | 0.20376 | 0.98546 | -0.27605 | 0.98378 | -0.30837 | 18.6594
53 | 0.0015813 | 0.00039025 | -0.0015803 | -0.00039575 | 1.0218e-06 | -5.4957e-06 | 0.0023798 | 0.0023819 | 0.0023819 | 0.98785 | -0.23056 | 0.98715 | -0.24421 | 0.65438
54 | 0.00077888 | 0.00019491 | -0.00077887 | -0.0001952 | 1.2267e-08 | -2.9556e-07 | 0.001174 | 0.0011741 | 0.0011741 | 0.98715 | -0.24421 | 0.98714 | -0.24454 | 0.32255
55 | 0.00067548 | 0.00016884 | -0.00067547 | -0.00016929 | 1.3829e-08 | -4.4932e-07 | 0.0010162 | 0.0010163 | 0.0010163 | 0.98897 | -0.20946 | 0.98894 | -0.20989 | 0.27921
56 | -0.0019648 | -0.00049243 | 0.0019649 | 0.00049214 | 9.0532e-08 | -2.9555e-07 | 0.0029584 | 0.0029582 | 0.0029584 | 0.98828 | -0.22277 | 0.98833 | -0.2218 | 0.81274
57 | -0.0019649 | -0.00049214 | 0.0019651 | 0.00049153 | 1.8515e-07 | -6.0466e-07 | 0.0029582 | 0.002958 | 0.0029582 | 0.98833 | -0.2218 | 0.98843 | -0.21983 | 0.8127
58 | -0.0030921 | -0.00077397 | 0.0030924 | 0.00077363 | 3.705e-07 | -3.4752e-07 | 0.0046545 | 0.0046543 | 0.0046545 | 0.98843 | -0.21983 | 0.98856 | -0.21731 | 1.2787
59 | 0.0058776 | 0.0014528 | -0.0058773 | -0.0014527 | 3.1946e-07 | 6.4774e-08 | 0.0088412 | 0.0088412 | 0.0088412 | 0.98843 | -0.22002 | 0.98837 | -0.22117 | 2.4289
60 | 0.0055621 | 0.0013737 | -0.0055617 | -0.0013736 | 4.1579e-07 | 6.3132e-08 | 0.0083668 | 0.0083668 | 0.0083668 | 0.98837 | -0.22117 | 0.98829 | -0.22276 | 2.2986
61 | 0.0050602 | 0.0012479 | -0.0050597 | -0.0012479 | 4.4754e-07 | 2.251e-08 | 0.0076117 | 0.0076118 | 0.0076118 | 0.98829 | -0.22276 | 0.98819 | -0.22463 | 2.0912
62 | 0.0049604 | 0.001223 | -0.004959 | -0.001223 | 1.4031e-06 | 3.7473e-08 | 0.0074623 | 0.0074626 | 0.0074626 | 0.98819 | -0.22463 | 0.98789 | -0.23065 | 2.0502
63 | 0.004959 | 0.001223 | -0.0049583 | -0.001223 | 7.0448e-07 | 1.9041e-08 | 0.0074626 | 0.0074627 | 0.0074627 | 0.98789 | -0.23065 | 0.98773 | -0.23366 | 2.0502
64 | 0.003921 | 0.000963 | -0.0039207 | -0.00096312 | 3.4657e-07 | -1.1797e-07 | 0.0059 | 0.0059002 | 0.0059002 | 0.98773 | -0.23366 | 0.98764 | -0.23555 | 1.6209
65 | 0.0037781 | 0.00092738 | -0.003774 | -0.00092907 | 4.0604e-06 | -1.682e-06 | 0.0056853 | 0.0056868 | 0.0056868 | 0.98764 | -0.23555 | 0.98648 | -0.25845 | 1.5623
66 | 0.0035963 | 0.00088452 | -0.0035943 | -0.00088555 | 1.9802e-06 | -1.0269e-06 | 0.0054187 | 0.0054196 | 0.0054196 | 0.98648 | -0.25845 | 0.98589 | -0.27017 | 1.4889
67 | 0.0035943 | 0.00088555 | -0.0035911 | -0.00088721 | 3.2227e-06 | -1.6639e-06 | 0.0054196 | 0.0054209 | 0.0054209 | 0.98589 | -0.27017 | 0.98492 | -0.28922 | 1.4892
68 | 0.0014345 | 0.00035268 | -0.0014339 | -0.00035645 | 5.7225e-07 | -3.7734e-06 | 0.0021648 | 0.0021662 | 0.0021662 | 0.98492 | -0.28922 | 0.98449 | -0.29768 | 0.59512
69 | 0.0021566 | 0.00053454 | -0.0021564 | -0.00053517 | 2.4703e-07 | -6.3248e-07 | 0.0032561 | 0.0032564 | 0.0032564 | 0.98492 | -0.28922 | 0.9848 | -0.29164 | 0.89461
70 | 0.00092018 | 0.00022896 | -0.00092012 | -0.00022998 | 6.0367e-08 | -1.0201e-06 | 0.0013902 | 0.0013906 | 0.0013906 | 0.98449 | -0.29768 | 0.98442 | -0.29907 | 0.38203
71 | 0.00051372 | 0.00012749 | -0.00051369 | -0.00012874 | 2.2597e-08 | -1.2572e-06 | 0.00077601 | 0.00077646 | 0.00077646 | 0.98449 | -0.29768 | 0.98445 | -0.29861 | 0.21331
72 | 0.0020632 | 0.00051183 | -0.0020632 | -0.00051192 | 3.3679e-08 | -9.616e-08 | 0.0031156 | 0.0031157 | 0.0031157 | 0.9848 | -0.29164 | 0.98478 | -0.29199 | 0.85596
73 | 0.00092012 | 0.00022998 | -0.00092009 | -0.00023055 | 3.3545e-08 | -5.6655e-07 | 0.0013906 | 0.0013908 | 0.0013908 | 0.98442 | -0.29907 | 0.98438 | -0.29983 | 0.38209
74 | 0.00019558 | 4.8971e-05 | -0.00019558 | -4.9016e-05 | 1.1649e-10 | -4.5113e-08 | 0.00029562 | 0.00029564 | 0.00029564 | 0.98438 | -0.29983 | 0.98438 | -0.29984 | 0.081219
75 | 0.0014781 | 0.00036548 | -0.0014781 | -0.00036565 | 2.8602e-08 | -1.7651e-07 | 0.0022317 | 0.0022318 | 0.0022318 | 0.98476 | -0.29241 | 0.98474 | -0.29282 | 0.61313
76 | -0.0014781 | -0.00036548 | 0.0014782 | 0.0003653 | 2.917e-08 | -1.8004e-07 | 0.0022317 | 0.0022317 | 0.0022317 | 0.98476 | -0.29241 | 0.98478 | -0.29199 | 0.61312
77 | 0.0014272 | 0.00035289 | -0.0014271 | -0.00035309 | 3.0419e-08 | -2.0276e-07 | 0.0021548 | 0.0021549 | 0.0021549 | 0.98474 | -0.29282 | 0.98472 | -0.29327 | 0.59201
78 | -0.00031564 | -7.9106e-05 | 0.00031564 | 7.8585e-05 | 3.5052e-09 | -5.206e-07 | 0.00047698 | 0.00047679 | 0.00047698 | 0.98469 | -0.29388 | 0.9847 | -0.29365 | 0.13104
79 | -0.00031564 | -7.8585e-05 | 0.00031564 | 7.8544e-05 | 2.7644e-10 | -4.1077e-08 | 0.00047679 | 0.00047678 | 0.00047679 | 0.9847 | -0.29365 | 0.9847 | -0.29363 | 0.13099
80 | -0.00060777 | -0.00014883 | 0.00060777 | 0.00014865 | 4.7471e-09 | -1.884e-07 | 0.00091719 | 0.00091712 | 0.00091719 | 0.9847 | -0.29363 | 0.98471 | -0.29346 | 0.25198
81 | 0.00029213 | 7.029e-05 | -0.00029211 | -7.3209e-05 | 1.6793e-08 | -2.9192e-06 | 0.00044042 | 0.00044144 | 0.00044144 | 0.9847 | -0.29363 | 0.98464 | -0.29485 | 0.12128
82 | 0.0014271 | 0.00035309 | -0.0014271 | -0.00035318 | 1.2823e-08 | -8.5465e-08 | 0.0021549 | 0.002155 | 0.002155 | 0.98472 | -0.29327 | 0.98471 | -0.29346 | 0.59202
83 | 0.00081935 | 0.00020453 | -0.00081931 | -0.0002052 | 3.1055e-08 | -6.675e-07 | 0.0012378 | 0.0012381 | 0.0012381 | 0.98471 | -0.29346 | 0.98467 | -0.29426 | 0.34013
84 | 0.00012266 | 3.06e-05 | -0.00012266 | -3.0742e-05 | 1.4347e-10 | -1.4158e-07 | 0.00018531 | 0.00018536 | 0.00018536 | 0.98467 | -0.29426 | 0.98467 | -0.29428 | 0.050924

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32364 | 0.082549

## res_load
| p_mw | q_mvar
0 | 0.09326 | 0.023373
1 | 0.040233 | 0.010083
2 | 0.024593 | 0.0061635
3 | 0.00064568 | 0.00016182
4 | 0.00075498 | 0.00018922
5 | 0.00035203 | 8.8226e-05
6 | 0.00028831 | 7.2258e-05
7 | 0.00038619 | 9.6788e-05
8 | 0.00015329 | 3.8417e-05
9 | 0.00021264 | 5.3292e-05
10 | 0.0010492 | 0.00026294
11 | 0.00018594 | 4.6602e-05
12 | 0.00030719 | 7.6988e-05
13 | 0.0013408 | 0.00033605
14 | 0.0052122 | 0.0013063
15 | 0.0013813 | 0.00034619
16 | 0.0015123 | 0.00037903
17 | 0.00089792 | 0.00022504
18 | 0.0016868 | 0.00042276
19 | 0.0020271 | 0.00050805
20 | 0.00071494 | 0.00017918
21 | 0.0010016 | 0.00025102
22 | 0.00089103 | 0.00022331
23 | 0.095016 | 0.023813
24 | 0.0010468 | 0.00026235
25 | 0.001447 | 0.00036264
26 | 0.023771 | 0.0059576
27 | 0.00069403 | 0.00017394
28 | 0.0022759 | 0.00057039
29 | 0.0010867 | 0.00027236
30 | 0.00080137 | 0.00020084
31 | 0.00077887 | 0.0001952
32 | 0.00069181 | 0.00017338
33 | 0.00067547 | 0.00016929
34 | 0.0019648 | 0.00049243
35 | 0.001127 | 0.00028244
36 | 0.00031517 | 7.8989e-05
37 | 0.00050151 | 0.00012569
38 | 0.00023622 | 5.9203e-05
39 | 9.9306e-05 | 2.4888e-05
40 | 0.0010373 | 0.00025998
41 | 0.00014258 | 3.5734e-05
42 | 0.00017773 | 4.4543e-05
43 | 9.3141e-05 | 2.3343e-05
44 | 0.00047873 | 0.00011998
45 | 0.00051369 | 0.00012874
46 | 0.00072451 | 0.00018158
47 | 5.0932e-05 | 1.2765e-05
48 | 0.00058505 | 0.00014663
49 | 0.00031564 | 7.9106e-05
50 | 0.00019558 | 4.9016e-05
51 | 0.00029211 | 7.3209e-05
52 | 0.00069665 | 0.0001746
53 | 0.00012266 | 3.0742e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1