## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_112-12_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_112-12_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_112-12_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_112-12_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_112-12_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_112-12_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_112-12_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_112-12_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_112-12_0_4_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_112-12_0_4_node_124 | 0.4 | n |  | TRUE
10 | bus_LV_112-12_0_4_node_123 | 0.4 | n |  | TRUE
11 | bus_LV_112-12_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_112-12_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_112-12_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_112-12_0_4_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_112-12_0_4_node_126 | 0.4 | n |  | TRUE
16 | bus_LV_112-12_0_4_node_113 | 0.4 | n |  | TRUE
17 | bus_LV_112-12_0_4_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_112-12_0_4_node_119 | 0.4 | n |  | TRUE
19 | bus_LV_112-12_0_4_node_118 | 0.4 | n |  | TRUE
20 | bus_LV_112-12_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_112-12_0_4_node_95 | 0.4 | n |  | TRUE
22 | bus_LV_112-12_0_4_node_121 | 0.4 | n |  | TRUE
23 | bus_LV_112-12_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_112-12_0_4_node_125 | 0.4 | n |  | TRUE
25 | bus_LV_112-12_0_4_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_112-12_0_4_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_112-12_0_4_node_107 | 0.4 | n |  | TRUE
28 | bus_LV_112-12_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_112-12_0_4_node_9 | 0.4 | n |  | TRUE
30 | bus_LV_112-12_0_4_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_112-12_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_112-12_0_4_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_112-12_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_112-12_0_4_node_10 | 0.4 | n |  | TRUE
35 | bus_LV_112-12_0_4_node_11 | 0.4 | n |  | TRUE
36 | bus_LV_112-12_0_4_node_12 | 0.4 | n |  | TRUE
37 | bus_LV_112-12_0_4_node_13 | 0.4 | n |  | TRUE
38 | bus_LV_112-12_0_4_node_15 | 0.4 | n |  | TRUE
39 | bus_LV_112-12_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_112-12_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_112-12_0_4_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_112-12_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_112-12_0_4_node_134 | 0.4 | n |  | TRUE
44 | bus_LV_112-12_0_4_node_18 | 0.4 | n |  | TRUE
45 | bus_LV_112-12_0_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_112-12_0_4_node_16 | 0.4 | n |  | TRUE
47 | bus_LV_112-12_0_4_node_17 | 0.4 | n |  | TRUE
48 | bus_LV_112-12_0_4_node_19 | 0.4 | n |  | TRUE
49 | bus_LV_112-12_0_4_node_21 | 0.4 | n |  | TRUE
50 | bus_LV_112-12_0_4_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_112-12_0_4_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_112-12_0_4_node_106 | 0.4 | n |  | TRUE
53 | bus_LV_112-12_0_4_node_110 | 0.4 | n |  | TRUE
54 | bus_LV_112-12_0_4_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_112-12_0_4_node_26 | 0.4 | n |  | TRUE
56 | bus_LV_112-12_0_4_node_27 | 0.4 | n |  | TRUE
57 | bus_LV_112-12_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_112-12_0_4_node_31 | 0.4 | n |  | TRUE
59 | bus_LV_112-12_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_112-12_0_4_node_111 | 0.4 | n |  | TRUE
61 | bus_LV_112-12_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_112-12_0_4_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_112-12_0_4_node_120 | 0.4 | n |  | TRUE
64 | bus_LV_112-12_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_112-12_0_4_node_127 | 0.4 | n |  | TRUE
66 | bus_LV_112-12_0_4_node_116 | 0.4 | n |  | TRUE
67 | bus_LV_112-12_0_4_node_112 | 0.4 | n |  | TRUE
68 | bus_LV_112-12_0_4_node_34 | 0.4 | n |  | TRUE
69 | bus_LV_112-12_0_4_node_35 | 0.4 | n |  | TRUE
70 | bus_LV_112-12_0_4_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_112-12_0_4_node_43 | 0.4 | n |  | TRUE
72 | bus_LV_112-12_0_4_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_112-12_0_4_node_89 | 0.4 | n |  | TRUE
74 | bus_LV_112-12_0_4_node_128 | 0.4 | n |  | TRUE
75 | bus_LV_112-12_0_4_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_112-12_0_4_node_130 | 0.4 | n |  | TRUE
77 | bus_LV_112-12_0_4_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_112-12_0_4_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_112-12_0_4_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_112-12_0_4_node_122 | 0.4 | n |  | TRUE
81 | bus_LV_112-12_0_4_node_133 | 0.4 | n |  | TRUE
82 | bus_LV_112-12_0_4_node_93 | 0.4 | n |  | TRUE
83 | bus_LV_112-12_0_4_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_112-12_0_4_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_112-12_0_4_node_57 | 0.4 | n |  | TRUE
86 | bus_LV_112-12_0_4_node_58 | 0.4 | n |  | TRUE
87 | bus_LV_112-12_0_4_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_112-12_0_4_node_100 | 0.4 | n |  | TRUE
89 | bus_LV_112-12_0_4_node_97 | 0.4 | n |  | TRUE
90 | bus_LV_112-12_0_4_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_112-12_0_4_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_112-12_0_4_node_96 | 0.4 | n |  | TRUE
93 | bus_LV_112-12_0_4_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_112-12_0_4_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_112-12_0_4_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_112-12_0_4_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_112-12_0_4_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_112-12_0_4_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_112-12_0_4_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_112-12_0_4_node_70 | 0.4 | n |  | TRUE
101 | bus_LV_112-12_0_4_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_112-12_0_4_node_73 | 0.4 | n |  | TRUE
103 | bus_LV_112-12_0_4_node_132 | 0.4 | n |  | TRUE
104 | bus_LV_112-12_0_4_node_129 | 0.4 | n |  | TRUE
105 | bus_LV_112-12_0_4_node_72 | 0.4 | n |  | TRUE
106 | bus_LV_112-12_0_4_node_131 | 0.4 | n |  | TRUE
107 | bus_LV_112-12_0_4_node_74 | 0.4 | n |  | TRUE
108 | bus_LV_112-12_0_4_node_75 | 0.4 | n |  | TRUE
109 | bus_LV_112-12_0_4_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_112-12_0_4_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_112-12_0_4_node_85 | 0.4 | n |  | TRUE
112 | bus_LV_112-12_0_4_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_112-12_0_4_node_77 | 0.4 | n |  | TRUE
114 | bus_LV_112-12_0_4_node_79 | 0.4 | n |  | TRUE
115 | bus_LV_112-12_0_4_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_112-12_0_4_node_87 | 0.4 | n |  | TRUE
117 | bus_LV_112-12_0_4_node_86 | 0.4 | n |  | TRUE
118 | bus_LV_112-12_0_4_node_84 | 0.4 | n |  | TRUE
119 | bus_LV_112-12_0_4_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_112-12_0_4_node_98 | 0.4 | n |  | TRUE
121 | bus_LV_112-12_0_4_node_99 | 0.4 | n |  | TRUE
122 | bus_LV_112-12_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_112-12_0_4_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_112-12_0_4_node_117 | 0.4 | n |  | TRUE
125 | bus_MV_8_1_node_151 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_112-12_0_4_load_0 | 0 | 0.026085 | 0.0065376 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_112-12_0_4_load_3 | 2 | 0.017686 | 0.0044326 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_112-12_0_4_load_23 | 6 | 0.011704 | 0.0029334 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_112-12_0_4_load_30 | 8 | 0.025322 | 0.0063462 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_112-12_0_4_load_124 | 9 | 0.013464 | 0.0033745 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_112-12_0_4_load_123 | 10 | 0.012036 | 0.0030165 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_112-12_0_4_load_5 | 13 | 0.03177 | 0.0079623 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_112-12_0_4_load_126 | 15 | 0.001565 | 0.00039222 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_112-12_0_4_load_113 | 16 | 0.0016457 | 0.00041246 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_112-12_0_4_load_119 | 18 | 0.0005381 | 0.00013486 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_112-12_0_4_load_118 | 19 | 0.0071468 | 0.0017912 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_112-12_0_4_load_95 | 21 | 0.00095483 | 0.0002393 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_112-12_0_4_load_121 | 22 | 0.0087133 | 0.0021838 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_112-12_0_4_load_125 | 24 | 0.012036 | 0.0030164 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_112-12_0_4_load_109 | 26 | 0.0023424 | 0.00058705 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_112-12_0_4_load_107 | 27 | 0.0051748 | 0.0012969 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_112-12_0_4_load_33 | 30 | 0.0054301 | 0.0013609 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_112-12_0_4_load_32 | 31 | 0.014414 | 0.0036125 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_112-12_0_4_load_20 | 33 | 0.0078623 | 0.0019705 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_112-12_0_4_load_10 | 34 | 0.0038394 | 0.00096224 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_112-12_0_4_load_11 | 35 | 0.0010889 | 0.0002729 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_112-12_0_4_load_15 | 38 | 0.0024326 | 0.00060968 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_112-12_0_4_load_39 | 39 | 0.0032984 | 0.00082666 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_112-12_0_4_load_65 | 41 | 0.0017245 | 0.0004322 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_112-12_0_4_load_134 | 43 | 0.0040689 | 0.0010198 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_112-12_0_4_load_66 | 45 | 0.0019675 | 0.0004931 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_112-12_0_4_load_16 | 46 | 0.0036246 | 0.00090841 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_112-12_0_4_load_21 | 49 | 0.0080136 | 0.0020084 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_112-12_0_4_load_61 | 50 | 0.0015052 | 0.00037724 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_112-12_0_4_load_59 | 51 | 0.0015242 | 0.00038201 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_112-12_0_4_load_110 | 53 | 0.0058345 | 0.0014623 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_112-12_0_4_load_108 | 54 | 0.0012889 | 0.00032304 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_112-12_0_4_load_26 | 55 | 0.014107 | 0.0035355 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_112-12_0_4_load_27 | 56 | 0.017614 | 0.0044145 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_112-12_0_4_load_31 | 58 | 0.0024019 | 0.00060196 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_112-12_0_4_load_37 | 59 | 0.013077 | 0.0032773 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_112-12_0_4_load_120 | 63 | 0.0009594 | 0.00024045 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_112-12_0_4_load_127 | 65 | 0.0023678 | 0.00059343 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_112-12_0_4_load_116 | 66 | 0.0021385 | 0.00053596 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_112-12_0_4_load_112 | 67 | 0.003095 | 0.00077567 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_112-12_0_4_load_34 | 68 | 0.0077177 | 0.0019342 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_112-12_0_4_load_35 | 69 | 0.0040408 | 0.0010127 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_112-12_0_4_load_101 | 70 | 0.0015106 | 0.0003786 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_112-12_0_4_load_43 | 71 | 0.0023172 | 0.00058075 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_112-12_0_4_load_44 | 72 | 0.0090374 | 0.002265 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_112-12_0_4_load_89 | 73 | 0.0026903 | 0.00067425 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_112-12_0_4_load_128 | 74 | 0.00077846 | 0.0001951 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_112-12_0_4_load_114 | 77 | 0.0017535 | 0.00043946 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_112-12_0_4_load_67 | 78 | 0.0035051 | 0.00087846 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_112-12_0_4_load_68 | 79 | 0.0032385 | 0.00081164 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_112-12_0_4_load_122 | 80 | 0.0011227 | 0.00028137 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_112-12_0_4_load_133 | 81 | 0.0020853 | 0.00052262 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_112-12_0_4_load_80 | 83 | 0.00084598 | 0.00021202 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_112-12_0_4_load_57 | 85 | 0.0011948 | 0.00029944 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_112-12_0_4_load_58 | 86 | 0.0012952 | 0.00032461 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_112-12_0_4_load_97 | 89 | 0.0013463 | 0.00033742 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_112-12_0_4_load_104 | 90 | 0.0032808 | 0.00082224 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_112-12_0_4_load_102 | 91 | 0.0030427 | 0.00076258 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_112-12_0_4_load_96 | 92 | 0.0018775 | 0.00047054 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_112-12_0_4_load_62 | 93 | 0.00069146 | 0.0001733 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_112-12_0_4_load_63 | 94 | 0.0023742 | 0.00059503 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_112-12_0_4_load_64 | 95 | 0.0043102 | 0.0010802 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_112-12_0_4_load_88 | 96 | 0.0060845 | 0.0015249 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_112-12_0_4_load_94 | 98 | 0.0064234 | 0.0016099 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_112-12_0_4_load_73 | 102 | 0.0022161 | 0.0005554 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_112-12_0_4_load_132 | 103 | 0.00051615 | 0.00012936 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_112-12_0_4_load_72 | 105 | 0.0013506 | 0.00033848 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_112-12_0_4_load_131 | 106 | 0.00014011 | 3.5115e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_112-12_0_4_load_74 | 107 | 0.0039731 | 0.00099576 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_112-12_0_4_load_90 | 110 | 0.0027019 | 0.00067716 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_112-12_0_4_load_85 | 111 | 0.0033728 | 0.00084532 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_112-12_0_4_load_91 | 112 | 0.0021801 | 0.00054638 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_112-12_0_4_load_77 | 113 | 0.0022409 | 0.00056162 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_112-12_0_4_load_79 | 114 | 0.0085028 | 0.002131 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_112-12_0_4_load_81 | 115 | 0.00089976 | 0.0002255 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_112-12_0_4_load_87 | 116 | 0.00065512 | 0.00016419 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_112-12_0_4_load_86 | 117 | 0.00077238 | 0.00019358 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_112-12_0_4_load_84 | 118 | 0.0013364 | 0.00033494 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_112-12_0_4_load_92 | 119 | 0.0013741 | 0.00034438 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_112-12_0_4_load_98 | 120 | 0.00096015 | 0.00024064 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_112-12_0_4_load_99 | 121 | 0.001936 | 0.0004852 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_112-12_0_4_load_105 | 122 | 0.0029064 | 0.00072841 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_112-12_0_4_load_115 | 123 | 0.0043635 | 0.0010936 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_112-12_0_4_load_117 | 124 | 0.0023355 | 0.00058532 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_112-12_0_4_line_0 |  | 0 | 1 | 0.02654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_112-12_0_4_line_1 |  | 1 | 2 | 0.02818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_112-12_0_4_line_2 |  | 1 | 3 | 0.036717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_112-12_0_4_line_3 |  | 2 | 7 | 0.01974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_112-12_0_4_line_4 |  | 3 | 8 | 0.025462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_112-12_0_4_line_5 |  | 4 | 5 | 0.010856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_112-12_0_4_line_6 |  | 4 | 6 | 0.020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_112-12_0_4_line_7 |  | 5 | 9 | 0.011578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_112-12_0_4_line_8 |  | 5 | 10 | 0.015597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_112-12_0_4_line_9 |  | 6 | 11 | 0.025924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_112-12_0_4_line_10 |  | 7 | 12 | 0.012134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_112-12_0_4_line_11 |  | 7 | 11 | 0.026749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_112-12_0_4_line_12 |  | 7 | 13 | 0.024242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_112-12_0_4_line_13 |  | 8 | 28 | 0.021104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_112-12_0_4_line_14 |  | 11 | 23 | 0.026593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_112-12_0_4_line_15 |  | 12 | 29 | 0.041964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_112-12_0_4_line_16 |  | 14 | 15 | 0.012763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_112-12_0_4_line_17 |  | 14 | 16 | 0.0088612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_112-12_0_4_line_18 |  | 15 | 81 | 0.013808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_112-12_0_4_line_19 |  | 16 | 60 | 0.037431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_112-12_0_4_line_20 |  | 17 | 18 | 2.8575e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_112-12_0_4_line_21 |  | 17 | 19 | 0.018493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_112-12_0_4_line_22 |  | 19 | 26 | 0.00078558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_112-12_0_4_line_23 |  | 20 | 21 | 0.010375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_112-12_0_4_line_24 |  | 20 | 22 | 0.026269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_112-12_0_4_line_25 |  | 21 | 82 | 0.0061298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_112-12_0_4_line_26 |  | 22 | 80 | 0.00053902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_112-12_0_4_line_27 |  | 23 | 24 | 0.024492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_112-12_0_4_line_28 |  | 25 | 26 | 0.015779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_112-12_0_4_line_29 |  | 25 | 27 | 0.022578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_112-12_0_4_line_30 |  | 27 | 54 | 0.023025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_112-12_0_4_line_31 |  | 28 | 58 | 0.031304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_112-12_0_4_line_32 |  | 29 | 30 | 0.026638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_112-12_0_4_line_33 |  | 29 | 31 | 0.039392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_112-12_0_4_line_34 |  | 30 | 32 | 0.0092204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_112-12_0_4_line_35 |  | 31 | 33 | 0.045299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_112-12_0_4_line_36 |  | 32 | 40 | 0.015343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_112-12_0_4_line_37 |  | 32 | 36 | 0.007604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_112-12_0_4_line_38 |  | 33 | 47 | 0.0074793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_112-12_0_4_line_39 |  | 34 | 35 | 0.0081723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_112-12_0_4_line_40 |  | 34 | 36 | 0.018003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_112-12_0_4_line_41 |  | 35 | 37 | 0.022734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_112-12_0_4_line_42 |  | 36 | 38 | 0.010541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_112-12_0_4_line_43 |  | 37 | 39 | 0.0008243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_112-12_0_4_line_44 |  | 38 | 41 | 0.025589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_112-12_0_4_line_45 |  | 39 | 42 | 0.011571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_112-12_0_4_line_46 |  | 40 | 43 | 0.004955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_112-12_0_4_line_47 |  | 40 | 44 | 0.016535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_112-12_0_4_line_48 |  | 41 | 45 | 0.019203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_112-12_0_4_line_49 |  | 42 | 71 | 0.042762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_112-12_0_4_line_50 |  | 42 | 72 | 0.025177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_112-12_0_4_line_51 |  | 44 | 49 | 0.003524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_112-12_0_4_line_52 |  | 45 | 98 | 0.025917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_112-12_0_4_line_53 |  | 46 | 47 | 0.016357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_112-12_0_4_line_54 |  | 47 | 48 | 0.0478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_112-12_0_4_line_55 |  | 48 | 50 | 0.034536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_112-12_0_4_line_56 |  | 50 | 51 | 0.0089988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_112-12_0_4_line_57 |  | 51 | 85 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_112-12_0_4_line_58 |  | 52 | 53 | 0.028452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_112-12_0_4_line_59 |  | 52 | 54 | 0.022925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_112-12_0_4_line_60 |  | 53 | 76 | 0.0074915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_112-12_0_4_line_61 |  | 55 | 56 | 0.018556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_112-12_0_4_line_62 |  | 56 | 57 | 0.01816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_112-12_0_4_line_63 |  | 57 | 59 | 0.021939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_112-12_0_4_line_64 |  | 58 | 60 | 0.0060789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_112-12_0_4_line_65 |  | 59 | 64 | 0.014166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_112-12_0_4_line_66 |  | 60 | 67 | 0.015251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_112-12_0_4_line_67 |  | 61 | 62 | 0.033646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_112-12_0_4_line_68 |  | 61 | 63 | 0.031314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_112-12_0_4_line_69 |  | 61 | 64 | 0.041991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_112-12_0_4_line_70 |  | 62 | 65 | 0.016193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_112-12_0_4_line_71 |  | 62 | 66 | 0.016497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_112-12_0_4_line_72 |  | 63 | 70 | 0.019116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_112-12_0_4_line_73 |  | 64 | 68 | 0.0059314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_112-12_0_4_line_74 |  | 65 | 76 | 0.016512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_112-12_0_4_line_75 |  | 66 | 77 | 0.0094422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_112-12_0_4_line_76 |  | 68 | 69 | 0.012612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_112-12_0_4_line_77 |  | 70 | 87 | 0.0093983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_112-12_0_4_line_78 |  | 71 | 73 | 0.021181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_112-12_0_4_line_79 |  | 74 | 75 | 0.035206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_112-12_0_4_line_80 |  | 75 | 104 | 0.005578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_112-12_0_4_line_81 |  | 77 | 123 | 0.0026503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_112-12_0_4_line_82 |  | 78 | 79 | 0.019358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_112-12_0_4_line_83 |  | 79 | 99 | 0.016907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_112-12_0_4_line_84 |  | 82 | 98 | 0.020282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_112-12_0_4_line_85 |  | 82 | 119 | 0.019285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_112-12_0_4_line_86 |  | 83 | 84 | 0.011623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_112-12_0_4_line_87 |  | 84 | 115 | 0.0084487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_112-12_0_4_line_88 |  | 84 | 113 | 0.032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_112-12_0_4_line_89 |  | 85 | 86 | 0.00036234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_112-12_0_4_line_90 |  | 86 | 87 | 0.02944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_112-12_0_4_line_91 |  | 87 | 88 | 0.031072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_112-12_0_4_line_92 |  | 87 | 89 | 0.0091151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_112-12_0_4_line_93 |  | 88 | 90 | 0.012597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_112-12_0_4_line_94 |  | 88 | 91 | 0.037811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_112-12_0_4_line_95 |  | 89 | 92 | 0.022449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_112-12_0_4_line_96 |  | 92 | 120 | 0.0040135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_112-12_0_4_line_97 |  | 93 | 94 | 0.032177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_112-12_0_4_line_98 |  | 94 | 95 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_112-12_0_4_line_99 |  | 95 | 96 | 0.0049404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_112-12_0_4_line_100 |  | 96 | 97 | 0.0072697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_112-12_0_4_line_101 |  | 97 | 110 | 0.019528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_112-12_0_4_line_102 |  | 97 | 108 | 0.014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_112-12_0_4_line_103 |  | 99 | 100 | 0.012671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_112-12_0_4_line_104 |  | 99 | 101 | 0.025646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_112-12_0_4_line_105 |  | 100 | 102 | 0.016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_112-12_0_4_line_106 |  | 101 | 103 | 0.0052505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_112-12_0_4_line_107 |  | 102 | 105 | 0.0018429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_112-12_0_4_line_108 |  | 103 | 106 | 0.011162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_112-12_0_4_line_109 |  | 104 | 106 | 0.0063085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_112-12_0_4_line_110 |  | 105 | 107 | 0.028564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_112-12_0_4_line_111 |  | 107 | 108 | 0.010592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_112-12_0_4_line_112 |  | 108 | 109 | 0.022329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_112-12_0_4_line_113 |  | 109 | 111 | 0.018813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_112-12_0_4_line_114 |  | 109 | 112 | 0.018928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_112-12_0_4_line_115 |  | 111 | 118 | 0.015418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_112-12_0_4_line_116 |  | 112 | 119 | 0.021134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_112-12_0_4_line_117 |  | 113 | 114 | 0.0028908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_112-12_0_4_line_118 |  | 115 | 116 | 0.001976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_112-12_0_4_line_119 |  | 116 | 117 | 0.0029954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_112-12_0_4_line_120 |  | 117 | 118 | 0.013451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_112-12_0_4_line_121 |  | 120 | 121 | 0.0078588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_112-12_0_4_line_122 |  | 121 | 122 | 0.0095098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_112-12_0_4_line_123 |  | 123 | 124 | 0.017079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_112-12_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 125 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2704562.1311 | 1236284.7961 | 2704580.8216 | 1236265.9543
1 | 2704562.1311 | 1236284.7961 | 2704583.0511 | 1236303.6764
2 | 2704534.8334 | 1236260.1525 | 2704562.1311 | 1236284.7961
3 | 2704597.7058 | 1236316.9024 | 2704583.0511 | 1236303.6764
4 | 2704534.8334 | 1236260.1525 | 2704551.336 | 1236240.7617
5 | 2704534.7741 | 1236300.0597 | 2704543.0897 | 1236307.0669
6 | 2704543.0897 | 1236307.0669 | 2704558.6684 | 1236319.6382
7 | 2704534.7741 | 1236300.0597 | 2704525.9209 | 1236292.5984
8 | 2704534.7741 | 1236300.0597 | 2704524.3521 | 1236311.6629
9 | 2704578.8428 | 1236335.9182 | 2704558.6684 | 1236319.6382
10 | 2704597.7058 | 1236316.9024 | 2704608.8349 | 1236311.9946
11 | 2704597.7058 | 1236316.9024 | 2704578.8428 | 1236335.9182
12 | 2704597.7058 | 1236316.9024 | 2704613.7489 | 1236335.0765
13 | 2704565.0139 | 1236224.6899 | 2704551.336 | 1236240.7617
14 | 2704578.8428 | 1236335.9182 | 2704575.5525 | 1236339.2406 | 2704564.0672 | 1236357.9304
15 | 2704643.0446 | 1236296.9967 | 2704639.0327 | 1236294.0238 | 2704634.4205 | 1236297.6231 | 2704616.5788 | 1236312.7871 | 2704608.8349 | 1236311.9946
16 | 2704504.9428 | 1236233.1727 | 2704496.1099 | 1236242.3855
17 | 2704504.9428 | 1236233.1727 | 2704511.1975 | 1236226.8958
18 | 2704486.5538 | 1236252.3528 | 2704496.1099 | 1236242.3855
19 | 2704537.533 | 1236200.9771 | 2704527.719 | 1236206.8422 | 2704513.2948 | 1236224.791 | 2704511.1975 | 1236226.8958
20 | 2704473.0056 | 1236193.8699 | 2704472.9811 | 1236193.8847
21 | 2704473.0056 | 1236193.8699 | 2704488.0347 | 1236183.0944
22 | 2704488.6731 | 1236182.6367 | 2704488.0347 | 1236183.0944
23 | 2704581.6814 | 1236384.016 | 2704590.55 | 1236389.4007
24 | 2704581.6814 | 1236384.016 | 2704561.7458 | 1236401.1217
25 | 2704595.7896 | 1236392.582 | 2704590.55 | 1236389.4007
26 | 2704561.7458 | 1236401.1217 | 2704561.3367 | 1236401.4727
27 | 2704564.0672 | 1236357.9304 | 2704549.4589 | 1236349.3891 | 2704543.5401 | 1236344.6702
28 | 2704500.4834 | 1236172.1922 | 2704490.3833 | 1236181.4105 | 2704488.6731 | 1236182.6367
29 | 2704500.4834 | 1236172.1922 | 2704505.2382 | 1236168.662 | 2704513.7934 | 1236158.6382 | 2704515.6027 | 1236155.6679
30 | 2704515.6027 | 1236155.6679 | 2704527.5807 | 1236136.0035
31 | 2704565.0139 | 1236224.6899 | 2704559.7334 | 1236220.2491 | 2704560.3417 | 1236219.6594 | 2704542.4371 | 1236204.3499
32 | 2704643.0446 | 1236296.9967 | 2704661.382 | 1236316.3189
33 | 2704643.0446 | 1236296.9967 | 2704658.6078 | 1236289.1538 | 2704673.1001 | 1236272.6497
34 | 2704667.7291 | 1236323.007 | 2704661.382 | 1236316.3189
35 | 2704673.1001 | 1236272.6497 | 2704702.9894 | 1236238.6111
36 | 2704676.272 | 1236310.2477 | 2704667.7291 | 1236323.007
37 | 2704673.322 | 1236328.1761 | 2704667.7291 | 1236323.007
38 | 2704707.9244 | 1236232.991 | 2704702.9894 | 1236238.6111
39 | 2704689.2652 | 1236328.8242 | 2704695.0431 | 1236334.6037
40 | 2704673.322 | 1236328.1761 | 2704677.6848 | 1236325.4175 | 2704683.9668 | 1236324.9835 | 2704689.2652 | 1236328.8242
41 | 2704711.1163 | 1236350.6815 | 2704695.0431 | 1236334.6037
42 | 2704673.322 | 1236328.1761 | 2704665.7522 | 1236335.5112
43 | 2704711.703 | 1236351.2605 | 2704711.1163 | 1236350.6815
44 | 2704665.7522 | 1236335.5112 | 2704654.5567 | 1236346.3594 | 2704646.1563 | 1236351.7836
45 | 2704719.9391 | 1236359.3881 | 2704711.703 | 1236351.2605
46 | 2704672.4991 | 1236307.0232 | 2704676.272 | 1236310.2477
47 | 2704688.6292 | 1236299.2237 | 2704676.272 | 1236310.2477
48 | 2704630.0236 | 1236362.2003 | 2704646.1563 | 1236351.7836
49 | 2704719.9391 | 1236359.3881 | 2704688.9717 | 1236388.8779
50 | 2704719.9391 | 1236359.3881 | 2704737.4448 | 1236377.4835
51 | 2704688.6292 | 1236299.2237 | 2704686.66 | 1236296.2979
52 | 2704630.0236 | 1236362.2003 | 2704614.6093 | 1236372.1533 | 2704609.1204 | 1236377.3649
53 | 2704707.9244 | 1236232.991 | 2704720.4668 | 1236243.4906
54 | 2704707.9244 | 1236232.991 | 2704739.4998 | 1236197.0312
55 | 2704739.4998 | 1236197.0312 | 2704712.0003 | 1236176.1377
56 | 2704704.835 | 1236170.6937 | 2704712.0003 | 1236176.1377
57 | 2704688.2761 | 1236158.1126 | 2704704.835 | 1236170.6937
58 | 2704539.5063 | 1236116.4251 | 2704549.6909 | 1236123.4763 | 2704562.4755 | 1236133.2033
59 | 2704539.5063 | 1236116.4251 | 2704527.5807 | 1236136.0035
60 | 2704568.4376 | 1236137.7394 | 2704562.4755 | 1236133.2033
61 | 2704613.4283 | 1236236.6956 | 2704613.2231 | 1236236.9257 | 2704612.538 | 1236241.8729 | 2704603.6606 | 1236251.713
62 | 2704625.5154 | 1236223.1427 | 2704613.4283 | 1236236.6956
63 | 2704625.5154 | 1236223.1427 | 2704628.8705 | 1236226.0262 | 2704632.0006 | 1236225.3586 | 2704641.0299 | 1236214.2504
64 | 2704537.533 | 1236200.9771 | 2704539.8732 | 1236203.042 | 2704541.3277 | 1236203.4012 | 2704542.4371 | 1236204.3499
65 | 2704649.9648 | 1236203.2582 | 2704641.0299 | 1236214.2504
66 | 2704537.533 | 1236200.9771 | 2704529.861 | 1236194.804 | 2704533.079 | 1236190.4351
67 | 2704594.319 | 1236157.7324 | 2704607.5804 | 1236168.8522 | 2704612.8664 | 1236177.7075 | 2704618.4396 | 1236175.415
68 | 2704618.4396 | 1236175.415 | 2704620.8458 | 1236173.7339 | 2704637.9161 | 1236151.6844 | 2704638.3691 | 1236151.4875
69 | 2704649.9648 | 1236203.2582 | 2704618.4396 | 1236175.415
70 | 2704594.319 | 1236157.7324 | 2704581.4987 | 1236147.8407
71 | 2704594.319 | 1236157.7324 | 2704584.3565 | 1236170.8813
72 | 2704655.9007 | 1236143.8681 | 2704638.3691 | 1236151.4875
73 | 2704649.9648 | 1236203.2582 | 2704650.8145 | 1236204.007 | 2704655.5373 | 1236203.1563 | 2704655.5373 | 1236203.1563
74 | 2704568.4376 | 1236137.7394 | 2704571.8572 | 1236140.4016 | 2704581.4987 | 1236147.8407
75 | 2704578.6543 | 1236178.4073 | 2704584.3565 | 1236170.8813
76 | 2704655.5373 | 1236203.1563 | 2704663.6643 | 1236193.5122
77 | 2704664.5201 | 1236140.122 | 2704655.9007 | 1236143.8681
78 | 2704670.9369 | 1236397.3425 | 2704675.7404 | 1236397.9164 | 2704681.8886 | 1236395.623 | 2704688.9717 | 1236388.8779
79 | 2704704.5431 | 1236477.9073 | 2704718.339 | 1236462.1051 | 2704727.696 | 1236451.3852
80 | 2704704.5431 | 1236477.9073 | 2704709.0175 | 1236481.2554
81 | 2704578.6543 | 1236178.4073 | 2704577.0538 | 1236180.5197
82 | 2704668.7254 | 1236538.8756 | 2704681.7721 | 1236524.5747
83 | 2704687.9722 | 1236509.4394 | 2704687.7251 | 1236513.5826 | 2704686.6507 | 1236517.8558 | 2704684.4574 | 1236521.6312 | 2704681.7721 | 1236524.5747
84 | 2704595.7896 | 1236392.582 | 2704601.5315 | 1236384.9995 | 2704604.5027 | 1236381.7493 | 2704609.1204 | 1236377.3649
85 | 2704595.7896 | 1236392.582 | 2704608.5976 | 1236401.9146 | 2704611.2446 | 1236404.1084
86 | 2704591.105 | 1236470.3144 | 2704581.9764 | 1236477.5093
87 | 2704591.105 | 1236470.3144 | 2704597.7533 | 1236465.1009
88 | 2704591.105 | 1236470.3144 | 2704613.7591 | 1236492.9154
89 | 2704687.9876 | 1236157.8934 | 2704688.2761 | 1236158.1126
90 | 2704664.5201 | 1236140.122 | 2704668.1998 | 1236143.0557 | 2704673.3343 | 1236146.7601 | 2704687.9876 | 1236157.8934
91 | 2704693.5274 | 1236128.7688 | 2704664.5201 | 1236140.122
92 | 2704664.5201 | 1236140.122 | 2704657.2852 | 1236134.5774
93 | 2704693.5274 | 1236128.7688 | 2704705.0594 | 1236123.7002
94 | 2704693.5274 | 1236128.7688 | 2704676.5423 | 1236107.7646 | 2704668.1031 | 1236101.027
95 | 2704639.4665 | 1236120.922 | 2704657.2852 | 1236134.5774
96 | 2704639.4665 | 1236120.922 | 2704636.2808 | 1236118.4806
97 | 2704693.2133 | 1236421.474 | 2704700.4721 | 1236414.7762 | 2704696.7376 | 1236410.2403 | 2704684.6627 | 1236421.3748
98 | 2704671.1559 | 1236433.6275 | 2704673.2029 | 1236431.9421 | 2704684.6627 | 1236421.3748
99 | 2704671.1559 | 1236433.6275 | 2704668.5488 | 1236435.7742 | 2704667.4892 | 1236436.9235
100 | 2704662.8893 | 1236442.5463 | 2704664.633 | 1236440.2308 | 2704666.4809 | 1236438.0172 | 2704667.4892 | 1236436.9235
101 | 2704662.8893 | 1236442.5463 | 2704676.3071 | 1236456.7714
102 | 2704662.8893 | 1236442.5463 | 2704660.8972 | 1236444.7796 | 2704659.375 | 1236446.1205 | 2704651.3893 | 1236451.3282
103 | 2704684.567 | 1236497.3924 | 2704685.8576 | 1236499.7391 | 2704686.9951 | 1236502.6169 | 2704687.6132 | 1236505.7636 | 2704687.9722 | 1236509.4394
104 | 2704702.2738 | 1236497.1487 | 2704704.5286 | 1236499.3234 | 2704700.728 | 1236503.2594 | 2704695.3979 | 1236511.0937 | 2704687.9722 | 1236509.4394
105 | 2704684.567 | 1236497.3924 | 2704677.5449 | 1236491.731 | 2704675.4894 | 1236489.8378 | 2704673.6148 | 1236487.5585 | 2704672.8275 | 1236486.2752
106 | 2704702.2738 | 1236497.1487 | 2704705.9428 | 1236493.3928
107 | 2704671.8639 | 1236484.7043 | 2704672.8275 | 1236486.2752
108 | 2704713.7426 | 1236485.4085 | 2704705.9428 | 1236493.3928
109 | 2704709.0175 | 1236481.2554 | 2704711.46 | 1236483.0887 | 2704713.7426 | 1236485.4085 | 2704713.7426 | 1236485.4085
110 | 2704671.8639 | 1236484.7043 | 2704656.928 | 1236460.3569
111 | 2704651.3893 | 1236451.3282 | 2704656.928 | 1236460.3569
112 | 2704639.1859 | 1236432.6101 | 2704644.1061 | 1236439.8689 | 2704647.9956 | 1236445.9199 | 2704651.3893 | 1236451.3282
113 | 2704639.1859 | 1236432.6101 | 2704624.3819 | 1236444.2191
114 | 2704639.1859 | 1236432.6101 | 2704633.3706 | 1236425.0352 | 2704627.0981 | 1236418.0638
115 | 2704612.2499 | 1236453.7329 | 2704624.3819 | 1236444.2191
116 | 2704627.0981 | 1236418.0638 | 2704620.6747 | 1236411.9238 | 2704611.2446 | 1236404.1084
117 | 2704615.8055 | 1236494.957 | 2704613.7591 | 1236492.9154
118 | 2704599.3082 | 1236463.8816 | 2704597.7533 | 1236465.1009
119 | 2704599.3082 | 1236463.8816 | 2704601.6653 | 1236462.0332
120 | 2704612.2499 | 1236453.7329 | 2704601.6653 | 1236462.0332
121 | 2704636.2808 | 1236118.4806 | 2704634.3868 | 1236117.0291 | 2704629.5911 | 1236114.3929
122 | 2704629.5911 | 1236114.3929 | 2704624.1469 | 1236111.4 | 2704622.197 | 1236108.7412
123 | 2704577.0538 | 1236180.5197 | 2704566.7397 | 1236194.1326

## bus_geodata
| x | y | coords
0 | 2704580.8216 | 1236265.9543
1 | 2704562.1311 | 1236284.7961
2 | 2704583.0511 | 1236303.6764
3 | 2704534.8334 | 1236260.1525
4 | 2704543.0897 | 1236307.0669
5 | 2704534.7741 | 1236300.0597
6 | 2704558.6684 | 1236319.6382
7 | 2704597.7058 | 1236316.9024
8 | 2704551.336 | 1236240.7617
9 | 2704525.9209 | 1236292.5984
10 | 2704524.3521 | 1236311.6629
11 | 2704578.8428 | 1236335.9182
12 | 2704608.8349 | 1236311.9946
13 | 2704613.7489 | 1236335.0765
14 | 2704504.9428 | 1236233.1727
15 | 2704496.1099 | 1236242.3855
16 | 2704511.1975 | 1236226.8958
17 | 2704473.0056 | 1236193.8699
18 | 2704472.9811 | 1236193.8847
19 | 2704488.0347 | 1236183.0944
20 | 2704581.6814 | 1236384.016
21 | 2704590.55 | 1236389.4007
22 | 2704561.7458 | 1236401.1217
23 | 2704564.0672 | 1236357.9304
24 | 2704543.5401 | 1236344.6702
25 | 2704500.4834 | 1236172.1922
26 | 2704488.6731 | 1236182.6367
27 | 2704515.6027 | 1236155.6679
28 | 2704565.0139 | 1236224.6899
29 | 2704643.0446 | 1236296.9967
30 | 2704661.382 | 1236316.3189
31 | 2704673.1001 | 1236272.6497
32 | 2704667.7291 | 1236323.007
33 | 2704702.9894 | 1236238.6111
34 | 2704689.2652 | 1236328.8242
35 | 2704695.0431 | 1236334.6037
36 | 2704673.322 | 1236328.1761
37 | 2704711.1163 | 1236350.6815
38 | 2704665.7522 | 1236335.5112
39 | 2704711.703 | 1236351.2605
40 | 2704676.272 | 1236310.2477
41 | 2704646.1563 | 1236351.7836
42 | 2704719.9391 | 1236359.3881
43 | 2704672.4991 | 1236307.0232
44 | 2704688.6292 | 1236299.2237
45 | 2704630.0236 | 1236362.2003
46 | 2704720.4668 | 1236243.4906
47 | 2704707.9244 | 1236232.991
48 | 2704739.4998 | 1236197.0312
49 | 2704686.66 | 1236296.2979
50 | 2704712.0003 | 1236176.1377
51 | 2704704.8351 | 1236170.6937
52 | 2704539.5063 | 1236116.4251
53 | 2704562.4755 | 1236133.2033
54 | 2704527.5807 | 1236136.0035
55 | 2704603.6606 | 1236251.713
56 | 2704613.4283 | 1236236.6956
57 | 2704625.5154 | 1236223.1427
58 | 2704542.4371 | 1236204.3499
59 | 2704641.0299 | 1236214.2504
60 | 2704537.533 | 1236200.9771
61 | 2704618.4396 | 1236175.415
62 | 2704594.319 | 1236157.7324
63 | 2704638.3691 | 1236151.4875
64 | 2704649.9648 | 1236203.2582
65 | 2704581.4987 | 1236147.8407
66 | 2704584.3565 | 1236170.8813
67 | 2704533.079 | 1236190.4351
68 | 2704655.5373 | 1236203.1563
69 | 2704663.6643 | 1236193.5122
70 | 2704655.9007 | 1236143.8681
71 | 2704688.9717 | 1236388.8779
72 | 2704737.4448 | 1236377.4835
73 | 2704670.9369 | 1236397.3425
74 | 2704727.696 | 1236451.3852
75 | 2704704.5431 | 1236477.9073
76 | 2704568.4376 | 1236137.7394
77 | 2704578.6543 | 1236178.4073
78 | 2704668.7254 | 1236538.8756
79 | 2704681.7721 | 1236524.5747
80 | 2704561.3367 | 1236401.4727
81 | 2704486.5538 | 1236252.3528
82 | 2704595.7896 | 1236392.582
83 | 2704581.9764 | 1236477.5093
84 | 2704591.105 | 1236470.3144
85 | 2704688.2761 | 1236158.1126
86 | 2704687.9876 | 1236157.8934
87 | 2704664.5201 | 1236140.122
88 | 2704693.5274 | 1236128.7688
89 | 2704657.2852 | 1236134.5774
90 | 2704705.0594 | 1236123.7002
91 | 2704668.1031 | 1236101.027
92 | 2704639.4665 | 1236120.922
93 | 2704693.2133 | 1236421.474
94 | 2704684.6627 | 1236421.3748
95 | 2704671.1559 | 1236433.6275
96 | 2704667.4892 | 1236436.9235
97 | 2704662.8893 | 1236442.5463
98 | 2704609.1204 | 1236377.3649
99 | 2704687.9722 | 1236509.4394
100 | 2704684.567 | 1236497.3924
101 | 2704702.2738 | 1236497.1487
102 | 2704672.8275 | 1236486.2752
103 | 2704705.9428 | 1236493.3928
104 | 2704709.0175 | 1236481.2554
105 | 2704671.8639 | 1236484.7043
106 | 2704713.7426 | 1236485.4085
107 | 2704656.928 | 1236460.3569
108 | 2704651.3893 | 1236451.3282
109 | 2704639.1859 | 1236432.6101
110 | 2704676.3071 | 1236456.7714
111 | 2704624.3819 | 1236444.2191
112 | 2704627.0981 | 1236418.0638
113 | 2704613.7591 | 1236492.9154
114 | 2704615.8055 | 1236494.957
115 | 2704597.7533 | 1236465.1009
116 | 2704599.3082 | 1236463.8816
117 | 2704601.6653 | 1236462.0332
118 | 2704612.2499 | 1236453.7329
119 | 2704611.2446 | 1236404.1084
120 | 2704636.2808 | 1236118.4806
121 | 2704629.5911 | 1236114.3929
122 | 2704622.197 | 1236108.7412
123 | 2704577.0538 | 1236180.5197
124 | 2704566.7397 | 1236194.1326
125 | 2704597.7058 | 1236316.9024

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99545 | -0.087524 | 0.026085 | 0.0065376
1 | 0.99608 | -0.075354 | 0 | 0
2 | 0.99767 | -0.044608 | 0.017686 | 0.0044326
3 | 0.99487 | -0.098681 | 0 | 0
4 | 0.99657 | -0.06591 | 0 | 0
5 | 0.99632 | -0.070769 | 0 | 0
6 | 0.99704 | -0.056955 | 0.011704 | 0.0029334
7 | 0.99911 | -0.017031 | 0 | 0
8 | 0.99403 | -0.11489 | 0.025322 | 0.0063462
9 | 0.99618 | -0.073507 | 0.013464 | 0.0033745
10 | 0.99615 | -0.074066 | 0.012036 | 0.0030165
11 | 0.99791 | -0.040058 | 0 | 0
12 | 1 | 0 | -0.4261 | -0.1084
13 | 0.99841 | -0.030488 | 0.03177 | 0.0079623
14 | 0.99325 | -0.12985 | 0 | 0
15 | 0.99321 | -0.13067 | 0.001565 | 0.00039222
16 | 0.99328 | -0.12928 | 0.0016457 | 0.00041246
17 | 0.97164 | -0.54641 | 0 | 0
18 | 0.97164 | -0.54641 | 0.0005381 | 0.00013486
19 | 0.97165 | -0.54622 | 0.0071468 | 0.0017912
20 | 0.98354 | -0.31552 | 0 | 0
21 | 0.98364 | -0.31368 | 0.00095483 | 0.0002393
22 | 0.98331 | -0.32017 | 0.0087133 | 0.0021838
23 | 0.99762 | -0.045662 | 0 | 0
24 | 0.99735 | -0.050826 | 0.012036 | 0.0030164
25 | 0.97181 | -0.54319 | 0 | 0
26 | 0.97166 | -0.54611 | 0.0023424 | 0.00058705
27 | 0.97202 | -0.53901 | 0.0051748 | 0.0012969
28 | 0.99382 | -0.11891 | 0 | 0
29 | 0.99498 | -0.094948 | 0 | 0
30 | 0.9921 | -0.15008 | 0.0054301 | 0.0013609
31 | 0.9924 | -0.14401 | 0.014414 | 0.0036125
32 | 0.99115 | -0.16835 | 0 | 0
33 | 0.98973 | -0.19493 | 0.0078623 | 0.0019705
34 | 0.99009 | -0.18893 | 0.0038394 | 0.00096224
35 | 0.98995 | -0.19161 | 0.0010889 | 0.0002729
36 | 0.99045 | -0.18181 | 0 | 0
37 | 0.98959 | -0.19863 | 0 | 0
38 | 0.9897 | -0.19632 | 0.0024326 | 0.00060968
39 | 0.98957 | -0.19888 | 0.0032984 | 0.00082666
40 | 0.99098 | -0.17164 | 0 | 0
41 | 0.98792 | -0.23052 | 0.0017245 | 0.0004322
42 | 0.98942 | -0.20178 | 0 | 0
43 | 0.99096 | -0.17199 | 0.0040689 | 0.0010198
44 | 0.99086 | -0.17399 | 0 | 0
45 | 0.98662 | -0.25568 | 0.0019675 | 0.0004931
46 | 0.98926 | -0.2039 | 0.0036246 | 0.00090841
47 | 0.98931 | -0.20284 | 0 | 0
48 | 0.98674 | -0.252 | 0 | 0
49 | 0.99084 | -0.17449 | 0.0080136 | 0.0020084
50 | 0.98489 | -0.28768 | 0.0015052 | 0.00037724
51 | 0.98441 | -0.29687 | 0.0015242 | 0.00038201
52 | 0.9727 | -0.52559 | 0 | 0
53 | 0.97313 | -0.51695 | 0.0058345 | 0.0014623
54 | 0.97234 | -0.53256 | 0.0012889 | 0.00032304
55 | 0.97087 | -0.56159 | 0.014107 | 0.0035355
56 | 0.97112 | -0.55675 | 0.017614 | 0.0044145
57 | 0.97166 | -0.54611 | 0 | 0
58 | 0.99351 | -0.12488 | 0.0024019 | 0.00060196
59 | 0.9723 | -0.53327 | 0.013077 | 0.0032773
60 | 0.99346 | -0.12578 | 0 | 0
61 | 0.97511 | -0.47795 | 0 | 0
62 | 0.97401 | -0.49974 | 0 | 0
63 | 0.9778 | -0.42537 | 0.0009594 | 0.00024045
64 | 0.9729 | -0.52158 | 0 | 0
65 | 0.97363 | -0.50709 | 0.0023678 | 0.00059343
66 | 0.97384 | -0.50295 | 0.0021385 | 0.00053596
67 | 0.99342 | -0.12661 | 0.003095 | 0.00077567
68 | 0.97283 | -0.52287 | 0.0077177 | 0.0019342
69 | 0.97278 | -0.5238 | 0.0040408 | 0.0010127
70 | 0.97945 | -0.39308 | 0.0015106 | 0.0003786
71 | 0.98923 | -0.20559 | 0.0023172 | 0.00058075
72 | 0.98922 | -0.20583 | 0.0090374 | 0.002265
73 | 0.98918 | -0.20661 | 0.0026903 | 0.00067425
74 | 0.97937 | -0.39706 | 0.00077846 | 0.0001951
75 | 0.9794 | -0.39656 | 0 | 0
76 | 0.97329 | -0.51387 | 0 | 0
77 | 0.97377 | -0.50442 | 0.0017535 | 0.00043946
78 | 0.97929 | -0.3987 | 0.0035051 | 0.00087846
79 | 0.97935 | -0.39747 | 0.0032385 | 0.00081164
80 | 0.98331 | -0.32019 | 0.0011227 | 0.00028137
81 | 0.99319 | -0.13118 | 0.0020853 | 0.00052262
82 | 0.9837 | -0.31249 | 0 | 0
83 | 0.97995 | -0.38585 | 0.00084598 | 0.00021202
84 | 0.97995 | -0.38567 | 0 | 0
85 | 0.98333 | -0.31787 | 0.0011948 | 0.00029944
86 | 0.98329 | -0.3186 | 0.0012952 | 0.00032461
87 | 0.98028 | -0.37699 | 0 | 0
88 | 0.9801 | -0.38055 | 0 | 0
89 | 0.9802 | -0.37848 | 0.0013463 | 0.00033742
90 | 0.98006 | -0.3813 | 0.0032808 | 0.00082224
91 | 0.97999 | -0.38264 | 0.0030427 | 0.00076258
92 | 0.98004 | -0.38161 | 0.0018775 | 0.00047054
93 | 0.97975 | -0.38975 | 0.00069146 | 0.0001733
94 | 0.97977 | -0.38935 | 0.0023742 | 0.00059503
95 | 0.97982 | -0.38833 | 0.0043102 | 0.0010802
96 | 0.97985 | -0.38767 | 0.0060845 | 0.0015249
97 | 0.97994 | -0.38589 | 0 | 0
98 | 0.98492 | -0.28882 | 0.0064234 | 0.0016099
99 | 0.97946 | -0.3954 | 0 | 0
100 | 0.97956 | -0.39351 | 0 | 0
101 | 0.97943 | -0.39607 | 0 | 0
102 | 0.97968 | -0.39109 | 0.0022161 | 0.0005554
103 | 0.97942 | -0.3962 | 0.00051615 | 0.00012936
104 | 0.9794 | -0.39648 | 0 | 0
105 | 0.9797 | -0.39075 | 0.0013506 | 0.00033848
106 | 0.97941 | -0.39639 | 0.00014011 | 3.5115e-05
107 | 0.98001 | -0.38465 | 0.0039731 | 0.00099576
108 | 0.98016 | -0.38163 | 0 | 0
109 | 0.98082 | -0.36872 | 0 | 0
110 | 0.97989 | -0.38685 | 0.0027019 | 0.00067716
111 | 0.9805 | -0.37507 | 0.0033728 | 0.00084532
112 | 0.9817 | -0.35141 | 0.0021801 | 0.00054638
113 | 0.97964 | -0.39192 | 0.0022409 | 0.00056162
114 | 0.97961 | -0.39236 | 0.0085028 | 0.002131
115 | 0.98005 | -0.3839 | 0.00089976 | 0.0002255
116 | 0.98007 | -0.38345 | 0.00065512 | 0.00016419
117 | 0.9801 | -0.38273 | 0.00077238 | 0.00019358
118 | 0.98028 | -0.37934 | 0.0013364 | 0.00033494
119 | 0.98273 | -0.33129 | 0.0013741 | 0.00034438
120 | 0.98002 | -0.38203 | 0.00096015 | 0.00024064
121 | 0.97999 | -0.38272 | 0.001936 | 0.0004852
122 | 0.97996 | -0.38322 | 0.0029064 | 0.00072841
123 | 0.97375 | -0.50474 | 0.0043635 | 0.0010936
124 | 0.97372 | -0.50548 | 0.0023355 | 0.00058532
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026085 | -0.0065376 | 0.0261 | 0.0065469 | 1.5132e-05 | 9.3393e-06 | 0.038993 | 0.038993 | 0.038993 | 0.99545 | -0.087524 | 0.99608 | -0.075354 | 10.7124
1 | -0.06229 | -0.015643 | 0.062381 | 0.015702 | 9.1525e-05 | 5.8209e-05 | 0.093065 | 0.093065 | 0.093065 | 0.99608 | -0.075354 | 0.99767 | -0.044608 | 25.5672
2 | 0.036189 | 0.0090964 | -0.036149 | -0.0090711 | 4.0257e-05 | 2.5287e-05 | 0.054072 | 0.054072 | 0.054072 | 0.99608 | -0.075354 | 0.99487 | -0.098681 | 14.855
3 | -0.080067 | -0.020134 | 0.080173 | 0.020201 | 0.00010561 | 6.7333e-05 | 0.11944 | 0.11944 | 0.11944 | 0.99767 | -0.044608 | 0.99911 | -0.017031 | 32.8141
4 | 0.036149 | 0.0090711 | -0.036121 | -0.0090536 | 2.7918e-05 | 1.7537e-05 | 0.054072 | 0.054072 | 0.054072 | 0.99487 | -0.098681 | 0.99403 | -0.11489 | 14.855
5 | 0.02551 | 0.0063965 | -0.025504 | -0.0063929 | 5.9066e-06 | 3.6388e-06 | 0.03809 | 0.038091 | 0.038091 | 0.99657 | -0.06591 | 0.99632 | -0.070769 | 10.4644
6 | -0.02551 | -0.0063965 | 0.025521 | 0.0064032 | 1.0892e-05 | 6.7096e-06 | 0.03809 | 0.03809 | 0.03809 | 0.99657 | -0.06591 | 0.99704 | -0.056955 | 10.4644
7 | 0.013466 | 0.0033754 | -0.013464 | -0.0033745 | 1.7562e-06 | 9.732e-07 | 0.020112 | 0.020112 | 0.020112 | 0.99632 | -0.070769 | 0.99618 | -0.073507 | 5.5253
8 | 0.012038 | 0.0030175 | -0.012036 | -0.0030165 | 1.8905e-06 | 1.0068e-06 | 0.017979 | 0.017979 | 0.017979 | 0.99632 | -0.070769 | 0.99615 | -0.074066 | 4.9392
9 | -0.037225 | -0.0093366 | 0.037255 | 0.0093555 | 3.0008e-05 | 1.8866e-05 | 0.055558 | 0.055558 | 0.055558 | 0.99704 | -0.056955 | 0.99791 | -0.040058 | 15.2633
10 | -0.16131 | -0.040586 | 0.16145 | 0.04067 | 0.00013138 | 8.3767e-05 | 0.24031 | 0.24031 | 0.24031 | 0.99911 | -0.017031 | 1 | 0 | 33.0092
11 | 0.049351 | 0.01241 | -0.049297 | -0.012375 | 5.4211e-05 | 3.4345e-05 | 0.073515 | 0.073515 | 0.073515 | 0.99911 | -0.017031 | 0.99791 | -0.040058 | 20.1963
12 | 0.03179 | 0.007975 | -0.03177 | -0.0079623 | 2.0381e-05 | 1.2727e-05 | 0.047349 | 0.04735 | 0.04735 | 0.99911 | -0.017031 | 0.99841 | -0.030488 | 13.0081
13 | 0.0108 | 0.0027074 | -0.010798 | -0.0027063 | 2.0685e-06 | 1.0503e-06 | 0.016167 | 0.016167 | 0.016167 | 0.99403 | -0.11489 | 0.99382 | -0.11891 | 4.4415
14 | 0.012042 | 0.0030197 | -0.012038 | -0.003018 | 3.2154e-06 | 1.7105e-06 | 0.017956 | 0.017956 | 0.017956 | 0.99791 | -0.040058 | 0.99762 | -0.045662 | 4.9331
15 | 0.263 | 0.067733 | -0.26179 | -0.06696 | 0.001209 | 0.00077269 | 0.392 | 0.392 | 0.392 | 1 | 0 | 0.99498 | -0.094948 | 53.8456
16 | 0.0036505 | 0.00091463 | -0.0036503 | -0.0009147 | 1.4314e-07 | -7.3573e-08 | 0.0054688 | 0.0054688 | 0.0054688 | 0.99325 | -0.12985 | 0.99321 | -0.13067 | 1.5024
17 | -0.0036505 | -0.00091463 | 0.0036506 | 0.00091457 | 9.938e-08 | -5.109e-08 | 0.0054688 | 0.0054687 | 0.0054688 | 0.99325 | -0.12985 | 0.99328 | -0.12928 | 1.5024
18 | 0.0020853 | 0.00052248 | -0.0020853 | -0.00052262 | 5.0541e-08 | -1.4635e-07 | 0.0031242 | 0.0031242 | 0.0031242 | 0.99321 | -0.13067 | 0.99319 | -0.13118 | 0.8583
19 | -0.0052963 | -0.001327 | 0.0052972 | 0.0013271 | 8.8359e-07 | 8.092e-08 | 0.0079342 | 0.007934 | 0.0079342 | 0.99328 | -0.12928 | 0.99346 | -0.12578 | 2.1797
20 | 0.0005381 | 0.00013486 | -0.0005381 | -0.00013486 | 7.407e-12 | -3.5238e-10 | 0.00082407 | 0.00082407 | 0.00082407 | 0.97164 | -0.54641 | 0.97164 | -0.54641 | 0.22639
21 | -0.0005381 | -0.00013486 | 0.00053811 | 0.00013463 | 4.7089e-09 | -2.2604e-07 | 0.00082407 | 0.00082399 | 0.00082407 | 0.97164 | -0.54641 | 0.97165 | -0.54622 | 0.22639
22 | -0.0076849 | -0.0019258 | 0.007685 | 0.0019258 | 4.0803e-08 | 1.6383e-08 | 0.011769 | 0.011769 | 0.011769 | 0.97165 | -0.54622 | 0.97166 | -0.54611 | 3.2332
23 | -0.0098381 | -0.0024662 | 0.009839 | 0.0024666 | 8.6197e-07 | 4.1998e-07 | 0.014884 | 0.014884 | 0.014884 | 0.98354 | -0.31552 | 0.98364 | -0.31368 | 4.0891
24 | 0.0098381 | 0.0024662 | -0.0098359 | -0.0024651 | 2.1824e-06 | 1.0634e-06 | 0.014884 | 0.014885 | 0.014885 | 0.98354 | -0.31552 | 0.98331 | -0.32017 | 4.0892
25 | -0.010794 | -0.0027059 | 0.010794 | 0.0027062 | 6.1289e-07 | 3.1444e-07 | 0.016329 | 0.016329 | 0.016329 | 0.98364 | -0.31368 | 0.9837 | -0.31249 | 4.4859
26 | 0.0011227 | 0.00028136 | -0.0011227 | -0.00028137 | 5.8322e-10 | -6.4642e-09 | 0.0016989 | 0.0016989 | 0.0016989 | 0.98331 | -0.32017 | 0.98331 | -0.32019 | 0.46674
27 | 0.012038 | 0.003018 | -0.012036 | -0.0030164 | 2.9614e-06 | 1.5756e-06 | 0.017956 | 0.017957 | 0.017957 | 0.99762 | -0.045662 | 0.99735 | -0.050826 | 4.9331
28 | 0.010029 | 0.0025136 | -0.010027 | -0.0025129 | 1.3953e-06 | 6.975e-07 | 0.015356 | 0.015356 | 0.015356 | 0.97181 | -0.54319 | 0.97166 | -0.54611 | 4.2187
29 | -0.010029 | -0.0025136 | 0.010031 | 0.0025146 | 1.9965e-06 | 9.9796e-07 | 0.015356 | 0.015356 | 0.015356 | 0.97181 | -0.54319 | 0.97202 | -0.53901 | 4.2187
30 | -0.015206 | -0.0038115 | 0.01521 | 0.0038142 | 4.6786e-06 | 2.7088e-06 | 0.023278 | 0.023278 | 0.023278 | 0.97202 | -0.53901 | 0.97234 | -0.53256 | 6.395
31 | 0.010798 | 0.0027063 | -0.010794 | -0.0027048 | 3.0683e-06 | 1.5582e-06 | 0.016167 | 0.016167 | 0.016167 | 0.99382 | -0.11891 | 0.99351 | -0.12488 | 4.4415
32 | 0.11833 | 0.030094 | -0.11802 | -0.029893 | 0.0003134 | 0.00020023 | 0.17713 | 0.17713 | 0.17713 | 0.99498 | -0.094948 | 0.9921 | -0.15008 | 48.6608
33 | 0.14346 | 0.036867 | -0.14312 | -0.03665 | 0.00034101 | 0.00021722 | 0.21487 | 0.21487 | 0.21487 | 0.99498 | -0.094948 | 0.9924 | -0.14401 | 29.5153
34 | 0.11259 | 0.028533 | -0.11249 | -0.028469 | 9.8732e-05 | 6.3069e-05 | 0.16898 | 0.16898 | 0.16898 | 0.9921 | -0.15008 | 0.99115 | -0.16835 | 46.4233
35 | 0.1287 | 0.033037 | -0.12839 | -0.032835 | 0.00031723 | 0.00020186 | 0.19326 | 0.19326 | 0.19326 | 0.9924 | -0.14401 | 0.98973 | -0.19493 | 26.5466
36 | 0.012086 | 0.0030296 | -0.012084 | -0.0030286 | 1.8942e-06 | 1.0146e-06 | 0.018144 | 0.018144 | 0.018144 | 0.99115 | -0.16835 | 0.99098 | -0.17164 | 4.9847
37 | 0.10041 | 0.02544 | -0.10034 | -0.025398 | 6.4876e-05 | 4.1423e-05 | 0.15084 | 0.15084 | 0.15084 | 0.99115 | -0.16835 | 0.99045 | -0.18181 | 41.4386
38 | 0.12052 | 0.030865 | -0.12048 | -0.030835 | 4.6166e-05 | 2.9354e-05 | 0.18144 | 0.18144 | 0.18144 | 0.98973 | -0.19493 | 0.98931 | -0.20284 | 24.9229
39 | 0.018445 | 0.0046262 | -0.018443 | -0.0046248 | 2.3553e-06 | 1.4023e-06 | 0.027723 | 0.027723 | 0.027723 | 0.99009 | -0.18893 | 0.98995 | -0.19161 | 7.6162
40 | -0.022285 | -0.0055885 | 0.022292 | 0.0055931 | 7.5733e-06 | 4.6153e-06 | 0.033493 | 0.033493 | 0.033493 | 0.99009 | -0.18893 | 0.99045 | -0.18181 | 9.2014
41 | 0.017354 | 0.0043519 | -0.017348 | -0.0043485 | 5.8015e-06 | 3.4208e-06 | 0.026086 | 0.026086 | 0.026086 | 0.98995 | -0.19161 | 0.98959 | -0.19863 | 7.1666
42 | 0.078048 | 0.019805 | -0.077994 | -0.019771 | 5.4427e-05 | 3.4698e-05 | 0.11734 | 0.11734 | 0.11734 | 0.99045 | -0.18181 | 0.9897 | -0.19632 | 32.2373
43 | 0.017348 | 0.0043485 | -0.017348 | -0.0043484 | 2.1035e-07 | 1.2403e-07 | 0.026086 | 0.026086 | 0.026086 | 0.98959 | -0.19863 | 0.98957 | -0.19888 | 7.1666
44 | 0.075561 | 0.019161 | -0.075437 | -0.019082 | 0.00012402 | 7.9045e-05 | 0.11369 | 0.11369 | 0.11369 | 0.9897 | -0.19632 | 0.98792 | -0.23052 | 31.2325
45 | 0.01405 | 0.0035217 | -0.014048 | -0.0035206 | 1.9367e-06 | 1.0909e-06 | 0.021127 | 0.021127 | 0.021127 | 0.98957 | -0.19888 | 0.98942 | -0.20178 | 5.804
46 | 0.0040689 | 0.0010197 | -0.0040689 | -0.0010198 | 6.9362e-08 | -1.9446e-08 | 0.0061097 | 0.0061097 | 0.0061097 | 0.99098 | -0.17164 | 0.99096 | -0.17199 | 1.6785
47 | 0.0080147 | 0.0020088 | -0.0080138 | -0.0020085 | 8.9805e-07 | 3.6175e-07 | 0.012035 | 0.012035 | 0.012035 | 0.99098 | -0.17164 | 0.99086 | -0.17399 | 3.3062
48 | 0.073713 | 0.01865 | -0.073624 | -0.018593 | 8.8869e-05 | 5.6631e-05 | 0.11109 | 0.11109 | 0.11109 | 0.98792 | -0.23052 | 0.98662 | -0.25568 | 30.5189
49 | 0.0050085 | 0.0012548 | -0.0050076 | -0.0012548 | 9.0983e-07 | 3.3192e-08 | 0.0075323 | 0.0075325 | 0.0075325 | 0.98942 | -0.20178 | 0.98923 | -0.20559 | 2.0694
50 | 0.0090392 | 0.0022658 | -0.0090374 | -0.002265 | 1.7449e-06 | 7.9342e-07 | 0.013594 | 0.013594 | 0.013594 | 0.98942 | -0.20178 | 0.98922 | -0.20583 | 3.7347
51 | 0.0080138 | 0.0020085 | -0.0080136 | -0.0020084 | 1.914e-07 | 7.7105e-08 | 0.012035 | 0.012035 | 0.012035 | 0.99086 | -0.17399 | 0.99084 | -0.17449 | 3.3062
52 | 0.071656 | 0.0181 | -0.071543 | -0.018028 | 0.00011362 | 7.2385e-05 | 0.10812 | 0.10812 | 0.10812 | 0.98662 | -0.25568 | 0.98492 | -0.28882 | 29.7038
53 | -0.0036246 | -0.00090841 | 0.0036248 | 0.00090832 | 1.8233e-07 | -9.3329e-08 | 0.0054521 | 0.005452 | 0.0054521 | 0.98926 | -0.2039 | 0.98931 | -0.20284 | 1.4978
54 | 0.11685 | 0.029927 | -0.11658 | -0.029751 | 0.00027758 | 0.00017643 | 0.17599 | 0.17599 | 0.17599 | 0.98931 | -0.20284 | 0.98674 | -0.252 | 24.1741
55 | 0.11658 | 0.029751 | -0.11637 | -0.029623 | 0.00020056 | 0.00012748 | 0.17599 | 0.17599 | 0.17599 | 0.98674 | -0.252 | 0.98489 | -0.28768 | 24.1741
56 | 0.11487 | 0.029246 | -0.11482 | -0.029214 | 5.0916e-05 | 3.2357e-05 | 0.17371 | 0.17371 | 0.17371 | 0.98489 | -0.28768 | 0.98441 | -0.29687 | 23.8618
57 | 0.11329 | 0.028832 | -0.11318 | -0.028759 | 0.00011457 | 7.2794e-05 | 0.17141 | 0.17141 | 0.17141 | 0.98441 | -0.29687 | 0.98333 | -0.31787 | 23.5453
58 | -0.016505 | -0.0041405 | 0.016511 | 0.0041445 | 6.8024e-06 | 4.0002e-06 | 0.02525 | 0.02525 | 0.02525 | 0.9727 | -0.52559 | 0.97313 | -0.51695 | 6.9368
59 | 0.016505 | 0.0041405 | -0.016499 | -0.0041372 | 5.481e-06 | 3.2234e-06 | 0.02525 | 0.02525 | 0.02525 | 0.9727 | -0.52559 | 0.97234 | -0.53256 | 6.9368
60 | -0.022346 | -0.0056067 | 0.022349 | 0.0056087 | 3.2804e-06 | 2.0064e-06 | 0.034171 | 0.034171 | 0.034171 | 0.97313 | -0.51695 | 0.97329 | -0.51387 | 9.3878
61 | -0.014107 | -0.0035355 | 0.01411 | 0.0035373 | 3.2527e-06 | 1.8522e-06 | 0.021621 | 0.021621 | 0.021621 | 0.97087 | -0.56159 | 0.97112 | -0.55675 | 5.9397
62 | -0.031724 | -0.0079518 | 0.03174 | 0.0079619 | 1.6091e-05 | 1.0074e-05 | 0.04861 | 0.04861 | 0.04861 | 0.97112 | -0.55675 | 0.97166 | -0.54611 | 13.3544
63 | -0.03174 | -0.0079619 | 0.031759 | 0.007974 | 1.9441e-05 | 1.217e-05 | 0.04861 | 0.04861 | 0.04861 | 0.97166 | -0.54611 | 0.9723 | -0.53327 | 13.3544
64 | 0.0083926 | 0.0021028 | -0.0083923 | -0.0021027 | 3.6017e-07 | 1.5179e-07 | 0.01257 | 0.01257 | 0.01257 | 0.99351 | -0.12488 | 0.99346 | -0.12578 | 3.4532
65 | -0.044836 | -0.011251 | 0.044861 | 0.011267 | 2.5015e-05 | 1.5834e-05 | 0.068622 | 0.068622 | 0.068622 | 0.9723 | -0.53327 | 0.9729 | -0.52158 | 18.8523
66 | 0.0030951 | 0.00077555 | -0.003095 | -0.00077567 | 1.2291e-07 | -1.1881e-07 | 0.0046358 | 0.0046358 | 0.0046358 | 0.99346 | -0.12578 | 0.99342 | -0.12661 | 1.2736
67 | 0.035363 | 0.0088904 | -0.035326 | -0.0088672 | 3.6756e-05 | 2.3105e-05 | 0.053974 | 0.053974 | 0.053974 | 0.97511 | -0.47795 | 0.97401 | -0.49974 | 14.828
68 | -0.092102 | -0.02318 | 0.092334 | 0.023328 | 0.00023208 | 0.00014814 | 0.14058 | 0.14058 | 0.14058 | 0.97511 | -0.47795 | 0.9778 | -0.42537 | 38.6213
69 | 0.056739 | 0.01429 | -0.056621 | -0.014215 | 0.00011811 | 7.5071e-05 | 0.086608 | 0.086608 | 0.086608 | 0.97511 | -0.47795 | 0.9729 | -0.52158 | 23.7934
70 | 0.024733 | 0.0062119 | -0.024724 | -0.0062066 | 8.6718e-06 | 5.3485e-06 | 0.03779 | 0.03779 | 0.03779 | 0.97401 | -0.49974 | 0.97363 | -0.50709 | 10.3819
71 | 0.010593 | 0.0026553 | -0.010592 | -0.0026545 | 1.6203e-06 | 8.3171e-07 | 0.016184 | 0.016184 | 0.016184 | 0.97401 | -0.49974 | 0.97384 | -0.50295 | 4.4461
72 | -0.093293 | -0.023569 | 0.093438 | 0.023661 | 0.00014463 | 9.2322e-05 | 0.14204 | 0.14204 | 0.14204 | 0.9778 | -0.42537 | 0.97945 | -0.39308 | 39.0224
73 | 0.011759 | 0.0029473 | -0.011759 | -0.0029469 | 7.1952e-07 | 3.8684e-07 | 0.017986 | 0.017986 | 0.017986 | 0.9729 | -0.52158 | 0.97283 | -0.52287 | 4.9411
74 | 0.022356 | 0.0056132 | -0.022349 | -0.0056087 | 7.2301e-06 | 4.422e-06 | 0.034171 | 0.034171 | 0.034171 | 0.97363 | -0.50709 | 0.97329 | -0.51387 | 9.3877
75 | 0.0084532 | 0.0021185 | -0.0084526 | -0.0021182 | 5.9072e-07 | 2.6059e-07 | 0.012916 | 0.012916 | 0.012916 | 0.97384 | -0.50295 | 0.97377 | -0.50442 | 3.5484
76 | 0.004041 | 0.0010127 | -0.0040408 | -0.0010127 | 1.8068e-07 | -4.0945e-08 | 0.0061809 | 0.006181 | 0.006181 | 0.97283 | -0.52287 | 0.97278 | -0.5238 | 1.6981
77 | -0.094948 | -0.024039 | 0.095022 | 0.024086 | 7.3423e-05 | 4.6872e-05 | 0.14434 | 0.14434 | 0.14434 | 0.97945 | -0.39308 | 0.98028 | -0.37699 | 39.6529
78 | 0.0026904 | 0.00067406 | -0.0026903 | -0.00067425 | 1.3009e-07 | -1.8865e-07 | 0.0040469 | 0.004047 | 0.004047 | 0.98923 | -0.20559 | 0.98918 | -0.20661 | 1.1118
79 | -0.00077846 | -0.0001951 | 0.00077847 | 0.00019467 | 1.8466e-08 | -4.3122e-07 | 0.0011827 | 0.0011826 | 0.0011827 | 0.97937 | -0.39706 | 0.9794 | -0.39656 | 0.32493
80 | -0.00077847 | -0.00019467 | 0.00077848 | 0.0001946 | 2.9253e-09 | -6.8324e-08 | 0.0011826 | 0.0011826 | 0.0011826 | 0.9794 | -0.39656 | 0.9794 | -0.39648 | 0.32489
81 | 0.0066991 | 0.0016788 | -0.006699 | -0.0016788 | 1.0415e-07 | 3.3686e-08 | 0.010237 | 0.010237 | 0.010237 | 0.97377 | -0.50442 | 0.97375 | -0.50474 | 2.8123
82 | -0.0035051 | -0.00087846 | 0.0035053 | 0.00087835 | 2.0591e-07 | -1.1179e-07 | 0.005326 | 0.0053259 | 0.005326 | 0.97929 | -0.3987 | 0.97935 | -0.39747 | 1.4632
83 | -0.0067438 | -0.00169 | 0.0067445 | 0.0016902 | 6.6565e-07 | 2.1325e-07 | 0.010246 | 0.010246 | 0.010246 | 0.97935 | -0.39747 | 0.97946 | -0.3954 | 2.8149
84 | -0.065046 | -0.016371 | 0.065119 | 0.016418 | 7.3671e-05 | 4.6891e-05 | 0.098417 | 0.098417 | 0.098417 | 0.9837 | -0.31249 | 0.98492 | -0.28882 | 27.0377
85 | 0.054251 | 0.013665 | -0.054202 | -0.013634 | 4.8733e-05 | 3.0945e-05 | 0.082089 | 0.082089 | 0.082089 | 0.9837 | -0.31249 | 0.98273 | -0.33129 | 22.5518
86 | -0.00084598 | -0.00021202 | 0.00084599 | 0.00021188 | 7.1924e-09 | -1.4183e-07 | 0.0012846 | 0.0012845 | 0.0012846 | 0.97995 | -0.38585 | 0.97995 | -0.38567 | 0.35291
87 | -0.011593 | -0.0029062 | 0.011594 | 0.0029067 | 9.8182e-07 | 5.2191e-07 | 0.017604 | 0.017604 | 0.017604 | 0.97995 | -0.38567 | 0.98005 | -0.3839 | 4.8362
88 | 0.010747 | 0.0026943 | -0.010744 | -0.0026927 | 3.1959e-06 | 1.6423e-06 | 0.016319 | 0.016319 | 0.016319 | 0.97995 | -0.38567 | 0.97964 | -0.39192 | 4.4833
89 | 0.11198 | 0.028459 | -0.11198 | -0.028457 | 3.9085e-06 | 2.4968e-06 | 0.1696 | 0.1696 | 0.1696 | 0.98333 | -0.31787 | 0.98329 | -0.3186 | 46.5939
90 | 0.11069 | 0.028132 | -0.11038 | -0.027934 | 0.00031027 | 0.0001982 | 0.16764 | 0.16764 | 0.16764 | 0.98329 | -0.3186 | 0.98028 | -0.37699 | 46.0555
91 | 0.006325 | 0.0015847 | -0.0063239 | -0.0015845 | 1.0741e-06 | 2.9575e-07 | 0.0096009 | 0.009601 | 0.009601 | 0.98028 | -0.37699 | 0.9801 | -0.38055 | 2.6376
92 | 0.0090284 | 0.0022629 | -0.0090278 | -0.0022626 | 6.4201e-07 | 2.9598e-07 | 0.013705 | 0.013705 | 0.013705 | 0.98028 | -0.37699 | 0.9802 | -0.37848 | 3.7651
93 | 0.0032809 | 0.00082216 | -0.0032808 | -0.00082224 | 1.1721e-07 | -8.373e-08 | 0.0049811 | 0.0049812 | 0.0049812 | 0.9801 | -0.38055 | 0.98006 | -0.3813 | 1.3685
94 | 0.003043 | 0.00076229 | -0.0030427 | -0.00076258 | 3.0264e-07 | -2.8276e-07 | 0.0046199 | 0.0046201 | 0.0046201 | 0.9801 | -0.38055 | 0.97999 | -0.38264 | 1.2692
95 | 0.0076815 | 0.0019252 | -0.0076803 | -0.0019247 | 1.1448e-06 | 4.4971e-07 | 0.011661 | 0.011661 | 0.011661 | 0.9802 | -0.37848 | 0.98004 | -0.38161 | 3.2036
96 | 0.0058029 | 0.0014542 | -0.0058027 | -0.0014542 | 1.1683e-07 | 2.4199e-08 | 0.0088105 | 0.0088105 | 0.0088105 | 0.98004 | -0.38161 | 0.98002 | -0.38203 | 2.4205
97 | -0.00069146 | -0.0001733 | 0.00069148 | 0.0001729 | 1.3306e-08 | -3.9671e-07 | 0.0010502 | 0.00105 | 0.0010502 | 0.97975 | -0.38975 | 0.97977 | -0.38935 | 0.28851
98 | -0.0030657 | -0.00076793 | 0.0030658 | 0.0007678 | 1.4827e-07 | -1.3483e-07 | 0.0046558 | 0.0046557 | 0.0046558 | 0.97977 | -0.38935 | 0.97982 | -0.38833 | 1.2791
99 | -0.007376 | -0.001848 | 0.0073762 | 0.0018481 | 2.3246e-07 | 8.6546e-08 | 0.011201 | 0.011201 | 0.011201 | 0.97982 | -0.38833 | 0.97985 | -0.38767 | 3.0773
100 | -0.013461 | -0.003373 | 0.013462 | 0.0033737 | 1.1391e-06 | 6.3746e-07 | 0.020442 | 0.020441 | 0.020442 | 0.97985 | -0.38767 | 0.97994 | -0.38589 | 5.6158
101 | 0.002702 | 0.00067699 | -0.0027019 | -0.00067716 | 1.2327e-07 | -1.6711e-07 | 0.0041029 | 0.0041029 | 0.0041029 | 0.97994 | -0.38589 | 0.97989 | -0.38685 | 1.1272
102 | -0.016164 | -0.0040507 | 0.016167 | 0.0040526 | 3.2822e-06 | 1.9175e-06 | 0.024544 | 0.024544 | 0.024544 | 0.97994 | -0.38589 | 0.98016 | -0.38163 | 6.7429
103 | -0.0081793 | -0.0020487 | 0.00818 | 0.002049 | 7.3364e-07 | 3.1004e-07 | 0.012426 | 0.012426 | 0.012426 | 0.97946 | -0.3954 | 0.97956 | -0.39351 | 3.4137
104 | 0.0014348 | 0.00035851 | -0.0014348 | -0.0003588 | 4.5682e-08 | -2.9353e-07 | 0.0021794 | 0.0021795 | 0.0021795 | 0.97946 | -0.3954 | 0.97943 | -0.39607 | 0.59877
105 | -0.00818 | -0.002049 | 0.008181 | 0.0020494 | 9.4208e-07 | 3.9808e-07 | 0.012426 | 0.012426 | 0.012426 | 0.97956 | -0.39351 | 0.97968 | -0.39109 | 3.4136
106 | 0.0014348 | 0.0003588 | -0.0014347 | -0.00035886 | 9.3531e-09 | -6.0091e-08 | 0.0021795 | 0.0021795 | 0.0021795 | 0.97943 | -0.39607 | 0.97942 | -0.3962 | 0.59877
107 | -0.010397 | -0.0026048 | 0.010397 | 0.0026049 | 1.7233e-07 | 8.7089e-08 | 0.015792 | 0.015792 | 0.015792 | 0.97968 | -0.39109 | 0.9797 | -0.39075 | 4.3383
108 | 0.0009186 | 0.0002295 | -0.00091859 | -0.00022964 | 8.1499e-09 | -1.3525e-07 | 0.0013954 | 0.0013954 | 0.0013954 | 0.97942 | -0.3962 | 0.97941 | -0.39639 | 0.38335
109 | -0.00077848 | -0.0001946 | 0.00077848 | 0.00019452 | 3.3083e-09 | -7.7272e-08 | 0.0011826 | 0.0011825 | 0.0011826 | 0.9794 | -0.39648 | 0.97941 | -0.39639 | 0.32488
110 | -0.011748 | -0.0029434 | 0.011751 | 0.0029452 | 3.4101e-06 | 1.8227e-06 | 0.017843 | 0.017843 | 0.017843 | 0.9797 | -0.39075 | 0.98001 | -0.38465 | 4.9019
111 | -0.015724 | -0.003941 | 0.015727 | 0.0039423 | 2.2642e-06 | 1.3156e-06 | 0.023875 | 0.023875 | 0.023875 | 0.98001 | -0.38465 | 0.98016 | -0.38163 | 6.5592
112 | -0.031894 | -0.0079949 | 0.031913 | 0.0080072 | 1.9631e-05 | 1.2282e-05 | 0.04842 | 0.04842 | 0.04842 | 0.98016 | -0.38163 | 0.98082 | -0.36872 | 13.3021
113 | 0.018642 | 0.0046771 | -0.018637 | -0.0046737 | 5.6439e-06 | 3.3747e-06 | 0.028284 | 0.028284 | 0.028284 | 0.98082 | -0.36872 | 0.9805 | -0.37507 | 7.7704
114 | -0.050556 | -0.012684 | 0.050597 | 0.012711 | 4.176e-05 | 2.6487e-05 | 0.076704 | 0.076704 | 0.076704 | 0.98082 | -0.36872 | 0.9817 | -0.35141 | 21.0725
115 | 0.015264 | 0.0038284 | -0.015261 | -0.0038266 | 3.1027e-06 | 1.7913e-06 | 0.023166 | 0.023166 | 0.023166 | 0.9805 | -0.37507 | 0.98028 | -0.37934 | 6.3642
116 | -0.052778 | -0.013257 | 0.052828 | 0.013289 | 5.0731e-05 | 3.22e-05 | 0.080008 | 0.080008 | 0.080008 | 0.9817 | -0.35141 | 0.98273 | -0.33129 | 21.9803
117 | 0.008503 | 0.0021311 | -0.0085028 | -0.002131 | 1.8083e-07 | 7.9337e-08 | 0.012916 | 0.012916 | 0.012916 | 0.97964 | -0.39192 | 0.97961 | -0.39236 | 3.5482
118 | -0.012494 | -0.0031322 | 0.012494 | 0.0031324 | 2.6665e-07 | 1.4576e-07 | 0.01897 | 0.01897 | 0.01897 | 0.98005 | -0.3839 | 0.98007 | -0.38345 | 5.2115
119 | -0.013149 | -0.0032966 | 0.01315 | 0.0032968 | 4.4772e-07 | 2.4879e-07 | 0.019965 | 0.019965 | 0.019965 | 0.98007 | -0.38345 | 0.9801 | -0.38273 | 5.4848
120 | -0.013922 | -0.0034904 | 0.013924 | 0.0034917 | 2.2536e-06 | 1.2728e-06 | 0.021137 | 0.021137 | 0.021137 | 0.9801 | -0.38273 | 0.98028 | -0.37934 | 5.8069
121 | 0.0048426 | 0.0012135 | -0.0048424 | -0.0012135 | 1.5932e-07 | 2.9476e-09 | 0.0073527 | 0.0073527 | 0.0073527 | 0.98002 | -0.38203 | 0.97999 | -0.38272 | 2.02
122 | 0.0029064 | 0.00072833 | -0.0029064 | -0.00072841 | 6.9454e-08 | -7.5364e-08 | 0.0044131 | 0.0044132 | 0.0044132 | 0.97999 | -0.38272 | 0.97996 | -0.38322 | 1.2124
123 | 0.0023356 | 0.00058516 | -0.0023355 | -0.00058532 | 8.158e-08 | -1.6024e-07 | 0.0035689 | 0.003569 | 0.003569 | 0.97375 | -0.50474 | 0.97372 | -0.50548 | 0.9805

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4261 | 0.1084

## res_load
| p_mw | q_mvar
0 | 0.026085 | 0.0065376
1 | 0.017686 | 0.0044326
2 | 0.011704 | 0.0029334
3 | 0.025322 | 0.0063462
4 | 0.013464 | 0.0033745
5 | 0.012036 | 0.0030165
6 | 0.03177 | 0.0079623
7 | 0.001565 | 0.00039222
8 | 0.0016457 | 0.00041246
9 | 0.0005381 | 0.00013486
10 | 0.0071468 | 0.0017912
11 | 0.00095483 | 0.0002393
12 | 0.0087133 | 0.0021838
13 | 0.012036 | 0.0030164
14 | 0.0023424 | 0.00058705
15 | 0.0051748 | 0.0012969
16 | 0.0054301 | 0.0013609
17 | 0.014414 | 0.0036125
18 | 0.0078623 | 0.0019705
19 | 0.0038394 | 0.00096224
20 | 0.0010889 | 0.0002729
21 | 0.0024326 | 0.00060968
22 | 0.0032984 | 0.00082666
23 | 0.0017245 | 0.0004322
24 | 0.0040689 | 0.0010198
25 | 0.0019675 | 0.0004931
26 | 0.0036246 | 0.00090841
27 | 0.0080136 | 0.0020084
28 | 0.0015052 | 0.00037724
29 | 0.0015242 | 0.00038201
30 | 0.0058345 | 0.0014623
31 | 0.0012889 | 0.00032304
32 | 0.014107 | 0.0035355
33 | 0.017614 | 0.0044145
34 | 0.0024019 | 0.00060196
35 | 0.013077 | 0.0032773
36 | 0.0009594 | 0.00024045
37 | 0.0023678 | 0.00059343
38 | 0.0021385 | 0.00053596
39 | 0.003095 | 0.00077567
40 | 0.0077177 | 0.0019342
41 | 0.0040408 | 0.0010127
42 | 0.0015106 | 0.0003786
43 | 0.0023172 | 0.00058075
44 | 0.0090374 | 0.002265
45 | 0.0026903 | 0.00067425
46 | 0.00077846 | 0.0001951
47 | 0.0017535 | 0.00043946
48 | 0.0035051 | 0.00087846
49 | 0.0032385 | 0.00081164
50 | 0.0011227 | 0.00028137
51 | 0.0020853 | 0.00052262
52 | 0.00084598 | 0.00021202
53 | 0.0011948 | 0.00029944
54 | 0.0012952 | 0.00032461
55 | 0.0013463 | 0.00033742
56 | 0.0032808 | 0.00082224
57 | 0.0030427 | 0.00076258
58 | 0.0018775 | 0.00047054
59 | 0.00069146 | 0.0001733
60 | 0.0023742 | 0.00059503
61 | 0.0043102 | 0.0010802
62 | 0.0060845 | 0.0015249
63 | 0.0064234 | 0.0016099
64 | 0.0022161 | 0.0005554
65 | 0.00051615 | 0.00012936
66 | 0.0013506 | 0.00033848
67 | 0.00014011 | 3.5115e-05
68 | 0.0039731 | 0.00099576
69 | 0.0027019 | 0.00067716
70 | 0.0033728 | 0.00084532
71 | 0.0021801 | 0.00054638
72 | 0.0022409 | 0.00056162
73 | 0.0085028 | 0.002131
74 | 0.00089976 | 0.0002255
75 | 0.00065512 | 0.00016419
76 | 0.00077238 | 0.00019358
77 | 0.0013364 | 0.00033494
78 | 0.0013741 | 0.00034438
79 | 0.00096015 | 0.00024064
80 | 0.001936 | 0.0004852
81 | 0.0029064 | 0.00072841
82 | 0.0043635 | 0.0010936
83 | 0.0023355 | 0.00058532

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1