## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_112-1_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_112-1_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_112-1_0_7_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_112-1_0_7_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_112-1_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_112-1_0_7_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_112-1_0_7_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_112-1_0_7_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_112-1_0_7_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_112-1_0_7_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_112-1_0_7_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_112-1_0_7_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_112-1_0_7_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_112-1_0_7_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_112-1_0_7_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_112-1_0_7_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_112-1_0_7_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_112-1_0_7_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_112-1_0_7_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_112-1_0_7_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_112-1_0_7_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_112-1_0_7_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_112-1_0_7_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_112-1_0_7_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_112-1_0_7_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_112-1_0_7_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_112-1_0_7_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_112-1_0_7_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_112-1_0_7_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_112-1_0_7_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_112-1_0_7_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_112-1_0_7_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_112-1_0_7_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_112-1_0_7_node_225 | 0.4 | n |  | TRUE
34 | bus_LV_112-1_0_7_node_224 | 0.4 | n |  | TRUE
35 | bus_LV_112-1_0_7_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_112-1_0_7_node_215 | 0.4 | n |  | TRUE
37 | bus_LV_112-1_0_7_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_112-1_0_7_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_112-1_0_7_node_117 | 0.4 | n |  | TRUE
40 | bus_LV_112-1_0_7_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_112-1_0_7_node_75 | 0.4 | n |  | TRUE
42 | bus_LV_112-1_0_7_node_161 | 0.4 | n |  | TRUE
43 | bus_LV_112-1_0_7_node_160 | 0.4 | n |  | TRUE
44 | bus_LV_112-1_0_7_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_112-1_0_7_node_242 | 0.4 | n |  | TRUE
46 | bus_LV_112-1_0_7_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_112-1_0_7_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_112-1_0_7_node_198 | 0.4 | n |  | TRUE
49 | bus_LV_112-1_0_7_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_112-1_0_7_node_196 | 0.4 | n |  | TRUE
51 | bus_LV_112-1_0_7_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_112-1_0_7_node_93 | 0.4 | n |  | TRUE
53 | bus_LV_112-1_0_7_node_94 | 0.4 | n |  | TRUE
54 | bus_LV_112-1_0_7_node_92 | 0.4 | n |  | TRUE
55 | bus_LV_112-1_0_7_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_112-1_0_7_node_236 | 0.4 | n |  | TRUE
57 | bus_LV_112-1_0_7_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_112-1_0_7_node_227 | 0.4 | n |  | TRUE
59 | bus_LV_112-1_0_7_node_199 | 0.4 | n |  | TRUE
60 | bus_LV_112-1_0_7_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_112-1_0_7_node_197 | 0.4 | n |  | TRUE
62 | bus_LV_112-1_0_7_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_112-1_0_7_node_116 | 0.4 | n |  | TRUE
64 | bus_LV_112-1_0_7_node_162 | 0.4 | n |  | TRUE
65 | bus_LV_112-1_0_7_node_240 | 0.4 | n |  | TRUE
66 | bus_LV_112-1_0_7_node_181 | 0.4 | n |  | TRUE
67 | bus_LV_112-1_0_7_node_184 | 0.4 | n |  | TRUE
68 | bus_LV_112-1_0_7_node_185 | 0.4 | n |  | TRUE
69 | bus_LV_112-1_0_7_node_275 | 0.4 | n |  | TRUE
70 | bus_LV_112-1_0_7_node_115 | 0.4 | n |  | TRUE
71 | bus_LV_112-1_0_7_node_114 | 0.4 | n |  | TRUE
72 | bus_LV_112-1_0_7_node_112 | 0.4 | n |  | TRUE
73 | bus_LV_112-1_0_7_node_113 | 0.4 | n |  | TRUE
74 | bus_LV_112-1_0_7_node_91 | 0.4 | n |  | TRUE
75 | bus_LV_112-1_0_7_node_210 | 0.4 | n |  | TRUE
76 | bus_LV_112-1_0_7_node_200 | 0.4 | n |  | TRUE
77 | bus_LV_112-1_0_7_node_201 | 0.4 | n |  | TRUE
78 | bus_LV_112-1_0_7_node_241 | 0.4 | n |  | TRUE
79 | bus_LV_112-1_0_7_node_239 | 0.4 | n |  | TRUE
80 | bus_LV_112-1_0_7_node_180 | 0.4 | n |  | TRUE
81 | bus_LV_112-1_0_7_node_189 | 0.4 | n |  | TRUE
82 | bus_LV_112-1_0_7_node_183 | 0.4 | n |  | TRUE
83 | bus_LV_112-1_0_7_node_212 | 0.4 | n |  | TRUE
84 | bus_LV_112-1_0_7_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_112-1_0_7_node_52 | 0.4 | n |  | TRUE
86 | bus_LV_112-1_0_7_node_53 | 0.4 | n |  | TRUE
87 | bus_LV_112-1_0_7_node_54 | 0.4 | n |  | TRUE
88 | bus_LV_112-1_0_7_node_55 | 0.4 | n |  | TRUE
89 | bus_LV_112-1_0_7_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_112-1_0_7_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_112-1_0_7_node_58 | 0.4 | n |  | TRUE
92 | bus_LV_112-1_0_7_node_59 | 0.4 | n |  | TRUE
93 | bus_LV_112-1_0_7_node_60 | 0.4 | n |  | TRUE
94 | bus_LV_112-1_0_7_node_154 | 0.4 | n |  | TRUE
95 | bus_LV_112-1_0_7_node_122 | 0.4 | n |  | TRUE
96 | bus_LV_112-1_0_7_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_112-1_0_7_node_147 | 0.4 | n |  | TRUE
98 | bus_LV_112-1_0_7_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_112-1_0_7_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_112-1_0_7_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_112-1_0_7_node_124 | 0.4 | n |  | TRUE
102 | bus_LV_112-1_0_7_node_120 | 0.4 | n |  | TRUE
103 | bus_LV_112-1_0_7_node_62 | 0.4 | n |  | TRUE
104 | bus_LV_112-1_0_7_node_63 | 0.4 | n |  | TRUE
105 | bus_LV_112-1_0_7_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_112-1_0_7_node_64 | 0.4 | n |  | TRUE
107 | bus_LV_112-1_0_7_node_65 | 0.4 | n |  | TRUE
108 | bus_LV_112-1_0_7_node_66 | 0.4 | n |  | TRUE
109 | bus_LV_112-1_0_7_node_67 | 0.4 | n |  | TRUE
110 | bus_LV_112-1_0_7_node_68 | 0.4 | n |  | TRUE
111 | bus_LV_112-1_0_7_node_69 | 0.4 | n |  | TRUE
112 | bus_LV_112-1_0_7_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_112-1_0_7_node_74 | 0.4 | n |  | TRUE
114 | bus_LV_112-1_0_7_node_70 | 0.4 | n |  | TRUE
115 | bus_LV_112-1_0_7_node_71 | 0.4 | n |  | TRUE
116 | bus_LV_112-1_0_7_node_73 | 0.4 | n |  | TRUE
117 | bus_LV_112-1_0_7_node_76 | 0.4 | n |  | TRUE
118 | bus_LV_112-1_0_7_node_77 | 0.4 | n |  | TRUE
119 | bus_LV_112-1_0_7_node_78 | 0.4 | n |  | TRUE
120 | bus_LV_112-1_0_7_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_112-1_0_7_node_79 | 0.4 | n |  | TRUE
122 | bus_LV_112-1_0_7_node_228 | 0.4 | n |  | TRUE
123 | bus_LV_112-1_0_7_node_175 | 0.4 | n |  | TRUE
124 | bus_LV_112-1_0_7_node_173 | 0.4 | n |  | TRUE
125 | bus_LV_112-1_0_7_node_80 | 0.4 | n |  | TRUE
126 | bus_LV_112-1_0_7_node_229 | 0.4 | n |  | TRUE
127 | bus_LV_112-1_0_7_node_81 | 0.4 | n |  | TRUE
128 | bus_LV_112-1_0_7_node_276 | 0.4 | n |  | TRUE
129 | bus_LV_112-1_0_7_node_87 | 0.4 | n |  | TRUE
130 | bus_LV_112-1_0_7_node_88 | 0.4 | n |  | TRUE
131 | bus_LV_112-1_0_7_node_89 | 0.4 | n |  | TRUE
132 | bus_LV_112-1_0_7_node_90 | 0.4 | n |  | TRUE
133 | bus_LV_112-1_0_7_node_226 | 0.4 | n |  | TRUE
134 | bus_LV_112-1_0_7_node_171 | 0.4 | n |  | TRUE
135 | bus_LV_112-1_0_7_node_96 | 0.4 | n |  | TRUE
136 | bus_LV_112-1_0_7_node_97 | 0.4 | n |  | TRUE
137 | bus_LV_112-1_0_7_node_98 | 0.4 | n |  | TRUE
138 | bus_LV_112-1_0_7_node_99 | 0.4 | n |  | TRUE
139 | bus_LV_112-1_0_7_node_100 | 0.4 | n |  | TRUE
140 | bus_LV_112-1_0_7_node_101 | 0.4 | n |  | TRUE
141 | bus_LV_112-1_0_7_node_244 | 0.4 | n |  | TRUE
142 | bus_LV_112-1_0_7_node_109 | 0.4 | n |  | TRUE
143 | bus_LV_112-1_0_7_node_243 | 0.4 | n |  | TRUE
144 | bus_LV_112-1_0_7_node_102 | 0.4 | n |  | TRUE
145 | bus_LV_112-1_0_7_node_103 | 0.4 | n |  | TRUE
146 | bus_LV_112-1_0_7_node_104 | 0.4 | n |  | TRUE
147 | bus_LV_112-1_0_7_node_105 | 0.4 | n |  | TRUE
148 | bus_LV_112-1_0_7_node_106 | 0.4 | n |  | TRUE
149 | bus_LV_112-1_0_7_node_107 | 0.4 | n |  | TRUE
150 | bus_LV_112-1_0_7_node_108 | 0.4 | n |  | TRUE
151 | bus_LV_112-1_0_7_node_110 | 0.4 | n |  | TRUE
152 | bus_LV_112-1_0_7_node_111 | 0.4 | n |  | TRUE
153 | bus_LV_112-1_0_7_node_247 | 0.4 | n |  | TRUE
154 | bus_LV_112-1_0_7_node_118 | 0.4 | n |  | TRUE
155 | bus_LV_112-1_0_7_node_119 | 0.4 | n |  | TRUE
156 | bus_LV_112-1_0_7_node_249 | 0.4 | n |  | TRUE
157 | bus_LV_112-1_0_7_node_246 | 0.4 | n |  | TRUE
158 | bus_LV_112-1_0_7_node_144 | 0.4 | n |  | TRUE
159 | bus_LV_112-1_0_7_node_165 | 0.4 | n |  | TRUE
160 | bus_LV_112-1_0_7_node_274 | 0.4 | n |  | TRUE
161 | bus_LV_112-1_0_7_node_142 | 0.4 | n |  | TRUE
162 | bus_LV_112-1_0_7_node_166 | 0.4 | n |  | TRUE
163 | bus_LV_112-1_0_7_node_121 | 0.4 | n |  | TRUE
164 | bus_LV_112-1_0_7_node_123 | 0.4 | n |  | TRUE
165 | bus_LV_112-1_0_7_node_125 | 0.4 | n |  | TRUE
166 | bus_LV_112-1_0_7_node_126 | 0.4 | n |  | TRUE
167 | bus_LV_112-1_0_7_node_127 | 0.4 | n |  | TRUE
168 | bus_LV_112-1_0_7_node_132 | 0.4 | n |  | TRUE
169 | bus_LV_112-1_0_7_node_131 | 0.4 | n |  | TRUE
170 | bus_LV_112-1_0_7_node_129 | 0.4 | n |  | TRUE
171 | bus_LV_112-1_0_7_node_169 | 0.4 | n |  | TRUE
172 | bus_LV_112-1_0_7_node_136 | 0.4 | n |  | TRUE
173 | bus_LV_112-1_0_7_node_133 | 0.4 | n |  | TRUE
174 | bus_LV_112-1_0_7_node_134 | 0.4 | n |  | TRUE
175 | bus_LV_112-1_0_7_node_128 | 0.4 | n |  | TRUE
176 | bus_LV_112-1_0_7_node_159 | 0.4 | n |  | TRUE
177 | bus_LV_112-1_0_7_node_130 | 0.4 | n |  | TRUE
178 | bus_LV_112-1_0_7_node_139 | 0.4 | n |  | TRUE
179 | bus_LV_112-1_0_7_node_152 | 0.4 | n |  | TRUE
180 | bus_LV_112-1_0_7_node_135 | 0.4 | n |  | TRUE
181 | bus_LV_112-1_0_7_node_137 | 0.4 | n |  | TRUE
182 | bus_LV_112-1_0_7_node_151 | 0.4 | n |  | TRUE
183 | bus_LV_112-1_0_7_node_138 | 0.4 | n |  | TRUE
184 | bus_LV_112-1_0_7_node_140 | 0.4 | n |  | TRUE
185 | bus_LV_112-1_0_7_node_141 | 0.4 | n |  | TRUE
186 | bus_LV_112-1_0_7_node_143 | 0.4 | n |  | TRUE
187 | bus_LV_112-1_0_7_node_145 | 0.4 | n |  | TRUE
188 | bus_LV_112-1_0_7_node_146 | 0.4 | n |  | TRUE
189 | bus_LV_112-1_0_7_node_148 | 0.4 | n |  | TRUE
190 | bus_LV_112-1_0_7_node_252 | 0.4 | n |  | TRUE
191 | bus_LV_112-1_0_7_node_149 | 0.4 | n |  | TRUE
192 | bus_LV_112-1_0_7_node_253 | 0.4 | n |  | TRUE
193 | bus_LV_112-1_0_7_node_254 | 0.4 | n |  | TRUE
194 | bus_LV_112-1_0_7_node_150 | 0.4 | n |  | TRUE
195 | bus_LV_112-1_0_7_node_168 | 0.4 | n |  | TRUE
196 | bus_LV_112-1_0_7_node_167 | 0.4 | n |  | TRUE
197 | bus_LV_112-1_0_7_node_153 | 0.4 | n |  | TRUE
198 | bus_LV_112-1_0_7_node_155 | 0.4 | n |  | TRUE
199 | bus_LV_112-1_0_7_node_156 | 0.4 | n |  | TRUE
200 | bus_LV_112-1_0_7_node_157 | 0.4 | n |  | TRUE
201 | bus_LV_112-1_0_7_node_158 | 0.4 | n |  | TRUE
202 | bus_LV_112-1_0_7_node_172 | 0.4 | n |  | TRUE
203 | bus_LV_112-1_0_7_node_170 | 0.4 | n |  | TRUE
204 | bus_LV_112-1_0_7_node_211 | 0.4 | n |  | TRUE
205 | bus_LV_112-1_0_7_node_235 | 0.4 | n |  | TRUE
206 | bus_LV_112-1_0_7_node_234 | 0.4 | n |  | TRUE
207 | bus_LV_112-1_0_7_node_237 | 0.4 | n |  | TRUE
208 | bus_LV_112-1_0_7_node_176 | 0.4 | n |  | TRUE
209 | bus_LV_112-1_0_7_node_177 | 0.4 | n |  | TRUE
210 | bus_LV_112-1_0_7_node_178 | 0.4 | n |  | TRUE
211 | bus_LV_112-1_0_7_node_179 | 0.4 | n |  | TRUE
212 | bus_LV_112-1_0_7_node_238 | 0.4 | n |  | TRUE
213 | bus_LV_112-1_0_7_node_182 | 0.4 | n |  | TRUE
214 | bus_LV_112-1_0_7_node_267 | 0.4 | n |  | TRUE
215 | bus_LV_112-1_0_7_node_186 | 0.4 | n |  | TRUE
216 | bus_LV_112-1_0_7_node_187 | 0.4 | n |  | TRUE
217 | bus_LV_112-1_0_7_node_188 | 0.4 | n |  | TRUE
218 | bus_LV_112-1_0_7_node_261 | 0.4 | n |  | TRUE
219 | bus_LV_112-1_0_7_node_258 | 0.4 | n |  | TRUE
220 | bus_LV_112-1_0_7_node_268 | 0.4 | n |  | TRUE
221 | bus_LV_112-1_0_7_node_190 | 0.4 | n |  | TRUE
222 | bus_LV_112-1_0_7_node_191 | 0.4 | n |  | TRUE
223 | bus_LV_112-1_0_7_node_192 | 0.4 | n |  | TRUE
224 | bus_LV_112-1_0_7_node_193 | 0.4 | n |  | TRUE
225 | bus_LV_112-1_0_7_node_194 | 0.4 | n |  | TRUE
226 | bus_LV_112-1_0_7_node_195 | 0.4 | n |  | TRUE
227 | bus_LV_112-1_0_7_node_202 | 0.4 | n |  | TRUE
228 | bus_LV_112-1_0_7_node_203 | 0.4 | n |  | TRUE
229 | bus_LV_112-1_0_7_node_204 | 0.4 | n |  | TRUE
230 | bus_LV_112-1_0_7_node_207 | 0.4 | n |  | TRUE
231 | bus_LV_112-1_0_7_node_205 | 0.4 | n |  | TRUE
232 | bus_LV_112-1_0_7_node_206 | 0.4 | n |  | TRUE
233 | bus_LV_112-1_0_7_node_208 | 0.4 | n |  | TRUE
234 | bus_LV_112-1_0_7_node_209 | 0.4 | n |  | TRUE
235 | bus_LV_112-1_0_7_node_214 | 0.4 | n |  | TRUE
236 | bus_LV_112-1_0_7_node_219 | 0.4 | n |  | TRUE
237 | bus_LV_112-1_0_7_node_216 | 0.4 | n |  | TRUE
238 | bus_LV_112-1_0_7_node_223 | 0.4 | n |  | TRUE
239 | bus_LV_112-1_0_7_node_221 | 0.4 | n |  | TRUE
240 | bus_LV_112-1_0_7_node_217 | 0.4 | n |  | TRUE
241 | bus_LV_112-1_0_7_node_218 | 0.4 | n |  | TRUE
242 | bus_LV_112-1_0_7_node_220 | 0.4 | n |  | TRUE
243 | bus_LV_112-1_0_7_node_222 | 0.4 | n |  | TRUE
244 | bus_LV_112-1_0_7_node_230 | 0.4 | n |  | TRUE
245 | bus_LV_112-1_0_7_node_231 | 0.4 | n |  | TRUE
246 | bus_LV_112-1_0_7_node_232 | 0.4 | n |  | TRUE
247 | bus_LV_112-1_0_7_node_233 | 0.4 | n |  | TRUE
248 | bus_LV_112-1_0_7_node_245 | 0.4 | n |  | TRUE
249 | bus_LV_112-1_0_7_node_248 | 0.4 | n |  | TRUE
250 | bus_LV_112-1_0_7_node_250 | 0.4 | n |  | TRUE
251 | bus_LV_112-1_0_7_node_251 | 0.4 | n |  | TRUE
252 | bus_LV_112-1_0_7_node_277 | 0.4 | n |  | TRUE
253 | bus_LV_112-1_0_7_node_278 | 0.4 | n |  | TRUE
254 | bus_LV_112-1_0_7_node_255 | 0.4 | n |  | TRUE
255 | bus_LV_112-1_0_7_node_256 | 0.4 | n |  | TRUE
256 | bus_LV_112-1_0_7_node_257 | 0.4 | n |  | TRUE
257 | bus_LV_112-1_0_7_node_259 | 0.4 | n |  | TRUE
258 | bus_LV_112-1_0_7_node_260 | 0.4 | n |  | TRUE
259 | bus_LV_112-1_0_7_node_262 | 0.4 | n |  | TRUE
260 | bus_LV_112-1_0_7_node_263 | 0.4 | n |  | TRUE
261 | bus_LV_112-1_0_7_node_264 | 0.4 | n |  | TRUE
262 | bus_LV_112-1_0_7_node_265 | 0.4 | n |  | TRUE
263 | bus_LV_112-1_0_7_node_271 | 0.4 | n |  | TRUE
264 | bus_LV_112-1_0_7_node_272 | 0.4 | n |  | TRUE
265 | bus_LV_112-1_0_7_node_266 | 0.4 | n |  | TRUE
266 | bus_LV_112-1_0_7_node_270 | 0.4 | n |  | TRUE
267 | bus_LV_112-1_0_7_node_273 | 0.4 | n |  | TRUE
268 | bus_LV_112-1_0_7_node_269 | 0.4 | n |  | TRUE
269 | bus_MV_355_0_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_112-1_0_7_load_0 | 0 | 0.00087721 | 0.00021985 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_112-1_0_7_load_1 | 1 | 0.0019996 | 0.00050115 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_112-1_0_7_load_3 | 2 | 0.0019048 | 0.0004774 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_112-1_0_7_load_6 | 3 | 0.00048847 | 0.00012242 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_112-1_0_7_load_21 | 5 | 0.00055573 | 0.00013928 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_112-1_0_7_load_7 | 7 | 0.00058461 | 0.00014652 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_112-1_0_7_load_31 | 8 | 0.00088985 | 0.00022302 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_112-1_0_7_load_19 | 9 | 0.00025838 | 6.4756e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_112-1_0_7_load_16 | 10 | 0.0010625 | 0.00026628 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_112-1_0_7_load_30 | 11 | 0.0011105 | 0.00027833 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_112-1_0_7_load_29 | 12 | 0.0017935 | 0.0004495 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_112-1_0_7_load_8 | 13 | 0.00027451 | 6.8799e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_112-1_0_7_load_9 | 14 | 0.00074638 | 0.00018706 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_112-1_0_7_load_10 | 18 | 0.00023813 | 5.9681e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_112-1_0_7_load_11 | 19 | 0.00068361 | 0.00017133 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_112-1_0_7_load_12 | 20 | 0.0002385 | 5.9775e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_112-1_0_7_load_14 | 22 | 0.0002381 | 5.9674e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_112-1_0_7_load_15 | 23 | 0.00045294 | 0.00011352 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_112-1_0_7_load_17 | 24 | 0.00043257 | 0.00010841 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_112-1_0_7_load_22 | 25 | 0.00075687 | 0.00018969 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_112-1_0_7_load_25 | 26 | 0.00056344 | 0.00014121 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_112-1_0_7_load_23 | 27 | 0.00056379 | 0.0001413 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_112-1_0_7_load_20 | 28 | 0.0022049 | 0.0005526 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_112-1_0_7_load_24 | 31 | 0.0005142 | 0.00012887 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_112-1_0_7_load_33 | 32 | 0.0012821 | 0.00032133 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_112-1_0_7_load_225 | 33 | 0.0010845 | 0.0002718 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_112-1_0_7_load_224 | 34 | 0.00096499 | 0.00024185 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_112-1_0_7_load_50 | 35 | 0.001133 | 0.00028396 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_112-1_0_7_load_215 | 36 | 0.0021348 | 0.00053504 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_112-1_0_7_load_48 | 37 | 0.0012257 | 0.00030718 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_112-1_0_7_load_75 | 41 | 0.0010169 | 0.00025487 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_112-1_0_7_load_161 | 42 | 0.0021017 | 0.00052674 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_112-1_0_7_load_160 | 43 | 0.0014998 | 0.00037588 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_112-1_0_7_load_242 | 45 | 0.00092362 | 0.00023148 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_112-1_0_7_load_198 | 48 | 0.0054174 | 0.0013577 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_112-1_0_7_load_196 | 50 | 0.0010223 | 0.0002562 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_112-1_0_7_load_94 | 53 | 0.0063368 | 0.0015882 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_112-1_0_7_load_92 | 54 | 0.0067758 | 0.0016982 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_112-1_0_7_load_236 | 56 | 0.037425 | 0.0093795 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_112-1_0_7_load_227 | 58 | 0.0045832 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_112-1_0_7_load_199 | 59 | 0.0020229 | 0.00050699 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_112-1_0_7_load_162 | 64 | 0.00098225 | 0.00024618 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_112-1_0_7_load_181 | 66 | 0.0015017 | 0.00037636 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_112-1_0_7_load_185 | 68 | 0.002853 | 0.00071503 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_112-1_0_7_load_275 | 69 | 0.0038037 | 0.0009533 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_112-1_0_7_load_115 | 70 | 0.0018658 | 0.00046761 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_112-1_0_7_load_114 | 71 | 0.0024126 | 0.00060466 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_112-1_0_7_load_112 | 72 | 0.0073542 | 0.0018431 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_112-1_0_7_load_113 | 73 | 0.0067818 | 0.0016997 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_112-1_0_7_load_91 | 74 | 0.0058766 | 0.0014728 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_112-1_0_7_load_210 | 75 | 0.0014914 | 0.00037377 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_112-1_0_7_load_200 | 76 | 0.0024899 | 0.00062402 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_112-1_0_7_load_201 | 77 | 0.002027 | 0.00050802 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_112-1_0_7_load_241 | 78 | 0.00095183 | 0.00023855 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_112-1_0_7_load_239 | 79 | 0.0009691 | 0.00024288 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_112-1_0_7_load_180 | 80 | 0.0028875 | 0.00072368 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_112-1_0_7_load_189 | 81 | 0.0011141 | 0.00027921 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_112-1_0_7_load_183 | 82 | 0.0010506 | 0.0002633 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_112-1_0_7_load_51 | 84 | 0.0023922 | 0.00059955 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_112-1_0_7_load_52 | 85 | 0.00086896 | 0.00021778 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_112-1_0_7_load_54 | 87 | 0.0015486 | 0.00038811 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_112-1_0_7_load_56 | 89 | 0.0061287 | 0.001536 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_112-1_0_7_load_57 | 90 | 0.0011799 | 0.0002957 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_112-1_0_7_load_59 | 92 | 0.0020565 | 0.00051541 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_112-1_0_7_load_60 | 93 | 0.0016815 | 0.00042142 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_112-1_0_7_load_154 | 94 | 0.002541 | 0.00063684 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_112-1_0_7_load_61 | 96 | 0.0015942 | 0.00039955 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_112-1_0_7_load_82 | 100 | 0.0011101 | 0.00027821 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_112-1_0_7_load_120 | 102 | 0.0020233 | 0.00050709 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_112-1_0_7_load_62 | 103 | 0.00054748 | 0.00013721 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_112-1_0_7_load_85 | 105 | 0.00093358 | 0.00023398 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_112-1_0_7_load_64 | 106 | 0.001642 | 0.00041153 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_112-1_0_7_load_65 | 107 | 0.0054885 | 0.0013756 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_112-1_0_7_load_67 | 109 | 0.0046758 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_112-1_0_7_load_68 | 110 | 0.0011202 | 0.00028075 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_112-1_0_7_load_74 | 113 | 0.0018849 | 0.0004724 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_112-1_0_7_load_70 | 114 | 0.0090624 | 0.0022712 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_112-1_0_7_load_71 | 115 | 0.0062831 | 0.0015747 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_112-1_0_7_load_76 | 117 | 0.0016986 | 0.00042571 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_112-1_0_7_load_77 | 118 | 0.0079847 | 0.0020012 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_112-1_0_7_load_78 | 119 | 0.0018849 | 0.0004724 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_112-1_0_7_load_79 | 121 | 0.0055943 | 0.0014021 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_112-1_0_7_load_228 | 122 | 0.0018857 | 0.0004726 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_112-1_0_7_load_173 | 124 | 0.0043578 | 0.0010922 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_112-1_0_7_load_80 | 125 | 0.007431 | 0.0018624 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_112-1_0_7_load_229 | 126 | 0.0018863 | 0.00047276 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_112-1_0_7_load_81 | 127 | 0.014435 | 0.0036178 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_112-1_0_7_load_276 | 128 | 0.0014922 | 0.00037399 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_112-1_0_7_load_87 | 129 | 0.0014648 | 0.0003671 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_112-1_0_7_load_88 | 130 | 0.0024837 | 0.00062247 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_112-1_0_7_load_89 | 131 | 0.0020912 | 0.0005241 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_112-1_0_7_load_90 | 132 | 0.0015724 | 0.00039409 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_112-1_0_7_load_226 | 133 | 0.0012866 | 0.00032245 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_112-1_0_7_load_171 | 134 | 0.0043392 | 0.0010875 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_112-1_0_7_load_96 | 135 | 0.0018663 | 0.00046774 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_112-1_0_7_load_98 | 137 | 0.0016595 | 0.0004159 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_112-1_0_7_load_99 | 138 | 0.0015627 | 0.00039166 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_112-1_0_7_load_100 | 139 | 0.0015632 | 0.00039178 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_112-1_0_7_load_101 | 140 | 0.0016736 | 0.00041944 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_112-1_0_7_load_109 | 142 | 0.0016736 | 0.00041944 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_112-1_0_7_load_243 | 143 | 0.00166 | 0.00041604 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_112-1_0_7_load_102 | 144 | 0.0028788 | 0.00072149 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_112-1_0_7_load_103 | 145 | 0.0025904 | 0.00064921 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_112-1_0_7_load_105 | 147 | 0.0026189 | 0.00065636 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_112-1_0_7_load_108 | 150 | 0.0014205 | 0.00035602 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_112-1_0_7_load_111 | 152 | 0.0017487 | 0.00043826 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_112-1_0_7_load_118 | 154 | 0.0046146 | 0.0011565 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_112-1_0_7_load_119 | 155 | 0.0025353 | 0.0006354 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_112-1_0_7_load_249 | 156 | 0.0025353 | 0.00063541 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_112-1_0_7_load_246 | 157 | 0.0016296 | 0.00040842 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_112-1_0_7_load_165 | 159 | 0.0023163 | 0.00058052 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_112-1_0_7_load_274 | 160 | 0.0038031 | 0.00095315 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_112-1_0_7_load_166 | 162 | 0.002561 | 0.00064184 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_112-1_0_7_load_121 | 163 | 0.0020404 | 0.00051138 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_112-1_0_7_load_123 | 164 | 0.0020193 | 0.00050609 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_112-1_0_7_load_125 | 165 | 0.0019004 | 0.00047628 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_112-1_0_7_load_127 | 167 | 0.0024071 | 0.00060327 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_112-1_0_7_load_132 | 168 | 0.0020099 | 0.00050374 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_112-1_0_7_load_129 | 170 | 0.0021066 | 0.00052797 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_112-1_0_7_load_169 | 171 | 0.0024776 | 0.00062096 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_112-1_0_7_load_136 | 172 | 0.0021321 | 0.00053436 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_112-1_0_7_load_133 | 173 | 0.0020621 | 0.00051681 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_112-1_0_7_load_134 | 174 | 0.0023264 | 0.00058304 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_112-1_0_7_load_128 | 175 | 0.0020649 | 0.00051752 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_112-1_0_7_load_159 | 176 | 0.0023144 | 0.00058003 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_112-1_0_7_load_130 | 177 | 0.0020594 | 0.00051612 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_112-1_0_7_load_139 | 178 | 0.0020728 | 0.0005195 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_112-1_0_7_load_152 | 179 | 0.0020253 | 0.00050759 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_112-1_0_7_load_135 | 180 | 0.0020645 | 0.00051741 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_112-1_0_7_load_137 | 181 | 0.0021743 | 0.00054493 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_112-1_0_7_load_151 | 182 | 0.0021098 | 0.00052877 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_112-1_0_7_load_138 | 183 | 0.0021437 | 0.00053727 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_112-1_0_7_load_140 | 184 | 0.0052488 | 0.0013155 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_112-1_0_7_load_141 | 185 | 0.0050167 | 0.0012573 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_112-1_0_7_load_145 | 187 | 0.0022561 | 0.00056544 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_112-1_0_7_load_146 | 188 | 0.0045574 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_112-1_0_7_load_148 | 189 | 0.0017904 | 0.00044871 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_112-1_0_7_load_149 | 191 | 0.0017904 | 0.00044871 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_112-1_0_7_load_253 | 192 | 0.008665 | 0.0021716 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_112-1_0_7_load_150 | 194 | 0.0017305 | 0.00043371 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_112-1_0_7_load_168 | 195 | 0.0017568 | 0.0004403 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_112-1_0_7_load_167 | 196 | 0.005201 | 0.0013035 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_112-1_0_7_load_153 | 197 | 0.0041253 | 0.0010339 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_112-1_0_7_load_155 | 198 | 0.0022447 | 0.00056257 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_112-1_0_7_load_156 | 199 | 0.0023322 | 0.0005845 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_112-1_0_7_load_157 | 200 | 0.0025948 | 0.00065031 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_112-1_0_7_load_158 | 201 | 0.0023116 | 0.00057934 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_112-1_0_7_load_172 | 202 | 0.0046751 | 0.0011717 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_112-1_0_7_load_170 | 203 | 0.0043077 | 0.0010796 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_112-1_0_7_load_211 | 204 | 0.010006 | 0.0025078 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_112-1_0_7_load_235 | 205 | 0.0018784 | 0.00047076 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_112-1_0_7_load_234 | 206 | 0.0018793 | 0.00047098 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_112-1_0_7_load_237 | 207 | 0.0009582 | 0.00024015 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_112-1_0_7_load_176 | 208 | 0.0019708 | 0.00049393 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_112-1_0_7_load_177 | 209 | 0.0010249 | 0.00025687 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_112-1_0_7_load_178 | 210 | 0.00087788 | 0.00022002 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_112-1_0_7_load_179 | 211 | 0.00092402 | 0.00023158 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_112-1_0_7_load_238 | 212 | 0.0018205 | 0.00045627 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_112-1_0_7_load_182 | 213 | 0.0013137 | 0.00032924 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_112-1_0_7_load_267 | 214 | 0.0011141 | 0.00027921 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_112-1_0_7_load_186 | 215 | 0.0011096 | 0.00027808 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_112-1_0_7_load_187 | 216 | 0.0011096 | 0.00027808 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_112-1_0_7_load_188 | 217 | 0.0011096 | 0.00027808 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_112-1_0_7_load_261 | 218 | 0.0018879 | 0.00047315 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_112-1_0_7_load_268 | 220 | 0.0011134 | 0.00027904 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_112-1_0_7_load_190 | 221 | 0.0021013 | 0.00052665 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_112-1_0_7_load_191 | 222 | 0.0034151 | 0.0008559 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_112-1_0_7_load_192 | 223 | 0.0022774 | 0.00057076 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_112-1_0_7_load_193 | 224 | 0.0015387 | 0.00038563 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_112-1_0_7_load_194 | 225 | 0.0015319 | 0.00038394 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_112-1_0_7_load_195 | 226 | 0.0015286 | 0.00038311 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_112-1_0_7_load_202 | 227 | 0.0040876 | 0.0010245 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_112-1_0_7_load_203 | 228 | 0.0015218 | 0.00038139 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_112-1_0_7_load_204 | 229 | 0.0024843 | 0.00062262 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_112-1_0_7_load_207 | 230 | 0.0023816 | 0.00059689 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_112-1_0_7_load_205 | 231 | 0.0015361 | 0.00038499 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_112-1_0_7_load_206 | 232 | 0.0029493 | 0.00073916 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_112-1_0_7_load_208 | 233 | 0.0028178 | 0.00070621 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_112-1_0_7_load_219 | 236 | 0.0012848 | 0.00032201 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_112-1_0_7_load_216 | 237 | 0.0012336 | 0.00030916 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_112-1_0_7_load_223 | 238 | 0.0011356 | 0.0002846 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_112-1_0_7_load_221 | 239 | 0.00080832 | 0.00020258 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_112-1_0_7_load_217 | 240 | 0.0011894 | 0.0002981 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_112-1_0_7_load_218 | 241 | 0.00056579 | 0.0001418 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_112-1_0_7_load_220 | 242 | 0.0011264 | 0.00028231 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_112-1_0_7_load_222 | 243 | 0.0015406 | 0.00038611 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_112-1_0_7_load_230 | 244 | 0.0018851 | 0.00047246 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_112-1_0_7_load_231 | 245 | 0.0018849 | 0.0004724 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_112-1_0_7_load_232 | 246 | 0.0018785 | 0.0004708 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_112-1_0_7_load_233 | 247 | 0.0018773 | 0.00047051 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_112-1_0_7_load_245 | 248 | 0.0016295 | 0.0004084 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_112-1_0_7_load_248 | 249 | 0.0023443 | 0.00058754 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_112-1_0_7_load_250 | 250 | 0.0023443 | 0.00058754 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_112-1_0_7_load_251 | 251 | 0.0023138 | 0.00057989 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_112-1_0_7_load_277 | 252 | 0.0078027 | 0.0019555 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_112-1_0_7_load_278 | 253 | 0.0026751 | 0.00067045 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_112-1_0_7_load_255 | 254 | 0.0013813 | 0.00034618 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_112-1_0_7_load_256 | 255 | 0.0011096 | 0.00027808 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_112-1_0_7_load_259 | 257 | 0.0010634 | 0.00026651 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_112-1_0_7_load_260 | 258 | 0.0012569 | 0.00031502 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_112-1_0_7_load_262 | 259 | 0.0013813 | 0.00034618 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_112-1_0_7_load_263 | 260 | 0.0013599 | 0.00034081 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_112-1_0_7_load_264 | 261 | 0.0012566 | 0.00031494 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_112-1_0_7_load_265 | 262 | 0.0013813 | 0.00034619 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_112-1_0_7_load_271 | 263 | 0.0013108 | 0.00032851 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_112-1_0_7_load_272 | 264 | 0.0012574 | 0.00031514 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_112-1_0_7_load_266 | 265 | 0.0015362 | 0.000385 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_112-1_0_7_load_270 | 266 | 0.0010814 | 0.00027103 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_112-1_0_7_load_273 | 267 | 0.0012569 | 0.00031502 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_112-1_0_7_load_269 | 268 | 0.0011141 | 0.00027921 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 149 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_112-1_0_7_line_0 |  | 0 | 1 | 0.031379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_112-1_0_7_line_1 |  | 1 | 2 | 0.031063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_112-1_0_7_line_2 |  | 2 | 3 | 0.018124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_112-1_0_7_line_3 |  | 3 | 7 | 0.001826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_112-1_0_7_line_4 |  | 4 | 5 | 0.033499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_112-1_0_7_line_5 |  | 4 | 6 | 0.047268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_112-1_0_7_line_6 |  | 5 | 8 | 0.036661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_112-1_0_7_line_7 |  | 6 | 9 | 0.068295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_112-1_0_7_line_8 |  | 6 | 10 | 0.019691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_112-1_0_7_line_9 |  | 7 | 13 | 0.0086983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_112-1_0_7_line_10 |  | 8 | 30 | 0.023014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_112-1_0_7_line_11 |  | 9 | 28 | 0.011886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_112-1_0_7_line_12 |  | 10 | 21 | 0.014206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_112-1_0_7_line_13 |  | 11 | 12 | 0.022746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_112-1_0_7_line_14 |  | 12 | 29 | 0.021915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_112-1_0_7_line_15 |  | 13 | 14 | 0.0046819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_112-1_0_7_line_16 |  | 14 | 15 | 0.17963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_112-1_0_7_line_17 |  | 15 | 16 | 0.007018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_112-1_0_7_line_18 |  | 15 | 17 | 0.065052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_112-1_0_7_line_19 |  | 16 | 37 | 0.01391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_112-1_0_7_line_20 |  | 17 | 42 | 0.01676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_112-1_0_7_line_21 |  | 17 | 43 | 0.017122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_112-1_0_7_line_22 |  | 18 | 19 | 0.0076231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_112-1_0_7_line_23 |  | 18 | 20 | 0.0047977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_112-1_0_7_line_24 |  | 19 | 21 | 0.012201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_112-1_0_7_line_25 |  | 20 | 22 | 0.0047975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_112-1_0_7_line_26 |  | 21 | 23 | 0.062675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_112-1_0_7_line_27 |  | 22 | 24 | 0.0078808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_112-1_0_7_line_28 |  | 23 | 25 | 0.0076133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_112-1_0_7_line_29 |  | 24 | 26 | 0.014133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_112-1_0_7_line_30 |  | 26 | 27 | 0.011883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_112-1_0_7_line_31 |  | 27 | 31 | 0.021557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_112-1_0_7_line_32 |  | 28 | 29 | 0.03102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_112-1_0_7_line_33 |  | 30 | 32 | 0.11306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_112-1_0_7_line_34 |  | 32 | 35 | 0.023806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_112-1_0_7_line_35 |  | 33 | 34 | 0.019052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_112-1_0_7_line_36 |  | 34 | 243 | 0.005325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_112-1_0_7_line_37 |  | 35 | 36 | 0.034853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_112-1_0_7_line_38 |  | 36 | 83 | 0.00078362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_112-1_0_7_line_39 |  | 37 | 66 | 0.0060554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_112-1_0_7_line_40 |  | 38 | 39 | 0.040492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_112-1_0_7_line_41 |  | 38 | 40 | 0.037734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_112-1_0_7_line_42 |  | 38 | 41 | 0.034685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_112-1_0_7_line_43 |  | 39 | 69 | 0.023112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_112-1_0_7_line_44 |  | 39 | 63 | 0.040904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_112-1_0_7_line_45 |  | 40 | 44 | 0.017551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_112-1_0_7_line_46 |  | 40 | 45 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_112-1_0_7_line_47 |  | 43 | 71 | 0.020872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_112-1_0_7_line_48 |  | 44 | 59 | 0.025499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_112-1_0_7_line_49 |  | 44 | 60 | 0.030319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_112-1_0_7_line_50 |  | 45 | 57 | 0.046103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_112-1_0_7_line_51 |  | 46 | 47 | 0.024402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_112-1_0_7_line_52 |  | 46 | 48 | 0.099314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_112-1_0_7_line_53 |  | 47 | 67 | 0.011578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_112-1_0_7_line_54 |  | 47 | 68 | 0.015138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_112-1_0_7_line_55 |  | 48 | 49 | 0.085772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_112-1_0_7_line_56 |  | 49 | 50 | 0.023302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_112-1_0_7_line_57 |  | 50 | 60 | 0.0055096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_112-1_0_7_line_58 |  | 51 | 52 | 0.023447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_112-1_0_7_line_59 |  | 51 | 53 | 0.023137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_112-1_0_7_line_60 |  | 51 | 54 | 0.018244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_112-1_0_7_line_61 |  | 52 | 72 | 0.006884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_112-1_0_7_line_62 |  | 52 | 73 | 0.023557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_112-1_0_7_line_63 |  | 53 | 71 | 0.038268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_112-1_0_7_line_64 |  | 54 | 74 | 0.030942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_112-1_0_7_line_65 |  | 55 | 56 | 0.015078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_112-1_0_7_line_66 |  | 55 | 57 | 0.074123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_112-1_0_7_line_67 |  | 55 | 58 | 0.019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_112-1_0_7_line_68 |  | 57 | 65 | 0.03608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_112-1_0_7_line_69 |  | 59 | 75 | 0.046198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_112-1_0_7_line_70 |  | 60 | 61 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_112-1_0_7_line_71 |  | 61 | 76 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_112-1_0_7_line_72 |  | 61 | 77 | 0.021786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_112-1_0_7_line_73 |  | 62 | 63 | 0.002593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_112-1_0_7_line_74 |  | 62 | 64 | 0.017062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_112-1_0_7_line_75 |  | 63 | 70 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_112-1_0_7_line_76 |  | 65 | 78 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_112-1_0_7_line_77 |  | 65 | 79 | 0.016561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_112-1_0_7_line_78 |  | 66 | 80 | 0.0048028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_112-1_0_7_line_79 |  | 67 | 81 | 0.0027861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_112-1_0_7_line_80 |  | 67 | 82 | 0.010436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_112-1_0_7_line_81 |  | 69 | 160 | 0.027579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_112-1_0_7_line_82 |  | 70 | 152 | 0.013817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_112-1_0_7_line_83 |  | 74 | 132 | 0.0050007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_112-1_0_7_line_84 |  | 75 | 204 | 0.043457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_112-1_0_7_line_85 |  | 76 | 229 | 0.0035467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_112-1_0_7_line_86 |  | 77 | 230 | 0.0029874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_112-1_0_7_line_87 |  | 78 | 207 | 0.0055325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_112-1_0_7_line_88 |  | 79 | 212 | 0.0076145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_112-1_0_7_line_89 |  | 80 | 213 | 0.0011652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_112-1_0_7_line_90 |  | 81 | 214 | 0.0061758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_112-1_0_7_line_91 |  | 82 | 213 | 0.0061001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_112-1_0_7_line_92 |  | 83 | 235 | 0.025265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_112-1_0_7_line_93 |  | 83 | 234 | 0.040915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_112-1_0_7_line_94 |  | 84 | 85 | 0.024455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_112-1_0_7_line_95 |  | 84 | 86 | 0.045992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_112-1_0_7_line_96 |  | 85 | 87 | 0.016355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_112-1_0_7_line_97 |  | 86 | 88 | 0.095605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_112-1_0_7_line_98 |  | 86 | 89 | 0.033602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_112-1_0_7_line_99 |  | 87 | 90 | 0.0059632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_112-1_0_7_line_100 |  | 88 | 91 | 0.047994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_112-1_0_7_line_101 |  | 88 | 92 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_112-1_0_7_line_102 |  | 90 | 93 | 0.010446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_112-1_0_7_line_103 |  | 91 | 94 | 0.031084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_112-1_0_7_line_104 |  | 92 | 95 | 0.012588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_112-1_0_7_line_105 |  | 93 | 96 | 0.0094275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_112-1_0_7_line_106 |  | 94 | 97 | 0.0058426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_112-1_0_7_line_107 |  | 95 | 101 | 0.00172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_112-1_0_7_line_108 |  | 95 | 102 | 0.012371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_112-1_0_7_line_109 |  | 96 | 103 | 0.010529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_112-1_0_7_line_110 |  | 97 | 190 | 0.03677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_112-1_0_7_line_111 |  | 97 | 187 | 0.0063097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_112-1_0_7_line_112 |  | 98 | 99 | 0.059613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_112-1_0_7_line_113 |  | 98 | 100 | 0.11288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_112-1_0_7_line_114 |  | 99 | 128 | 0.11281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_112-1_0_7_line_115 |  | 100 | 104 | 0.053679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_112-1_0_7_line_116 |  | 101 | 166 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_112-1_0_7_line_117 |  | 101 | 167 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_112-1_0_7_line_118 |  | 102 | 163 | 0.011144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_112-1_0_7_line_119 |  | 103 | 104 | 0.013737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_112-1_0_7_line_120 |  | 104 | 105 | 0.0096626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_112-1_0_7_line_121 |  | 106 | 107 | 0.0013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_112-1_0_7_line_122 |  | 106 | 108 | 0.046822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_112-1_0_7_line_123 |  | 107 | 109 | 0.0023316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_112-1_0_7_line_124 |  | 108 | 110 | 0.051314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_112-1_0_7_line_125 |  | 110 | 111 | 0.069647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_112-1_0_7_line_126 |  | 111 | 112 | 0.16861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_112-1_0_7_line_127 |  | 112 | 113 | 0.016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_112-1_0_7_line_128 |  | 112 | 114 | 0.010618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_112-1_0_7_line_129 |  | 113 | 119 | 0.0071782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_112-1_0_7_line_130 |  | 114 | 115 | 0.022672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_112-1_0_7_line_131 |  | 115 | 116 | 0.025591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_112-1_0_7_line_132 |  | 116 | 117 | 0.023875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_112-1_0_7_line_133 |  | 116 | 118 | 0.038216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_112-1_0_7_line_134 |  | 117 | 120 | 0.017639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_112-1_0_7_line_135 |  | 118 | 121 | 0.00079274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_112-1_0_7_line_136 |  | 119 | 122 | 0.013495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_112-1_0_7_line_137 |  | 120 | 123 | 0.007924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_112-1_0_7_line_138 |  | 120 | 124 | 0.013314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_112-1_0_7_line_139 |  | 121 | 125 | 0.039574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_112-1_0_7_line_140 |  | 122 | 126 | 0.0071775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_112-1_0_7_line_141 |  | 123 | 133 | 0.0068531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_112-1_0_7_line_142 |  | 124 | 134 | 0.022674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_112-1_0_7_line_143 |  | 125 | 127 | 0.02026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_112-1_0_7_line_144 |  | 126 | 244 | 0.014097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_112-1_0_7_line_145 |  | 129 | 130 | 0.022209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_112-1_0_7_line_146 |  | 130 | 131 | 0.016041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_112-1_0_7_line_147 |  | 131 | 132 | 0.021884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_112-1_0_7_line_148 |  | 133 | 207 | 0.0029521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_112-1_0_7_line_149 |  | 134 | 203 | 0.028112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_112-1_0_7_line_150 |  | 135 | 136 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_112-1_0_7_line_151 |  | 135 | 137 | 0.016276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_112-1_0_7_line_152 |  | 136 | 138 | 0.0047594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_112-1_0_7_line_153 |  | 136 | 139 | 0.0059936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_112-1_0_7_line_154 |  | 139 | 140 | 0.018688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_112-1_0_7_line_155 |  | 140 | 141 | 0.0055068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_112-1_0_7_line_156 |  | 141 | 142 | 0.0054637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_112-1_0_7_line_157 |  | 141 | 143 | 0.012599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_112-1_0_7_line_158 |  | 142 | 148 | 0.0098904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_112-1_0_7_line_159 |  | 143 | 248 | 0.014527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_112-1_0_7_line_160 |  | 144 | 145 | 0.017669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_112-1_0_7_line_161 |  | 144 | 146 | 0.0095128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_112-1_0_7_line_162 |  | 145 | 147 | 0.0037844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_112-1_0_7_line_163 |  | 146 | 148 | 0.023766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_112-1_0_7_line_164 |  | 146 | 149 | 0.024064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_112-1_0_7_line_165 |  | 148 | 150 | 0.011534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_112-1_0_7_line_166 |  | 149 | 151 | 0.007537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
167 | LV_112-1_0_7_line_167 |  | 149 | 152 | 0.0050282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_112-1_0_7_line_168 |  | 150 | 153 | 0.0032385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_112-1_0_7_line_169 |  | 151 | 154 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_112-1_0_7_line_170 |  | 151 | 155 | 0.030112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_112-1_0_7_line_171 |  | 153 | 156 | 0.0072184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_112-1_0_7_line_172 |  | 153 | 157 | 0.013732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_112-1_0_7_line_173 |  | 154 | 158 | 0.018036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_112-1_0_7_line_174 |  | 155 | 159 | 0.007539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_112-1_0_7_line_175 |  | 156 | 250 | 0.013721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_112-1_0_7_line_176 |  | 157 | 249 | 0.013189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_112-1_0_7_line_177 |  | 158 | 161 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_112-1_0_7_line_178 |  | 159 | 162 | 0.022197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_112-1_0_7_line_179 |  | 161 | 185 | 0.00196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_112-1_0_7_line_180 |  | 162 | 196 | 0.016018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_112-1_0_7_line_181 |  | 163 | 164 | 0.00041756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_112-1_0_7_line_182 |  | 164 | 165 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_112-1_0_7_line_183 |  | 165 | 168 | 0.00019823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_112-1_0_7_line_184 |  | 166 | 169 | 0.016581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_112-1_0_7_line_185 |  | 166 | 170 | 0.0085813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_112-1_0_7_line_186 |  | 167 | 171 | 0.011407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_112-1_0_7_line_187 |  | 168 | 172 | 0.010929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_112-1_0_7_line_188 |  | 169 | 173 | 0.015406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_112-1_0_7_line_189 |  | 169 | 174 | 0.0083199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_112-1_0_7_line_190 |  | 170 | 175 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_112-1_0_7_line_191 |  | 171 | 176 | 0.0098046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_112-1_0_7_line_192 |  | 172 | 180 | 0.00031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_112-1_0_7_line_193 |  | 173 | 178 | 0.0080006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_112-1_0_7_line_194 |  | 174 | 179 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_112-1_0_7_line_195 |  | 175 | 177 | 0.007702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_112-1_0_7_line_196 |  | 176 | 201 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_112-1_0_7_line_197 |  | 178 | 181 | 0.011331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_112-1_0_7_line_198 |  | 179 | 182 | 0.015407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_112-1_0_7_line_199 |  | 181 | 183 | 0.016248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_112-1_0_7_line_200 |  | 182 | 197 | 0.0059173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_112-1_0_7_line_201 |  | 183 | 184 | 0.0073911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_112-1_0_7_line_202 |  | 185 | 186 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_112-1_0_7_line_203 |  | 186 | 187 | 0.0097804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_112-1_0_7_line_204 |  | 188 | 189 | 0.0011862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_112-1_0_7_line_205 |  | 189 | 191 | 0.00037777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_112-1_0_7_line_206 |  | 190 | 192 | 0.021147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_112-1_0_7_line_207 |  | 190 | 193 | 0.012533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_112-1_0_7_line_208 |  | 191 | 194 | 0.010034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_112-1_0_7_line_209 |  | 193 | 252 | 0.020004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_112-1_0_7_line_210 |  | 193 | 253 | 0.004075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_112-1_0_7_line_211 |  | 194 | 195 | 0.0097632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_112-1_0_7_line_212 |  | 195 | 196 | 0.0028129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_112-1_0_7_line_213 |  | 198 | 199 | 0.0074082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_112-1_0_7_line_214 |  | 198 | 200 | 0.0058014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_112-1_0_7_line_215 |  | 199 | 201 | 0.0080927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_112-1_0_7_line_216 |  | 202 | 203 | 0.021488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_112-1_0_7_line_217 |  | 205 | 206 | 0.011026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_112-1_0_7_line_218 |  | 206 | 247 | 0.013817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_112-1_0_7_line_219 |  | 208 | 209 | 0.0036395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_112-1_0_7_line_220 |  | 209 | 210 | 0.0055727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_112-1_0_7_line_221 |  | 210 | 211 | 0.0051924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_112-1_0_7_line_222 |  | 211 | 212 | 0.0051453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_112-1_0_7_line_223 |  | 214 | 220 | 0.0061766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_112-1_0_7_line_224 |  | 215 | 216 | 0.0061528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_112-1_0_7_line_225 |  | 216 | 217 | 0.0061525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_112-1_0_7_line_226 |  | 217 | 218 | 0.0089521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_112-1_0_7_line_227 |  | 218 | 219 | 0.0045603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_112-1_0_7_line_228 |  | 219 | 259 | 0.011364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_112-1_0_7_line_229 |  | 219 | 255 | 0.0081085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_112-1_0_7_line_230 |  | 220 | 268 | 0.0061766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_112-1_0_7_line_231 |  | 221 | 222 | 0.018482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_112-1_0_7_line_232 |  | 221 | 223 | 0.0069448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_112-1_0_7_line_233 |  | 222 | 224 | 0.012849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_112-1_0_7_line_234 |  | 224 | 225 | 0.0062197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_112-1_0_7_line_235 |  | 225 | 226 | 0.0062178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_112-1_0_7_line_236 |  | 226 | 227 | 0.00069446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_112-1_0_7_line_237 |  | 227 | 228 | 0.0055248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_112-1_0_7_line_238 |  | 228 | 229 | 0.017399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_112-1_0_7_line_239 |  | 230 | 231 | 0.0099238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_112-1_0_7_line_240 |  | 231 | 232 | 0.018829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_112-1_0_7_line_241 |  | 232 | 233 | 0.015363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_112-1_0_7_line_242 |  | 233 | 234 | 0.011082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_112-1_0_7_line_243 |  | 235 | 236 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_112-1_0_7_line_244 |  | 235 | 237 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_112-1_0_7_line_245 |  | 236 | 239 | 0.021353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_112-1_0_7_line_246 |  | 237 | 240 | 0.034906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_112-1_0_7_line_247 |  | 238 | 239 | 0.040687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_112-1_0_7_line_248 |  | 240 | 241 | 0.013976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_112-1_0_7_line_249 |  | 241 | 242 | 0.0079864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_112-1_0_7_line_250 |  | 242 | 243 | 0.01515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_112-1_0_7_line_251 |  | 244 | 245 | 0.0071782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_112-1_0_7_line_252 |  | 245 | 246 | 0.013293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_112-1_0_7_line_253 |  | 246 | 247 | 0.0071763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_112-1_0_7_line_254 |  | 250 | 251 | 0.0032373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_112-1_0_7_line_255 |  | 254 | 255 | 0.0033311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_112-1_0_7_line_256 |  | 254 | 256 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_112-1_0_7_line_257 |  | 256 | 257 | 0.006285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_112-1_0_7_line_258 |  | 256 | 258 | 0.0047423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_112-1_0_7_line_259 |  | 257 | 260 | 0.0080534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_112-1_0_7_line_260 |  | 258 | 261 | 0.0061245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_112-1_0_7_line_261 |  | 259 | 262 | 0.0063018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_112-1_0_7_line_262 |  | 260 | 263 | 0.0060504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_112-1_0_7_line_263 |  | 261 | 264 | 0.0061282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_112-1_0_7_line_264 |  | 262 | 265 | 0.0019213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_112-1_0_7_line_265 |  | 263 | 266 | 0.0061472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_112-1_0_7_line_266 |  | 264 | 267 | 0.0046261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_112-1_0_7_line_267 |  | 266 | 268 | 0.01253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_112-1_0_7_trafo_107 | 0.63 MVA 20/0.4 kV | 269 | 149 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2702584.1512 | 1234290.367 | 2702580.1488 | 1234296.5099 | 2702565.6283 | 1234315.6778
1 | 2702548.5967 | 1234341.5704 | 2702556.0611 | 1234328.307 | 2702565.6283 | 1234315.6778
2 | 2702539.708 | 1234357.3647 | 2702548.5967 | 1234341.5704
3 | 2702539.708 | 1234357.3647 | 2702538.8124 | 1234358.956
4 | 2702780.7271 | 1234297.1425 | 2702779.044 | 1234306.4649 | 2702779.5313 | 1234325.5543 | 2702781.2538 | 1234330.1734
5 | 2702780.7271 | 1234297.1425 | 2702789.4322 | 1234279.7466 | 2702806.7166 | 1234257.9069
6 | 2702794.0635 | 1234364.5234 | 2702781.2538 | 1234330.1734
7 | 2702806.7166 | 1234257.9069 | 2702840.1674 | 1234207.1141 | 2702840.9638 | 1234199.6798
8 | 2702806.7166 | 1234257.9069 | 2702825.5077 | 1234263.7909
9 | 2702534.5464 | 1234366.5364 | 2702538.8124 | 1234358.956
10 | 2702800.9476 | 1234386.4818 | 2702794.4142 | 1234365.464 | 2702794.0635 | 1234364.5234
11 | 2702842.2299 | 1234187.8614 | 2702840.9638 | 1234199.6798
12 | 2702839.3187 | 1234267.0557 | 2702829.4583 | 1234265.028 | 2702825.5077 | 1234263.7909
13 | 2702801.5393 | 1234128.2194 | 2702818.4366 | 1234143.446
14 | 2702834.7166 | 1234158.1162 | 2702818.4366 | 1234143.446
15 | 2702534.5464 | 1234366.5364 | 2702532.504 | 1234370.1654 | 2702532.2932 | 1234370.6381
16 | 2702470.9534 | 1234539.42 | 2702477.0731 | 1234522.1681 | 2702481.275 | 1234510.3205 | 2702516.0363 | 1234412.313 | 2702523.3502 | 1234391.6792 | 2702525.0614 | 1234386.8495 | 2702532.2932 | 1234370.6381
17 | 2702470.9534 | 1234539.42 | 2702476.4731 | 1234543.774
18 | 2702453.9979 | 1234576.9782 | 2702453.7602 | 1234574.083 | 2702453.6606 | 1234572.8359 | 2702446.2806 | 1234573.1867 | 2702445.6915 | 1234565.2039 | 2702466.0963 | 1234563.7991 | 2702466.3515 | 1234557.343 | 2702467.6349 | 1234548.7809 | 2702470.9534 | 1234539.42
19 | 2702476.4731 | 1234543.774 | 2702490.1614 | 1234541.3007
20 | 2702453.9979 | 1234576.9782 | 2702460.3891 | 1234576.4546 | 2702467.0427 | 1234584.4198
21 | 2702453.9979 | 1234576.9782 | 2702444.9267 | 1234587.5964 | 2702442.658 | 1234589.7906
22 | 2702851.2687 | 1234269.5199 | 2702858.8908 | 1234269.3924
23 | 2702863.6879 | 1234269.3122 | 2702858.8908 | 1234269.3924
24 | 2702839.3187 | 1234267.0557 | 2702851.2687 | 1234269.5199
25 | 2702863.6879 | 1234269.3122 | 2702868.4847 | 1234269.2321
26 | 2702839.3187 | 1234267.0557 | 2702838.2923 | 1234287.8536 | 2702845.076 | 1234299.224 | 2702872.3627 | 1234307.8292
27 | 2702876.3644 | 1234269.1003 | 2702868.4847 | 1234269.2321
28 | 2702879.6235 | 1234310.119 | 2702872.3627 | 1234307.8292
29 | 2702876.3644 | 1234269.1003 | 2702883.2813 | 1234268.9847 | 2702890.1304 | 1234266.7156
30 | 2702890.1304 | 1234266.7156 | 2702901.4102 | 1234262.9785
31 | 2702921.8736 | 1234256.1988 | 2702921.8736 | 1234256.1988 | 2702901.4102 | 1234262.9785
32 | 2702834.7166 | 1234158.1162 | 2702837.399 | 1234165.4237 | 2702842.7142 | 1234183.3403 | 2702842.2299 | 1234187.8614
33 | 2702800.9476 | 1234386.4818 | 2702801.4219 | 1234423.3733 | 2702793.9395 | 1234486.9251 | 2702792.9775 | 1234499.0573
34 | 2702791.4811 | 1234522.815 | 2702792.6417 | 1234503.2927 | 2702792.9775 | 1234499.0573
35 | 2702871.3923 | 1234516.3591 | 2702881.6855 | 1234516.2322 | 2702890.3871 | 1234517.2272
36 | 2702866.0677 | 1234516.4247 | 2702871.3923 | 1234516.3591
37 | 2702791.4811 | 1234522.815 | 2702790.9221 | 1234532.2181 | 2702791.4236 | 1234550.0402 | 2702792.2056 | 1234557.6042
38 | 2702792.2861 | 1234558.3837 | 2702792.2056 | 1234557.6042
39 | 2702490.1614 | 1234541.3007 | 2702496.1203 | 1234540.2239
40 | 2702694.7043 | 1234645.1731 | 2702687.0518 | 1234645.9637 | 2702677.8282 | 1234643.925 | 2702674.3308 | 1234642.5969 | 2702673.341 | 1234662.1834
41 | 2702694.7043 | 1234645.1731 | 2702695.492 | 1234636.836 | 2702702.0015 | 1234638.661 | 2702704.2564 | 1234634.3522 | 2702706.0521 | 1234632.5152 | 2702708.8254 | 1234631.0621 | 2702711.1146 | 1234630.9015 | 2702720.4624 | 1234633.6429
42 | 2702694.7043 | 1234645.1731 | 2702694.9987 | 1234659.2332 | 2702695.7966 | 1234667.3754 | 2702696.6156 | 1234675.618 | 2702697.3542 | 1234679.7092
43 | 2702673.341 | 1234662.1834 | 2702651.1393 | 1234668.6066
44 | 2702653.5715 | 1234639.5582 | 2702663.911 | 1234639.2366 | 2702674.3308 | 1234642.5969 | 2702673.341 | 1234662.1834
45 | 2702720.4624 | 1234633.6429 | 2702722.3447 | 1234628.1157 | 2702724.4584 | 1234621.9031 | 2702725.9744 | 1234616.9812
46 | 2702720.4624 | 1234633.6429 | 2702737.6739 | 1234639.2894
47 | 2702442.658 | 1234589.7906 | 2702441.8316 | 1234590.5898 | 2702434.9087 | 1234596.486 | 2702425.9276 | 1234602.1713
48 | 2702725.9744 | 1234616.9812 | 2702730.31 | 1234618.435 | 2702742.6813 | 1234620.1391 | 2702750.5096 | 1234623.2875
49 | 2702707.2041 | 1234599.1767 | 2702712.4015 | 1234601.1458 | 2702711.3554 | 1234604.7193 | 2702711.7702 | 1234609.6301 | 2702715.1442 | 1234612.4017 | 2702720.2539 | 1234615.0586 | 2702725.9744 | 1234616.9812
50 | 2702781.4434 | 1234652.0667 | 2702765.4623 | 1234645.9079 | 2702751.7308 | 1234641.4338 | 2702746.1177 | 1234642.0594 | 2702737.6739 | 1234639.2894
51 | 2702502.2287 | 1234556.9503 | 2702501.5643 | 1234549.3887 | 2702518.3004 | 1234547.7985
52 | 2702502.2287 | 1234556.9503 | 2702516.1183 | 1234558.4244 | 2702560.6351 | 1234570.2236 | 2702598.8716 | 1234579.2706
53 | 2702518.2656 | 1234536.2225 | 2702518.3004 | 1234547.7985
54 | 2702518.3004 | 1234547.7985 | 2702533.1705 | 1234550.6331
55 | 2702680.8002 | 1234604.2687 | 2702676.4392 | 1234602.9701 | 2702630.9526 | 1234586.8612 | 2702598.8716 | 1234579.2706
56 | 2702680.8002 | 1234604.2687 | 2702684.7733 | 1234604.7933 | 2702691.5986 | 1234602.8097 | 2702699.6879 | 1234599.5248 | 2702702.1153 | 1234597.0649
57 | 2702707.2041 | 1234599.1767 | 2702702.1153 | 1234597.0649
58 | 2702369.6553 | 1234622.47 | 2702361.6991 | 1234621.1209 | 2702346.2898 | 1234622.1674
59 | 2702369.6553 | 1234622.47 | 2702389.2073 | 1234621.773 | 2702392.6076 | 1234620.6758
60 | 2702369.6553 | 1234622.47 | 2702367.6255 | 1234633.4989 | 2702362.0755 | 1234637.8129
61 | 2702345.992 | 1234615.2904 | 2702346.2898 | 1234622.1674
62 | 2702328.9227 | 1234616.4529 | 2702329.6072 | 1234623.3031 | 2702346.2898 | 1234622.1674
63 | 2702425.9276 | 1234602.1713 | 2702410.3537 | 1234612.03 | 2702398.7921 | 1234618.6803 | 2702392.6076 | 1234620.6758
64 | 2702335.5842 | 1234653.7465 | 2702359.2845 | 1234639.9823 | 2702362.0755 | 1234637.8129
65 | 2702818.8424 | 1234677.4328 | 2702832.5878 | 1234683.7198
66 | 2702781.4434 | 1234652.0667 | 2702782.6931 | 1234648.9749 | 2702794.1537 | 1234653.8657 | 2702809.3308 | 1234659.2323 | 2702837.4482 | 1234674.9751 | 2702832.5878 | 1234683.7198
67 | 2702832.5878 | 1234683.7198 | 2702831.1541 | 1234686.5082 | 2702824.8883 | 1234701.1465
68 | 2702761.325 | 1234681.9969 | 2702777.3007 | 1234659.5897 | 2702781.4434 | 1234652.0667
69 | 2702750.5096 | 1234623.2875 | 2702768.1912 | 1234630.399 | 2702776.1802 | 1234636.4084 | 2702791.9621 | 1234643.1038
70 | 2702716.6924 | 1234588.1101 | 2702712.3424 | 1234592.3048 | 2702707.2041 | 1234599.1767
71 | 2702716.6924 | 1234588.1101 | 2702711.1113 | 1234581.631 | 2702705.4 | 1234577.459
72 | 2702716.6924 | 1234588.1101 | 2702724.1112 | 1234584.2021 | 2702731.9468 | 1234582.0248 | 2702737.2114 | 1234582.2163
73 | 2702653.5715 | 1234639.5582 | 2702654.0471 | 1234637.0089
74 | 2702654.0471 | 1234637.0089 | 2702657.1805 | 1234620.2368
75 | 2702653.5715 | 1234639.5582 | 2702619.0433 | 1234648.7083
76 | 2702761.325 | 1234681.9969 | 2702758.1594 | 1234686.4344 | 2702753.3151 | 1234700.1303
77 | 2702761.325 | 1234681.9969 | 2702745.9617 | 1234675.8125
78 | 2702496.1203 | 1234540.2239 | 2702500.8465 | 1234539.37
79 | 2702518.2656 | 1234536.2225 | 2702520.9798 | 1234535.5936
80 | 2702518.2656 | 1234536.2225 | 2702507.996 | 1234538.0781
81 | 2702624.647 | 1234676.2711 | 2702651.1393 | 1234668.6066
82 | 2702619.0433 | 1234648.7083 | 2702605.6878 | 1234652.2476
83 | 2702335.5842 | 1234653.7465 | 2702331.2599 | 1234656.2579
84 | 2702791.9621 | 1234643.1038 | 2702798.0128 | 1234645.6707 | 2702831.4713 | 1234661.1946
85 | 2702705.4 | 1234577.459 | 2702702.536 | 1234575.367 | 2702702.536 | 1234575.367
86 | 2702740.1968 | 1234582.3249 | 2702737.2114 | 1234582.2163
87 | 2702753.3151 | 1234700.1303 | 2702751.4703 | 1234705.3461
88 | 2702738.898 | 1234672.969 | 2702738.898 | 1234672.969 | 2702745.9617 | 1234675.8125
89 | 2702501.9931 | 1234539.1628 | 2702500.8465 | 1234539.37
90 | 2702520.9798 | 1234535.5936 | 2702526.9962 | 1234534.1995
91 | 2702501.9931 | 1234539.1628 | 2702507.996 | 1234538.0781
92 | 2702792.2861 | 1234558.3837 | 2702817.4564 | 1234555.4725
93 | 2702792.6148 | 1234598.8754 | 2702795.0301 | 1234589.2433 | 2702792.2861 | 1234558.3837
94 | 2702296.4117 | 1234750.4339 | 2702294.5032 | 1234750.6724 | 2702271.9782 | 1234750.1336
95 | 2702341.8999 | 1234743.7833 | 2702327.0357 | 1234746.6072 | 2702296.4117 | 1234750.4339
96 | 2702255.6279 | 1234749.7426 | 2702271.9782 | 1234750.1336
97 | 2702341.8999 | 1234743.7833 | 2702436.0978 | 1234725.9262
98 | 2702341.8999 | 1234743.7833 | 2702334.8122 | 1234710.9365
99 | 2702249.6664 | 1234749.6 | 2702255.6279 | 1234749.7426
100 | 2702436.0978 | 1234725.9262 | 2702483.3867 | 1234716.9681
101 | 2702436.0978 | 1234725.9262 | 2702432.3374 | 1234708.8953
102 | 2702249.6664 | 1234749.6 | 2702249.6664 | 1234749.6 | 2702239.7832 | 1234752.9834
103 | 2702483.3867 | 1234716.9681 | 2702506.0402 | 1234712.4443 | 2702513.4819 | 1234709.5551
104 | 2702429.6235 | 1234696.6036 | 2702432.3374 | 1234708.8953
105 | 2702239.7832 | 1234752.9834 | 2702230.8639 | 1234756.0369 | 2702230.8639 | 1234756.0369
106 | 2702518.9285 | 1234707.4406 | 2702513.4819 | 1234709.5551
107 | 2702430.1137 | 1234694.9553 | 2702429.6235 | 1234696.6036
108 | 2702429.6235 | 1234696.6036 | 2702421.7588 | 1234697.4131 | 2702417.3749 | 1234698.2582
109 | 2702222.3509 | 1234762.2329 | 2702230.8639 | 1234756.0369
110 | 2702528.3533 | 1234742.9855 | 2702518.9285 | 1234707.4406
111 | 2702518.9285 | 1234707.4406 | 2702524.4136 | 1234704.3221
112 | 2702246.452 | 1234981.9974 | 2702255.0102 | 1234981.333 | 2702256.7979 | 1234953.5762 | 2702257.3943 | 1234930.369
113 | 2702257.3943 | 1234930.369 | 2702251.929 | 1234893.4138 | 2702245.6706 | 1234863.8283 | 2702239.576 | 1234826.9179 | 2702238.0258 | 1234819.1974
114 | 2702246.452 | 1234981.9974 | 2702242.3282 | 1234991.5558 | 2702234.8803 | 1234999.4003 | 2702205.9207 | 1235012.8011 | 2702180.2123 | 1235036.9994 | 2702157.1662 | 1235045.5096
115 | 2702213.5012 | 1234772.5173 | 2702223.8566 | 1234784.4488 | 2702233.0309 | 1234800.3408 | 2702236.529 | 1234811.7429 | 2702238.0258 | 1234819.1974
116 | 2702424.7221 | 1234674.4024 | 2702430.1137 | 1234694.9553
117 | 2702430.1137 | 1234694.9553 | 2702441.3452 | 1234692.5137
118 | 2702417.3749 | 1234698.2582 | 2702406.4321 | 1234700.3676
119 | 2702213.5012 | 1234772.5173 | 2702218.8197 | 1234764.8029 | 2702222.3509 | 1234762.2329
120 | 2702213.5012 | 1234772.5173 | 2702204.6525 | 1234768.6355
121 | 2702601.1492 | 1234909.7985 | 2702601.1192 | 1234908.4293
122 | 2702602.1769 | 1234956.6096 | 2702601.1492 | 1234909.7985
123 | 2702601.068 | 1234906.0983 | 2702601.1192 | 1234908.4293
124 | 2702602.1769 | 1234956.6096 | 2702653.4904 | 1234956.5439
125 | 2702723.1375 | 1234956.4548 | 2702653.4904 | 1234956.5439
126 | 2702723.1375 | 1234956.4548 | 2702725.9109 | 1234942.7368 | 2702729.8783 | 1234924.3249 | 2702731.8271 | 1234906.2004 | 2702733.3073 | 1234892.4045 | 2702734.5603 | 1234870.2984 | 2702733.3606 | 1234850.8185 | 2702732.6855 | 1234837.7637 | 2702731.6007 | 1234824.7684 | 2702725.2928 | 1234789.4216
127 | 2702725.2928 | 1234789.4216 | 2702741.4848 | 1234791.0209
128 | 2702725.2928 | 1234789.4216 | 2702722.7174 | 1234779.1207
129 | 2702741.4848 | 1234791.0209 | 2702748.6282 | 1234791.7264
130 | 2702722.7174 | 1234779.1207 | 2702717.2182 | 1234757.1253
131 | 2702711.0111 | 1234732.2984 | 2702717.2182 | 1234757.1253
132 | 2702711.0111 | 1234732.2984 | 2702734.0258 | 1234725.9459
133 | 2702711.0111 | 1234732.2984 | 2702705.0618 | 1234733.9857 | 2702698.1379 | 1234735.9898 | 2702674.2242 | 1234742.6507
134 | 2702751.3816 | 1234722.8669 | 2702736.3725 | 1234725.2981 | 2702734.0258 | 1234725.9459
135 | 2702673.4606 | 1234742.8634 | 2702674.2242 | 1234742.6507
136 | 2702748.6282 | 1234791.7264 | 2702754.6388 | 1234792.3201 | 2702762.0464 | 1234793.1623
137 | 2702750.6172 | 1234714.9811 | 2702751.3816 | 1234722.8669
138 | 2702751.3816 | 1234722.8669 | 2702762.987 | 1234721.133 | 2702764.5664 | 1234721.1311
139 | 2702673.4606 | 1234742.8634 | 2702635.3377 | 1234753.4821
140 | 2702762.0464 | 1234793.1623 | 2702769.1779 | 1234793.9731
141 | 2702750.6172 | 1234714.9811 | 2702750.4859 | 1234708.1292
142 | 2702764.5664 | 1234721.1311 | 2702772.617 | 1234721.1217 | 2702783.08 | 1234722.8484 | 2702786.9219 | 1234724.029
143 | 2702615.8207 | 1234758.9184 | 2702635.3377 | 1234753.4821
144 | 2702769.1779 | 1234793.9731 | 2702783.1851 | 1234795.5656
145 | 2702276.5038 | 1234680.8301 | 2702297.09 | 1234672.4972
146 | 2702297.09 | 1234672.4972 | 2702311.9593 | 1234666.4784
147 | 2702311.9593 | 1234666.4784 | 2702317.5767 | 1234664.2046 | 2702331.2599 | 1234656.2579
148 | 2702751.4703 | 1234705.3461 | 2702750.4859 | 1234708.1292
149 | 2702813.7936 | 1234732.2863 | 2702786.9219 | 1234724.029
150 | 2702660.5857 | 1234687.0707 | 2702664.0456 | 1234699.6797
151 | 2702657.1009 | 1234709.1049 | 2702665.92 | 1234706.5109 | 2702664.0456 | 1234699.6797
152 | 2702660.5857 | 1234687.0707 | 2702665.1517 | 1234685.7277
153 | 2702660.5857 | 1234687.0707 | 2702654.8344 | 1234688.7573
154 | 2702654.8344 | 1234688.7573 | 2702636.9018 | 1234694.016
155 | 2702631.6176 | 1234695.5657 | 2702636.9018 | 1234694.016
156 | 2702631.6176 | 1234695.5657 | 2702626.3751 | 1234697.1048
157 | 2702631.6176 | 1234695.5657 | 2702635.107 | 1234707.6716
158 | 2702616.6724 | 1234698.6766 | 2702622.1745 | 1234698.338 | 2702626.3751 | 1234697.1048
159 | 2702629.4951 | 1234716.3113 | 2702636.9743 | 1234714.15 | 2702635.107 | 1234707.6716
160 | 2702584.327 | 1234686.3045 | 2702589.2557 | 1234684.8595 | 2702590.6243 | 1234682.3256 | 2702599.779 | 1234679.2635
161 | 2702608.8005 | 1234676.246 | 2702599.779 | 1234679.2635
162 | 2702580.6954 | 1234687.3692 | 2702584.327 | 1234686.3045
163 | 2702608.8005 | 1234676.246 | 2702610.4384 | 1234680.9111 | 2702616.6724 | 1234698.6766
164 | 2702600.8273 | 1234653.5357 | 2702608.8005 | 1234676.246
165 | 2702616.6724 | 1234698.6766 | 2702605.5429 | 1234701.7052
166 | 2702600.8273 | 1234653.5357 | 2702593.6619 | 1234655.936
167 | 2702600.8273 | 1234653.5357 | 2702605.6878 | 1234652.2476
168 | 2702602.4181 | 1234702.5556 | 2702605.5429 | 1234701.7052
169 | 2702593.6619 | 1234655.936 | 2702575.8781 | 1234666.5942
170 | 2702593.6619 | 1234655.936 | 2702580.2756 | 1234634.0996 | 2702576.76 | 1234631.2918
171 | 2702602.4181 | 1234702.5556 | 2702595.4528 | 1234704.4505
172 | 2702602.4181 | 1234702.5556 | 2702606.3405 | 1234715.7159
173 | 2702560.408 | 1234675.8659 | 2702575.8781 | 1234666.5942
174 | 2702576.76 | 1234631.2918 | 2702571.3816 | 1234626.9962 | 2702570.7447 | 1234626.8402
175 | 2702582.2132 | 1234708.0523 | 2702595.4528 | 1234704.4505
176 | 2702601.5197 | 1234723.8784 | 2702608.1212 | 1234721.6907 | 2702606.3405 | 1234715.7159
177 | 2702560.408 | 1234675.8659 | 2702548.0421 | 1234686.1269
178 | 2702570.7447 | 1234626.8402 | 2702558.9351 | 1234623.9458 | 2702548.8979 | 1234624.0727
179 | 2702548.0421 | 1234686.1269 | 2702546.5338 | 1234687.3786
180 | 2702533.5527 | 1234627.7662 | 2702533.5527 | 1234627.7662 | 2702542.9499 | 1234624.1479 | 2702548.8979 | 1234624.0727
181 | 2702406.0221 | 1234700.4466 | 2702406.4321 | 1234700.3676
182 | 2702406.0221 | 1234700.4466 | 2702391.2662 | 1234703.2911
183 | 2702391.0716 | 1234703.3286 | 2702391.2662 | 1234703.2911
184 | 2702440.7069 | 1234669.83 | 2702424.7221 | 1234674.4024
185 | 2702424.7221 | 1234674.4024 | 2702416.2915 | 1234676.0033
186 | 2702451.0892 | 1234691.5656 | 2702441.898 | 1234694.2579 | 2702441.3452 | 1234692.5137 | 2702441.3452 | 1234692.5137
187 | 2702391.0716 | 1234703.3286 | 2702380.3401 | 1234705.3973
188 | 2702440.7069 | 1234669.83 | 2702439.3768 | 1234667.0606 | 2702437.6489 | 1234663.2168 | 2702436.0646 | 1234660.265 | 2702435.0721 | 1234655.6003
189 | 2702440.7069 | 1234669.83 | 2702448.7054 | 1234667.54
190 | 2702399.7043 | 1234679.1531 | 2702416.2915 | 1234676.0033
191 | 2702451.0892 | 1234691.5656 | 2702460.4984 | 1234688.8095
192 | 2702380.0287 | 1234705.4573 | 2702380.3401 | 1234705.3973
193 | 2702435.0721 | 1234655.6003 | 2702433.5785 | 1234648.5801 | 2702434.3674 | 1234648.3446
194 | 2702448.7054 | 1234667.54 | 2702459.8756 | 1234664.3417
195 | 2702392.1375 | 1234680.59 | 2702399.7043 | 1234679.1531
196 | 2702473.7594 | 1234684.9252 | 2702460.4984 | 1234688.8095
197 | 2702445.225 | 1234645.1033 | 2702434.3674 | 1234648.3446
198 | 2702474.6875 | 1234660.1009 | 2702459.8756 | 1234664.3417
199 | 2702445.225 | 1234645.1033 | 2702460.7939 | 1234640.4556
200 | 2702480.3762 | 1234658.4721 | 2702474.6875 | 1234660.1009
201 | 2702467.8762 | 1234638.3414 | 2702460.7939 | 1234640.4556
202 | 2702532.5809 | 1234698.9586 | 2702546.5338 | 1234687.3786
203 | 2702532.5809 | 1234698.9586 | 2702527.1475 | 1234702.7678 | 2702524.4136 | 1234704.3221
204 | 2702533.3121 | 1234648.9329 | 2702534.1118 | 1234649.809
205 | 2702533.3121 | 1234648.9329 | 2702533.0574 | 1234648.6539
206 | 2702528.3533 | 1234742.9855 | 2702511.2748 | 1234747.7723 | 2702510.3786 | 1234744.4321
207 | 2702528.3533 | 1234742.9855 | 2702534.3607 | 1234741.4436 | 2702540.7272 | 1234741.4646
208 | 2702529.0799 | 1234639.5201 | 2702532.2608 | 1234647.7812 | 2702533.0574 | 1234648.6539
209 | 2702540.7272 | 1234741.4646 | 2702553.5773 | 1234738.2283 | 2702551.9803 | 1234731.6291
210 | 2702540.7272 | 1234741.4646 | 2702539.6975 | 1234737.5216
211 | 2702532.5523 | 1234630.3953 | 2702529.0799 | 1234639.5201 | 2702529.0799 | 1234639.5201
212 | 2702533.5527 | 1234627.7662 | 2702532.5523 | 1234630.3953
213 | 2702481.5258 | 1234682.6504 | 2702488.6353 | 1234680.5679
214 | 2702494.2028 | 1234678.9371 | 2702488.6353 | 1234680.5679
215 | 2702481.5258 | 1234682.6504 | 2702473.7594 | 1234684.9252
216 | 2702833.166 | 1234741.4928 | 2702816.7865 | 1234733.206 | 2702813.7936 | 1234732.2863
217 | 2702824.3848 | 1234800.2498 | 2702828.0114 | 1234800.6622 | 2702835.2593 | 1234799.2933
218 | 2702810.6558 | 1234798.6889 | 2702824.3848 | 1234800.2498
219 | 2702744.3637 | 1234658.0269 | 2702745.6139 | 1234654.6089
220 | 2702744.3637 | 1234658.0269 | 2702742.4493 | 1234663.2604
221 | 2702742.4493 | 1234663.2604 | 2702740.6656 | 1234668.1368
222 | 2702738.898 | 1234672.969 | 2702740.6656 | 1234668.1368
223 | 2702526.9962 | 1234534.1995 | 2702533.0134 | 1234532.8053
224 | 2702558.1779 | 1234554.2756 | 2702564.1942 | 1234552.9873
225 | 2702564.1942 | 1234552.9873 | 2702570.2104 | 1234551.699
226 | 2702570.2104 | 1234551.699 | 2702578.964 | 1234549.8245
227 | 2702582.9351 | 1234547.6359 | 2702579.4924 | 1234549.7114 | 2702578.964 | 1234549.8245
228 | 2702582.9351 | 1234547.6359 | 2702585.9494 | 1234545.8199 | 2702593.6389 | 1234544.2643
229 | 2702582.9351 | 1234547.6359 | 2702581.049 | 1234539.7498
230 | 2702533.0134 | 1234532.8053 | 2702539.0307 | 1234531.411
231 | 2702640.0658 | 1234554.8949 | 2702658.4186 | 1234557.0774
232 | 2702633.1696 | 1234554.0748 | 2702640.0658 | 1234554.8949
233 | 2702668.2789 | 1234564.1202 | 2702666.7477 | 1234563.6175 | 2702661.6152 | 1234557.4575 | 2702658.4186 | 1234557.0774
234 | 2702674.1883 | 1234566.0603 | 2702668.2789 | 1234564.1202
235 | 2702680.0959 | 1234567.9998 | 2702674.1883 | 1234566.0603
236 | 2702680.0959 | 1234567.9998 | 2702680.7558 | 1234568.2164
237 | 2702686.0049 | 1234569.9397 | 2702680.7558 | 1234568.2164
238 | 2702686.0049 | 1234569.9397 | 2702702.536 | 1234575.367
239 | 2702740.1968 | 1234582.3249 | 2702744.7711 | 1234582.4913 | 2702749.9236 | 1234583.9184
240 | 2702749.9236 | 1234583.9184 | 2702762.0707 | 1234587.2829 | 2702767.8903 | 1234589.4916
241 | 2702782.2537 | 1234594.943 | 2702767.8903 | 1234589.4916
242 | 2702792.6148 | 1234598.8754 | 2702782.2537 | 1234594.943
243 | 2702817.4564 | 1234555.4725 | 2702831.7321 | 1234556.9881
244 | 2702817.4564 | 1234555.4725 | 2702817.1387 | 1234543.9002
245 | 2702831.7321 | 1234556.9881 | 2702848.742 | 1234558.7941 | 2702852.9405 | 1234558.1492
246 | 2702817.1387 | 1234543.9002 | 2702816.8528 | 1234533.4899 | 2702821.6738 | 1234516.972 | 2702828.9582 | 1234516.8822
247 | 2702852.9405 | 1234558.1492 | 2702888.2304 | 1234552.7286 | 2702892.9914 | 1234551.2578
248 | 2702828.9582 | 1234516.8822 | 2702842.9331 | 1234516.7099
249 | 2702842.9331 | 1234516.7099 | 2702850.919 | 1234516.6115
250 | 2702866.0677 | 1234516.4247 | 2702850.919 | 1234516.6115
251 | 2702783.1851 | 1234795.5656 | 2702790.3173 | 1234796.3765
252 | 2702790.3173 | 1234796.3765 | 2702803.5254 | 1234797.8782
253 | 2702803.5254 | 1234797.8782 | 2702810.6558 | 1234798.6889
254 | 2702579.0894 | 1234708.9021 | 2702582.2132 | 1234708.0523
255 | 2702580.2741 | 1234536.5101 | 2702581.049 | 1234539.7498
256 | 2702576.6086 | 1234521.1846 | 2702580.2741 | 1234536.5101
257 | 2702576.6086 | 1234521.1846 | 2702570.8943 | 1234523.8014
258 | 2702576.6086 | 1234521.1846 | 2702579.0963 | 1234520.0489 | 2702581.071 | 1234519.687
259 | 2702563.1204 | 1234525.8292 | 2702569.8932 | 1234524.2599 | 2702570.8943 | 1234523.8014
260 | 2702581.071 | 1234519.687 | 2702587.0953 | 1234518.5831
261 | 2702593.6389 | 1234544.2643 | 2702599.8155 | 1234543.0148
262 | 2702557.2261 | 1234527.1949 | 2702563.1204 | 1234525.8292
263 | 2702587.0953 | 1234518.5831 | 2702593.1231 | 1234517.4786
264 | 2702601.6987 | 1234542.6338 | 2702599.8155 | 1234543.0148
265 | 2702551.2376 | 1234528.5825 | 2702557.2261 | 1234527.1949
266 | 2702597.6734 | 1234516.6448 | 2702593.1231 | 1234517.4786
267 | 2702539.0307 | 1234531.411 | 2702551.2376 | 1234528.5825

## bus_geodata
| x | y | coords
0 | 2702584.1512 | 1234290.367
1 | 2702565.6283 | 1234315.6778
2 | 2702548.5967 | 1234341.5704
3 | 2702539.708 | 1234357.3647
4 | 2702780.7271 | 1234297.1425
5 | 2702781.2538 | 1234330.1734
6 | 2702806.7166 | 1234257.9069
7 | 2702538.8124 | 1234358.956
8 | 2702794.0635 | 1234364.5234
9 | 2702840.9638 | 1234199.6798
10 | 2702825.5077 | 1234263.7909
11 | 2702801.5393 | 1234128.2194
12 | 2702818.4366 | 1234143.446
13 | 2702534.5464 | 1234366.5364
14 | 2702532.2932 | 1234370.6381
15 | 2702470.9534 | 1234539.42
16 | 2702476.4731 | 1234543.774
17 | 2702453.9979 | 1234576.9782
18 | 2702858.8908 | 1234269.3924
19 | 2702851.2687 | 1234269.5199
20 | 2702863.6879 | 1234269.3122
21 | 2702839.3187 | 1234267.0557
22 | 2702868.4847 | 1234269.2321
23 | 2702872.3627 | 1234307.8292
24 | 2702876.3644 | 1234269.1003
25 | 2702879.6235 | 1234310.119
26 | 2702890.1304 | 1234266.7156
27 | 2702901.4102 | 1234262.9785
28 | 2702842.2299 | 1234187.8614
29 | 2702834.7166 | 1234158.1162
30 | 2702800.9476 | 1234386.4818
31 | 2702921.8736 | 1234256.1988
32 | 2702792.9775 | 1234499.0573
33 | 2702890.3871 | 1234517.2272
34 | 2702871.3923 | 1234516.3591
35 | 2702791.4811 | 1234522.815
36 | 2702792.2056 | 1234557.6042
37 | 2702490.1614 | 1234541.3007
38 | 2702694.7043 | 1234645.1731
39 | 2702673.341 | 1234662.1835
40 | 2702720.4624 | 1234633.6429
41 | 2702697.3542 | 1234679.7092
42 | 2702467.0427 | 1234584.4198
43 | 2702442.658 | 1234589.7906
44 | 2702725.9744 | 1234616.9812
45 | 2702737.6739 | 1234639.2894
46 | 2702502.2287 | 1234556.9503
47 | 2702518.3004 | 1234547.7985
48 | 2702598.8716 | 1234579.2706
49 | 2702680.8002 | 1234604.2687
50 | 2702702.1153 | 1234597.0649
51 | 2702369.6553 | 1234622.47
52 | 2702346.2898 | 1234622.1674
53 | 2702392.6076 | 1234620.6758
54 | 2702362.0755 | 1234637.8129
55 | 2702832.5878 | 1234683.7198
56 | 2702818.8424 | 1234677.4328
57 | 2702781.4434 | 1234652.0667
58 | 2702824.8883 | 1234701.1465
59 | 2702750.5096 | 1234623.2875
60 | 2702707.2041 | 1234599.1767
61 | 2702716.6924 | 1234588.1101
62 | 2702654.0471 | 1234637.0089
63 | 2702653.5715 | 1234639.5582
64 | 2702657.1805 | 1234620.2368
65 | 2702761.325 | 1234681.9969
66 | 2702496.1203 | 1234540.2239
67 | 2702518.2656 | 1234536.2225
68 | 2702533.1705 | 1234550.6331
69 | 2702651.1393 | 1234668.6066
70 | 2702619.0433 | 1234648.7083
71 | 2702425.9276 | 1234602.1713
72 | 2702345.992 | 1234615.2904
73 | 2702328.9227 | 1234616.4529
74 | 2702335.5842 | 1234653.7465
75 | 2702791.9621 | 1234643.1038
76 | 2702705.4 | 1234577.459
77 | 2702737.2114 | 1234582.2163
78 | 2702753.3151 | 1234700.1303
79 | 2702745.9617 | 1234675.8125
80 | 2702500.8465 | 1234539.37
81 | 2702520.9798 | 1234535.5936
82 | 2702507.996 | 1234538.0781
83 | 2702792.2861 | 1234558.3837
84 | 2702296.4118 | 1234750.4339
85 | 2702271.9782 | 1234750.1336
86 | 2702341.8999 | 1234743.7833
87 | 2702255.6279 | 1234749.7426
88 | 2702436.0978 | 1234725.9262
89 | 2702334.8122 | 1234710.9365
90 | 2702249.6664 | 1234749.6
91 | 2702483.3867 | 1234716.9681
92 | 2702432.3374 | 1234708.8953
93 | 2702239.7832 | 1234752.9834
94 | 2702513.4819 | 1234709.5551
95 | 2702429.6235 | 1234696.6036
96 | 2702230.8639 | 1234756.0369
97 | 2702518.9285 | 1234707.4406
98 | 2702257.3943 | 1234930.369
99 | 2702246.452 | 1234981.9974
100 | 2702238.0258 | 1234819.1974
101 | 2702430.1137 | 1234694.9553
102 | 2702417.3749 | 1234698.2582
103 | 2702222.3509 | 1234762.2329
104 | 2702213.5012 | 1234772.5173
105 | 2702204.6525 | 1234768.6355
106 | 2702601.1492 | 1234909.7985
107 | 2702601.1192 | 1234908.4292
108 | 2702602.1769 | 1234956.6096
109 | 2702601.068 | 1234906.0983
110 | 2702653.4904 | 1234956.5439
111 | 2702723.1375 | 1234956.4548
112 | 2702725.2928 | 1234789.4216
113 | 2702741.4848 | 1234791.0209
114 | 2702722.7174 | 1234779.1207
115 | 2702717.2182 | 1234757.1253
116 | 2702711.0111 | 1234732.2984
117 | 2702734.0258 | 1234725.9459
118 | 2702674.2242 | 1234742.6507
119 | 2702748.6282 | 1234791.7264
120 | 2702751.3816 | 1234722.8669
121 | 2702673.4606 | 1234742.8634
122 | 2702762.0464 | 1234793.1623
123 | 2702750.6172 | 1234714.9811
124 | 2702764.5664 | 1234721.1311
125 | 2702635.3377 | 1234753.4821
126 | 2702769.1779 | 1234793.9731
127 | 2702615.8207 | 1234758.9184
128 | 2702157.1662 | 1235045.5096
129 | 2702276.5038 | 1234680.8301
130 | 2702297.09 | 1234672.4972
131 | 2702311.9593 | 1234666.4784
132 | 2702331.2599 | 1234656.2579
133 | 2702750.4859 | 1234708.1292
134 | 2702786.9219 | 1234724.029
135 | 2702664.0456 | 1234699.6797
136 | 2702660.5857 | 1234687.0707
137 | 2702657.1009 | 1234709.1049
138 | 2702665.1517 | 1234685.7277
139 | 2702654.8344 | 1234688.7573
140 | 2702636.9018 | 1234694.016
141 | 2702631.6176 | 1234695.5657
142 | 2702626.3751 | 1234697.1048
143 | 2702635.107 | 1234707.6716
144 | 2702599.779 | 1234679.2635
145 | 2702584.327 | 1234686.3045
146 | 2702608.8005 | 1234676.246
147 | 2702580.6954 | 1234687.3692
148 | 2702616.6724 | 1234698.6766
149 | 2702600.8273 | 1234653.5357
150 | 2702605.5429 | 1234701.7052
151 | 2702593.6619 | 1234655.936
152 | 2702605.6878 | 1234652.2476
153 | 2702602.4181 | 1234702.5556
154 | 2702575.8781 | 1234666.5942
155 | 2702576.76 | 1234631.2918
156 | 2702595.4528 | 1234704.4505
157 | 2702606.3405 | 1234715.7159
158 | 2702560.408 | 1234675.8659
159 | 2702570.7447 | 1234626.8402
160 | 2702624.647 | 1234676.2711
161 | 2702548.0421 | 1234686.1269
162 | 2702548.8979 | 1234624.0727
163 | 2702406.4321 | 1234700.3676
164 | 2702406.0221 | 1234700.4466
165 | 2702391.2662 | 1234703.2911
166 | 2702424.7221 | 1234674.4024
167 | 2702441.3452 | 1234692.5137
168 | 2702391.0716 | 1234703.3286
169 | 2702440.7069 | 1234669.83
170 | 2702416.2915 | 1234676.0033
171 | 2702451.0892 | 1234691.5656
172 | 2702380.3401 | 1234705.3973
173 | 2702435.0721 | 1234655.6003
174 | 2702448.7054 | 1234667.54
175 | 2702399.7043 | 1234679.1531
176 | 2702460.4984 | 1234688.8096
177 | 2702392.1375 | 1234680.59
178 | 2702434.3674 | 1234648.3446
179 | 2702459.8756 | 1234664.3417
180 | 2702380.0287 | 1234705.4573
181 | 2702445.225 | 1234645.1033
182 | 2702474.6875 | 1234660.1009
183 | 2702460.7939 | 1234640.4556
184 | 2702467.8762 | 1234638.3414
185 | 2702546.5338 | 1234687.3786
186 | 2702532.5809 | 1234698.9586
187 | 2702524.4136 | 1234704.3221
188 | 2702534.1118 | 1234649.809
189 | 2702533.3121 | 1234648.9329
190 | 2702528.3533 | 1234742.9855
191 | 2702533.0574 | 1234648.6539
192 | 2702510.3786 | 1234744.4321
193 | 2702540.7272 | 1234741.4646
194 | 2702529.0799 | 1234639.5201
195 | 2702532.5523 | 1234630.3953
196 | 2702533.5527 | 1234627.7662
197 | 2702480.3762 | 1234658.4721
198 | 2702488.6353 | 1234680.5679
199 | 2702481.5258 | 1234682.6504
200 | 2702494.2028 | 1234678.9371
201 | 2702473.7594 | 1234684.9252
202 | 2702833.166 | 1234741.4928
203 | 2702813.7936 | 1234732.2863
204 | 2702831.4713 | 1234661.1946
205 | 2702835.2593 | 1234799.2933
206 | 2702824.3848 | 1234800.2498
207 | 2702751.4703 | 1234705.3461
208 | 2702745.6139 | 1234654.6089
209 | 2702744.3637 | 1234658.0269
210 | 2702742.4493 | 1234663.2604
211 | 2702740.6656 | 1234668.1368
212 | 2702738.898 | 1234672.969
213 | 2702501.9931 | 1234539.1628
214 | 2702526.9962 | 1234534.1995
215 | 2702558.1779 | 1234554.2756
216 | 2702564.1942 | 1234552.9873
217 | 2702570.2104 | 1234551.699
218 | 2702578.964 | 1234549.8245
219 | 2702582.9351 | 1234547.6359
220 | 2702533.0134 | 1234532.8053
221 | 2702640.0658 | 1234554.8949
222 | 2702658.4186 | 1234557.0774
223 | 2702633.1696 | 1234554.0748
224 | 2702668.2789 | 1234564.1202
225 | 2702674.1883 | 1234566.0603
226 | 2702680.0959 | 1234567.9998
227 | 2702680.7558 | 1234568.2164
228 | 2702686.0049 | 1234569.9397
229 | 2702702.536 | 1234575.367
230 | 2702740.1968 | 1234582.3249
231 | 2702749.9236 | 1234583.9184
232 | 2702767.8903 | 1234589.4916
233 | 2702782.2537 | 1234594.943
234 | 2702792.6148 | 1234598.8754
235 | 2702817.4564 | 1234555.4725
236 | 2702831.7321 | 1234556.9881
237 | 2702817.1387 | 1234543.9002
238 | 2702892.9914 | 1234551.2578
239 | 2702852.9405 | 1234558.1492
240 | 2702828.9582 | 1234516.8822
241 | 2702842.9331 | 1234516.7099
242 | 2702850.919 | 1234516.6115
243 | 2702866.0677 | 1234516.4247
244 | 2702783.1851 | 1234795.5656
245 | 2702790.3173 | 1234796.3765
246 | 2702803.5254 | 1234797.8782
247 | 2702810.6558 | 1234798.6889
248 | 2702629.4951 | 1234716.3113
249 | 2702601.5197 | 1234723.8784
250 | 2702582.2132 | 1234708.0523
251 | 2702579.0894 | 1234708.9021
252 | 2702551.9803 | 1234731.6291
253 | 2702539.6975 | 1234737.5216
254 | 2702580.2741 | 1234536.5101
255 | 2702581.049 | 1234539.7498
256 | 2702576.6086 | 1234521.1846
257 | 2702570.8943 | 1234523.8014
258 | 2702581.071 | 1234519.687
259 | 2702593.6389 | 1234544.2643
260 | 2702563.1204 | 1234525.8292
261 | 2702587.0953 | 1234518.5831
262 | 2702599.8155 | 1234543.0148
263 | 2702557.2261 | 1234527.1949
264 | 2702593.1231 | 1234517.4786
265 | 2702601.6987 | 1234542.6338
266 | 2702551.2376 | 1234528.5825
267 | 2702597.6734 | 1234516.6448
268 | 2702539.0307 | 1234531.411
269 | 2702593.6619 | 1234655.936

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97721 | -0.43814 | 0.00087721 | 0.00021985
1 | 0.97724 | -0.43764 | 0.0019996 | 0.00050115
2 | 0.97732 | -0.43601 | 0.0019048 | 0.0004774
3 | 0.9774 | -0.43443 | 0.00048847 | 0.00012242
4 | 0.9771 | -0.44077 | 0 | 0
5 | 0.97744 | -0.43397 | 0.00055573 | 0.00013928
6 | 0.97661 | -0.45037 | 0 | 0
7 | 0.97741 | -0.43425 | 0.00058461 | 0.00014652
8 | 0.97784 | -0.42616 | 0.00088985 | 0.00022302
9 | 0.97627 | -0.45708 | 0.00025838 | 6.4756e-05
10 | 0.97651 | -0.45244 | 0.0010625 | 0.00026628
11 | 0.97605 | -0.46147 | 0.0011105 | 0.00027833
12 | 0.97607 | -0.461 | 0.0017935 | 0.0004495
13 | 0.97746 | -0.43332 | 0.00027451 | 6.8799e-05
14 | 0.97748 | -0.4328 | 0.00074638 | 0.00018706
15 | 0.97863 | -0.41028 | 0 | 0
16 | 0.97872 | -0.40856 | 0 | 0
17 | 0.97721 | -0.438 | 0 | 0
18 | 0.97638 | -0.45483 | 0.00023813 | 5.9681e-05
19 | 0.9764 | -0.45444 | 0.00068361 | 0.00017133
20 | 0.97637 | -0.45505 | 0.0002385 | 5.9775e-05
21 | 0.97644 | -0.45366 | 0 | 0
22 | 0.97636 | -0.45525 | 0.0002381 | 5.9674e-05
23 | 0.97637 | -0.45505 | 0.00045294 | 0.00011352
24 | 0.97635 | -0.45555 | 0.00043257 | 0.00010841
25 | 0.97637 | -0.45515 | 0.00075687 | 0.00018969
26 | 0.97633 | -0.45598 | 0.00056344 | 0.00014121
27 | 0.97631 | -0.45621 | 0.00056379 | 0.0001413
28 | 0.97621 | -0.45819 | 0.0022049 | 0.0005526
29 | 0.97613 | -0.45984 | 0 | 0
30 | 0.97811 | -0.42089 | 0 | 0
31 | 0.9763 | -0.45641 | 0.0005142 | 0.00012887
32 | 0.97943 | -0.39502 | 0.0012821 | 0.00032133
33 | 0.9795 | -0.39363 | 0.0010845 | 0.0002718
34 | 0.97952 | -0.39325 | 0.00096499 | 0.00024185
35 | 0.97973 | -0.38903 | 0.001133 | 0.00028396
36 | 0.98022 | -0.37954 | 0.0021348 | 0.00053504
37 | 0.97889 | -0.40517 | 0.0012257 | 0.00030718
38 | 0.9894 | -0.20139 | 0 | 0
39 | 0.9925 | -0.14205 | 0 | 0
40 | 0.98652 | -0.25686 | 0 | 0
41 | 0.98937 | -0.20202 | 0.0010169 | 0.00025487
42 | 0.97718 | -0.43864 | 0.0021017 | 0.00052674
43 | 0.9765 | -0.45196 | 0.0014998 | 0.00037588
44 | 0.98581 | -0.27051 | 0 | 0
45 | 0.98587 | -0.26949 | 0.00092362 | 0.00023148
46 | 0.98003 | -0.38283 | 0 | 0
47 | 0.97952 | -0.39288 | 0 | 0
48 | 0.98213 | -0.342 | 0.0054174 | 0.0013577
49 | 0.98404 | -0.30478 | 0 | 0
50 | 0.98456 | -0.2947 | 0.0010223 | 0.0002562
51 | 0.97347 | -0.51166 | 0 | 0
52 | 0.97316 | -0.51776 | 0 | 0
53 | 0.97421 | -0.49703 | 0.0063368 | 0.0015882
54 | 0.97312 | -0.51847 | 0.0067758 | 0.0016982
55 | 0.98133 | -0.35772 | 0 | 0
56 | 0.98081 | -0.36794 | 0.037425 | 0.0093795
57 | 0.98421 | -0.30153 | 0 | 0
58 | 0.98125 | -0.35931 | 0.0045832 | 0.0011487
59 | 0.9855 | -0.27669 | 0.0020229 | 0.00050699
60 | 0.98469 | -0.29229 | 0 | 0
61 | 0.98384 | -0.30878 | 0 | 0
62 | 0.9957 | -0.081156 | 0 | 0
63 | 0.9957 | -0.081111 | 0 | 0
64 | 0.99568 | -0.081451 | 0.00098225 | 0.00024618
65 | 0.98327 | -0.31985 | 0 | 0
66 | 0.97897 | -0.40366 | 0.0015017 | 0.00037636
67 | 0.97928 | -0.39751 | 0 | 0
68 | 0.97948 | -0.39367 | 0.002853 | 0.00071503
69 | 0.99234 | -0.14516 | 0.0038037 | 0.0009533
70 | 0.99851 | -0.02806 | 0.0018658 | 0.00046761
71 | 0.97566 | -0.46844 | 0.0024126 | 0.00060466
72 | 0.97311 | -0.51869 | 0.0073542 | 0.0018431
73 | 0.97301 | -0.5207 | 0.0067818 | 0.0016997
74 | 0.97273 | -0.52615 | 0.0058766 | 0.0014728
75 | 0.98501 | -0.28623 | 0.0014914 | 0.00037377
76 | 0.98351 | -0.31525 | 0.0024899 | 0.00062402
77 | 0.98304 | -0.3244 | 0.002027 | 0.00050802
78 | 0.98278 | -0.32932 | 0.00095183 | 0.00023855
79 | 0.98315 | -0.32211 | 0.0009691 | 0.00024288
80 | 0.97903 | -0.40243 | 0.0028875 | 0.00072368
81 | 0.97921 | -0.39884 | 0.0011141 | 0.00027921
82 | 0.97913 | -0.40043 | 0.0010506 | 0.0002633
83 | 0.98023 | -0.3793 | 0 | 0
84 | 0.98139 | -0.35808 | 0.0023922 | 0.00059955
85 | 0.98114 | -0.36294 | 0.00086896 | 0.00021778
86 | 0.98195 | -0.34697 | 0 | 0
87 | 0.98099 | -0.36593 | 0.0015486 | 0.00038811
88 | 0.98367 | -0.31333 | 0 | 0
89 | 0.98176 | -0.35069 | 0.0061287 | 0.001536
90 | 0.98094 | -0.36685 | 0.0011799 | 0.0002957
91 | 0.98735 | -0.24188 | 0 | 0
92 | 0.98265 | -0.33329 | 0.0020565 | 0.00051541
93 | 0.98087 | -0.36825 | 0.0016815 | 0.00042142
94 | 0.98974 | -0.19589 | 0.002541 | 0.00063684
95 | 0.98194 | -0.34725 | 0 | 0
96 | 0.98082 | -0.36922 | 0.0015942 | 0.00039955
97 | 0.9902 | -0.18701 | 0 | 0
98 | 0.98045 | -0.3765 | 0 | 0
99 | 0.98037 | -0.37811 | 0 | 0
100 | 0.98061 | -0.37343 | 0.0011101 | 0.00027821
101 | 0.98186 | -0.34872 | 0 | 0
102 | 0.98178 | -0.35043 | 0.0020233 | 0.00050709
103 | 0.98078 | -0.37 | 0.00054748 | 0.00013721
104 | 0.98073 | -0.37089 | 0 | 0
105 | 0.98073 | -0.37105 | 0.00093358 | 0.00023398
106 | 0.97215 | -0.53779 | 0.001642 | 0.00041153
107 | 0.97213 | -0.53804 | 0.0054885 | 0.0013756
108 | 0.97266 | -0.5276 | 0 | 0
109 | 0.97212 | -0.53824 | 0.0046758 | 0.0011719
110 | 0.97323 | -0.51644 | 0.0011202 | 0.00028075
111 | 0.97407 | -0.49988 | 0 | 0
112 | 0.9761 | -0.4599 | 0 | 0
113 | 0.97582 | -0.46551 | 0.0018849 | 0.0004724
114 | 0.97641 | -0.45373 | 0.0090624 | 0.0022712
115 | 0.97727 | -0.43683 | 0.0062831 | 0.0015747
116 | 0.9784 | -0.41485 | 0 | 0
117 | 0.98023 | -0.37902 | 0.0016986 | 0.00042571
118 | 0.97714 | -0.43954 | 0.0079847 | 0.0020012
119 | 0.9757 | -0.46773 | 0.0018849 | 0.0004724
120 | 0.98161 | -0.3521 | 0 | 0
121 | 0.97712 | -0.43994 | 0.0055943 | 0.0014021
122 | 0.97551 | -0.47146 | 0.0018857 | 0.0004726
123 | 0.98236 | -0.3375 | 0 | 0
124 | 0.98139 | -0.35636 | 0.0043578 | 0.0010922
125 | 0.97631 | -0.45575 | 0.007431 | 0.0018624
126 | 0.97543 | -0.47319 | 0.0018863 | 0.00047276
127 | 0.97604 | -0.4611 | 0.014435 | 0.0036178
128 | 0.98021 | -0.38117 | 0.0014922 | 0.00037399
129 | 0.97248 | -0.53106 | 0.0014648 | 0.0003671
130 | 0.97251 | -0.53046 | 0.0024837 | 0.00062247
131 | 0.97257 | -0.52929 | 0.0020912 | 0.0005241
132 | 0.9727 | -0.52685 | 0.0015724 | 0.00039409
133 | 0.98258 | -0.33329 | 0.0012866 | 0.00032245
134 | 0.98111 | -0.36183 | 0.0043392 | 0.0010875
135 | 0.9983 | -0.032725 | 0.0018663 | 0.00046774
136 | 0.99834 | -0.031919 | 0 | 0
137 | 0.99827 | -0.033198 | 0.0016595 | 0.0004159
138 | 0.99833 | -0.032049 | 0.0015627 | 0.00039166
139 | 0.99837 | -0.031385 | 0.0015632 | 0.00039178
140 | 0.99848 | -0.029211 | 0.0016736 | 0.00041944
141 | 0.99852 | -0.02841 | 0 | 0
142 | 0.99858 | -0.0273 | 0.0016736 | 0.00041944
143 | 0.99848 | -0.029134 | 0.00166 | 0.00041604
144 | 0.99919 | -0.015603 | 0.0028788 | 0.00072149
145 | 0.9991 | -0.01721 | 0.0025904 | 0.00064921
146 | 0.99926 | -0.014259 | 0 | 0
147 | 0.9991 | -0.017383 | 0.0026189 | 0.00065636
148 | 0.9987 | -0.025002 | 0 | 0
149 | 1 | 0 | -0.52719 | -0.13494
150 | 0.99857 | -0.02754 | 0.0014205 | 0.00035602
151 | 0.99951 | -0.0092512 | 0 | 0
152 | 0.9996 | -0.007507 | 0.0017487 | 0.00043826
153 | 0.99853 | -0.028173 | 0 | 0
154 | 0.99728 | -0.051498 | 0.0046146 | 0.0011565
155 | 0.99885 | -0.021995 | 0.0025353 | 0.0006354
156 | 0.99849 | -0.02908 | 0.0025353 | 0.00063541
157 | 0.99849 | -0.029127 | 0.0016296 | 0.00040842
158 | 0.99542 | -0.086939 | 0 | 0
159 | 0.9987 | -0.024854 | 0.0023163 | 0.00058052
160 | 0.99224 | -0.14702 | 0.0038031 | 0.00095315
161 | 0.99376 | -0.11858 | 0 | 0
162 | 0.99831 | -0.032378 | 0.002561 | 0.00064184
163 | 0.98165 | -0.35288 | 0.0020404 | 0.00051138
164 | 0.98165 | -0.35295 | 0.0020193 | 0.00050609
165 | 0.98153 | -0.35516 | 0.0019004 | 0.00047628
166 | 0.98126 | -0.36045 | 0 | 0
167 | 0.98169 | -0.35219 | 0.0024071 | 0.00060327
168 | 0.98153 | -0.35518 | 0.0020099 | 0.00050374
169 | 0.98089 | -0.36775 | 0 | 0
170 | 0.98121 | -0.36142 | 0.0021066 | 0.00052797
171 | 0.98154 | -0.35513 | 0.0024776 | 0.00062096
172 | 0.98149 | -0.35601 | 0.0021321 | 0.00053436
173 | 0.9807 | -0.37157 | 0.0020621 | 0.00051681
174 | 0.98081 | -0.36934 | 0.0023264 | 0.00058304
175 | 0.98115 | -0.36268 | 0.0020649 | 0.00051752
176 | 0.98143 | -0.35723 | 0.0023144 | 0.00058003
177 | 0.98113 | -0.36297 | 0.0020594 | 0.00051612
178 | 0.98061 | -0.37326 | 0.0020728 | 0.0005195
179 | 0.98072 | -0.37108 | 0.0020253 | 0.00050759
180 | 0.98149 | -0.35602 | 0.0020645 | 0.00051741
181 | 0.98051 | -0.37522 | 0.0021743 | 0.00054493
182 | 0.98063 | -0.37282 | 0.0021098 | 0.00052877
183 | 0.9804 | -0.3774 | 0.0021437 | 0.00053727
184 | 0.98036 | -0.37811 | 0.0052488 | 0.0013155
185 | 0.99356 | -0.12245 | 0.0050167 | 0.0012573
186 | 0.99177 | -0.15673 | 0 | 0
187 | 0.99081 | -0.17528 | 0.0022561 | 0.00056544
188 | 0.99787 | -0.040918 | 0.0045574 | 0.0011422
189 | 0.99787 | -0.040823 | 0.0017904 | 0.00044871
190 | 0.98955 | -0.19953 | 0 | 0
191 | 0.99787 | -0.040781 | 0.0017904 | 0.00044871
192 | 0.98939 | -0.20279 | 0.008665 | 0.0021716
193 | 0.98943 | -0.20187 | 0 | 0
194 | 0.99795 | -0.039352 | 0.0017305 | 0.00043371
195 | 0.99803 | -0.037665 | 0.0017568 | 0.0004403
196 | 0.99806 | -0.037093 | 0.005201 | 0.0013035
197 | 0.98061 | -0.37327 | 0.0041253 | 0.0010339
198 | 0.98122 | -0.3613 | 0.0022447 | 0.00056257
199 | 0.98125 | -0.36065 | 0.0023322 | 0.0005845
200 | 0.98121 | -0.36157 | 0.0025948 | 0.00065031
201 | 0.98131 | -0.3596 | 0.0023116 | 0.00057934
202 | 0.98079 | -0.36822 | 0.0046751 | 0.0011717
203 | 0.98088 | -0.3664 | 0.0043077 | 0.0010796
204 | 0.98461 | -0.29405 | 0.010006 | 0.0025078
205 | 0.97502 | -0.48124 | 0.0018784 | 0.00047076
206 | 0.97504 | -0.48086 | 0.0018793 | 0.00047098
207 | 0.98265 | -0.33192 | 0.0009582 | 0.00024015
208 | 0.98304 | -0.32426 | 0.0019708 | 0.00049393
209 | 0.98305 | -0.32413 | 0.0010249 | 0.00025687
210 | 0.98306 | -0.32383 | 0.00087788 | 0.00022002
211 | 0.98308 | -0.32347 | 0.00092402 | 0.00023158
212 | 0.98311 | -0.32302 | 0.0018205 | 0.00045627
213 | 0.97905 | -0.40211 | 0.0013137 | 0.00032924
214 | 0.97907 | -0.40167 | 0.0011141 | 0.00027921
215 | 0.97774 | -0.42786 | 0.0011096 | 0.00027808
216 | 0.97774 | -0.42774 | 0.0011096 | 0.00027808
217 | 0.97775 | -0.42749 | 0.0011096 | 0.00027808
218 | 0.97778 | -0.42695 | 0.0018879 | 0.00047315
219 | 0.9778 | -0.42651 | 0 | 0
220 | 0.97893 | -0.40438 | 0.0011134 | 0.00027904
221 | 0.98278 | -0.32954 | 0.0021013 | 0.00052665
222 | 0.98285 | -0.32808 | 0.0034151 | 0.0008559
223 | 0.98277 | -0.32982 | 0.0022774 | 0.00057076
224 | 0.98295 | -0.32627 | 0.0015387 | 0.00038563
225 | 0.983 | -0.32522 | 0.0015319 | 0.00038394
226 | 0.98306 | -0.324 | 0.0015286 | 0.00038311
227 | 0.98307 | -0.32385 | 0.0040876 | 0.0010245
228 | 0.98315 | -0.32221 | 0.0015218 | 0.00038139
229 | 0.98344 | -0.31656 | 0.0024843 | 0.00062262
230 | 0.98294 | -0.32644 | 0.0023816 | 0.00059689
231 | 0.98261 | -0.33277 | 0.0015361 | 0.00038499
232 | 0.98202 | -0.34428 | 0.0029493 | 0.00073916
233 | 0.98158 | -0.35286 | 0.0028178 | 0.00070621
234 | 0.98129 | -0.35849 | 0 | 0
235 | 0.97997 | -0.38432 | 0 | 0
236 | 0.97993 | -0.38516 | 0.0012848 | 0.00032201
237 | 0.97989 | -0.38594 | 0.0012336 | 0.00030916
238 | 0.97985 | -0.38675 | 0.0011356 | 0.0002846
239 | 0.97989 | -0.38591 | 0.00080832 | 0.00020258
240 | 0.97968 | -0.39004 | 0.0011894 | 0.0002981
241 | 0.97961 | -0.39138 | 0.00056579 | 0.0001418
242 | 0.97958 | -0.39206 | 0.0011264 | 0.00028231
243 | 0.97953 | -0.39305 | 0.0015406 | 0.00038611
244 | 0.97528 | -0.4761 | 0.0018851 | 0.00047246
245 | 0.97521 | -0.47734 | 0.0018849 | 0.0004724
246 | 0.97512 | -0.47917 | 0.0018785 | 0.0004708
247 | 0.97508 | -0.47991 | 0.0018773 | 0.00047051
248 | 0.99846 | -0.029548 | 0.0016295 | 0.0004084
249 | 0.99846 | -0.029667 | 0.0023443 | 0.00058754
250 | 0.99843 | -0.030198 | 0.0023443 | 0.00058754
251 | 0.99842 | -0.030329 | 0.0023138 | 0.00057989
252 | 0.98929 | -0.20465 | 0.0078027 | 0.0019555
253 | 0.98942 | -0.20206 | 0.0026751 | 0.00067045
254 | 0.97791 | -0.42446 | 0.0013813 | 0.00034618
255 | 0.97788 | -0.42511 | 0.0011096 | 0.00027808
256 | 0.97808 | -0.42101 | 0 | 0
257 | 0.97818 | -0.41906 | 0.0010634 | 0.00026651
258 | 0.97806 | -0.42145 | 0.0012569 | 0.00031502
259 | 0.97776 | -0.4274 | 0.0013813 | 0.00034618
260 | 0.97832 | -0.41641 | 0.0013599 | 0.00034081
261 | 0.97804 | -0.42187 | 0.0012566 | 0.00031494
262 | 0.97774 | -0.42774 | 0.0013813 | 0.00034619
263 | 0.97843 | -0.41426 | 0.0013108 | 0.00032851
264 | 0.97803 | -0.42215 | 0.0012574 | 0.00031514
265 | 0.97774 | -0.42779 | 0.0015362 | 0.000385
266 | 0.97855 | -0.41194 | 0.0010814 | 0.00027103
267 | 0.97802 | -0.42226 | 0.0012569 | 0.00031502
268 | 0.9788 | -0.40696 | 0.0011141 | 0.00027921
269 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00087721 | -0.00021985 | 0.00087723 | 0.00021947 | 2.0992e-08 | -3.7969e-07 | 0.0013357 | 0.0013356 | 0.0013357 | 0.97721 | -0.43814 | 0.97724 | -0.43764 | 0.36696
1 | -0.0028768 | -0.00072062 | 0.0028771 | 0.00072037 | 2.235e-07 | -2.4618e-07 | 0.0043803 | 0.0043802 | 0.0043803 | 0.97724 | -0.43764 | 0.97732 | -0.43601 | 1.2034
2 | -0.0047819 | -0.0011978 | 0.0047823 | 0.0011978 | 3.6024e-07 | 3.4248e-09 | 0.0072804 | 0.0072803 | 0.0072804 | 0.97732 | -0.43601 | 0.9774 | -0.43443 | 2.0001
3 | -0.0052707 | -0.0013202 | 0.0052708 | 0.0013202 | 4.4088e-08 | 5.3304e-09 | 0.008024 | 0.008024 | 0.008024 | 0.9774 | -0.43443 | 0.97741 | -0.43425 | 2.2044
4 | -0.011121 | -0.0027856 | 0.011124 | 0.0027875 | 3.6027e-06 | 1.886e-06 | 0.016935 | 0.016935 | 0.016935 | 0.9771 | -0.44077 | 0.97744 | -0.43397 | 4.6525
5 | 0.011121 | 0.0027856 | -0.011116 | -0.0027829 | 5.0837e-06 | 2.6618e-06 | 0.016935 | 0.016935 | 0.016935 | 0.9771 | -0.44077 | 0.97661 | -0.45037 | 4.6525
6 | -0.01168 | -0.0029268 | 0.011684 | 0.0029291 | 4.3465e-06 | 2.3221e-06 | 0.017781 | 0.017781 | 0.017781 | 0.97744 | -0.43397 | 0.97784 | -0.42616 | 4.8849
7 | 0.0053697 | 0.0013448 | -0.005368 | -0.0013445 | 1.7143e-06 | 2.4287e-07 | 0.0081813 | 0.0081816 | 0.0081816 | 0.97661 | -0.45037 | 0.97627 | -0.45708 | 2.2477
8 | 0.0057458 | 0.0014382 | -0.0057453 | -0.001438 | 5.6586e-07 | 1.1579e-07 | 0.008754 | 0.0087541 | 0.0087541 | 0.97661 | -0.45037 | 0.97651 | -0.45244 | 2.405
9 | -0.0058554 | -0.0014667 | 0.0058556 | 0.0014668 | 2.5918e-07 | 5.6855e-08 | 0.008914 | 0.008914 | 0.008914 | 0.97741 | -0.43425 | 0.97746 | -0.43332 | 2.4489
10 | -0.012574 | -0.0031521 | 0.012577 | 0.0031538 | 3.1598e-06 | 1.7335e-06 | 0.019135 | 0.019135 | 0.019135 | 0.97784 | -0.42616 | 0.97811 | -0.42089 | 5.2568
11 | 0.0051096 | 0.0012798 | -0.0051094 | -0.0012797 | 2.7033e-07 | 2.4397e-08 | 0.0077878 | 0.0077878 | 0.0077878 | 0.97627 | -0.45708 | 0.97621 | -0.45819 | 2.1395
12 | 0.0046828 | 0.0011718 | -0.0046825 | -0.0011718 | 2.7122e-07 | -4.1325e-09 | 0.0071351 | 0.0071352 | 0.0071352 | 0.97651 | -0.45244 | 0.97644 | -0.45366 | 1.9602
13 | -0.0011105 | -0.00027833 | 0.0011106 | 0.00027806 | 2.4448e-08 | -2.6864e-07 | 0.001693 | 0.0016929 | 0.001693 | 0.97605 | -0.46147 | 0.97607 | -0.461 | 0.46512
14 | -0.0029041 | -0.00072756 | 0.0029042 | 0.00072739 | 1.6107e-07 | -1.7084e-07 | 0.0044272 | 0.0044271 | 0.0044272 | 0.97607 | -0.461 | 0.97613 | -0.45984 | 1.2163
15 | -0.0061301 | -0.0015356 | 0.0061303 | 0.0015356 | 1.5289e-07 | 3.9165e-08 | 0.0093319 | 0.0093318 | 0.0093319 | 0.97746 | -0.43332 | 0.97748 | -0.4328 | 2.5637
16 | -0.0068767 | -0.0017227 | 0.0068841 | 0.0017251 | 7.381e-06 | 2.4695e-06 | 0.010468 | 0.010467 | 0.010468 | 0.97748 | -0.4328 | 0.97863 | -0.41028 | 2.8758
17 | -0.05386 | -0.01358 | 0.053864 | 0.013583 | 4.4158e-06 | 2.4733e-06 | 0.081924 | 0.081924 | 0.081924 | 0.97863 | -0.41028 | 0.97872 | -0.40856 | 5.6266
18 | 0.046976 | 0.011855 | -0.046913 | -0.011817 | 6.2281e-05 | 3.8227e-05 | 0.071457 | 0.071457 | 0.071457 | 0.97863 | -0.41028 | 0.97721 | -0.438 | 9.8156
19 | -0.053864 | -0.013583 | 0.053873 | 0.013588 | 8.7521e-06 | 4.902e-06 | 0.081924 | 0.081923 | 0.081924 | 0.97872 | -0.40856 | 0.97889 | -0.40517 | 5.6266
20 | 0.0021018 | 0.00052657 | -0.0021017 | -0.00052674 | 6.4373e-08 | -1.6877e-07 | 0.0032003 | 0.0032004 | 0.0032004 | 0.97721 | -0.438 | 0.97718 | -0.43864 | 0.87923
21 | 0.044812 | 0.011291 | -0.044782 | -0.011272 | 2.9914e-05 | 1.893e-05 | 0.068257 | 0.068257 | 0.068257 | 0.97721 | -0.438 | 0.9765 | -0.45196 | 18.7519
22 | -0.0027889 | -0.00069819 | 0.0027889 | 0.00069813 | 5.1633e-08 | -6.2299e-08 | 0.00425 | 0.0042499 | 0.00425 | 0.97638 | -0.45483 | 0.9764 | -0.45444 | 1.1676
23 | 0.0025507 | 0.00063851 | -0.0025507 | -0.00063855 | 2.7184e-08 | -4.2607e-08 | 0.0038871 | 0.0038871 | 0.0038871 | 0.97638 | -0.45483 | 0.97637 | -0.45505 | 1.0679
24 | -0.0034725 | -0.00086946 | 0.0034727 | 0.00086939 | 1.2813e-07 | -7.0615e-08 | 0.0052917 | 0.0052917 | 0.0052917 | 0.9764 | -0.45444 | 0.97644 | -0.45366 | 1.4538
25 | 0.0023122 | 0.00057878 | -0.0023122 | -0.00057882 | 2.2337e-08 | -4.5705e-08 | 0.0035236 | 0.0035236 | 0.0035236 | 0.97637 | -0.45505 | 0.97636 | -0.45525 | 0.96803
26 | 0.0012099 | 0.00030238 | -0.0012098 | -0.00030311 | 7.9884e-08 | -7.3279e-07 | 0.0018435 | 0.0018437 | 0.0018437 | 0.97644 | -0.45366 | 0.97637 | -0.45505 | 0.50652
27 | 0.0020741 | 0.00051915 | -0.002074 | -0.00051923 | 2.9524e-08 | -7.9663e-08 | 0.0031607 | 0.0031608 | 0.0031608 | 0.97636 | -0.45525 | 0.97635 | -0.45555 | 0.86834
28 | 0.00075687 | 0.0001896 | -0.00075687 | -0.00018969 | 3.7986e-09 | -9.2786e-08 | 0.0011535 | 0.0011535 | 0.0011535 | 0.97637 | -0.45505 | 0.97637 | -0.45515 | 0.31689
29 | 0.0016415 | 0.00041082 | -0.0016414 | -0.00041097 | 3.3165e-08 | -1.5552e-07 | 0.0025015 | 0.0025016 | 0.0025016 | 0.97635 | -0.45555 | 0.97633 | -0.45598 | 0.68724
30 | 0.001078 | 0.00026976 | -0.001078 | -0.0002699 | 1.2027e-08 | -1.409e-07 | 0.0016428 | 0.0016429 | 0.0016429 | 0.97633 | -0.45598 | 0.97631 | -0.45621 | 0.45134
31 | 0.0005142 | 0.0001286 | -0.0005142 | -0.00012887 | 4.9645e-09 | -2.664e-07 | 0.00078361 | 0.00078371 | 0.00078371 | 0.97631 | -0.45621 | 0.9763 | -0.45641 | 0.2153
32 | 0.0029045 | 0.00072715 | -0.0029042 | -0.00072739 | 2.2798e-07 | -2.4189e-07 | 0.0044269 | 0.0044271 | 0.0044271 | 0.97621 | -0.45819 | 0.97613 | -0.45984 | 1.2162
33 | -0.012577 | -0.0031538 | 0.012593 | 0.0031623 | 1.5522e-05 | 8.5134e-06 | 0.019135 | 0.019134 | 0.019135 | 0.97811 | -0.42089 | 0.97943 | -0.39502 | 5.2568
34 | -0.013875 | -0.0034837 | 0.013879 | 0.0034859 | 3.9677e-06 | 2.2396e-06 | 0.021082 | 0.021082 | 0.021082 | 0.97943 | -0.39502 | 0.97973 | -0.38903 | 5.7918
35 | -0.0010845 | -0.0002718 | 0.0010845 | 0.00027157 | 1.9392e-08 | -2.274e-07 | 0.0016475 | 0.0016474 | 0.0016475 | 0.9795 | -0.39363 | 0.97952 | -0.39325 | 0.45262
36 | -0.0020495 | -0.00051342 | 0.0020495 | 0.00051337 | 1.9356e-08 | -5.4641e-08 | 0.0031134 | 0.0031134 | 0.0031134 | 0.97952 | -0.39325 | 0.97953 | -0.39305 | 0.85533
37 | -0.015012 | -0.0037699 | 0.015019 | 0.0037738 | 6.7959e-06 | 3.9103e-06 | 0.022803 | 0.022803 | 0.022803 | 0.97973 | -0.38903 | 0.98022 | -0.37954 | 6.2645
38 | -0.017154 | -0.0043088 | 0.017154 | 0.0043089 | 1.9931e-07 | 1.1768e-07 | 0.026043 | 0.026043 | 0.026043 | 0.98022 | -0.37954 | 0.98023 | -0.3793 | 7.1548
39 | -0.055099 | -0.013895 | 0.055103 | 0.013897 | 3.9853e-06 | 2.2461e-06 | 0.083787 | 0.083786 | 0.083787 | 0.97889 | -0.40517 | 0.97897 | -0.40366 | 5.7546
40 | -0.33349 | -0.084834 | 0.33445 | 0.085444 | 0.00095666 | 0.00061017 | 0.502 | 0.502 | 0.502 | 0.9894 | -0.20139 | 0.9925 | -0.14205 | 34.4783
41 | 0.33247 | 0.084579 | -0.33159 | -0.084014 | 0.00088607 | 0.00056515 | 0.50047 | 0.50048 | 0.50048 | 0.9894 | -0.20139 | 0.98652 | -0.25686 | 34.3733
42 | 0.001017 | 0.00025444 | -0.0010169 | -0.00025487 | 3.0425e-08 | -4.2596e-07 | 0.0015293 | 0.0015295 | 0.0015295 | 0.9894 | -0.20139 | 0.98937 | -0.20202 | 0.42019
43 | 0.0076083 | 0.0019067 | -0.0076071 | -0.0019063 | 1.1277e-06 | 4.2311e-07 | 0.011407 | 0.011407 | 0.011407 | 0.9925 | -0.14205 | 0.99234 | -0.14516 | 3.1338
44 | -0.34206 | -0.08735 | 0.34307 | 0.087995 | 0.0010108 | 0.00064479 | 0.51341 | 0.51341 | 0.51341 | 0.9925 | -0.14205 | 0.9957 | -0.081111 | 35.2617
45 | 0.17475 | 0.044256 | -0.17463 | -0.044184 | 0.00011446 | 7.2358e-05 | 0.26375 | 0.26375 | 0.26375 | 0.98652 | -0.25686 | 0.98581 | -0.27051 | 18.1144
46 | 0.15684 | 0.039758 | -0.15674 | -0.039698 | 9.5169e-05 | 5.9983e-05 | 0.23673 | 0.23673 | 0.23673 | 0.98652 | -0.25686 | 0.98587 | -0.26949 | 16.259
47 | 0.043282 | 0.010896 | -0.043248 | -0.010874 | 3.4066e-05 | 2.1541e-05 | 0.065972 | 0.065972 | 0.065972 | 0.9765 | -0.45196 | 0.97566 | -0.46844 | 18.1241
48 | 0.013534 | 0.0033954 | -0.01353 | -0.0033932 | 3.9908e-06 | 2.2291e-06 | 0.020429 | 0.020429 | 0.020429 | 0.98581 | -0.27051 | 0.9855 | -0.27669 | 5.6125
49 | 0.1611 | 0.040788 | -0.16093 | -0.040682 | 0.00016828 | 0.00010615 | 0.24332 | 0.24332 | 0.24332 | 0.98581 | -0.27051 | 0.98469 | -0.29229 | 16.7113
50 | 0.15582 | 0.039467 | -0.15558 | -0.039316 | 0.00023938 | 0.00015085 | 0.23534 | 0.23534 | 0.23534 | 0.98587 | -0.26949 | 0.98421 | -0.30153 | 16.1633
51 | 0.091123 | 0.022962 | -0.09108 | -0.022936 | 4.3821e-05 | 2.6816e-05 | 0.1384 | 0.1384 | 0.1384 | 0.98003 | -0.38283 | 0.97952 | -0.39288 | 9.5056
52 | -0.091123 | -0.022962 | 0.091302 | 0.023071 | 0.00017834 | 0.00010912 | 0.1384 | 0.1384 | 0.1384 | 0.98003 | -0.38283 | 0.98213 | -0.342 | 9.5055
53 | 0.088226 | 0.022221 | -0.088207 | -0.022209 | 1.951e-05 | 1.1903e-05 | 0.13407 | 0.13407 | 0.13407 | 0.97952 | -0.39288 | 0.97928 | -0.39751 | 9.2079
54 | 0.0028531 | 0.00071491 | -0.002853 | -0.00071503 | 1.0664e-07 | -1.2229e-07 | 0.0043342 | 0.0043343 | 0.0043343 | 0.97952 | -0.39288 | 0.97948 | -0.39367 | 1.1907
55 | -0.096719 | -0.024429 | 0.096892 | 0.024535 | 0.00017283 | 0.00010626 | 0.14661 | 0.1466 | 0.14661 | 0.98213 | -0.342 | 0.98404 | -0.30478 | 10.0691
56 | -0.096892 | -0.024535 | 0.096939 | 0.024564 | 4.6953e-05 | 2.8865e-05 | 0.1466 | 0.1466 | 0.1466 | 0.98404 | -0.30478 | 0.98456 | -0.2947 | 10.069
57 | -0.097961 | -0.024821 | 0.097972 | 0.024828 | 1.1337e-05 | 6.9753e-06 | 0.14815 | 0.14815 | 0.14815 | 0.98456 | -0.2947 | 0.98469 | -0.29229 | 10.1751
58 | 0.014141 | 0.0035456 | -0.014137 | -0.0035433 | 4.1087e-06 | 2.3381e-06 | 0.021617 | 0.021617 | 0.021617 | 0.97347 | -0.51166 | 0.97316 | -0.51776 | 5.9387
59 | -0.034419 | -0.0086311 | 0.034443 | 0.0086462 | 2.4018e-05 | 1.5084e-05 | 0.052613 | 0.052613 | 0.052613 | 0.97347 | -0.51166 | 0.97421 | -0.49703 | 14.4542
60 | 0.020277 | 0.0050855 | -0.020271 | -0.0050815 | 6.5731e-06 | 3.9801e-06 | 0.030997 | 0.030997 | 0.030997 | 0.97347 | -0.51166 | 0.97312 | -0.51847 | 8.5156
61 | 0.0073545 | 0.0018433 | -0.0073542 | -0.0018431 | 3.2646e-07 | 1.2341e-07 | 0.011246 | 0.011246 | 0.011246 | 0.97316 | -0.51776 | 0.97311 | -0.51869 | 3.0894
62 | 0.0067828 | 0.0017 | -0.0067818 | -0.0016997 | 9.5021e-07 | 3.155e-07 | 0.010371 | 0.010371 | 0.010371 | 0.97316 | -0.51776 | 0.97301 | -0.5207 | 2.8493
63 | -0.04078 | -0.010234 | 0.040835 | 0.01027 | 5.5685e-05 | 3.5161e-05 | 0.062292 | 0.062292 | 0.062292 | 0.97421 | -0.49703 | 0.97566 | -0.46844 | 17.1132
64 | 0.013495 | 0.0033833 | -0.01349 | -0.0033806 | 4.9411e-06 | 2.7781e-06 | 0.020636 | 0.020636 | 0.020636 | 0.97312 | -0.51847 | 0.97273 | -0.52615 | 5.6692
65 | 0.037443 | 0.009391 | -0.037425 | -0.0093795 | 1.8228e-05 | 1.1475e-05 | 0.056778 | 0.056778 | 0.056778 | 0.98133 | -0.35772 | 0.98081 | -0.36794 | 15.5984
66 | -0.042026 | -0.01054 | 0.042139 | 0.010611 | 0.00011289 | 7.1308e-05 | 0.063728 | 0.063728 | 0.063728 | 0.98133 | -0.35772 | 0.98421 | -0.30153 | 17.5077
67 | 0.0045836 | 0.0011486 | -0.0045832 | -0.0011487 | 3.4523e-07 | -1.9816e-08 | 0.0069502 | 0.0069502 | 0.0069502 | 0.98133 | -0.35772 | 0.98125 | -0.35931 | 1.9094
68 | 0.11344 | 0.028705 | -0.11334 | -0.028643 | 9.9614e-05 | 6.1921e-05 | 0.17161 | 0.17161 | 0.17161 | 0.98421 | -0.30153 | 0.98327 | -0.31985 | 11.7864
69 | 0.011507 | 0.0028862 | -0.011501 | -0.0028834 | 5.2301e-06 | 2.7589e-06 | 0.017375 | 0.017375 | 0.017375 | 0.9855 | -0.27669 | 0.98501 | -0.28623 | 4.7734
70 | 0.062959 | 0.015854 | -0.062909 | -0.015823 | 4.9614e-05 | 3.1567e-05 | 0.095168 | 0.095168 | 0.095168 | 0.98469 | -0.29229 | 0.98384 | -0.30878 | 26.145
71 | 0.022993 | 0.005768 | -0.022986 | -0.0057636 | 7.0868e-06 | 4.3372e-06 | 0.034778 | 0.034778 | 0.034778 | 0.98384 | -0.30878 | 0.98351 | -0.31525 | 9.5545
72 | 0.039916 | 0.010055 | -0.039886 | -0.010036 | 2.9794e-05 | 1.8792e-05 | 0.06039 | 0.06039 | 0.06039 | 0.98384 | -0.30878 | 0.98304 | -0.3244 | 16.5906
73 | -0.00098227 | -0.00024596 | 0.00098227 | 0.00024593 | 2.0951e-09 | -3.2386e-08 | 0.0014679 | 0.0014679 | 0.0014679 | 0.9957 | -0.081156 | 0.9957 | -0.081111 | 0.40326
74 | 0.00098227 | 0.00024596 | -0.00098225 | -0.00024618 | 1.3787e-08 | -2.131e-07 | 0.0014679 | 0.0014679 | 0.0014679 | 0.9957 | -0.081156 | 0.99568 | -0.081451 | 0.40328
75 | -0.34405 | -0.088241 | 0.34494 | 0.088807 | 0.00088775 | 0.0005663 | 0.51488 | 0.51488 | 0.51488 | 0.9957 | -0.081111 | 0.99851 | -0.02806 | 35.3624
76 | 0.10575 | 0.026741 | -0.10571 | -0.026711 | 4.8023e-05 | 2.9722e-05 | 0.16013 | 0.16013 | 0.16013 | 0.98327 | -0.31985 | 0.98278 | -0.32932 | 10.9977
77 | 0.0075886 | 0.0019018 | -0.0075878 | -0.0019015 | 8.1908e-07 | 3.1417e-07 | 0.011484 | 0.011484 | 0.011484 | 0.98327 | -0.31985 | 0.98315 | -0.32211 | 3.155
78 | -0.056604 | -0.014274 | 0.056608 | 0.014276 | 3.3355e-06 | 1.8931e-06 | 0.086069 | 0.086069 | 0.086069 | 0.97897 | -0.40366 | 0.97903 | -0.40243 | 5.9113
79 | 0.026333 | 0.0066087 | -0.026331 | -0.0066076 | 1.673e-06 | 1.0357e-06 | 0.040016 | 0.040016 | 0.040016 | 0.97928 | -0.39751 | 0.97921 | -0.39884 | 10.9935
80 | 0.061874 | 0.0156 | -0.061865 | -0.015595 | 8.6542e-06 | 5.0136e-06 | 0.094051 | 0.094051 | 0.094051 | 0.97928 | -0.39751 | 0.97913 | -0.40043 | 6.4595
81 | 0.0038034 | 0.000953 | -0.0038031 | -0.00095315 | 3.364e-07 | -1.4096e-07 | 0.0057032 | 0.0057033 | 0.0057033 | 0.99234 | -0.14516 | 0.99224 | -0.14702 | 1.5668
82 | -0.3468 | -0.089275 | 0.34715 | 0.089497 | 0.0003471 | 0.00022142 | 0.51766 | 0.51766 | 0.51766 | 0.99851 | -0.02806 | 0.9996 | -0.007507 | 35.5534
83 | 0.0076133 | 0.0019077 | -0.0076131 | -0.0019076 | 2.5435e-07 | 1.0071e-07 | 0.011646 | 0.011646 | 0.011646 | 0.97273 | -0.52615 | 0.9727 | -0.52685 | 3.1995
84 | 0.01001 | 0.0025097 | -0.010006 | -0.0025078 | 3.7267e-06 | 1.8322e-06 | 0.015122 | 0.015122 | 0.015122 | 0.98501 | -0.28623 | 0.98461 | -0.29405 | 4.1545
85 | 0.020496 | 0.0051396 | -0.020495 | -0.0051388 | 1.2791e-06 | 7.736e-07 | 0.031011 | 0.031011 | 0.031011 | 0.98351 | -0.31525 | 0.98344 | -0.31656 | 8.5196
86 | 0.037859 | 0.0095281 | -0.037856 | -0.0095257 | 3.6809e-06 | 2.3179e-06 | 0.057321 | 0.057321 | 0.057321 | 0.98304 | -0.3244 | 0.98294 | -0.32644 | 15.7476
87 | 0.10475 | 0.026473 | -0.10474 | -0.026465 | 1.3061e-05 | 8.0784e-06 | 0.15869 | 0.15869 | 0.15869 | 0.98278 | -0.32932 | 0.98265 | -0.33192 | 10.8987
88 | 0.0066187 | 0.0016587 | -0.0066184 | -0.0016586 | 2.8654e-07 | 8.6833e-08 | 0.010017 | 0.010017 | 0.010017 | 0.98315 | -0.32211 | 0.98311 | -0.32302 | 2.7521
89 | -0.059495 | -0.014999 | 0.059496 | 0.015 | 8.9384e-07 | 5.1345e-07 | 0.090458 | 0.090458 | 0.090458 | 0.97903 | -0.40243 | 0.97905 | -0.40211 | 6.2128
90 | 0.025217 | 0.0063284 | -0.025214 | -0.0063263 | 3.4014e-06 | 2.0992e-06 | 0.038323 | 0.038323 | 0.038323 | 0.97921 | -0.39884 | 0.97907 | -0.40167 | 10.5284
91 | 0.060815 | 0.015332 | -0.06081 | -0.015329 | 4.8883e-06 | 2.8217e-06 | 0.092454 | 0.092454 | 0.092454 | 0.97913 | -0.40043 | 0.97905 | -0.40211 | 6.3499
92 | 0.010939 | 0.0027411 | -0.010937 | -0.0027398 | 2.6127e-06 | 1.3537e-06 | 0.016606 | 0.016606 | 0.016606 | 0.98023 | -0.3793 | 0.97997 | -0.38432 | 4.5622
93 | -0.028093 | -0.0070501 | 0.028121 | 0.0070674 | 2.7909e-05 | 1.7345e-05 | 0.04265 | 0.042649 | 0.04265 | 0.98023 | -0.3793 | 0.98129 | -0.35849 | 11.7169
94 | 0.010963 | 0.0027444 | -0.01096 | -0.0027431 | 2.5335e-06 | 1.3125e-06 | 0.016621 | 0.016621 | 0.016621 | 0.98139 | -0.35808 | 0.98114 | -0.36294 | 4.5662
95 | -0.013355 | -0.003344 | 0.013362 | 0.0033479 | 7.0711e-06 | 3.944e-06 | 0.020248 | 0.020248 | 0.020248 | 0.98139 | -0.35808 | 0.98195 | -0.34697 | 5.5627
96 | 0.010091 | 0.0025253 | -0.01009 | -0.0025246 | 1.4363e-06 | 7.1273e-07 | 0.015303 | 0.015303 | 0.015303 | 0.98114 | -0.36294 | 0.98099 | -0.36593 | 4.2042
97 | -0.019492 | -0.0048842 | 0.019523 | 0.004903 | 3.1278e-05 | 1.8806e-05 | 0.029537 | 0.029536 | 0.029537 | 0.98195 | -0.34697 | 0.98367 | -0.31333 | 8.1145
98 | 0.0061298 | 0.0015363 | -0.0061287 | -0.001536 | 1.0872e-06 | 2.7085e-07 | 0.0092888 | 0.009289 | 0.009289 | 0.98195 | -0.34697 | 0.98176 | -0.35069 | 2.5519
99 | 0.0085412 | 0.0021365 | -0.0085409 | -0.0021363 | 3.7527e-07 | 1.6489e-07 | 0.012954 | 0.012954 | 0.012954 | 0.98099 | -0.36593 | 0.98094 | -0.36685 | 3.5589
100 | -0.083122 | -0.020897 | 0.083406 | 0.021078 | 0.00028466 | 0.00018157 | 0.12576 | 0.12576 | 0.12576 | 0.98367 | -0.31333 | 0.98735 | -0.24188 | 34.5501
101 | 0.063599 | 0.015994 | -0.063538 | -0.015955 | 6.056e-05 | 3.8538e-05 | 0.096226 | 0.096226 | 0.096226 | 0.98367 | -0.31333 | 0.98265 | -0.33329 | 26.4357
102 | 0.007361 | 0.0018406 | -0.0073605 | -0.0018405 | 4.8829e-07 | 1.8064e-07 | 0.011165 | 0.011165 | 0.011165 | 0.98094 | -0.36685 | 0.98087 | -0.36825 | 3.0672
103 | -0.083406 | -0.021078 | 0.083591 | 0.021196 | 0.00018436 | 0.00011759 | 0.12576 | 0.12576 | 0.12576 | 0.98735 | -0.24188 | 0.98974 | -0.19589 | 34.55
104 | 0.061482 | 0.01544 | -0.061441 | -0.015414 | 4.0925e-05 | 2.6033e-05 | 0.093112 | 0.093112 | 0.093112 | 0.98265 | -0.33329 | 0.98194 | -0.34725 | 25.5802
105 | 0.005679 | 0.001419 | -0.0056787 | -0.001419 | 2.6231e-07 | 4.889e-08 | 0.0086138 | 0.0086138 | 0.0086138 | 0.98087 | -0.36825 | 0.98082 | -0.36922 | 2.3664
106 | -0.086132 | -0.021833 | 0.086169 | 0.021856 | 3.679e-05 | 2.347e-05 | 0.12958 | 0.12958 | 0.12958 | 0.98974 | -0.19589 | 0.9902 | -0.18701 | 35.5995
107 | 0.047246 | 0.011855 | -0.047243 | -0.011853 | 3.3067e-06 | 2.0946e-06 | 0.071601 | 0.071601 | 0.071601 | 0.98194 | -0.34725 | 0.98186 | -0.34872 | 19.6707
108 | 0.014195 | 0.0035587 | -0.014192 | -0.0035574 | 2.1465e-06 | 1.2173e-06 | 0.021511 | 0.021511 | 0.021511 | 0.98194 | -0.34725 | 0.98178 | -0.35043 | 5.9095
109 | 0.0040845 | 0.0010194 | -0.0040844 | -0.0010195 | 1.5154e-07 | -3.5893e-08 | 0.0061952 | 0.0061952 | 0.0061952 | 0.98082 | -0.36922 | 0.98078 | -0.37 | 1.702
110 | 0.019158 | 0.004806 | -0.019146 | -0.0047992 | 1.143e-05 | 6.8424e-06 | 0.028791 | 0.028791 | 0.028791 | 0.9902 | -0.18701 | 0.98955 | -0.19953 | 7.9096
111 | -0.10533 | -0.026662 | 0.10539 | 0.0267 | 5.9347e-05 | 3.7901e-05 | 0.15837 | 0.15837 | 0.15837 | 0.9902 | -0.18701 | 0.99081 | -0.17528 | 43.5091
112 | 0.0014926 | 0.00037203 | -0.0014925 | -0.00037271 | 1.1465e-07 | -6.7836e-07 | 0.0022645 | 0.0022648 | 0.0022648 | 0.98045 | -0.3765 | 0.98037 | -0.37811 | 0.62219
113 | -0.0014926 | -0.00037203 | 0.0014928 | 0.00037074 | 2.1703e-07 | -1.2849e-06 | 0.0022645 | 0.002264 | 0.0022645 | 0.98045 | -0.3765 | 0.98061 | -0.37343 | 0.62212
114 | 0.0014925 | 0.00037271 | -0.0014922 | -0.00037399 | 2.1703e-07 | -1.2833e-06 | 0.0022648 | 0.0022653 | 0.0022653 | 0.98037 | -0.37811 | 0.98021 | -0.38117 | 0.62233
115 | -0.0026029 | -0.00064895 | 0.0026032 | 0.00064848 | 3.1381e-07 | -4.7642e-07 | 0.0039485 | 0.0039482 | 0.0039485 | 0.98061 | -0.37343 | 0.98073 | -0.37089 | 1.0847
116 | 0.030553 | 0.0076682 | -0.030536 | -0.0076575 | 1.7085e-05 | 1.0666e-05 | 0.046307 | 0.046307 | 0.046307 | 0.98186 | -0.34872 | 0.98126 | -0.36045 | 12.7217
117 | 0.01669 | 0.004185 | -0.016687 | -0.0041833 | 2.7577e-06 | 1.6196e-06 | 0.025294 | 0.025294 | 0.025294 | 0.98186 | -0.34872 | 0.98169 | -0.35219 | 6.949
118 | 0.012169 | 0.0030504 | -0.012168 | -0.0030496 | 1.4217e-06 | 7.6897e-07 | 0.018444 | 0.018444 | 0.018444 | 0.98178 | -0.35043 | 0.98165 | -0.35288 | 5.0671
119 | 0.0035369 | 0.00088226 | -0.0035368 | -0.00088234 | 1.4826e-07 | -7.8471e-08 | 0.0053646 | 0.0053647 | 0.0053647 | 0.98078 | -0.37 | 0.98073 | -0.37089 | 1.4738
120 | 0.00093359 | 0.00023386 | -0.00093358 | -0.00023398 | 7.2701e-09 | -1.1728e-07 | 0.0014164 | 0.0014165 | 0.0014165 | 0.98073 | -0.37089 | 0.98073 | -0.37105 | 0.38915
121 | 0.010165 | 0.0025475 | -0.010164 | -0.0025474 | 1.2432e-07 | 6.2583e-08 | 0.015558 | 0.015558 | 0.015558 | 0.97215 | -0.53779 | 0.97213 | -0.53804 | 4.2743
122 | -0.011807 | -0.002959 | 0.011812 | 0.0029621 | 5.7343e-06 | 3.0891e-06 | 0.018072 | 0.018071 | 0.018072 | 0.97215 | -0.53779 | 0.97266 | -0.5276 | 4.9647
123 | 0.0046759 | 0.0011719 | -0.0046758 | -0.0011719 | 4.4788e-08 | -2.4273e-10 | 0.0071572 | 0.0071572 | 0.0071572 | 0.97213 | -0.53804 | 0.97212 | -0.53824 | 1.9663
124 | -0.011812 | -0.0029621 | 0.011819 | 0.0029655 | 6.2841e-06 | 3.3846e-06 | 0.018071 | 0.018071 | 0.018071 | 0.97266 | -0.5276 | 0.97323 | -0.51644 | 4.9647
125 | -0.012939 | -0.0032462 | 0.012949 | 0.0032519 | 1.0222e-05 | 5.6762e-06 | 0.019784 | 0.019784 | 0.019784 | 0.97323 | -0.51644 | 0.97407 | -0.49988 | 5.4352
126 | -0.012949 | -0.0032519 | 0.012974 | 0.0032656 | 2.4746e-05 | 1.3734e-05 | 0.019784 | 0.019783 | 0.019784 | 0.97407 | -0.49988 | 0.9761 | -0.4599 | 5.4351
127 | 0.018839 | 0.0047255 | -0.018834 | -0.0047225 | 5.033e-06 | 3.0178e-06 | 0.028721 | 0.028721 | 0.028721 | 0.9761 | -0.4599 | 0.97582 | -0.46551 | 7.8903
128 | -0.031813 | -0.0079911 | 0.031822 | 0.007997 | 9.3674e-06 | 5.8624e-06 | 0.048504 | 0.048503 | 0.048504 | 0.9761 | -0.4599 | 0.97641 | -0.45373 | 13.3251
129 | 0.016949 | 0.0042501 | -0.016947 | -0.004249 | 1.7982e-06 | 1.0612e-06 | 0.025846 | 0.025847 | 0.025847 | 0.97582 | -0.46551 | 0.9757 | -0.46773 | 7.1007
130 | -0.040885 | -0.010268 | 0.040918 | 0.010289 | 3.3014e-05 | 2.0845e-05 | 0.062314 | 0.062314 | 0.062314 | 0.97641 | -0.45373 | 0.97727 | -0.43683 | 17.1193
131 | -0.047201 | -0.011864 | 0.04725 | 0.011895 | 4.9584e-05 | 3.1413e-05 | 0.071881 | 0.071881 | 0.071881 | 0.97727 | -0.43683 | 0.9784 | -0.41485 | 19.7475
132 | -0.082758 | -0.020817 | 0.0829 | 0.020908 | 0.0001419 | 9.0514e-05 | 0.12589 | 0.12589 | 0.12589 | 0.9784 | -0.41485 | 0.98023 | -0.37902 | 34.5856
133 | 0.035508 | 0.0089222 | -0.035466 | -0.0088959 | 4.1806e-05 | 2.6277e-05 | 0.054011 | 0.054011 | 0.054011 | 0.9784 | -0.41485 | 0.97714 | -0.43954 | 14.8382
134 | -0.084598 | -0.021334 | 0.084708 | 0.021403 | 0.00010917 | 6.9648e-05 | 0.12847 | 0.12847 | 0.12847 | 0.98023 | -0.37902 | 0.98161 | -0.3521 | 35.294
135 | 0.027481 | 0.0068947 | -0.027481 | -0.0068944 | 5.207e-07 | 3.2332e-07 | 0.041852 | 0.041852 | 0.041852 | 0.97714 | -0.43954 | 0.97712 | -0.43994 | 11.4977
136 | 0.015062 | 0.0037766 | -0.01506 | -0.0037751 | 2.6706e-06 | 1.5406e-06 | 0.022972 | 0.022972 | 0.022972 | 0.9757 | -0.46773 | 0.97551 | -0.47146 | 6.311
137 | -0.1024 | -0.025839 | 0.10247 | 0.025885 | 7.1654e-05 | 4.5758e-05 | 0.15529 | 0.15529 | 0.15529 | 0.98161 | -0.3521 | 0.98236 | -0.3375 | 42.661
138 | 0.017689 | 0.004436 | -0.017686 | -0.0044338 | 3.5902e-06 | 2.1295e-06 | 0.026816 | 0.026816 | 0.026816 | 0.98161 | -0.3521 | 0.98139 | -0.35636 | 7.3671
139 | 0.021886 | 0.0054923 | -0.02187 | -0.0054823 | 1.6488e-05 | 1.0057e-05 | 0.033332 | 0.033333 | 0.033333 | 0.97712 | -0.43994 | 0.97631 | -0.45575 | 9.1573
140 | 0.013174 | 0.0033025 | -0.013173 | -0.0033019 | 1.0869e-06 | 6.0604e-07 | 0.020096 | 0.020096 | 0.020096 | 0.97551 | -0.47146 | 0.97543 | -0.47319 | 5.5208
141 | -0.10247 | -0.025885 | 0.10249 | 0.025898 | 2.0657e-05 | 1.296e-05 | 0.15529 | 0.15529 | 0.15529 | 0.98236 | -0.3375 | 0.98258 | -0.33329 | 14.2203
142 | 0.013328 | 0.0033417 | -0.013324 | -0.0033397 | 3.4725e-06 | 1.936e-06 | 0.020209 | 0.020209 | 0.020209 | 0.98139 | -0.35636 | 0.98111 | -0.36183 | 5.5519
143 | 0.014439 | 0.0036199 | -0.014435 | -0.0036178 | 3.6795e-06 | 2.1016e-06 | 0.022007 | 0.022007 | 0.022007 | 0.97631 | -0.45575 | 0.97604 | -0.4611 | 6.0459
144 | 0.011287 | 0.0028291 | -0.011285 | -0.0028283 | 1.5673e-06 | 8.271e-07 | 0.017218 | 0.017218 | 0.017218 | 0.97543 | -0.47319 | 0.97528 | -0.4761 | 4.7303
145 | -0.0014648 | -0.0003671 | 0.0014648 | 0.00036685 | 4.1833e-08 | -2.4878e-07 | 0.0022413 | 0.0022412 | 0.0022413 | 0.97248 | -0.53106 | 0.97251 | -0.53046 | 0.61573
146 | -0.0039485 | -0.00098933 | 0.0039487 | 0.00098927 | 2.1955e-07 | -5.8539e-08 | 0.0060414 | 0.0060413 | 0.0060414 | 0.97251 | -0.53046 | 0.97257 | -0.52929 | 1.6597
147 | -0.0060399 | -0.0015134 | 0.0060406 | 0.0015136 | 7.0075e-07 | 1.7688e-07 | 0.0092408 | 0.0092407 | 0.0092408 | 0.97257 | -0.52929 | 0.9727 | -0.52685 | 2.5387
148 | -0.10378 | -0.02622 | 0.10378 | 0.026225 | 6.8421e-06 | 4.2294e-06 | 0.15723 | 0.15723 | 0.15723 | 0.98258 | -0.33329 | 0.98265 | -0.33192 | 10.7991
149 | 0.0089852 | 0.0022522 | -0.0089833 | -0.0022513 | 1.9578e-06 | 8.9807e-07 | 0.013628 | 0.013628 | 0.013628 | 0.98111 | -0.36183 | 0.98088 | -0.3664 | 3.7439
150 | -0.0035258 | -0.00088346 | 0.003526 | 0.00088337 | 1.3542e-07 | -8.4292e-08 | 0.0052554 | 0.0052553 | 0.0052554 | 0.9983 | -0.032725 | 0.99834 | -0.031919 | 1.4438
151 | 0.0016595 | 0.00041571 | -0.0016595 | -0.0004159 | 3.7345e-08 | -1.889e-07 | 0.0024735 | 0.0024736 | 0.0024736 | 0.9983 | -0.032725 | 0.99827 | -0.033198 | 0.67956
152 | 0.0015627 | 0.0003916 | -0.0015627 | -0.00039166 | 9.683e-09 | -5.6036e-08 | 0.0023292 | 0.0023292 | 0.0023292 | 0.99834 | -0.031919 | 0.99833 | -0.032049 | 0.6399
153 | -0.0050887 | -0.001275 | 0.0050888 | 0.001275 | 1.2929e-07 | 4.3742e-09 | 0.0075845 | 0.0075845 | 0.0075845 | 0.99834 | -0.031919 | 0.99837 | -0.031385 | 2.0837
154 | -0.006652 | -0.0016668 | 0.0066527 | 0.001667 | 6.8883e-07 | 1.9646e-07 | 0.0099144 | 0.0099143 | 0.0099144 | 0.99837 | -0.031385 | 0.99848 | -0.029211 | 2.7237
155 | -0.0083263 | -0.0020864 | 0.0083266 | 0.0020865 | 3.1795e-07 | 1.3146e-07 | 0.012408 | 0.012408 | 0.012408 | 0.99848 | -0.029211 | 0.99852 | -0.02841 | 3.4089
156 | -0.011616 | -0.0029107 | 0.011617 | 0.002911 | 6.1396e-07 | 3.2146e-07 | 0.017311 | 0.017311 | 0.017311 | 0.99852 | -0.02841 | 0.99858 | -0.0273 | 4.7557
157 | 0.0032897 | 0.00082417 | -0.0032896 | -0.00082427 | 1.1354e-07 | -9.2127e-08 | 0.0049022 | 0.0049023 | 0.0049023 | 0.99852 | -0.02841 | 0.99848 | -0.029134 | 1.3468
158 | -0.013291 | -0.0033305 | 0.013292 | 0.0033313 | 1.4547e-06 | 8.016e-07 | 0.019804 | 0.019804 | 0.019804 | 0.99858 | -0.0273 | 0.9987 | -0.025002 | 5.4408
159 | 0.0016296 | 0.00040823 | -0.0016295 | -0.0004084 | 3.2127e-08 | -1.6945e-07 | 0.0024284 | 0.0024285 | 0.0024285 | 0.99848 | -0.029134 | 0.99846 | -0.029548 | 0.66717
160 | 0.0052097 | 0.0013056 | -0.0052093 | -0.0013055 | 3.9883e-07 | 2.3842e-08 | 0.0077584 | 0.0077584 | 0.0077584 | 0.99919 | -0.015603 | 0.9991 | -0.01721 | 2.1314
161 | -0.0080885 | -0.002027 | 0.008089 | 0.0020273 | 5.1759e-07 | 2.0665e-07 | 0.012046 | 0.012045 | 0.012046 | 0.99919 | -0.015603 | 0.99926 | -0.014259 | 3.3092
162 | 0.0026189 | 0.00065632 | -0.0026189 | -0.00065636 | 2.1591e-08 | -3.5742e-08 | 0.0039005 | 0.0039005 | 0.0039005 | 0.9991 | -0.01721 | 0.9991 | -0.017383 | 1.0716
163 | 0.025896 | 0.0064951 | -0.025883 | -0.0064869 | 1.3254e-05 | 8.1714e-06 | 0.038564 | 0.038564 | 0.038564 | 0.99926 | -0.014259 | 0.9987 | -0.025002 | 10.5945
164 | -0.033985 | -0.0085224 | 0.034008 | 0.0085368 | 2.3113e-05 | 1.4477e-05 | 0.050609 | 0.050609 | 0.050609 | 0.99926 | -0.014259 | 1 | 0 | 13.9036
165 | 0.012591 | 0.0031557 | -0.012589 | -0.0031548 | 1.5221e-06 | 8.2327e-07 | 0.018759 | 0.018759 | 0.018759 | 0.9987 | -0.025002 | 0.99857 | -0.02754 | 5.1537
166 | 0.14251 | 0.036389 | -0.14244 | -0.036349 | 6.369e-05 | 4.0564e-05 | 0.21229 | 0.21229 | 0.21229 | 1 | 0 | 0.99951 | -0.0092512 | 29.1612
167 | 0.34903 | 0.090016 | -0.3489 | -0.089935 | 0.00012759 | 8.1396e-05 | 0.52026 | 0.52026 | 0.52026 | 1 | 0 | 0.9996 | -0.007507 | 35.7321
168 | 0.011168 | 0.0027988 | -0.011168 | -0.0027986 | 3.3637e-07 | 1.7291e-07 | 0.016643 | 0.016643 | 0.016643 | 0.99857 | -0.02754 | 0.99853 | -0.028173 | 4.5722
169 | 0.11818 | 0.030256 | -0.11793 | -0.030102 | 0.00024127 | 0.00015414 | 0.17616 | 0.17616 | 0.17616 | 0.99951 | -0.0092512 | 0.99728 | -0.051498 | 48.3955
170 | 0.024269 | 0.0060929 | -0.024254 | -0.0060838 | 1.4744e-05 | 9.0417e-06 | 0.036134 | 0.036134 | 0.036134 | 0.99951 | -0.0092512 | 0.99885 | -0.021995 | 9.927
171 | 0.007194 | 0.0018029 | -0.0071937 | -0.0018028 | 3.111e-07 | 1.0468e-07 | 0.01072 | 0.01072 | 0.01072 | 0.99853 | -0.028173 | 0.99849 | -0.02908 | 2.9452
172 | 0.0039742 | 0.00099576 | -0.003974 | -0.00099583 | 1.8061e-07 | -6.403e-08 | 0.0059222 | 0.0059223 | 0.0059223 | 0.99853 | -0.028173 | 0.99849 | -0.029127 | 1.627
173 | 0.11332 | 0.028945 | -0.11313 | -0.028821 | 0.0001938 | 0.0001238 | 0.16927 | 0.16927 | 0.16927 | 0.99728 | -0.051498 | 0.99542 | -0.086939 | 46.504
174 | 0.021719 | 0.0054484 | -0.021716 | -0.0054466 | 2.96e-06 | 1.7957e-06 | 0.032357 | 0.032357 | 0.032357 | 0.99885 | -0.021995 | 0.9987 | -0.024854 | 8.8894
175 | 0.0046584 | 0.0011674 | -0.0046581 | -0.0011674 | 2.4797e-07 | -2.075e-08 | 0.0069422 | 0.0069422 | 0.0069422 | 0.99849 | -0.02908 | 0.99843 | -0.030198 | 1.9072
176 | 0.0023444 | 0.00058741 | -0.0023443 | -0.00058754 | 6.0371e-08 | -1.3386e-07 | 0.0034937 | 0.0034938 | 0.0034938 | 0.99849 | -0.029127 | 0.99846 | -0.029667 | 0.95983
177 | 0.11313 | 0.028821 | -0.11295 | -0.028711 | 0.00017239 | 0.00011012 | 0.16927 | 0.16927 | 0.16927 | 0.99542 | -0.086939 | 0.99376 | -0.11858 | 46.504
178 | 0.0194 | 0.0048661 | -0.019393 | -0.0048619 | 6.9553e-06 | 4.1611e-06 | 0.028906 | 0.028906 | 0.028906 | 0.9987 | -0.024854 | 0.99831 | -0.032378 | 7.9413
179 | 0.11295 | 0.028711 | -0.11293 | -0.028698 | 2.1061e-05 | 1.3454e-05 | 0.16927 | 0.16927 | 0.16927 | 0.99376 | -0.11858 | 0.99356 | -0.12245 | 46.504
180 | 0.016832 | 0.0042201 | -0.016828 | -0.0042179 | 3.7811e-06 | 2.2105e-06 | 0.025089 | 0.025089 | 0.025089 | 0.99831 | -0.032378 | 0.99806 | -0.037093 | 6.8927
181 | 0.010127 | 0.0025382 | -0.010127 | -0.0025382 | 3.6901e-08 | 1.8338e-08 | 0.015351 | 0.015351 | 0.015351 | 0.98165 | -0.35288 | 0.98165 | -0.35295 | 4.2174
182 | 0.0081079 | 0.0020321 | -0.0081071 | -0.0020317 | 8.5123e-07 | 3.5483e-07 | 0.01229 | 0.01229 | 0.01229 | 0.98165 | -0.35295 | 0.98153 | -0.35516 | 3.3765
183 | 0.0062067 | 0.0015555 | -0.0062067 | -0.0015555 | 6.5822e-09 | 1.7069e-09 | 0.0094094 | 0.0094094 | 0.0094094 | 0.98153 | -0.35516 | 0.98153 | -0.35518 | 2.585
184 | 0.024304 | 0.0060959 | -0.024296 | -0.0060907 | 8.4469e-06 | 5.1966e-06 | 0.036858 | 0.036858 | 0.036858 | 0.98126 | -0.36045 | 0.98089 | -0.36775 | 10.1257
185 | 0.0062315 | 0.0015616 | -0.0062312 | -0.0015615 | 2.8734e-07 | 7.5505e-08 | 0.0094495 | 0.0094496 | 0.0094496 | 0.98126 | -0.36045 | 0.98121 | -0.36142 | 2.596
186 | 0.01428 | 0.0035801 | -0.014278 | -0.0035789 | 2.0042e-06 | 1.1385e-06 | 0.021646 | 0.021646 | 0.021646 | 0.98169 | -0.35219 | 0.98154 | -0.35513 | 5.9466
187 | 0.0041968 | 0.0010517 | -0.0041966 | -0.0010518 | 1.659e-07 | -3.1952e-08 | 0.0063623 | 0.0063624 | 0.0063624 | 0.98153 | -0.35518 | 0.98149 | -0.35601 | 1.7479
188 | 0.013707 | 0.0034366 | -0.013705 | -0.0034352 | 2.498e-06 | 1.4043e-06 | 0.020794 | 0.020794 | 0.020794 | 0.98089 | -0.36775 | 0.9807 | -0.37157 | 5.7127
189 | 0.010589 | 0.0026541 | -0.010588 | -0.0026537 | 8.0506e-07 | 4.1023e-07 | 0.016064 | 0.016064 | 0.016064 | 0.98089 | -0.36775 | 0.98081 | -0.36934 | 4.4131
190 | 0.0041246 | 0.0010335 | -0.0041243 | -0.0010336 | 2.4771e-07 | -5.4712e-08 | 0.0062548 | 0.0062549 | 0.0062549 | 0.98121 | -0.36142 | 0.98115 | -0.36268 | 1.7184
191 | 0.0118 | 0.002958 | -0.011799 | -0.0029573 | 1.1767e-06 | 6.2918e-07 | 0.01789 | 0.01789 | 0.01789 | 0.98154 | -0.35513 | 0.98143 | -0.35723 | 4.9148
192 | 0.0020645 | 0.0005174 | -0.0020645 | -0.00051741 | 1.1646e-09 | -3.2623e-09 | 0.0031299 | 0.0031299 | 0.0031299 | 0.98149 | -0.35601 | 0.98149 | -0.35602 | 0.85987
193 | 0.011642 | 0.0029184 | -0.011641 | -0.0029179 | 9.3626e-07 | 4.9827e-07 | 0.017665 | 0.017665 | 0.017665 | 0.9807 | -0.37157 | 0.98061 | -0.37326 | 4.8531
194 | 0.0082617 | 0.0020707 | -0.0082611 | -0.0020704 | 6.8454e-07 | 2.9148e-07 | 0.012534 | 0.012534 | 0.012534 | 0.98081 | -0.36934 | 0.98072 | -0.37108 | 3.4435
195 | 0.0020594 | 0.00051604 | -0.0020594 | -0.00051612 | 2.8174e-08 | -7.9239e-08 | 0.0031232 | 0.0031233 | 0.0031233 | 0.98115 | -0.36268 | 0.98113 | -0.36297 | 0.85804
196 | 0.0094848 | 0.0023773 | -0.0094838 | -0.0023768 | 1.0716e-06 | 5.1125e-07 | 0.014381 | 0.014381 | 0.014381 | 0.98143 | -0.35723 | 0.98131 | -0.3596 | 3.9508
197 | 0.0095687 | 0.0023984 | -0.0095678 | -0.002398 | 8.9585e-07 | 4.3041e-07 | 0.01452 | 0.01452 | 0.01452 | 0.98061 | -0.37326 | 0.98051 | -0.37522 | 3.989
198 | 0.0062357 | 0.0015628 | -0.0062352 | -0.0015627 | 5.1719e-07 | 1.3661e-07 | 0.0094613 | 0.0094614 | 0.0094614 | 0.98072 | -0.37108 | 0.98063 | -0.37282 | 2.5993
199 | 0.0073935 | 0.001853 | -0.0073927 | -0.0018528 | 7.6708e-07 | 2.8602e-07 | 0.01122 | 0.01122 | 0.01122 | 0.98051 | -0.37522 | 0.9804 | -0.3774 | 3.0825
200 | 0.0041254 | 0.0010339 | -0.0041253 | -0.0010339 | 8.6955e-08 | -1.9e-08 | 0.0062599 | 0.00626 | 0.00626 | 0.98063 | -0.37282 | 0.98061 | -0.37327 | 1.7198
201 | 0.005249 | 0.0013155 | -0.0052488 | -0.0013155 | 1.7591e-07 | 1.9386e-08 | 0.0079667 | 0.0079667 | 0.0079667 | 0.9804 | -0.3774 | 0.98036 | -0.37811 | 2.1887
202 | 0.10792 | 0.027441 | -0.10774 | -0.027327 | 0.00017792 | 0.00011364 | 0.16176 | 0.16176 | 0.16176 | 0.99356 | -0.12245 | 0.99177 | -0.15673 | 44.4399
203 | 0.10774 | 0.027327 | -0.10764 | -0.027266 | 9.5971e-05 | 6.1295e-05 | 0.16176 | 0.16176 | 0.16176 | 0.99177 | -0.15673 | 0.99081 | -0.17528 | 44.4399
204 | -0.0045574 | -0.0011422 | 0.0045574 | 0.0011422 | 2.0544e-08 | -2.3475e-09 | 0.006796 | 0.006796 | 0.006796 | 0.99787 | -0.040918 | 0.99787 | -0.040823 | 1.867
205 | -0.0063478 | -0.0015909 | 0.0063478 | 0.0015909 | 1.2693e-08 | 3.1889e-09 | 0.0094658 | 0.0094658 | 0.0094658 | 0.99787 | -0.040823 | 0.99787 | -0.040781 | 2.6005
206 | 0.0086663 | 0.0021722 | -0.008665 | -0.0021716 | 1.3468e-06 | 5.9031e-07 | 0.013032 | 0.013032 | 0.013032 | 0.98955 | -0.19953 | 0.98939 | -0.20279 | 3.5802
207 | 0.01048 | 0.0026269 | -0.010479 | -0.0026264 | 1.1672e-06 | 5.8604e-07 | 0.015759 | 0.015759 | 0.015759 | 0.98955 | -0.19953 | 0.98943 | -0.20187 | 4.3295
208 | -0.0081382 | -0.0020396 | 0.0081387 | 0.0020398 | 5.5414e-07 | 2.2356e-07 | 0.012136 | 0.012136 | 0.012136 | 0.99787 | -0.040781 | 0.99795 | -0.039352 | 3.3339
209 | 0.0078037 | 0.0019559 | -0.0078027 | -0.0019555 | 1.0332e-06 | 4.0439e-07 | 0.011736 | 0.011736 | 0.011736 | 0.98943 | -0.20187 | 0.98929 | -0.20465 | 3.2242
210 | 0.0026752 | 0.00067041 | -0.0026751 | -0.00067045 | 2.4734e-08 | -3.6507e-08 | 0.0040232 | 0.0040232 | 0.0040232 | 0.98943 | -0.20187 | 0.98942 | -0.20206 | 1.1053
211 | -0.0098692 | -0.0024735 | 0.00987 | 0.0024739 | 7.9286e-07 | 3.7985e-07 | 0.014716 | 0.014716 | 0.014716 | 0.99795 | -0.039352 | 0.99803 | -0.037665 | 4.0428
212 | -0.011627 | -0.0029142 | 0.011627 | 0.0029144 | 3.1699e-07 | 1.6611e-07 | 0.017335 | 0.017335 | 0.017335 | 0.99803 | -0.037665 | 0.99806 | -0.037093 | 4.7624
213 | -0.0048395 | -0.0012128 | 0.0048396 | 0.0012128 | 1.4963e-07 | 2.1863e-09 | 0.007339 | 0.007339 | 0.007339 | 0.98122 | -0.3613 | 0.98125 | -0.36065 | 2.0162
214 | 0.0025948 | 0.00065026 | -0.0025948 | -0.00065031 | 3.3686e-08 | -5.1719e-08 | 0.003935 | 0.003935 | 0.003935 | 0.98122 | -0.3613 | 0.98121 | -0.36157 | 1.081
215 | -0.0071718 | -0.0017973 | 0.0071722 | 0.0017975 | 3.5895e-07 | 1.275e-07 | 0.010876 | 0.010876 | 0.010876 | 0.98125 | -0.36065 | 0.98131 | -0.3596 | 2.9878
216 | -0.0046751 | -0.0011717 | 0.0046755 | 0.0011717 | 4.0538e-07 | -1.1752e-08 | 0.007093 | 0.0070929 | 0.007093 | 0.98079 | -0.36822 | 0.98088 | -0.3664 | 1.9486
217 | -0.0018784 | -0.00047076 | 0.0018784 | 0.00047065 | 3.3978e-08 | -1.1577e-07 | 0.0028667 | 0.0028666 | 0.0028667 | 0.97502 | -0.48124 | 0.97504 | -0.48086 | 0.78755
218 | -0.0037577 | -0.00094163 | 0.0037578 | 0.00094157 | 1.7039e-07 | -6.3293e-08 | 0.0057346 | 0.0057345 | 0.0057346 | 0.97504 | -0.48086 | 0.97508 | -0.47991 | 1.5754
219 | -0.0019708 | -0.00049393 | 0.0019708 | 0.0004939 | 1.2146e-08 | -3.8369e-08 | 0.0029832 | 0.0029832 | 0.0029832 | 0.98304 | -0.32426 | 0.98305 | -0.32413 | 0.81956
220 | -0.0029958 | -0.00075077 | 0.0029958 | 0.00075072 | 4.297e-08 | -4.3152e-08 | 0.0045346 | 0.0045346 | 0.0045346 | 0.98305 | -0.32413 | 0.98306 | -0.32383 | 1.2458
221 | -0.0038737 | -0.00097074 | 0.0038737 | 0.00097072 | 6.6941e-08 | -2.2992e-08 | 0.0058634 | 0.0058633 | 0.0058634 | 0.98306 | -0.32383 | 0.98308 | -0.32347 | 1.6108
222 | -0.0047978 | -0.0012023 | 0.0047979 | 0.0012023 | 1.0175e-07 | -1.1746e-10 | 0.007262 | 0.0072619 | 0.007262 | 0.98308 | -0.32347 | 0.98311 | -0.32302 | 1.995
223 | 0.0241 | 0.0060471 | -0.024097 | -0.0060452 | 3.1079e-06 | 1.9114e-06 | 0.03663 | 0.03663 | 0.03663 | 0.97907 | -0.40167 | 0.97893 | -0.40438 | 10.0633
224 | -0.0011096 | -0.00027808 | 0.0011096 | 0.00027801 | 6.5791e-09 | -7.2955e-08 | 0.0016886 | 0.0016886 | 0.0016886 | 0.97774 | -0.42786 | 0.97774 | -0.42774 | 0.46391
225 | -0.0022191 | -0.00055609 | 0.0022192 | 0.00055603 | 2.6315e-08 | -6.0323e-08 | 0.0033772 | 0.0033772 | 0.0033772 | 0.97774 | -0.42774 | 0.97775 | -0.42749 | 0.92782
226 | -0.0033287 | -0.00083411 | 0.0033288 | 0.00083406 | 8.615e-08 | -5.7145e-08 | 0.0050658 | 0.0050658 | 0.0050658 | 0.97775 | -0.42749 | 0.97778 | -0.42695 | 1.3917
227 | -0.0052167 | -0.0013072 | 0.0052168 | 0.0013072 | 1.0778e-07 | 1.1779e-08 | 0.0079388 | 0.0079388 | 0.0079388 | 0.97778 | -0.42695 | 0.9778 | -0.42651 | 2.181
228 | 0.004299 | 0.0010773 | -0.0042988 | -0.0010773 | 1.824e-07 | -2.5807e-08 | 0.0065421 | 0.0065422 | 0.0065422 | 0.9778 | -0.42651 | 0.97776 | -0.4274 | 1.7973
229 | -0.0095158 | -0.0023845 | 0.0095164 | 0.0023848 | 6.3762e-07 | 3.0636e-07 | 0.014481 | 0.014481 | 0.014481 | 0.9778 | -0.42651 | 0.97788 | -0.42511 | 3.9783
230 | 0.022983 | 0.0057662 | -0.022981 | -0.0057644 | 2.8273e-06 | 1.7319e-06 | 0.034938 | 0.034938 | 0.034938 | 0.97893 | -0.40438 | 0.9788 | -0.40696 | 9.5983
231 | -0.0043787 | -0.0010973 | 0.0043791 | 0.0010973 | 3.0463e-07 | -3.9246e-08 | 0.0066298 | 0.0066297 | 0.0066298 | 0.98278 | -0.32954 | 0.98285 | -0.32808 | 1.8214
232 | 0.0022774 | 0.00057069 | -0.0022774 | -0.00057076 | 3.0965e-08 | -6.8181e-08 | 0.0034482 | 0.0034482 | 0.0034482 | 0.98278 | -0.32954 | 0.98277 | -0.32982 | 0.94731
233 | -0.0077941 | -0.0019532 | 0.0077948 | 0.0019535 | 6.709e-07 | 2.6652e-07 | 0.0118 | 0.0118 | 0.0118 | 0.98285 | -0.32808 | 0.98295 | -0.32627 | 3.2418
234 | -0.0093335 | -0.0023391 | 0.009334 | 0.0023393 | 4.6563e-07 | 2.1916e-07 | 0.014129 | 0.014129 | 0.014129 | 0.98295 | -0.32627 | 0.983 | -0.32522 | 3.8817
235 | -0.010866 | -0.0027233 | 0.010867 | 0.0027236 | 6.3082e-07 | 3.249e-07 | 0.016448 | 0.016448 | 0.016448 | 0.983 | -0.32522 | 0.98306 | -0.324 | 4.5187
236 | -0.012395 | -0.0031067 | 0.012395 | 0.0031067 | 9.1671e-08 | 4.9865e-08 | 0.018762 | 0.018762 | 0.018762 | 0.98306 | -0.324 | 0.98307 | -0.32385 | 5.1544
237 | -0.016483 | -0.0041312 | 0.016484 | 0.004132 | 1.2896e-06 | 7.553e-07 | 0.024949 | 0.024949 | 0.024949 | 0.98307 | -0.32385 | 0.98315 | -0.32221 | 6.8542
238 | -0.018006 | -0.0045133 | 0.018011 | 0.0045162 | 4.8458e-06 | 2.8806e-06 | 0.027252 | 0.027252 | 0.027252 | 0.98315 | -0.32221 | 0.98344 | -0.31656 | 7.4869
239 | 0.035474 | 0.0089289 | -0.035463 | -0.0089221 | 1.0738e-05 | 6.7465e-06 | 0.053716 | 0.053716 | 0.053716 | 0.98294 | -0.32644 | 0.98261 | -0.33277 | 14.7571
240 | 0.033927 | 0.0085371 | -0.033909 | -0.0085254 | 1.8647e-05 | 1.1696e-05 | 0.05139 | 0.05139 | 0.05139 | 0.98261 | -0.33277 | 0.98202 | -0.34428 | 14.1181
241 | 0.030959 | 0.0077863 | -0.030947 | -0.0077783 | 1.2684e-05 | 7.9232e-06 | 0.046921 | 0.046921 | 0.046921 | 0.98202 | -0.34428 | 0.98158 | -0.35286 | 12.8904
242 | 0.028129 | 0.0070721 | -0.028121 | -0.0070674 | 7.5594e-06 | 4.698e-06 | 0.042649 | 0.042649 | 0.042649 | 0.98158 | -0.35286 | 0.98129 | -0.35849 | 11.7169
243 | 0.003229 | 0.00080839 | -0.0032288 | -0.00080848 | 1.294e-07 | -9.805e-08 | 0.0049026 | 0.0049027 | 0.0049027 | 0.97997 | -0.38432 | 0.97993 | -0.38516 | 1.3469
244 | 0.0077079 | 0.0019314 | -0.0077073 | -0.0019312 | 5.9465e-07 | 2.3473e-07 | 0.011704 | 0.011704 | 0.011704 | 0.97997 | -0.38432 | 0.97989 | -0.38594 | 3.2153
245 | 0.001944 | 0.00048648 | -0.0019439 | -0.0004867 | 6.9767e-08 | -2.2435e-07 | 0.0029517 | 0.0029518 | 0.0029518 | 0.97993 | -0.38516 | 0.97989 | -0.38591 | 0.81093
246 | 0.0064737 | 0.001622 | -0.0064724 | -0.0016216 | 1.265e-06 | 3.6998e-07 | 0.0098305 | 0.0098307 | 0.0098307 | 0.97989 | -0.38594 | 0.97968 | -0.39004 | 2.7007
247 | -0.0011356 | -0.0002846 | 0.0011356 | 0.00028412 | 4.5369e-08 | -4.8347e-07 | 0.0017245 | 0.0017243 | 0.0017245 | 0.97985 | -0.38675 | 0.97989 | -0.38591 | 0.47376
248 | 0.005283 | 0.0013235 | -0.0052827 | -0.0013235 | 3.3745e-07 | 3.9997e-08 | 0.008024 | 0.0080241 | 0.0080241 | 0.97968 | -0.39004 | 0.97961 | -0.39138 | 2.2044
249 | 0.0047169 | 0.0011817 | -0.0047167 | -0.0011817 | 1.5374e-07 | -2.1526e-09 | 0.0071647 | 0.0071647 | 0.0071647 | 0.97961 | -0.39138 | 0.97958 | -0.39206 | 1.9683
250 | 0.0035903 | 0.00089939 | -0.0035901 | -0.00089948 | 1.6897e-07 | -8.2569e-08 | 0.0054536 | 0.0054537 | 0.0054537 | 0.97958 | -0.39206 | 0.97953 | -0.39305 | 1.4983
251 | 0.0094 | 0.0023558 | -0.0093994 | -0.0023556 | 5.5368e-07 | 2.6479e-07 | 0.014342 | 0.014342 | 0.014342 | 0.97528 | -0.4761 | 0.97521 | -0.47734 | 3.9401
252 | 0.0075146 | 0.0018832 | -0.0075139 | -0.0018829 | 6.5536e-07 | 2.5359e-07 | 0.011466 | 0.011466 | 0.011466 | 0.97521 | -0.47734 | 0.97512 | -0.47917 | 3.15
253 | 0.0056354 | 0.0014121 | -0.0056352 | -0.0014121 | 1.9901e-07 | 3.7846e-08 | 0.0085994 | 0.0085994 | 0.0085994 | 0.97512 | -0.47917 | 0.97508 | -0.47991 | 2.3625
254 | 0.0023138 | 0.00057985 | -0.0023138 | -0.00057989 | 1.4436e-08 | -3.3098e-08 | 0.0034484 | 0.0034484 | 0.0034484 | 0.99843 | -0.030198 | 0.99842 | -0.030329 | 0.94736
255 | 0.010626 | 0.002663 | -0.010626 | -0.0026629 | 3.2659e-07 | 1.6723e-07 | 0.016169 | 0.016169 | 0.016169 | 0.97791 | -0.42446 | 0.97788 | -0.42511 | 4.4421
256 | -0.012008 | -0.0030092 | 0.01201 | 0.0030103 | 1.9727e-06 | 1.0648e-06 | 0.018271 | 0.018271 | 0.018271 | 0.97791 | -0.42446 | 0.97808 | -0.42101 | 5.0195
257 | -0.017038 | -0.0042703 | 0.017039 | 0.0042712 | 1.5835e-06 | 9.3456e-07 | 0.025921 | 0.025921 | 0.025921 | 0.97808 | -0.42101 | 0.97818 | -0.41906 | 7.121
258 | 0.0050282 | 0.00126 | -0.005028 | -0.00126 | 1.0406e-07 | 7.0828e-09 | 0.0076496 | 0.0076496 | 0.0076496 | 0.97808 | -0.42101 | 0.97806 | -0.42145 | 2.1015
259 | -0.018103 | -0.0045377 | 0.018105 | 0.0045391 | 2.2902e-06 | 1.3646e-06 | 0.027538 | 0.027538 | 0.027538 | 0.97818 | -0.41906 | 0.97832 | -0.41641 | 7.5654
260 | 0.0037711 | 0.00094496 | -0.003771 | -0.00094499 | 7.56e-08 | -2.8477e-08 | 0.0057373 | 0.0057373 | 0.0057373 | 0.97806 | -0.42145 | 0.97804 | -0.42187 | 1.5762
261 | 0.0029175 | 0.00073112 | -0.0029175 | -0.00073117 | 4.6588e-08 | -4.922e-08 | 0.0044401 | 0.0044401 | 0.0044401 | 0.97776 | -0.4274 | 0.97774 | -0.42774 | 1.2198
262 | -0.019465 | -0.0048799 | 0.019467 | 0.0048811 | 1.9888e-06 | 1.1968e-06 | 0.029606 | 0.029606 | 0.029606 | 0.97832 | -0.41641 | 0.97843 | -0.41426 | 8.1336
263 | 0.0025144 | 0.00063005 | -0.0025144 | -0.00063011 | 3.3631e-08 | -5.5381e-08 | 0.0038255 | 0.0038255 | 0.0038255 | 0.97804 | -0.42187 | 0.97803 | -0.42215 | 1.051
264 | 0.0015362 | 0.00038498 | -0.0015362 | -0.000385 | 3.938e-09 | -2.1577e-08 | 0.0023379 | 0.0023379 | 0.0023379 | 0.97774 | -0.42774 | 0.97774 | -0.42779 | 0.64227
265 | -0.020778 | -0.0052096 | 0.02078 | 0.005211 | 2.3019e-06 | 1.396e-06 | 0.0316 | 0.0316 | 0.0316 | 0.97843 | -0.41426 | 0.97855 | -0.41194 | 8.6813
266 | 0.0012569 | 0.00031496 | -0.0012569 | -0.00031502 | 6.3443e-09 | -5.3992e-08 | 0.0019124 | 0.0019124 | 0.0019124 | 0.97803 | -0.42215 | 0.97802 | -0.42226 | 0.52538
267 | -0.021861 | -0.005482 | 0.021867 | 0.0054852 | 5.1931e-06 | 3.1661e-06 | 0.033244 | 0.033244 | 0.033244 | 0.97855 | -0.41194 | 0.9788 | -0.40696 | 9.1331

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52719 | 0.13494

## res_load
| p_mw | q_mvar
0 | 0.00087721 | 0.00021985
1 | 0.0019996 | 0.00050115
2 | 0.0019048 | 0.0004774
3 | 0.00048847 | 0.00012242
4 | 0.00055573 | 0.00013928
5 | 0.00058461 | 0.00014652
6 | 0.00088985 | 0.00022302
7 | 0.00025838 | 6.4756e-05
8 | 0.0010625 | 0.00026628
9 | 0.0011105 | 0.00027833
10 | 0.0017935 | 0.0004495
11 | 0.00027451 | 6.8799e-05
12 | 0.00074638 | 0.00018706
13 | 0.00023813 | 5.9681e-05
14 | 0.00068361 | 0.00017133
15 | 0.0002385 | 5.9775e-05
16 | 0.0002381 | 5.9674e-05
17 | 0.00045294 | 0.00011352
18 | 0.00043257 | 0.00010841
19 | 0.00075687 | 0.00018969
20 | 0.00056344 | 0.00014121
21 | 0.00056379 | 0.0001413
22 | 0.0022049 | 0.0005526
23 | 0.0005142 | 0.00012887
24 | 0.0012821 | 0.00032133
25 | 0.0010845 | 0.0002718
26 | 0.00096499 | 0.00024185
27 | 0.001133 | 0.00028396
28 | 0.0021348 | 0.00053504
29 | 0.0012257 | 0.00030718
30 | 0.0010169 | 0.00025487
31 | 0.0021017 | 0.00052674
32 | 0.0014998 | 0.00037588
33 | 0.00092362 | 0.00023148
34 | 0.0054174 | 0.0013577
35 | 0.0010223 | 0.0002562
36 | 0.0063368 | 0.0015882
37 | 0.0067758 | 0.0016982
38 | 0.037425 | 0.0093795
39 | 0.0045832 | 0.0011487
40 | 0.0020229 | 0.00050699
41 | 0.00098225 | 0.00024618
42 | 0.0015017 | 0.00037636
43 | 0.002853 | 0.00071503
44 | 0.0038037 | 0.0009533
45 | 0.0018658 | 0.00046761
46 | 0.0024126 | 0.00060466
47 | 0.0073542 | 0.0018431
48 | 0.0067818 | 0.0016997
49 | 0.0058766 | 0.0014728
50 | 0.0014914 | 0.00037377
51 | 0.0024899 | 0.00062402
52 | 0.002027 | 0.00050802
53 | 0.00095183 | 0.00023855
54 | 0.0009691 | 0.00024288
55 | 0.0028875 | 0.00072368
56 | 0.0011141 | 0.00027921
57 | 0.0010506 | 0.0002633
58 | 0.0023922 | 0.00059955
59 | 0.00086896 | 0.00021778
60 | 0.0015486 | 0.00038811
61 | 0.0061287 | 0.001536
62 | 0.0011799 | 0.0002957
63 | 0.0020565 | 0.00051541
64 | 0.0016815 | 0.00042142
65 | 0.002541 | 0.00063684
66 | 0.0015942 | 0.00039955
67 | 0.0011101 | 0.00027821
68 | 0.0020233 | 0.00050709
69 | 0.00054748 | 0.00013721
70 | 0.00093358 | 0.00023398
71 | 0.001642 | 0.00041153
72 | 0.0054885 | 0.0013756
73 | 0.0046758 | 0.0011719
74 | 0.0011202 | 0.00028075
75 | 0.0018849 | 0.0004724
76 | 0.0090624 | 0.0022712
77 | 0.0062831 | 0.0015747
78 | 0.0016986 | 0.00042571
79 | 0.0079847 | 0.0020012
80 | 0.0018849 | 0.0004724
81 | 0.0055943 | 0.0014021
82 | 0.0018857 | 0.0004726
83 | 0.0043578 | 0.0010922
84 | 0.007431 | 0.0018624
85 | 0.0018863 | 0.00047276
86 | 0.014435 | 0.0036178
87 | 0.0014922 | 0.00037399
88 | 0.0014648 | 0.0003671
89 | 0.0024837 | 0.00062247
90 | 0.0020912 | 0.0005241
91 | 0.0015724 | 0.00039409
92 | 0.0012866 | 0.00032245
93 | 0.0043392 | 0.0010875
94 | 0.0018663 | 0.00046774
95 | 0.0016595 | 0.0004159
96 | 0.0015627 | 0.00039166
97 | 0.0015632 | 0.00039178
98 | 0.0016736 | 0.00041944
99 | 0.0016736 | 0.00041944
100 | 0.00166 | 0.00041604
101 | 0.0028788 | 0.00072149
102 | 0.0025904 | 0.00064921
103 | 0.0026189 | 0.00065636
104 | 0.0014205 | 0.00035602
105 | 0.0017487 | 0.00043826
106 | 0.0046146 | 0.0011565
107 | 0.0025353 | 0.0006354
108 | 0.0025353 | 0.00063541
109 | 0.0016296 | 0.00040842
110 | 0.0023163 | 0.00058052
111 | 0.0038031 | 0.00095315
112 | 0.002561 | 0.00064184
113 | 0.0020404 | 0.00051138
114 | 0.0020193 | 0.00050609
115 | 0.0019004 | 0.00047628
116 | 0.0024071 | 0.00060327
117 | 0.0020099 | 0.00050374
118 | 0.0021066 | 0.00052797
119 | 0.0024776 | 0.00062096
120 | 0.0021321 | 0.00053436
121 | 0.0020621 | 0.00051681
122 | 0.0023264 | 0.00058304
123 | 0.0020649 | 0.00051752
124 | 0.0023144 | 0.00058003
125 | 0.0020594 | 0.00051612
126 | 0.0020728 | 0.0005195
127 | 0.0020253 | 0.00050759
128 | 0.0020645 | 0.00051741
129 | 0.0021743 | 0.00054493
130 | 0.0021098 | 0.00052877
131 | 0.0021437 | 0.00053727
132 | 0.0052488 | 0.0013155
133 | 0.0050167 | 0.0012573
134 | 0.0022561 | 0.00056544
135 | 0.0045574 | 0.0011422
136 | 0.0017904 | 0.00044871
137 | 0.0017904 | 0.00044871
138 | 0.008665 | 0.0021716
139 | 0.0017305 | 0.00043371
140 | 0.0017568 | 0.0004403
141 | 0.005201 | 0.0013035
142 | 0.0041253 | 0.0010339
143 | 0.0022447 | 0.00056257
144 | 0.0023322 | 0.0005845
145 | 0.0025948 | 0.00065031
146 | 0.0023116 | 0.00057934
147 | 0.0046751 | 0.0011717
148 | 0.0043077 | 0.0010796
149 | 0.010006 | 0.0025078
150 | 0.0018784 | 0.00047076
151 | 0.0018793 | 0.00047098
152 | 0.0009582 | 0.00024015
153 | 0.0019708 | 0.00049393
154 | 0.0010249 | 0.00025687
155 | 0.00087788 | 0.00022002
156 | 0.00092402 | 0.00023158
157 | 0.0018205 | 0.00045627
158 | 0.0013137 | 0.00032924
159 | 0.0011141 | 0.00027921
160 | 0.0011096 | 0.00027808
161 | 0.0011096 | 0.00027808
162 | 0.0011096 | 0.00027808
163 | 0.0018879 | 0.00047315
164 | 0.0011134 | 0.00027904
165 | 0.0021013 | 0.00052665
166 | 0.0034151 | 0.0008559
167 | 0.0022774 | 0.00057076
168 | 0.0015387 | 0.00038563
169 | 0.0015319 | 0.00038394
170 | 0.0015286 | 0.00038311
171 | 0.0040876 | 0.0010245
172 | 0.0015218 | 0.00038139
173 | 0.0024843 | 0.00062262
174 | 0.0023816 | 0.00059689
175 | 0.0015361 | 0.00038499
176 | 0.0029493 | 0.00073916
177 | 0.0028178 | 0.00070621
178 | 0.0012848 | 0.00032201
179 | 0.0012336 | 0.00030916
180 | 0.0011356 | 0.0002846
181 | 0.00080832 | 0.00020258
182 | 0.0011894 | 0.0002981
183 | 0.00056579 | 0.0001418
184 | 0.0011264 | 0.00028231
185 | 0.0015406 | 0.00038611
186 | 0.0018851 | 0.00047246
187 | 0.0018849 | 0.0004724
188 | 0.0018785 | 0.0004708
189 | 0.0018773 | 0.00047051
190 | 0.0016295 | 0.0004084
191 | 0.0023443 | 0.00058754
192 | 0.0023443 | 0.00058754
193 | 0.0023138 | 0.00057989
194 | 0.0078027 | 0.0019555
195 | 0.0026751 | 0.00067045
196 | 0.0013813 | 0.00034618
197 | 0.0011096 | 0.00027808
198 | 0.0010634 | 0.00026651
199 | 0.0012569 | 0.00031502
200 | 0.0013813 | 0.00034618
201 | 0.0013599 | 0.00034081
202 | 0.0012566 | 0.00031494
203 | 0.0013813 | 0.00034619
204 | 0.0013108 | 0.00032851
205 | 0.0012574 | 0.00031514
206 | 0.0015362 | 0.000385
207 | 0.0010814 | 0.00027103
208 | 0.0012569 | 0.00031502
209 | 0.0011141 | 0.00027921

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1