## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_112-5_1_2_node_50 | 0.4 | n |  | TRUE
1 | bus_LV_112-5_1_2_node_51 | 0.4 | n |  | TRUE
2 | bus_LV_112-5_1_2_node_52 | 0.4 | n |  | TRUE
3 | bus_LV_112-5_1_2_node_53 | 0.4 | n |  | TRUE
4 | bus_LV_112-5_1_2_node_75 | 0.4 | n |  | TRUE
5 | bus_LV_112-5_1_2_node_76 | 0.4 | n |  | TRUE
6 | bus_LV_112-5_1_2_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_112-5_1_2_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_112-5_1_2_node_58 | 0.4 | n |  | TRUE
9 | bus_LV_112-5_1_2_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_112-5_1_2_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_112-5_1_2_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_112-5_1_2_node_61 | 0.4 | n |  | TRUE
13 | bus_LV_112-5_1_2_node_69 | 0.4 | n |  | TRUE
14 | bus_LV_112-5_1_2_node_77 | 0.4 | n |  | TRUE
15 | bus_LV_112-5_1_2_node_62 | 0.4 | n |  | TRUE
16 | bus_LV_112-5_1_2_node_63 | 0.4 | n |  | TRUE
17 | bus_LV_112-5_1_2_node_67 | 0.4 | n |  | TRUE
18 | bus_LV_112-5_1_2_node_65 | 0.4 | n |  | TRUE
19 | bus_LV_112-5_1_2_node_73 | 0.4 | n |  | TRUE
20 | bus_LV_112-5_1_2_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_112-5_1_2_node_74 | 0.4 | n |  | TRUE
22 | bus_LV_112-5_1_2_node_94 | 0.4 | n |  | TRUE
23 | bus_LV_112-5_1_2_node_89 | 0.4 | n |  | TRUE
24 | bus_LV_112-5_1_2_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_112-5_1_2_node_81 | 0.4 | n |  | TRUE
26 | bus_LV_112-5_1_2_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_112-5_1_2_node_80 | 0.4 | n |  | TRUE
28 | bus_MV_8_1_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_112-5_1_2_load_50 | 0 | 0.00064237 | 0.00016099 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_112-5_1_2_load_51 | 1 | 0.00014875 | 3.7281e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_112-5_1_2_load_52 | 2 | 0.0001415 | 3.5463e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_112-5_1_2_load_55 | 6 | 0.0013838 | 0.00034681 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_112-5_1_2_load_59 | 9 | 0.00080387 | 0.00020147 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_112-5_1_2_load_60 | 10 | 0.010372 | 0.0025994 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_112-5_1_2_load_61 | 12 | 0.0063443 | 0.00159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_112-5_1_2_load_69 | 13 | 0.0056132 | 0.0014068 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_112-5_1_2_load_77 | 14 | 0.0019997 | 0.00050116 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_112-5_1_2_load_62 | 15 | 0.0037015 | 0.00092769 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_112-5_1_2_load_63 | 16 | 0.0040949 | 0.0010263 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_112-5_1_2_load_65 | 18 | 0.003622 | 0.00090776 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_112-5_1_2_load_73 | 19 | 0.0055676 | 0.0013954 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_112-5_1_2_load_70 | 20 | 0.004306 | 0.0010792 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_112-5_1_2_load_74 | 21 | 0.0072055 | 0.0018059 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_112-5_1_2_load_94 | 22 | 0.00036971 | 9.2659e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_112-5_1_2_load_89 | 23 | 0.0019875 | 0.00049812 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_112-5_1_2_load_78 | 24 | 0.011424 | 0.0028631 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_112-5_1_2_load_79 | 26 | 0.037818 | 0.0094781 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_112-5_1_2_load_80 | 27 | 0.05986 | 0.015002 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_112-5_1_2_line_0 |  | 0 | 1 | 0.00045462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_112-5_1_2_line_1 |  | 0 | 2 | 0.00045703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_112-5_1_2_line_2 |  | 1 | 3 | 0.044304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_112-5_1_2_line_3 |  | 3 | 4 | 0.005578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_112-5_1_2_line_4 |  | 3 | 5 | 0.083116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_112-5_1_2_line_5 |  | 4 | 22 | 0.019579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_112-5_1_2_line_6 |  | 4 | 17 | 0.05575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_112-5_1_2_line_7 |  | 5 | 23 | 0.025758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_112-5_1_2_line_8 |  | 6 | 7 | 0.030629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_112-5_1_2_line_9 |  | 7 | 8 | 0.059628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_112-5_1_2_line_10 |  | 7 | 9 | 0.031326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_112-5_1_2_line_11 |  | 7 | 10 | 0.12315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_112-5_1_2_line_12 |  | 8 | 11 | 0.097881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_112-5_1_2_line_13 |  | 8 | 12 | 0.013166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_112-5_1_2_line_14 |  | 9 | 13 | 0.0057176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_112-5_1_2_line_15 |  | 10 | 14 | 0.015998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_112-5_1_2_line_16 |  | 11 | 17 | 0.1002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_112-5_1_2_line_17 |  | 11 | 18 | 0.029725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_112-5_1_2_line_18 |  | 12 | 15 | 0.015109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_112-5_1_2_line_19 |  | 13 | 20 | 0.02125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_112-5_1_2_line_20 |  | 14 | 24 | 0.0050435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_112-5_1_2_line_21 |  | 15 | 16 | 0.0097722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_112-5_1_2_line_22 |  | 17 | 19 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_112-5_1_2_line_23 |  | 19 | 21 | 0.017104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_112-5_1_2_line_24 |  | 24 | 25 | 0.055404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_112-5_1_2_line_25 |  | 25 | 27 | 0.031369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_112-5_1_2_line_26 |  | 26 | 27 | 0.081917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_112-5_1_2_trafo_78 | 0.63 MVA 20/0.4 kV | 28 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2704733.9663 | 1236444.1791 | 2704733.669 | 1236444.5231
1 | 2704734.2651 | 1236443.8333 | 2704733.9663 | 1236444.1791
2 | 2704704.5431 | 1236477.9073 | 2704718.339 | 1236462.1051 | 2704732.027 | 1236446.4233 | 2704733.669 | 1236444.5231
3 | 2704704.5431 | 1236477.9073 | 2704709.0175 | 1236481.2554
4 | 2704664.4999 | 1236543.5074 | 2704684.4574 | 1236521.6312 | 2704686.6507 | 1236517.8558 | 2704687.7251 | 1236513.5826 | 2704687.9722 | 1236509.4394 | 2704687.6132 | 1236505.7636 | 2704686.9951 | 1236502.6169 | 2704685.8576 | 1236499.7391 | 2704684.567 | 1236497.3924 | 2704689.4143 | 1236492.8966 | 2704704.5431 | 1236477.9073
5 | 2704722.1705 | 1236466.7206 | 2704709.0175 | 1236481.2554
6 | 2704694.4388 | 1236526.4218 | 2704692.8817 | 1236522.4469 | 2704692.2792 | 1236519.2783 | 2704692.0555 | 1236516.0831 | 2704692.3455 | 1236512.9413 | 2704693.0663 | 1236509.4069 | 2704694.0617 | 1236506.6112 | 2704695.522 | 1236504.0572 | 2704702.2738 | 1236497.1487 | 2704713.7426 | 1236485.4085 | 2704711.46 | 1236483.0887 | 2704709.0175 | 1236481.2554
7 | 2704664.4999 | 1236543.5074 | 2704659.6427 | 1236544.7005 | 2704645.1226 | 1236559.5332
8 | 2704908.2657 | 1236643.0387 | 2704921.8531 | 1236647.1818 | 2704931.9864 | 1236649.785 | 2704937.8113 | 1236651.0537
9 | 2704908.2657 | 1236643.0387 | 2704850.7239 | 1236626.7882
10 | 2704908.2657 | 1236643.0387 | 2704908.7462 | 1236648.3957 | 2704908.4848 | 1236653.3393 | 2704907.8871 | 1236657.6098 | 2704903.3596 | 1236673.6683
11 | 2704908.2657 | 1236643.0387 | 2704907.0672 | 1236636.7683 | 2704905.9115 | 1236631.9331 | 2704902.8329 | 1236623.2721 | 2704897.3181 | 1236611.1432 | 2704894.9791 | 1236604.7415 | 2704879.9565 | 1236537.8918 | 2704878.7507 | 1236529.8866 | 2704877.9895 | 1236524.0822
12 | 2704850.7239 | 1236626.7882 | 2704832.2306 | 1236621.4466 | 2704769.477 | 1236603.3035 | 2704761.9653 | 1236600.9581 | 2704756.6115 | 1236598.9844
13 | 2704850.7239 | 1236626.7882 | 2704848.5994 | 1236632.6663 | 2704847.4177 | 1236634.4357 | 2704846.1318 | 1236636.1143 | 2704844.1665 | 1236637.9264
14 | 2704903.3596 | 1236673.6683 | 2704901.8081 | 1236679.1714
15 | 2704877.9895 | 1236524.0822 | 2704875.9094 | 1236508.2199 | 2704875.9094 | 1236508.2199
16 | 2704694.4388 | 1236526.4218 | 2704699.9954 | 1236535.7825 | 2704707.8511 | 1236549.0978 | 2704708.6737 | 1236550.947 | 2704709.1089 | 1236552.8784 | 2704709.0811 | 1236554.4569 | 2704708.0964 | 1236557.9311 | 2704710.8408 | 1236558.958 | 2704713.4536 | 1236561.0056 | 2704715.5541 | 1236563.3444 | 2704720.7198 | 1236570.4076 | 2704725.1552 | 1236576.3903 | 2704728.0919 | 1236579.8114 | 2704731.4909 | 1236583.1961 | 2704736.1939 | 1236586.8818 | 2704742.3376 | 1236591.2713 | 2704747.8413 | 1236594.6153 | 2704751.8673 | 1236596.7768 | 2704756.6115 | 1236598.9844
17 | 2704756.6115 | 1236598.9844 | 2704767.9787 | 1236626.4503
18 | 2704844.1665 | 1236637.9264 | 2704833.0589 | 1236648.1688
19 | 2704896.0415 | 1236699.6244 | 2704901.8081 | 1236679.1714
20 | 2704876.8973 | 1236503.2741 | 2704875.9094 | 1236508.2199
21 | 2704825.8748 | 1236654.7933 | 2704833.0589 | 1236648.1688
22 | 2704694.4388 | 1236526.4218 | 2704703.1275 | 1236518.2576 | 2704708.9762 | 1236512.5569
23 | 2704721.2244 | 1236500.6187 | 2704708.9762 | 1236512.5569
24 | 2704904.4887 | 1236456.3403 | 2704884.7034 | 1236481.6882 | 2704879.3135 | 1236491.178 | 2704876.8973 | 1236503.2741
25 | 2704904.4887 | 1236456.3403 | 2704929.1293 | 1236475.7529
26 | 2704984.5623 | 1236436.8295 | 2704942.4755 | 1236486.2675 | 2704929.1293 | 1236475.7529

## bus_geodata
| x | y | coords
0 | 2704733.9663 | 1236444.1791
1 | 2704733.669 | 1236444.5231
2 | 2704734.2651 | 1236443.8333
3 | 2704704.5431 | 1236477.9073
4 | 2704709.0175 | 1236481.2554
5 | 2704664.4999 | 1236543.5074
6 | 2704937.8113 | 1236651.0537
7 | 2704908.2657 | 1236643.0387
8 | 2704850.7239 | 1236626.7882
9 | 2704903.3596 | 1236673.6683
10 | 2704877.9895 | 1236524.0822
11 | 2704756.6115 | 1236598.9844
12 | 2704844.1665 | 1236637.9264
13 | 2704901.8081 | 1236679.1714
14 | 2704875.9094 | 1236508.2199
15 | 2704833.0589 | 1236648.1688
16 | 2704825.8748 | 1236654.7933
17 | 2704694.4388 | 1236526.4218
18 | 2704767.9787 | 1236626.4503
19 | 2704708.9762 | 1236512.5569
20 | 2704896.0415 | 1236699.6244
21 | 2704721.2244 | 1236500.6187
22 | 2704722.1705 | 1236466.7206
23 | 2704645.1226 | 1236559.5332
24 | 2704876.8973 | 1236503.2741
25 | 2704904.4887 | 1236456.3403
26 | 2704984.5623 | 1236436.8295
27 | 2704929.1293 | 1236475.7529
28 | 2704904.4887 | 1236456.3403

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98842 | -0.22313 | 0.00064237 | 0.00016099
1 | 0.98842 | -0.22313 | 0.00014875 | 3.7281e-05
2 | 0.98842 | -0.22314 | 0.0001415 | 3.5463e-05
3 | 0.98846 | -0.22239 | 0 | 0
4 | 0.98847 | -0.2221 | 0 | 0
5 | 0.9883 | -0.22534 | 0 | 0
6 | 0.99369 | -0.12098 | 0.0013838 | 0.00034681
7 | 0.99373 | -0.12024 | 0 | 0
8 | 0.99188 | -0.15592 | 0 | 0
9 | 0.99342 | -0.12617 | 0.00080387 | 0.00020147
10 | 0.99891 | -0.020858 | 0.010372 | 0.0025994
11 | 0.99011 | -0.19014 | 0 | 0
12 | 0.99171 | -0.15922 | 0.0063443 | 0.00159
13 | 0.99337 | -0.12717 | 0.0056132 | 0.0014068
14 | 0.99973 | -0.005129 | 0.0019997 | 0.00050116
15 | 0.9916 | -0.16131 | 0.0037015 | 0.00092769
16 | 0.99157 | -0.16202 | 0.0040949 | 0.0010263
17 | 0.98864 | -0.21882 | 0 | 0
18 | 0.99002 | -0.19206 | 0.003622 | 0.00090776
19 | 0.9884 | -0.2234 | 0.0055676 | 0.0013954
20 | 0.99329 | -0.12879 | 0.004306 | 0.0010792
21 | 0.98829 | -0.2256 | 0.0072055 | 0.0018059
22 | 0.98846 | -0.22223 | 0.00036971 | 9.2659e-05
23 | 0.98826 | -0.22625 | 0.0019875 | 0.00049812
24 | 1 | 0 | -0.15883 | -0.039848
25 | 0.99505 | -0.094798 | 0 | 0
26 | 0.9894 | -0.20389 | 0.037818 | 0.0094781
27 | 0.99224 | -0.14889 | 0.05986 | 0.015002
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00078386 | -0.00019645 | 0.00078386 | 0.00019644 | 2.3741e-10 | -5.6752e-09 | 0.0011801 | 0.0011801 | 0.0011801 | 0.98842 | -0.22313 | 0.98842 | -0.22313 | 0.32419
1 | 0.0001415 | 3.5457e-05 | -0.0001415 | -3.5463e-05 | 7.8881e-12 | -5.8527e-09 | 0.00021302 | 0.00021302 | 0.00021302 | 0.98842 | -0.22313 | 0.98842 | -0.22314 | 0.058521
2 | -0.00093262 | -0.00023372 | 0.00093265 | 0.00023318 | 3.2745e-08 | -5.4691e-07 | 0.001404 | 0.0014038 | 0.001404 | 0.98842 | -0.22313 | 0.98846 | -0.22239 | 0.38572
3 | -0.0029205 | -0.00073013 | 0.0029206 | 0.00073009 | 4.0421e-08 | -4.5631e-08 | 0.0043959 | 0.0043959 | 0.0043959 | 0.98846 | -0.22239 | 0.98847 | -0.2221 | 1.2077
4 | 0.0019879 | 0.00049696 | -0.0019876 | -0.00049784 | 2.7908e-07 | -8.8662e-07 | 0.0029921 | 0.0029925 | 0.0029925 | 0.98846 | -0.22239 | 0.9883 | -0.22534 | 0.82211
5 | 0.00036971 | 9.2409e-05 | -0.00036971 | -9.2659e-05 | 2.2739e-09 | -2.4952e-07 | 0.00055647 | 0.00055656 | 0.00055656 | 0.98847 | -0.2221 | 0.98846 | -0.22223 | 0.1529
6 | -0.0032903 | -0.0008225 | 0.0032908 | 0.00082211 | 5.1272e-07 | -3.8662e-07 | 0.0049523 | 0.0049521 | 0.0049523 | 0.98847 | -0.2221 | 0.98864 | -0.21882 | 1.3605
7 | 0.0019876 | 0.00049784 | -0.0019875 | -0.00049812 | 8.6502e-08 | -2.747e-07 | 0.0029925 | 0.0029926 | 0.0029926 | 0.9883 | -0.22534 | 0.98826 | -0.22625 | 0.82214
8 | -0.0013838 | -0.00034681 | 0.0013838 | 0.00034644 | 4.9315e-08 | -3.6523e-07 | 0.0020722 | 0.002072 | 0.0020722 | 0.99369 | -0.12098 | 0.99373 | -0.12024 | 0.56928
9 | 0.033946 | 0.0085466 | -0.033888 | -0.0085104 | 5.7805e-05 | 3.6224e-05 | 0.050844 | 0.050845 | 0.050845 | 0.99373 | -0.12024 | 0.99188 | -0.15592 | 13.9683
10 | 0.010727 | 0.0026892 | -0.010724 | -0.0026876 | 3.031e-06 | 1.5341e-06 | 0.016063 | 0.016063 | 0.016063 | 0.99373 | -0.12024 | 0.99342 | -0.12617 | 4.4129
11 | -0.046056 | -0.011582 | 0.046276 | 0.011721 | 0.00021974 | 0.00013903 | 0.068979 | 0.068979 | 0.068979 | 0.99373 | -0.12024 | 0.99891 | -0.020858 | 18.9503
12 | 0.019744 | 0.0049649 | -0.019712 | -0.0049455 | 3.2216e-05 | 1.9357e-05 | 0.029626 | 0.029626 | 0.029626 | 0.99188 | -0.15592 | 0.99011 | -0.19014 | 8.139
13 | 0.014144 | 0.0035455 | -0.014142 | -0.0035443 | 2.2229e-06 | 1.2528e-06 | 0.021219 | 0.021219 | 0.021219 | 0.99188 | -0.15592 | 0.99171 | -0.15922 | 5.8294
14 | 0.00992 | 0.0024862 | -0.0099196 | -0.0024859 | 4.7339e-07 | 2.2895e-07 | 0.014859 | 0.014859 | 0.014859 | 0.99342 | -0.12617 | 0.99337 | -0.12717 | 4.0821
15 | -0.056648 | -0.014321 | 0.056691 | 0.014348 | 4.2764e-05 | 2.716e-05 | 0.084429 | 0.084429 | 0.084429 | 0.99891 | -0.020858 | 0.99973 | -0.005129 | 23.1947
16 | 0.016089 | 0.0040379 | -0.016067 | -0.0040251 | 2.1975e-05 | 1.2777e-05 | 0.024182 | 0.024183 | 0.024183 | 0.99011 | -0.19014 | 0.98864 | -0.21882 | 6.6436
17 | 0.0036223 | 0.00090759 | -0.003622 | -0.00090776 | 3.3035e-07 | -1.7084e-07 | 0.0054438 | 0.005444 | 0.005444 | 0.99011 | -0.19014 | 0.99002 | -0.19206 | 1.4956
18 | 0.0077974 | 0.0019542 | -0.0077966 | -0.0019539 | 7.7556e-07 | 3.0143e-07 | 0.0117 | 0.0117 | 0.0117 | 0.99171 | -0.15922 | 0.9916 | -0.16131 | 3.2142
19 | 0.0043063 | 0.0010791 | -0.004306 | -0.0010792 | 3.3159e-07 | -6.2864e-08 | 0.0064506 | 0.0064507 | 0.0064507 | 0.99337 | -0.12717 | 0.99329 | -0.12879 | 1.7722
20 | -0.05869 | -0.014849 | 0.058705 | 0.014858 | 1.4449e-05 | 9.1812e-06 | 0.087405 | 0.087405 | 0.087405 | 0.99973 | -0.005129 | 1 | 0 | 24.0124
21 | 0.0040951 | 0.0010262 | -0.0040949 | -0.0010263 | 1.3838e-07 | -3.7491e-08 | 0.0061451 | 0.0061451 | 0.0061451 | 0.9916 | -0.16131 | 0.99157 | -0.16202 | 1.6882
22 | 0.012777 | 0.003203 | -0.012774 | -0.0032015 | 2.7861e-06 | 1.5256e-06 | 0.019231 | 0.019231 | 0.019231 | 0.98864 | -0.21882 | 0.9884 | -0.2234 | 5.2832
23 | 0.0072062 | 0.0018061 | -0.0072055 | -0.0018059 | 7.549e-07 | 2.6395e-07 | 0.010849 | 0.010849 | 0.010849 | 0.9884 | -0.2234 | 0.98829 | -0.2256 | 2.9805
24 | 0.098478 | 0.02499 | -0.098031 | -0.024705 | 0.0004468 | 0.00028523 | 0.14665 | 0.14665 | 0.14665 | 1 | 0 | 0.99505 | -0.094798 | 40.2872
25 | 0.098031 | 0.024705 | -0.097778 | -0.024543 | 0.00025297 | 0.00016149 | 0.14665 | 0.14665 | 0.14665 | 0.99505 | -0.094798 | 0.99224 | -0.14889 | 40.2873
26 | -0.037818 | -0.0094781 | 0.037917 | 0.0095407 | 9.9373e-05 | 6.2544e-05 | 0.056877 | 0.056876 | 0.056877 | 0.9894 | -0.20389 | 0.99224 | -0.14889 | 15.6254

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.17026 | 0.042711

## res_load
| p_mw | q_mvar
0 | 0.00064237 | 0.00016099
1 | 0.00014875 | 3.7281e-05
2 | 0.0001415 | 3.5463e-05
3 | 0.0013838 | 0.00034681
4 | 0.00080387 | 0.00020147
5 | 0.010372 | 0.0025994
6 | 0.0063443 | 0.00159
7 | 0.0056132 | 0.0014068
8 | 0.0019997 | 0.00050116
9 | 0.0037015 | 0.00092769
10 | 0.0040949 | 0.0010263
11 | 0.003622 | 0.00090776
12 | 0.0055676 | 0.0013954
13 | 0.004306 | 0.0010792
14 | 0.0072055 | 0.0018059
15 | 0.00036971 | 9.2659e-05
16 | 0.0019875 | 0.00049812
17 | 0.011424 | 0.0028631
18 | 0.037818 | 0.0094781
19 | 0.05986 | 0.015002

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1