## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_112-9_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_112-9_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_112-9_0_5_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_112-9_0_5_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_112-9_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_112-9_0_5_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_112-9_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_112-9_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_112-9_0_5_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_112-9_0_5_node_66 | 0.4 | n |  | TRUE
10 | bus_LV_112-9_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_112-9_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_112-9_0_5_node_128 | 0.4 | n |  | TRUE
13 | bus_LV_112-9_0_5_node_127 | 0.4 | n |  | TRUE
14 | bus_LV_112-9_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_112-9_0_5_node_133 | 0.4 | n |  | TRUE
16 | bus_LV_112-9_0_5_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_112-9_0_5_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_112-9_0_5_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_112-9_0_5_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_112-9_0_5_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_112-9_0_5_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_112-9_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_112-9_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_112-9_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_112-9_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_112-9_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_112-9_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_112-9_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_112-9_0_5_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_112-9_0_5_node_58 | 0.4 | n |  | TRUE
31 | bus_LV_112-9_0_5_node_46 | 0.4 | n |  | TRUE
32 | bus_LV_112-9_0_5_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_112-9_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_112-9_0_5_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_112-9_0_5_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_112-9_0_5_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_112-9_0_5_node_56 | 0.4 | n |  | TRUE
38 | bus_LV_112-9_0_5_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_112-9_0_5_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_112-9_0_5_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_112-9_0_5_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_112-9_0_5_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_112-9_0_5_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_112-9_0_5_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_112-9_0_5_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_112-9_0_5_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_112-9_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_112-9_0_5_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_112-9_0_5_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_112-9_0_5_node_112 | 0.4 | n |  | TRUE
51 | bus_LV_112-9_0_5_node_124 | 0.4 | n |  | TRUE
52 | bus_LV_112-9_0_5_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_112-9_0_5_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_112-9_0_5_node_125 | 0.4 | n |  | TRUE
55 | bus_LV_112-9_0_5_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_112-9_0_5_node_106 | 0.4 | n |  | TRUE
57 | bus_LV_112-9_0_5_node_98 | 0.4 | n |  | TRUE
58 | bus_LV_112-9_0_5_node_104 | 0.4 | n |  | TRUE
59 | bus_LV_112-9_0_5_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_112-9_0_5_node_105 | 0.4 | n |  | TRUE
61 | bus_LV_112-9_0_5_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_112-9_0_5_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_112-9_0_5_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_112-9_0_5_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_112-9_0_5_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_112-9_0_5_node_129 | 0.4 | n |  | TRUE
67 | bus_LV_112-9_0_5_node_97 | 0.4 | n |  | TRUE
68 | bus_LV_112-9_0_5_node_96 | 0.4 | n |  | TRUE
69 | bus_LV_112-9_0_5_node_131 | 0.4 | n |  | TRUE
70 | bus_LV_112-9_0_5_node_102 | 0.4 | n |  | TRUE
71 | bus_LV_112-9_0_5_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_112-9_0_5_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_112-9_0_5_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_112-9_0_5_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_112-9_0_5_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_112-9_0_5_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_112-9_0_5_node_89 | 0.4 | n |  | TRUE
78 | bus_LV_112-9_0_5_node_130 | 0.4 | n |  | TRUE
79 | bus_LV_112-9_0_5_node_90 | 0.4 | n |  | TRUE
80 | bus_LV_112-9_0_5_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_112-9_0_5_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_112-9_0_5_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_112-9_0_5_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_112-9_0_5_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_112-9_0_5_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_112-9_0_5_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_112-9_0_5_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_112-9_0_5_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_112-9_0_5_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_112-9_0_5_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_112-9_0_5_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_112-9_0_5_node_87 | 0.4 | n |  | TRUE
93 | bus_LV_112-9_0_5_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_112-9_0_5_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_112-9_0_5_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_112-9_0_5_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_112-9_0_5_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_112-9_0_5_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_112-9_0_5_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_112-9_0_5_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_112-9_0_5_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_112-9_0_5_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_112-9_0_5_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_112-9_0_5_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_112-9_0_5_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_112-9_0_5_node_107 | 0.4 | n |  | TRUE
107 | bus_LV_112-9_0_5_node_118 | 0.4 | n |  | TRUE
108 | bus_LV_112-9_0_5_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_112-9_0_5_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_112-9_0_5_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_112-9_0_5_node_116 | 0.4 | n |  | TRUE
112 | bus_LV_112-9_0_5_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_112-9_0_5_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_112-9_0_5_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_112-9_0_5_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_112-9_0_5_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_112-9_0_5_node_121 | 0.4 | n |  | TRUE
118 | bus_LV_112-9_0_5_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_112-9_0_5_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_112-9_0_5_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_112-9_0_5_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_112-9_0_5_node_122 | 0.4 | n |  | TRUE
123 | bus_LV_112-9_0_5_node_123 | 0.4 | n |  | TRUE
124 | bus_LV_112-9_0_5_node_126 | 0.4 | n |  | TRUE
125 | bus_MV_8_1_node_72 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_112-9_0_5_load_0 | 0 | 0.0079371 | 0.0019892 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_112-9_0_5_load_9 | 2 | 0.0024412 | 0.00061183 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_112-9_0_5_load_10 | 3 | 0.0024745 | 0.00062016 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_112-9_0_5_load_48 | 5 | 0.0092897 | 0.0023282 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_112-9_0_5_load_66 | 9 | 0.0092958 | 0.0023297 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_112-9_0_5_load_128 | 12 | 0.0020461 | 0.00051279 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_112-9_0_5_load_127 | 13 | 0.0069471 | 0.0017411 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_112-9_0_5_load_133 | 15 | 0.0054905 | 0.001376 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_112-9_0_5_load_44 | 17 | 0.0048231 | 0.0012088 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_112-9_0_5_load_45 | 18 | 0.019299 | 0.0048369 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_112-9_0_5_load_49 | 19 | 0.0029793 | 0.00074667 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_112-9_0_5_load_60 | 20 | 0.008686 | 0.0021769 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_112-9_0_5_load_132 | 21 | 0.0022357 | 0.00056031 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_112-9_0_5_load_11 | 22 | 0.001162 | 0.00029123 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_112-9_0_5_load_15 | 26 | 0.0021104 | 0.00052891 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_112-9_0_5_load_54 | 29 | 0.0056065 | 0.0014051 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_112-9_0_5_load_46 | 31 | 0.0011136 | 0.0002791 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_112-9_0_5_load_59 | 32 | 0.0017405 | 0.00043621 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_112-9_0_5_load_42 | 34 | 0.0084994 | 0.0021301 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_112-9_0_5_load_53 | 35 | 0.0040672 | 0.0010193 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_112-9_0_5_load_39 | 36 | 0.070063 | 0.017559 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_112-9_0_5_load_56 | 37 | 0.00081504 | 0.00020427 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_112-9_0_5_load_51 | 38 | 0.0026118 | 0.00065458 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_112-9_0_5_load_20 | 41 | 0.0054949 | 0.0013771 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_112-9_0_5_load_21 | 42 | 0.0016077 | 0.00040292 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_112-9_0_5_load_24 | 45 | 0.0012088 | 0.00030297 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_112-9_0_5_load_25 | 46 | 0.0013491 | 0.00033812 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_112-9_0_5_load_26 | 47 | 0.001498 | 0.00037543 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_112-9_0_5_load_30 | 48 | 0.0087211 | 0.0021857 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_112-9_0_5_load_27 | 49 | 0.0017305 | 0.0004337 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_112-9_0_5_load_112 | 50 | 0.00062847 | 0.00015751 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_112-9_0_5_load_124 | 51 | 0.00045595 | 0.00011427 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_112-9_0_5_load_28 | 52 | 0.00079569 | 0.00019942 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_112-9_0_5_load_111 | 53 | 0.00045518 | 0.00011408 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_112-9_0_5_load_125 | 54 | 0.00046676 | 0.00011698 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_112-9_0_5_load_106 | 56 | 0.00063542 | 0.00015925 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_112-9_0_5_load_104 | 58 | 0.0017003 | 0.00042614 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_112-9_0_5_load_105 | 60 | 0.0011933 | 0.00029907 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_112-9_0_5_load_32 | 61 | 0.0023071 | 0.00057822 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_112-9_0_5_load_57 | 63 | 0.00068178 | 0.00017087 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_112-9_0_5_load_129 | 66 | 0.01123 | 0.0028144 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_112-9_0_5_load_97 | 67 | 0.0080482 | 0.0020171 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_112-9_0_5_load_96 | 68 | 0.0063316 | 0.0015868 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_112-9_0_5_load_131 | 69 | 0.0028958 | 0.00072576 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_112-9_0_5_load_102 | 70 | 0.062155 | 0.015578 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_112-9_0_5_load_50 | 71 | 0.0027522 | 0.00068977 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_112-9_0_5_load_61 | 72 | 0.0019518 | 0.00048918 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_112-9_0_5_load_62 | 73 | 0.0049663 | 0.0012447 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_112-9_0_5_load_64 | 75 | 0.043038 | 0.010786 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_112-9_0_5_load_89 | 77 | 0.058545 | 0.014673 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_112-9_0_5_load_130 | 78 | 0.0023594 | 0.00059133 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_112-9_0_5_load_90 | 79 | 0.079732 | 0.019983 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_112-9_0_5_load_76 | 82 | 0.0013042 | 0.00032687 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_112-9_0_5_load_71 | 83 | 0.0025815 | 0.00064699 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_112-9_0_5_load_67 | 84 | 0.0035195 | 0.00088208 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_112-9_0_5_load_68 | 85 | 0.0018294 | 0.0004585 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_112-9_0_5_load_69 | 86 | 0.0025376 | 0.00063598 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_112-9_0_5_load_70 | 87 | 0.0018947 | 0.00047487 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_112-9_0_5_load_72 | 88 | 0.0011009 | 0.00027592 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_112-9_0_5_load_73 | 89 | 0.0012677 | 0.00031772 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_112-9_0_5_load_74 | 90 | 0.0013879 | 0.00034784 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_112-9_0_5_load_75 | 91 | 0.001639 | 0.00041077 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_112-9_0_5_load_87 | 92 | 0.0027731 | 0.00069499 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_112-9_0_5_load_84 | 93 | 0.001404 | 0.00035188 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_112-9_0_5_load_85 | 94 | 0.0018286 | 0.00045829 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_112-9_0_5_load_79 | 95 | 0.0011508 | 0.00028842 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_112-9_0_5_load_80 | 96 | 0.0017309 | 0.00043382 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_112-9_0_5_load_81 | 97 | 0.0041191 | 0.0010324 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_112-9_0_5_load_82 | 98 | 0.001675 | 0.0004198 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_112-9_0_5_load_94 | 102 | 0.00053954 | 0.00013522 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_112-9_0_5_load_95 | 103 | 0.0012945 | 0.00032444 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_112-9_0_5_load_86 | 104 | 0.0013802 | 0.00034592 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_112-9_0_5_load_99 | 105 | 0.0055991 | 0.0014033 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_112-9_0_5_load_107 | 106 | 0.0014937 | 0.00037435 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_112-9_0_5_load_118 | 107 | 0.0020073 | 0.00050307 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_112-9_0_5_load_91 | 108 | 0.048348 | 0.012117 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_112-9_0_5_load_100 | 109 | 0.0017295 | 0.00043346 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_112-9_0_5_load_108 | 110 | 0.00083156 | 0.00020841 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_112-9_0_5_load_103 | 113 | 0.0004587 | 0.00011496 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_112-9_0_5_load_109 | 114 | 0.00045057 | 0.00011292 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_112-9_0_5_load_113 | 116 | 0.00084075 | 0.00021071 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_112-9_0_5_load_121 | 117 | 0.00088226 | 0.00022112 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_112-9_0_5_load_120 | 118 | 0.00061891 | 0.00015511 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_112-9_0_5_load_114 | 119 | 0.0018421 | 0.00046168 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_112-9_0_5_load_115 | 120 | 0.00043765 | 0.00010969 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_112-9_0_5_load_117 | 121 | 0.004104 | 0.0010286 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_112-9_0_5_load_122 | 122 | 0.00045867 | 0.00011495 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_112-9_0_5_load_123 | 123 | 0.00043105 | 0.00010803 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_112-9_0_5_load_126 | 124 | 0.00057106 | 0.00014312 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_112-9_0_5_line_0 |  | 0 | 1 | 0.0091588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_112-9_0_5_line_1 |  | 1 | 2 | 0.013456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_112-9_0_5_line_2 |  | 1 | 3 | 0.012292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_112-9_0_5_line_3 |  | 2 | 4 | 0.010081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_112-9_0_5_line_4 |  | 3 | 10 | 0.019262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_112-9_0_5_line_5 |  | 4 | 5 | 0.0053787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_112-9_0_5_line_6 |  | 5 | 19 | 0.0071881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_112-9_0_5_line_7 |  | 6 | 7 | 0.048062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_112-9_0_5_line_8 |  | 6 | 8 | 0.033604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_112-9_0_5_line_9 |  | 6 | 9 | 0.02108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_112-9_0_5_line_10 |  | 7 | 15 | 0.014195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_112-9_0_5_line_11 |  | 7 | 14 | 0.043759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_112-9_0_5_line_12 |  | 8 | 20 | 0.0057879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_112-9_0_5_line_13 |  | 9 | 10 | 0.023432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_112-9_0_5_line_14 |  | 11 | 12 | 0.029041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_112-9_0_5_line_15 |  | 11 | 13 | 0.025247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_112-9_0_5_line_16 |  | 12 | 21 | 0.0013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_112-9_0_5_line_17 |  | 13 | 14 | 0.0064339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_112-9_0_5_line_18 |  | 16 | 17 | 0.012649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_112-9_0_5_line_19 |  | 16 | 18 | 0.015205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_112-9_0_5_line_20 |  | 17 | 33 | 0.03215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_112-9_0_5_line_21 |  | 18 | 31 | 0.0025547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_112-9_0_5_line_22 |  | 19 | 71 | 0.0075116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_112-9_0_5_line_23 |  | 20 | 72 | 0.022349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_112-9_0_5_line_24 |  | 22 | 23 | 0.02142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_112-9_0_5_line_25 |  | 23 | 27 | 0.011836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_112-9_0_5_line_26 |  | 23 | 28 | 0.015307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_112-9_0_5_line_27 |  | 24 | 25 | 0.017229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_112-9_0_5_line_28 |  | 24 | 26 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_112-9_0_5_line_29 |  | 25 | 29 | 0.02117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_112-9_0_5_line_30 |  | 26 | 30 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_112-9_0_5_line_31 |  | 27 | 31 | 0.015704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_112-9_0_5_line_32 |  | 28 | 32 | 0.017911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_112-9_0_5_line_33 |  | 29 | 35 | 0.018603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_112-9_0_5_line_34 |  | 30 | 36 | 0.0086492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_112-9_0_5_line_35 |  | 30 | 37 | 0.02158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_112-9_0_5_line_36 |  | 32 | 40 | 0.038814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_112-9_0_5_line_37 |  | 33 | 34 | 0.018756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_112-9_0_5_line_38 |  | 35 | 39 | 0.0094555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_112-9_0_5_line_39 |  | 36 | 62 | 0.018237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_112-9_0_5_line_40 |  | 37 | 63 | 0.024054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_112-9_0_5_line_41 |  | 38 | 39 | 0.022868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_112-9_0_5_line_42 |  | 39 | 71 | 0.0059912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_112-9_0_5_line_43 |  | 40 | 63 | 0.021013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_112-9_0_5_line_44 |  | 41 | 42 | 0.017053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_112-9_0_5_line_45 |  | 41 | 43 | 0.015863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_112-9_0_5_line_46 |  | 42 | 44 | 0.017248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_112-9_0_5_line_47 |  | 43 | 45 | 0.011399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_112-9_0_5_line_48 |  | 43 | 46 | 0.013589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_112-9_0_5_line_49 |  | 43 | 47 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_112-9_0_5_line_50 |  | 44 | 48 | 0.015001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_112-9_0_5_line_51 |  | 45 | 49 | 0.017713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_112-9_0_5_line_52 |  | 46 | 50 | 0.0052245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_112-9_0_5_line_53 |  | 47 | 51 | 0.021368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_112-9_0_5_line_54 |  | 49 | 52 | 0.010519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_112-9_0_5_line_55 |  | 50 | 53 | 0.0015975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_112-9_0_5_line_56 |  | 51 | 54 | 0.0060408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_112-9_0_5_line_57 |  | 52 | 55 | 0.017358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_112-9_0_5_line_58 |  | 53 | 115 | 0.0096994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_112-9_0_5_line_59 |  | 54 | 124 | 0.0063139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_112-9_0_5_line_60 |  | 55 | 56 | 0.023807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_112-9_0_5_line_61 |  | 56 | 60 | 0.0064144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_112-9_0_5_line_62 |  | 57 | 58 | 0.056914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_112-9_0_5_line_63 |  | 57 | 59 | 0.028473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_112-9_0_5_line_64 |  | 58 | 112 | 0.016458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_112-9_0_5_line_65 |  | 59 | 67 | 0.014919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_112-9_0_5_line_66 |  | 60 | 113 | 0.0015794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_112-9_0_5_line_67 |  | 61 | 62 | 0.025031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_112-9_0_5_line_68 |  | 64 | 65 | 0.009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_112-9_0_5_line_69 |  | 64 | 66 | 0.032619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_112-9_0_5_line_70 |  | 65 | 68 | 0.0027789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_112-9_0_5_line_71 |  | 67 | 68 | 0.021999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_112-9_0_5_line_72 |  | 69 | 70 | 0.012144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_112-9_0_5_line_73 |  | 70 | 101 | 0.0045006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_112-9_0_5_line_74 |  | 72 | 73 | 0.020686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_112-9_0_5_line_75 |  | 73 | 74 | 0.014843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_112-9_0_5_line_76 |  | 74 | 75 | 0.022276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_112-9_0_5_line_77 |  | 74 | 76 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_112-9_0_5_line_78 |  | 75 | 77 | 0.0021317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_112-9_0_5_line_79 |  | 76 | 78 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_112-9_0_5_line_80 |  | 77 | 79 | 0.017943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_112-9_0_5_line_81 |  | 78 | 83 | 0.0010463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_112-9_0_5_line_82 |  | 79 | 108 | 0.024213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_112-9_0_5_line_83 |  | 80 | 81 | 0.003103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_112-9_0_5_line_84 |  | 80 | 82 | 0.020935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_112-9_0_5_line_85 |  | 81 | 92 | 0.029878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_112-9_0_5_line_86 |  | 81 | 93 | 0.010048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_112-9_0_5_line_87 |  | 82 | 91 | 0.0027323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_112-9_0_5_line_88 |  | 83 | 86 | 0.012943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_112-9_0_5_line_89 |  | 84 | 85 | 0.0052786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_112-9_0_5_line_90 |  | 84 | 86 | 0.013599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_112-9_0_5_line_91 |  | 85 | 87 | 0.0090061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_112-9_0_5_line_92 |  | 87 | 88 | 0.011571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_112-9_0_5_line_93 |  | 88 | 89 | 0.0073178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_112-9_0_5_line_94 |  | 89 | 90 | 0.001852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_112-9_0_5_line_95 |  | 90 | 91 | 0.010163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_112-9_0_5_line_96 |  | 93 | 94 | 0.0099415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_112-9_0_5_line_97 |  | 94 | 104 | 0.012841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_112-9_0_5_line_98 |  | 95 | 96 | 0.016095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_112-9_0_5_line_99 |  | 95 | 97 | 0.004932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_112-9_0_5_line_100 |  | 96 | 98 | 0.0058015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_112-9_0_5_line_101 |  | 97 | 99 | 0.01872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_112-9_0_5_line_102 |  | 98 | 100 | 0.0093654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_112-9_0_5_line_103 |  | 99 | 101 | 0.028552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_112-9_0_5_line_104 |  | 99 | 102 | 0.028569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_112-9_0_5_line_105 |  | 99 | 103 | 0.045766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_112-9_0_5_line_106 |  | 100 | 104 | 0.0054341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_112-9_0_5_line_107 |  | 101 | 105 | 0.0088547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_112-9_0_5_line_108 |  | 102 | 106 | 0.0085531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_112-9_0_5_line_109 |  | 103 | 107 | 0.00028933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_112-9_0_5_line_110 |  | 105 | 109 | 0.018363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_112-9_0_5_line_111 |  | 106 | 110 | 0.0066746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_112-9_0_5_line_112 |  | 107 | 111 | 0.032499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_112-9_0_5_line_113 |  | 109 | 112 | 0.01486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_112-9_0_5_line_114 |  | 110 | 114 | 0.019284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_112-9_0_5_line_115 |  | 111 | 119 | 0.014849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_112-9_0_5_line_116 |  | 114 | 115 | 0.0093918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_112-9_0_5_line_117 |  | 115 | 116 | 0.012947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_112-9_0_5_line_118 |  | 116 | 117 | 0.0060366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_112-9_0_5_line_119 |  | 117 | 118 | 0.016713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_112-9_0_5_line_120 |  | 118 | 122 | 0.0071714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_112-9_0_5_line_121 |  | 119 | 120 | 0.049141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_112-9_0_5_line_122 |  | 120 | 121 | 0.022412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_112-9_0_5_line_123 |  | 122 | 123 | 0.0020253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_112-9_0_5_trafo_90 | 0.63 MVA 20/0.4 kV | 125 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2704322.67 | 1236244.0887 | 2704317.2977 | 1236244.0055 | 2704313.7221 | 1236242.7614
1 | 2704322.67 | 1236244.0887 | 2704333.1978 | 1236244.107 | 2704335.0176 | 1236243.9165 | 2704335.8942 | 1236243.2545
2 | 2704322.67 | 1236244.0887 | 2704325.3691 | 1236247.2719 | 2704328.5382 | 1236249.5515 | 2704328.3582 | 1236253.7627
3 | 2704343.9385 | 1236237.1792 | 2704335.8942 | 1236243.2545
4 | 2704320.3608 | 1236271.2689 | 2704321.9696 | 1236267.1496 | 2704325.7314 | 1236259.3875 | 2704327.0075 | 1236256.9747 | 2704328.3582 | 1236253.7627
5 | 2704343.9385 | 1236237.1792 | 2704349.2697 | 1236237.8923
6 | 2704349.2697 | 1236237.8923 | 2704356.3943 | 1236238.8454
7 | 2704326.7543 | 1236332.539 | 2704334.1784 | 1236327.8436 | 2704342.8891 | 1236318.8453 | 2704348.8856 | 1236306.6635 | 2704341.1386 | 1236303.892 | 2704336.4702 | 1236305.5335
8 | 2704336.4702 | 1236305.5335 | 2704341.1386 | 1236303.892 | 2704348.8856 | 1236306.6635 | 2704367.6102 | 1236298.4973
9 | 2704336.4702 | 1236305.5335 | 2704334.9598 | 1236284.5072
10 | 2704326.7543 | 1236332.539 | 2704332.0097 | 1236345.7302
11 | 2704285.0292 | 1236332.9401 | 2704289.2566 | 1236335.7164 | 2704299.1605 | 1236337.6362 | 2704306.4879 | 1236337.5759 | 2704312.998 | 1236337.5124 | 2704322.1349 | 1236335.2711 | 2704326.7543 | 1236332.539
12 | 2704367.6102 | 1236298.4973 | 2704367.6664 | 1236304.285
13 | 2704320.3608 | 1236271.2689 | 2704334.3365 | 1236275.7844 | 2704334.6764 | 1236280.5607 | 2704334.9598 | 1236284.5072
14 | 2704261.898 | 1236312.3406 | 2704254.5085 | 1236315.9359 | 2704233.8124 | 1236318.2345
15 | 2704261.898 | 1236312.3406 | 2704267.2435 | 1236321.2746 | 2704279.6492 | 1236329.4114
16 | 2704232.4635 | 1236318.3843 | 2704233.8124 | 1236318.2345
17 | 2704285.0292 | 1236332.9401 | 2704279.6492 | 1236329.4114
18 | 2704409.8301 | 1236187.3544 | 2704419.6223 | 1236180.1432 | 2704420.0739 | 1236179.957
19 | 2704409.8301 | 1236187.3544 | 2704414.0451 | 1236197.7253 | 2704416.5622 | 1236200.8473
20 | 2704450.7365 | 1236181.9248 | 2704429.1676 | 1236176.208 | 2704420.0739 | 1236179.957
21 | 2704416.5622 | 1236200.8473 | 2704418.1657 | 1236202.8361
22 | 2704363.8395 | 1236239.8413 | 2704356.3943 | 1236238.8454
23 | 2704367.6664 | 1236304.285 | 2704367.7341 | 1236311.2536 | 2704371.1565 | 1236320.6432 | 2704372.9813 | 1236325.7104
24 | 2704439.596 | 1236212.43 | 2704435.4293 | 1236216.9491 | 2704429.7702 | 1236222.843 | 2704426.4043 | 1236229.0966
25 | 2704439.596 | 1236212.43 | 2704428.0224 | 1236215.0619
26 | 2704439.596 | 1236212.43 | 2704446.0455 | 1236205.4937 | 2704450.0889 | 1236209.7013
27 | 2704424.925 | 1236273.2519 | 2704407.9524 | 1236270.0178
28 | 2704424.925 | 1236273.2519 | 2704428.0226 | 1236281.7461 | 2704431.3072 | 1236288.2463
29 | 2704407.9524 | 1236270.0178 | 2704403.9921 | 1236262.3757 | 2704393.1573 | 1236256.0175
30 | 2704441.5741 | 1236301.3326 | 2704435.9732 | 1236294.8848 | 2704432.0307 | 1236289.6782 | 2704431.3072 | 1236288.2463
31 | 2704428.0224 | 1236215.0619 | 2704418.1657 | 1236202.8361
32 | 2704450.0889 | 1236209.7013 | 2704450.3234 | 1236212.7188 | 2704460.3658 | 1236223.7044
33 | 2704393.1573 | 1236256.0175 | 2704377.113 | 1236246.6025 | 2704377.113 | 1236246.6025
34 | 2704441.5741 | 1236301.3326 | 2704446.1982 | 1236305.6505 | 2704448.1157 | 1236306.9609
35 | 2704441.5741 | 1236301.3326 | 2704445.198 | 1236295.3918 | 2704455.3458 | 1236284.8661
36 | 2704486.5538 | 1236252.3528 | 2704484.7567 | 1236250.3864 | 2704460.3658 | 1236223.7044
37 | 2704450.7365 | 1236181.9248 | 2704456.2654 | 1236176.5513 | 2704457.601 | 1236169.903 | 2704456.5079 | 1236165.7807
38 | 2704369.7779 | 1236240.6357 | 2704377.113 | 1236246.6025
39 | 2704463.5957 | 1236316.5647 | 2704456.1524 | 1236312.4529 | 2704448.1157 | 1236306.9609
40 | 2704455.3458 | 1236284.8661 | 2704463.1608 | 1236276.76 | 2704472.0136 | 1236267.5234
41 | 2704369.7779 | 1236240.6357 | 2704380.6221 | 1236239.0139 | 2704392.0506 | 1236235.6878
42 | 2704369.7779 | 1236240.6357 | 2704363.8395 | 1236239.8413
43 | 2704486.5538 | 1236252.3528 | 2704472.0136 | 1236267.5234
44 | 2704536.955 | 1236532.5653 | 2704549.6547 | 1236543.9462
45 | 2704526.6958 | 1236520.7082 | 2704529.9802 | 1236526.3147 | 2704536.955 | 1236532.5653
46 | 2704562.5028 | 1236555.4537 | 2704553.8003 | 1236547.6613 | 2704549.6547 | 1236543.9462
47 | 2704526.6958 | 1236520.7082 | 2704535.684 | 1236513.6983
48 | 2704526.6958 | 1236520.7082 | 2704521.2967 | 1236508.2379
49 | 2704526.6958 | 1236520.7082 | 2704518.4671 | 1236522.9651 | 2704513.4564 | 1236526.461
50 | 2704562.5028 | 1236555.4537 | 2704566.4107 | 1236554.444 | 2704575.5372 | 1236560.5219
51 | 2704535.684 | 1236513.6983 | 2704549.6515 | 1236502.805
52 | 2704521.2967 | 1236508.2379 | 2704519.2209 | 1236503.4435
53 | 2704495.9318 | 1236538.6872 | 2704513.4564 | 1236526.461
54 | 2704549.6515 | 1236502.805 | 2704557.9464 | 1236496.3358
55 | 2704518.5861 | 1236501.9775 | 2704519.2209 | 1236503.4435
56 | 2704495.9318 | 1236538.6872 | 2704490.9776 | 1236542.1435
57 | 2704571.6336 | 1236485.6611 | 2704557.9464 | 1236496.3358
58 | 2704514.7324 | 1236493.0766 | 2704518.5861 | 1236501.9775
59 | 2704485.7994 | 1236545.7562 | 2704490.9776 | 1236542.1435
60 | 2704571.6336 | 1236485.6611 | 2704556.2447 | 1236467.4965
61 | 2704552.0984 | 1236462.6023 | 2704556.2447 | 1236467.4965
62 | 2704581.6814 | 1236384.016 | 2704538.4886 | 1236421.0775
63 | 2704556.8859 | 1236369.891 | 2704581.6814 | 1236384.016
64 | 2704525.9985 | 1236431.7947 | 2704538.4886 | 1236421.0775
65 | 2704556.8859 | 1236369.891 | 2704543.8819 | 1236362.5786
66 | 2704552.0984 | 1236462.6023 | 2704551.0775 | 1236461.3973
67 | 2704463.5957 | 1236316.5647 | 2704469.036 | 1236310.2 | 2704476.72 | 1236307.9445 | 2704483.1434 | 1236302.1513
68 | 2704522.2844 | 1236350.4339 | 2704526.6539 | 1236342.5603
69 | 2704526.6539 | 1236342.5603 | 2704507.7791 | 1236331.3086 | 2704514.337 | 1236322.9241
70 | 2704522.2844 | 1236350.4339 | 2704524.7066 | 1236351.796
71 | 2704524.7066 | 1236351.796 | 2704543.8819 | 1236362.5786
72 | 2704497.557 | 1236396.7057 | 2704497.9321 | 1236392.8045 | 2704498.4144 | 1236384.5939
73 | 2704497.1262 | 1236401.1856 | 2704497.557 | 1236396.7057
74 | 2704379.9899 | 1236345.1729 | 2704372.9813 | 1236325.7104
75 | 2704385.0189 | 1236359.1383 | 2704379.9899 | 1236345.1729
76 | 2704385.0189 | 1236359.1383 | 2704406.765 | 1236363.9681
77 | 2704387.9833 | 1236371.333 | 2704385.0189 | 1236359.1383
78 | 2704408.8461 | 1236364.4303 | 2704406.765 | 1236363.9681
79 | 2704387.9833 | 1236371.333 | 2704370.5074 | 1236376.4195
80 | 2704408.8461 | 1236364.4303 | 2704426.3626 | 1236368.3207
81 | 2704369.5027 | 1236376.7119 | 2704370.5074 | 1236376.4195
82 | 2704426.3626 | 1236368.3207 | 2704449.9995 | 1236373.5705
83 | 2704396.3613 | 1236405.7843 | 2704397.0954 | 1236408.7995
84 | 2704396.3613 | 1236405.7843 | 2704376.1554 | 1236411.2614
85 | 2704397.0954 | 1236408.7995 | 2704401.2347 | 1236433.3687 | 2704401.4575 | 1236438.3261
86 | 2704397.0954 | 1236408.7995 | 2704406.9658 | 1236410.6813
87 | 2704373.5183 | 1236411.9762 | 2704376.1554 | 1236411.2614
88 | 2704369.5027 | 1236376.7119 | 2704357.0753 | 1236380.3291
89 | 2704347.2703 | 1236387.3633 | 2704347.2703 | 1236387.3633 | 2704348.7954 | 1236392.4168
90 | 2704347.2703 | 1236387.3633 | 2704348.569 | 1236382.8049 | 2704357.0753 | 1236380.3291
91 | 2704348.7954 | 1236392.4168 | 2704351.3975 | 1236401.0388
92 | 2704355.3946 | 1236411.5629 | 2704354.4294 | 1236411.085 | 2704351.3975 | 1236401.0388
93 | 2704361.9524 | 1236414.8102 | 2704355.3946 | 1236411.5629
94 | 2704361.9524 | 1236414.8102 | 2704362.3453 | 1236415.0048 | 2704363.7097 | 1236414.6349
95 | 2704373.5183 | 1236411.9762 | 2704363.7097 | 1236414.6349
96 | 2704406.9658 | 1236410.6813 | 2704416.7314 | 1236412.5431
97 | 2704429.3453 | 1236414.9479 | 2704416.7314 | 1236412.5431
98 | 2704465.2982 | 1236422.2928 | 2704449.5362 | 1236419.0353
99 | 2704465.2982 | 1236422.2928 | 2704470.1282 | 1236423.291
100 | 2704449.5362 | 1236419.0353 | 2704443.8547 | 1236417.8611
101 | 2704488.1523 | 1236428.1373 | 2704484.6285 | 1236426.6742 | 2704481.1437 | 1236425.5676 | 2704470.1282 | 1236423.291
102 | 2704434.6832 | 1236415.9656 | 2704443.8547 | 1236417.8611
103 | 2704497.1262 | 1236401.1856 | 2704495.6022 | 1236409.076 | 2704493.6459 | 1236415.7355 | 2704491.1407 | 1236422.1853 | 2704488.1523 | 1236428.1373
104 | 2704488.1523 | 1236428.1373 | 2704495.3438 | 1236437.5153 | 2704505.568 | 1236450.7837
105 | 2704488.1523 | 1236428.1373 | 2704483.8127 | 1236435.6111 | 2704479.6549 | 1236441.7871 | 2704475.0548 | 1236447.7219 | 2704459.741 | 1236463.7522
106 | 2704434.6832 | 1236415.9656 | 2704429.3453 | 1236414.9479
107 | 2704497.1262 | 1236401.1856 | 2704503.202 | 1236407.6269
108 | 2704505.568 | 1236450.7837 | 2704507.1311 | 1236452.8121 | 2704506.3 | 1236458.7465
109 | 2704459.741 | 1236463.7522 | 2704459.5412 | 1236463.9614
110 | 2704503.202 | 1236407.6269 | 2704515.8018 | 1236420.9847
111 | 2704507.8922 | 1236465.2284 | 2704506.3 | 1236458.7465 | 2704506.3 | 1236458.7465
112 | 2704435.4683 | 1236485.7771 | 2704444.6944 | 1236477.5886 | 2704456.804 | 1236466.8266 | 2704459.5412 | 1236463.9614
113 | 2704525.9985 | 1236431.7947 | 2704515.8018 | 1236420.9847
114 | 2704507.8922 | 1236465.2284 | 2704512.4921 | 1236483.9559
115 | 2704435.4683 | 1236485.7771 | 2704443.2595 | 1236498.4181
116 | 2704514.7324 | 1236493.0766 | 2704512.4921 | 1236483.9559
117 | 2704514.7324 | 1236493.0766 | 2704504.2272 | 1236500.6435
118 | 2704504.2272 | 1236500.6435 | 2704499.329 | 1236504.1716
119 | 2704485.48 | 1236513.4506 | 2704488.2707 | 1236512.1368 | 2704499.329 | 1236504.1716
120 | 2704485.48 | 1236513.4506 | 2704478.9915 | 1236516.505
121 | 2704443.2595 | 1236498.4181 | 2704469.0434 | 1236540.2515
122 | 2704480.8026 | 1236559.3304 | 2704469.0434 | 1236540.2515
123 | 2704477.1591 | 1236517.3676 | 2704478.9915 | 1236516.505

## bus_geodata
| x | y | coords
0 | 2704313.7221 | 1236242.7614
1 | 2704322.67 | 1236244.0887
2 | 2704335.8942 | 1236243.2545
3 | 2704328.3582 | 1236253.7627
4 | 2704343.9385 | 1236237.1792
5 | 2704349.2697 | 1236237.8923
6 | 2704336.4702 | 1236305.5335
7 | 2704326.7543 | 1236332.539
8 | 2704367.6102 | 1236298.4973
9 | 2704334.9598 | 1236284.5072
10 | 2704320.3608 | 1236271.2689
11 | 2704261.898 | 1236312.3406
12 | 2704233.8124 | 1236318.2345
13 | 2704279.6492 | 1236329.4114
14 | 2704285.0292 | 1236332.9401
15 | 2704332.0097 | 1236345.7302
16 | 2704409.8301 | 1236187.3544
17 | 2704420.0739 | 1236179.957
18 | 2704416.5622 | 1236200.8473
19 | 2704356.3943 | 1236238.8454
20 | 2704367.6664 | 1236304.285
21 | 2704232.4635 | 1236318.3843
22 | 2704426.4043 | 1236229.0966
23 | 2704439.596 | 1236212.43
24 | 2704424.925 | 1236273.2519
25 | 2704407.9524 | 1236270.0178
26 | 2704431.3072 | 1236288.2463
27 | 2704428.0224 | 1236215.0619
28 | 2704450.0889 | 1236209.7013
29 | 2704393.1573 | 1236256.0175
30 | 2704441.5741 | 1236301.3326
31 | 2704418.1657 | 1236202.8361
32 | 2704460.3658 | 1236223.7044
33 | 2704450.7365 | 1236181.9248
34 | 2704456.5079 | 1236165.7807
35 | 2704377.113 | 1236246.6025
36 | 2704448.1157 | 1236306.9609
37 | 2704455.3458 | 1236284.866
38 | 2704392.0506 | 1236235.6878
39 | 2704369.7779 | 1236240.6357
40 | 2704486.5538 | 1236252.3528
41 | 2704536.955 | 1236532.5653
42 | 2704549.6547 | 1236543.9462
43 | 2704526.6958 | 1236520.7082
44 | 2704562.5028 | 1236555.4537
45 | 2704535.684 | 1236513.6983
46 | 2704521.2967 | 1236508.2379
47 | 2704513.4564 | 1236526.461
48 | 2704575.5372 | 1236560.5219
49 | 2704549.6515 | 1236502.805
50 | 2704519.2208 | 1236503.4435
51 | 2704495.9318 | 1236538.6872
52 | 2704557.9464 | 1236496.3358
53 | 2704518.5861 | 1236501.9775
54 | 2704490.9776 | 1236542.1435
55 | 2704571.6336 | 1236485.6611
56 | 2704556.2447 | 1236467.4965
57 | 2704581.6814 | 1236384.016
58 | 2704538.4886 | 1236421.0775
59 | 2704556.8859 | 1236369.891
60 | 2704552.0984 | 1236462.6023
61 | 2704483.1434 | 1236302.1513
62 | 2704463.5957 | 1236316.5647
63 | 2704472.0136 | 1236267.5234
64 | 2704526.6539 | 1236342.5603
65 | 2704522.2844 | 1236350.4339
66 | 2704514.337 | 1236322.9241
67 | 2704543.8819 | 1236362.5786
68 | 2704524.7066 | 1236351.796
69 | 2704498.4144 | 1236384.5939
70 | 2704497.557 | 1236396.7057
71 | 2704363.8395 | 1236239.8413
72 | 2704372.9813 | 1236325.7104
73 | 2704379.9899 | 1236345.1729
74 | 2704385.0189 | 1236359.1383
75 | 2704406.765 | 1236363.9681
76 | 2704387.9833 | 1236371.333
77 | 2704408.8461 | 1236364.4303
78 | 2704370.5074 | 1236376.4195
79 | 2704426.3626 | 1236368.3207
80 | 2704396.3613 | 1236405.7843
81 | 2704397.0954 | 1236408.7995
82 | 2704376.1554 | 1236411.2614
83 | 2704369.5027 | 1236376.7119
84 | 2704347.2703 | 1236387.3633
85 | 2704348.7954 | 1236392.4168
86 | 2704357.0753 | 1236380.3291
87 | 2704351.3975 | 1236401.0388
88 | 2704355.3946 | 1236411.5629
89 | 2704361.9524 | 1236414.8102
90 | 2704363.7097 | 1236414.6349
91 | 2704373.5183 | 1236411.9762
92 | 2704401.4575 | 1236438.3261
93 | 2704406.9658 | 1236410.6813
94 | 2704416.7314 | 1236412.5431
95 | 2704465.2982 | 1236422.2928
96 | 2704449.5362 | 1236419.0353
97 | 2704470.1282 | 1236423.291
98 | 2704443.8548 | 1236417.8611
99 | 2704488.1523 | 1236428.1373
100 | 2704434.6832 | 1236415.9656
101 | 2704497.1262 | 1236401.1856
102 | 2704505.568 | 1236450.7837
103 | 2704459.741 | 1236463.7522
104 | 2704429.3453 | 1236414.9479
105 | 2704503.202 | 1236407.627
106 | 2704506.3 | 1236458.7465
107 | 2704459.5412 | 1236463.9614
108 | 2704449.9995 | 1236373.5705
109 | 2704515.8018 | 1236420.9847
110 | 2704507.8922 | 1236465.2284
111 | 2704435.4683 | 1236485.7771
112 | 2704525.9985 | 1236431.7947
113 | 2704551.0775 | 1236461.3973
114 | 2704512.4921 | 1236483.9559
115 | 2704514.7324 | 1236493.0766
116 | 2704504.2272 | 1236500.6435
117 | 2704499.329 | 1236504.1716
118 | 2704485.48 | 1236513.4506
119 | 2704443.2595 | 1236498.4181
120 | 2704469.0434 | 1236540.2515
121 | 2704480.8026 | 1236559.3304
122 | 2704478.9915 | 1236516.505
123 | 2704477.1591 | 1236517.3676
124 | 2704485.7994 | 1236545.7562
125 | 2704434.424 | 1236370.1111

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98892 | -0.21116 | 0.0079371 | 0.0019892
1 | 0.98899 | -0.20986 | 0 | 0
2 | 0.98855 | -0.2184 | 0.0024412 | 0.00061183
3 | 0.98942 | -0.20163 | 0.0024745 | 0.00062016
4 | 0.98822 | -0.22469 | 0 | 0
5 | 0.98804 | -0.22805 | 0.0092897 | 0.0023282
6 | 0.99172 | -0.15749 | 0 | 0
7 | 0.99099 | -0.17174 | 0 | 0
8 | 0.99311 | -0.1309 | 0 | 0
9 | 0.99093 | -0.17264 | 0.0092958 | 0.0023297
10 | 0.9901 | -0.18854 | 0 | 0
11 | 0.99037 | -0.18368 | 0 | 0
12 | 0.99026 | -0.18589 | 0.0020461 | 0.00051279
13 | 0.99047 | -0.18175 | 0.0069471 | 0.0017411
14 | 0.99054 | -0.18047 | 0 | 0
15 | 0.99092 | -0.17313 | 0.0054905 | 0.001376
16 | 0.97153 | -0.55004 | 0 | 0
17 | 0.97137 | -0.55315 | 0.0048231 | 0.0012088
18 | 0.97172 | -0.5463 | 0.019299 | 0.0048369
19 | 0.98782 | -0.23224 | 0.0029793 | 0.00074667
20 | 0.99335 | -0.12633 | 0.008686 | 0.0021769
21 | 0.99026 | -0.18594 | 0.0022357 | 0.00056031
22 | 0.97264 | -0.52808 | 0.001162 | 0.00029123
23 | 0.97266 | -0.52762 | 0 | 0
24 | 0.98082 | -0.36769 | 0 | 0
25 | 0.98263 | -0.3326 | 0 | 0
26 | 0.97911 | -0.40106 | 0.0021104 | 0.00052891
27 | 0.97229 | -0.53498 | 0 | 0
28 | 0.97316 | -0.51779 | 0 | 0
29 | 0.98484 | -0.28966 | 0.0056065 | 0.0014051
30 | 0.9774 | -0.43462 | 0 | 0
31 | 0.9718 | -0.54476 | 0.0011136 | 0.0002791
32 | 0.97375 | -0.50629 | 0.0017405 | 0.00043621
33 | 0.97112 | -0.5582 | 0 | 0
34 | 0.97097 | -0.56115 | 0.0084994 | 0.0021301
35 | 0.98689 | -0.25021 | 0.0040672 | 0.0010193
36 | 0.97682 | -0.44605 | 0.070063 | 0.017559
37 | 0.97663 | -0.44965 | 0.00081504 | 0.00020427
38 | 0.98737 | -0.24094 | 0.0026118 | 0.00065458
39 | 0.98743 | -0.23987 | 0 | 0
40 | 0.97507 | -0.48018 | 0 | 0
41 | 0.98384 | -0.31062 | 0.0054949 | 0.0013771
42 | 0.98368 | -0.3138 | 0.0016077 | 0.00040292
43 | 0.98407 | -0.3061 | 0 | 0
44 | 0.98354 | -0.31651 | 0 | 0
45 | 0.98401 | -0.30734 | 0.0012088 | 0.00030297
46 | 0.98438 | -0.30003 | 0.0013491 | 0.00033812
47 | 0.98403 | -0.30689 | 0.001498 | 0.00037543
48 | 0.98342 | -0.31886 | 0.0087211 | 0.0021857
49 | 0.98393 | -0.30888 | 0.0017305 | 0.0004337
50 | 0.98451 | -0.29757 | 0.00062847 | 0.00015751
51 | 0.984 | -0.30747 | 0.00045595 | 0.00011427
52 | 0.9839 | -0.30946 | 0.00079569 | 0.00019942
53 | 0.98455 | -0.2968 | 0.00045518 | 0.00011408
54 | 0.984 | -0.30758 | 0.00046676 | 0.00011698
55 | 0.98386 | -0.31017 | 0 | 0
56 | 0.98381 | -0.31116 | 0.00063542 | 0.00015925
57 | 0.98141 | -0.35792 | 0 | 0
58 | 0.98276 | -0.33157 | 0.0017003 | 0.00042614
59 | 0.98074 | -0.37112 | 0 | 0
60 | 0.9838 | -0.31135 | 0.0011933 | 0.00029907
61 | 0.97672 | -0.44788 | 0.0023071 | 0.00057822
62 | 0.97678 | -0.44682 | 0 | 0
63 | 0.97579 | -0.46608 | 0.00068178 | 0.00017087
64 | 0.9799 | -0.38746 | 0 | 0
65 | 0.98 | -0.38563 | 0 | 0
66 | 0.97957 | -0.39411 | 0.01123 | 0.0028144
67 | 0.98038 | -0.37805 | 0.0080482 | 0.0020171
68 | 0.98003 | -0.38506 | 0.0063316 | 0.0015868
69 | 0.98403 | -0.30692 | 0.0028958 | 0.00072576
70 | 0.98406 | -0.30629 | 0.062155 | 0.015578
71 | 0.9876 | -0.23653 | 0.0027522 | 0.00068977
72 | 0.99432 | -0.10784 | 0.0019518 | 0.00048918
73 | 0.99523 | -0.090585 | 0.0049663 | 0.0012447
74 | 0.9959 | -0.077896 | 0 | 0
75 | 0.99783 | -0.04125 | 0.043038 | 0.010786
76 | 0.99538 | -0.087865 | 0 | 0
77 | 0.99803 | -0.037349 | 0.058545 | 0.014673
78 | 0.99462 | -0.10234 | 0.0023594 | 0.00059133
79 | 1 | 0 | -0.53278 | -0.13546
80 | 0.99091 | -0.17343 | 0 | 0
81 | 0.9908 | -0.17562 | 0 | 0
82 | 0.99168 | -0.15864 | 0.0013042 | 0.00032687
83 | 0.99457 | -0.10317 | 0.0025815 | 0.00064699
84 | 0.99351 | -0.12359 | 0.0035195 | 0.00088208
85 | 0.9933 | -0.12754 | 0.0018294 | 0.0004585
86 | 0.99405 | -0.11319 | 0.0025376 | 0.00063598
87 | 0.99295 | -0.13422 | 0.0018947 | 0.00047487
88 | 0.99251 | -0.14272 | 0.0011009 | 0.00027592
89 | 0.99223 | -0.14806 | 0.0012677 | 0.00031772
90 | 0.99216 | -0.1494 | 0.0013879 | 0.00034784
91 | 0.99178 | -0.1567 | 0.001639 | 0.00041077
92 | 0.99072 | -0.17709 | 0.0027731 | 0.00069499
93 | 0.99044 | -0.18261 | 0.001404 | 0.00035188
94 | 0.99008 | -0.18946 | 0.0018286 | 0.00045829
95 | 0.98836 | -0.22276 | 0.0011508 | 0.00028842
96 | 0.98891 | -0.2121 | 0.0017309 | 0.00043382
97 | 0.98819 | -0.226 | 0.0041191 | 0.0010324
98 | 0.98911 | -0.20822 | 0.001675 | 0.0004198
99 | 0.98696 | -0.24995 | 0 | 0
100 | 0.98944 | -0.20188 | 0 | 0
101 | 0.98433 | -0.30102 | 0 | 0
102 | 0.98606 | -0.26726 | 0.00053954 | 0.00013522
103 | 0.98655 | -0.25789 | 0.0012945 | 0.00032444
104 | 0.98963 | -0.19821 | 0.0013802 | 0.00034592
105 | 0.98405 | -0.30654 | 0.0055991 | 0.0014033
106 | 0.9858 | -0.27237 | 0.0014937 | 0.00037435
107 | 0.98655 | -0.25794 | 0.0020073 | 0.00050307
108 | 0.99894 | -0.020425 | 0.048348 | 0.012117
109 | 0.98355 | -0.31615 | 0.0017295 | 0.00043346
110 | 0.98561 | -0.27617 | 0.00083156 | 0.00020841
111 | 0.98635 | -0.26165 | 0 | 0
112 | 0.98318 | -0.32347 | 0 | 0
113 | 0.9838 | -0.31136 | 0.0004587 | 0.00011496
114 | 0.98506 | -0.28689 | 0.00045057 | 0.00011292
115 | 0.98479 | -0.29204 | 0 | 0
116 | 0.98475 | -0.29279 | 0.00084075 | 0.00021071
117 | 0.98474 | -0.29305 | 0.00088226 | 0.00022112
118 | 0.98472 | -0.29351 | 0.00061891 | 0.00015511
119 | 0.98627 | -0.26335 | 0.0018421 | 0.00046168
120 | 0.98606 | -0.26735 | 0.00043765 | 0.00010969
121 | 0.98598 | -0.269 | 0.004104 | 0.0010286
122 | 0.98471 | -0.29362 | 0.00045867 | 0.00011495
123 | 0.98471 | -0.29364 | 0.00043105 | 0.00010803
124 | 0.98399 | -0.30765 | 0.00057106 | 0.00014312
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0079371 | -0.0019892 | 0.0079376 | 0.0019894 | 4.8987e-07 | 1.96e-07 | 0.011943 | 0.011943 | 0.011943 | 0.98892 | -0.21116 | 0.98899 | -0.20986 | 3.281
1 | 0.14387 | 0.036639 | -0.14382 | -0.036601 | 5.9227e-05 | 3.7215e-05 | 0.21668 | 0.21668 | 0.21668 | 0.98899 | -0.20986 | 0.98855 | -0.2184 | 14.8818
2 | -0.15181 | -0.038628 | 0.15187 | 0.038666 | 6.0233e-05 | 3.7918e-05 | 0.22862 | 0.22862 | 0.22862 | 0.98899 | -0.20986 | 0.98942 | -0.20163 | 15.702
3 | 0.14137 | 0.03599 | -0.14133 | -0.035963 | 4.2878e-05 | 2.6925e-05 | 0.213 | 0.213 | 0.213 | 0.98855 | -0.2184 | 0.98822 | -0.22469 | 14.6294
4 | -0.15435 | -0.039286 | 0.15444 | 0.039348 | 9.7482e-05 | 6.1399e-05 | 0.23234 | 0.23234 | 0.23234 | 0.98942 | -0.20163 | 0.9901 | -0.18854 | 15.9576
5 | 0.14133 | 0.035963 | -0.14131 | -0.035948 | 2.2878e-05 | 1.4367e-05 | 0.213 | 0.213 | 0.213 | 0.98822 | -0.22469 | 0.98804 | -0.22805 | 14.6294
6 | 0.13202 | 0.03362 | -0.13199 | -0.033603 | 2.669e-05 | 1.6714e-05 | 0.19901 | 0.19901 | 0.19901 | 0.98804 | -0.22805 | 0.98782 | -0.23224 | 13.6686
7 | 0.016737 | 0.0041996 | -0.016726 | -0.0041929 | 1.1368e-05 | 6.6561e-06 | 0.025115 | 0.025115 | 0.025115 | 0.99172 | -0.15749 | 0.99099 | -0.17174 | 6.8998
8 | -0.18072 | -0.046027 | 0.18095 | 0.046174 | 0.00023208 | 0.00014679 | 0.27141 | 0.27141 | 0.27141 | 0.99172 | -0.15749 | 0.99311 | -0.1309 | 18.6411
9 | 0.16398 | 0.041828 | -0.16386 | -0.041752 | 0.00011989 | 7.5642e-05 | 0.2463 | 0.2463 | 0.2463 | 0.99172 | -0.15749 | 0.99093 | -0.17264 | 16.9162
10 | 0.0054908 | 0.0013761 | -0.0054905 | -0.001376 | 3.6185e-07 | 4.8708e-08 | 0.0082447 | 0.0082448 | 0.0082448 | 0.99099 | -0.17174 | 0.99092 | -0.17313 | 2.2651
11 | 0.011235 | 0.0028168 | -0.01123 | -0.0028144 | 4.6703e-06 | 2.4255e-06 | 0.01687 | 0.016871 | 0.016871 | 0.99099 | -0.17174 | 0.99054 | -0.18047 | 4.6348
12 | -0.18095 | -0.046174 | 0.18099 | 0.046199 | 3.9972e-05 | 2.5283e-05 | 0.27141 | 0.27141 | 0.27141 | 0.99311 | -0.1309 | 0.99335 | -0.12633 | 18.6411
13 | 0.15456 | 0.039422 | -0.15444 | -0.039348 | 0.00011859 | 7.4689e-05 | 0.23234 | 0.23234 | 0.23234 | 0.99093 | -0.17264 | 0.9901 | -0.18854 | 15.9576
14 | 0.0042822 | 0.001073 | -0.0042817 | -0.0010731 | 4.5081e-07 | -8.5139e-08 | 0.0064338 | 0.0064339 | 0.0064339 | 0.99037 | -0.18368 | 0.99026 | -0.18589 | 1.7676
15 | -0.0042822 | -0.001073 | 0.0042826 | 0.0010729 | 3.919e-07 | -7.4096e-08 | 0.0064338 | 0.0064337 | 0.0064338 | 0.99037 | -0.18368 | 0.99047 | -0.18175 | 1.7675
16 | 0.0022357 | 0.0005603 | -0.0022357 | -0.00056031 | 5.7438e-09 | -1.3784e-08 | 0.0033594 | 0.0033594 | 0.0033594 | 0.99026 | -0.18589 | 0.99026 | -0.18594 | 0.92292
17 | -0.01123 | -0.002814 | 0.01123 | 0.0028144 | 6.867e-07 | 3.5667e-07 | 0.016871 | 0.016871 | 0.016871 | 0.99047 | -0.18175 | 0.99054 | -0.18047 | 4.6348
18 | 0.013328 | 0.0033415 | -0.013326 | -0.0033404 | 1.9767e-06 | 1.1085e-06 | 0.020414 | 0.020414 | 0.020414 | 0.97153 | -0.55004 | 0.97137 | -0.55315 | 5.6081
19 | -0.013328 | -0.0033415 | 0.01333 | 0.0033428 | 2.376e-06 | 1.3323e-06 | 0.020414 | 0.020413 | 0.020414 | 0.97153 | -0.55004 | 0.97172 | -0.5463 | 5.6081
20 | 0.0085026 | 0.0021316 | -0.0085006 | -0.0021307 | 2.0454e-06 | 9.1119e-07 | 0.013025 | 0.013025 | 0.013025 | 0.97137 | -0.55315 | 0.97112 | -0.5582 | 3.5784
21 | -0.032629 | -0.0081797 | 0.032632 | 0.0081812 | 2.3919e-06 | 1.4991e-06 | 0.049967 | 0.049967 | 0.049967 | 0.97172 | -0.5463 | 0.9718 | -0.54476 | 13.7272
22 | 0.12901 | 0.032857 | -0.12899 | -0.03284 | 2.6648e-05 | 1.667e-05 | 0.19453 | 0.19453 | 0.19453 | 0.98782 | -0.23224 | 0.9876 | -0.23653 | 13.3603
23 | -0.18967 | -0.048376 | 0.18984 | 0.048484 | 0.0001695 | 0.00010732 | 0.28443 | 0.28442 | 0.28443 | 0.99335 | -0.12633 | 0.99432 | -0.10784 | 19.5347
24 | -0.001162 | -0.00029123 | 0.001162 | 0.00029098 | 2.5383e-08 | -2.496e-07 | 0.0017777 | 0.0017776 | 0.0017777 | 0.97264 | -0.52808 | 0.97266 | -0.52762 | 0.48839
25 | 0.033773 | 0.0084776 | -0.033761 | -0.0084701 | 1.1851e-05 | 7.4376e-06 | 0.051672 | 0.051672 | 0.051672 | 0.97266 | -0.52762 | 0.97229 | -0.53498 | 14.1956
26 | -0.034935 | -0.0087686 | 0.034951 | 0.0087789 | 1.6399e-05 | 1.0305e-05 | 0.05345 | 0.053449 | 0.05345 | 0.97266 | -0.52762 | 0.97316 | -0.51779 | 14.6839
27 | -0.11321 | -0.028603 | 0.1134 | 0.028725 | 0.00019078 | 0.00012188 | 0.17184 | 0.17184 | 0.17184 | 0.98082 | -0.36769 | 0.98263 | -0.3326 | 47.209
28 | 0.11321 | 0.028603 | -0.11303 | -0.028488 | 0.00018077 | 0.00011549 | 0.17184 | 0.17184 | 0.17184 | 0.98082 | -0.36769 | 0.97911 | -0.40106 | 47.209
29 | -0.1134 | -0.028725 | 0.11364 | 0.028875 | 0.00023442 | 0.00014976 | 0.17184 | 0.17184 | 0.17184 | 0.98263 | -0.3326 | 0.98484 | -0.28966 | 47.209
30 | 0.11092 | 0.027959 | -0.11075 | -0.027845 | 0.00017783 | 0.0001136 | 0.16863 | 0.16863 | 0.16863 | 0.97911 | -0.40106 | 0.9774 | -0.43462 | 46.3279
31 | 0.033761 | 0.0084701 | -0.033745 | -0.0084603 | 1.5724e-05 | 9.8686e-06 | 0.051672 | 0.051672 | 0.051672 | 0.97229 | -0.53498 | 0.9718 | -0.54476 | 14.1956
32 | -0.034951 | -0.0087789 | 0.034971 | 0.0087909 | 1.9188e-05 | 1.2058e-05 | 0.053449 | 0.053449 | 0.053449 | 0.97316 | -0.51779 | 0.97375 | -0.50629 | 14.6839
33 | -0.11925 | -0.03028 | 0.11947 | 0.030425 | 0.00022681 | 0.00014492 | 0.18031 | 0.18031 | 0.18031 | 0.98484 | -0.28966 | 0.98689 | -0.25021 | 49.5362
34 | 0.07241 | 0.018162 | -0.07237 | -0.018137 | 3.942e-05 | 2.512e-05 | 0.11024 | 0.11024 | 0.11024 | 0.9774 | -0.43462 | 0.97682 | -0.44605 | 30.2867
35 | 0.038336 | 0.0096827 | -0.038308 | -0.0096653 | 2.759e-05 | 1.7388e-05 | 0.05839 | 0.05839 | 0.05839 | 0.9774 | -0.43462 | 0.97663 | -0.44965 | 16.0413
36 | -0.036711 | -0.0092271 | 0.036757 | 0.009256 | 4.5823e-05 | 2.8844e-05 | 0.056109 | 0.056109 | 0.056109 | 0.97375 | -0.50629 | 0.97507 | -0.48018 | 15.4146
37 | 0.0085006 | 0.0021307 | -0.0084994 | -0.0021301 | 1.1933e-06 | 5.3169e-07 | 0.013025 | 0.013025 | 0.013025 | 0.97112 | -0.5582 | 0.97097 | -0.56115 | 3.5784
38 | -0.12354 | -0.031444 | 0.1236 | 0.031483 | 6.1629e-05 | 3.9201e-05 | 0.18644 | 0.18644 | 0.18644 | 0.98689 | -0.25021 | 0.98743 | -0.23987 | 25.6104
39 | 0.0023073 | 0.00057781 | -0.0023072 | -0.00057798 | 8.4484e-08 | -1.7422e-07 | 0.0035147 | 0.0035147 | 0.0035147 | 0.97682 | -0.44605 | 0.97678 | -0.44682 | 0.96559
40 | 0.037493 | 0.009461 | -0.037464 | -0.0094425 | 2.9459e-05 | 1.8553e-05 | 0.057148 | 0.057149 | 0.057149 | 0.97663 | -0.44965 | 0.97579 | -0.46608 | 15.7001
41 | -0.0026118 | -0.00065458 | 0.0026119 | 0.00065437 | 1.3285e-07 | -2.0747e-07 | 0.0039361 | 0.003936 | 0.0039361 | 0.98737 | -0.24094 | 0.98743 | -0.23987 | 1.0813
42 | -0.12621 | -0.032138 | 0.12623 | 0.03215 | 2.0358e-05 | 1.2722e-05 | 0.19038 | 0.19038 | 0.19038 | 0.98743 | -0.23987 | 0.9876 | -0.23653 | 13.0755
43 | -0.036757 | -0.009256 | 0.036782 | 0.0092716 | 2.4808e-05 | 1.5615e-05 | 0.056109 | 0.056109 | 0.056109 | 0.97507 | -0.48018 | 0.97579 | -0.46608 | 15.4146
44 | 0.010332 | 0.0025904 | -0.010331 | -0.0025896 | 1.5618e-06 | 7.8303e-07 | 0.015628 | 0.015628 | 0.015628 | 0.98384 | -0.31062 | 0.98368 | -0.3138 | 4.2933
45 | -0.015827 | -0.0039675 | 0.015831 | 0.0039695 | 3.4089e-06 | 1.9802e-06 | 0.023938 | 0.023938 | 0.023938 | 0.98384 | -0.31062 | 0.98407 | -0.3061 | 6.5765
46 | 0.0087232 | 0.0021866 | -0.0087221 | -0.0021861 | 1.1263e-06 | 5.0189e-07 | 0.013196 | 0.013196 | 0.013196 | 0.98368 | -0.3138 | 0.98354 | -0.31651 | 3.6252
47 | 0.0060234 | 0.0015089 | -0.006023 | -0.0015088 | 3.5457e-07 | 8.2119e-08 | 0.0091077 | 0.0091078 | 0.0091078 | 0.98407 | -0.3061 | 0.98401 | -0.30734 | 2.5021
48 | -0.024846 | -0.0062276 | 0.024853 | 0.0062321 | 7.1927e-06 | 4.4306e-06 | 0.03757 | 0.03757 | 0.03757 | 0.98407 | -0.3061 | 0.98438 | -0.30003 | 10.3214
49 | 0.0029919 | 0.00074929 | -0.0029918 | -0.0007494 | 1.1237e-07 | -1.141e-07 | 0.0045238 | 0.0045239 | 0.0045239 | 0.98407 | -0.3061 | 0.98403 | -0.30689 | 1.2428
50 | 0.0087221 | 0.0021861 | -0.0087211 | -0.0021857 | 9.7958e-07 | 4.3657e-07 | 0.013196 | 0.013196 | 0.013196 | 0.98354 | -0.31651 | 0.98342 | -0.31886 | 3.6252
51 | 0.0048142 | 0.0012058 | -0.0048139 | -0.0012058 | 3.5202e-07 | 2.9862e-10 | 0.0072798 | 0.0072798 | 0.0072798 | 0.98401 | -0.30734 | 0.98393 | -0.30888 | 2
52 | -0.026202 | -0.0065702 | 0.026205 | 0.0065721 | 3.0738e-06 | 1.9008e-06 | 0.039609 | 0.039609 | 0.039609 | 0.98438 | -0.30003 | 0.98451 | -0.29757 | 10.8816
53 | 0.0014938 | 0.00037398 | -0.0014938 | -0.00037422 | 4.0883e-08 | -2.4528e-07 | 0.0022587 | 0.0022588 | 0.0022588 | 0.98403 | -0.30689 | 0.984 | -0.30747 | 0.62056
54 | 0.0030834 | 0.00077212 | -0.0030833 | -0.0007722 | 8.5768e-08 | -7.8711e-08 | 0.0046628 | 0.0046629 | 0.0046629 | 0.98393 | -0.30888 | 0.9839 | -0.30946 | 1.281
55 | -0.026834 | -0.0067296 | 0.026835 | 0.0067302 | 9.8547e-07 | 6.1038e-07 | 0.040559 | 0.040559 | 0.040559 | 0.98451 | -0.29757 | 0.98455 | -0.2968 | 11.1426
56 | 0.0010378 | 0.00025995 | -0.0010378 | -0.00026002 | 5.5792e-09 | -7.3164e-08 | 0.0015694 | 0.0015694 | 0.0015694 | 0.984 | -0.30747 | 0.984 | -0.30758 | 0.43115
57 | 0.0022876 | 0.00057278 | -0.0022875 | -0.00057295 | 7.7904e-08 | -1.7058e-07 | 0.0034595 | 0.0034596 | 0.0034596 | 0.9839 | -0.30946 | 0.98386 | -0.31017 | 0.95044
58 | -0.02729 | -0.0068443 | 0.027296 | 0.0068481 | 6.1881e-06 | 3.837e-06 | 0.041247 | 0.041247 | 0.041247 | 0.98455 | -0.2968 | 0.98479 | -0.29204 | 11.3316
59 | 0.00057106 | 0.00014304 | -0.00057106 | -0.00014312 | 1.7657e-09 | -7.9074e-08 | 0.00086354 | 0.00086357 | 0.00086357 | 0.984 | -0.30758 | 0.98399 | -0.30765 | 0.23724
60 | 0.0022875 | 0.00057295 | -0.0022874 | -0.00057319 | 1.0686e-07 | -2.3393e-07 | 0.0034596 | 0.0034597 | 0.0034597 | 0.98386 | -0.31017 | 0.98381 | -0.31116 | 0.95047
61 | 0.001652 | 0.00041394 | -0.001652 | -0.00041401 | 1.5017e-08 | -7.1838e-08 | 0.0024986 | 0.0024986 | 0.0024986 | 0.98381 | -0.31116 | 0.9838 | -0.31135 | 0.68644
62 | -0.025645 | -0.0064396 | 0.025677 | 0.0064595 | 3.2274e-05 | 1.9935e-05 | 0.038887 | 0.038887 | 0.038887 | 0.98141 | -0.35792 | 0.98276 | -0.33157 | 10.6833
63 | 0.025645 | 0.0064396 | -0.025629 | -0.0064296 | 1.6146e-05 | 9.9742e-06 | 0.038887 | 0.038887 | 0.038887 | 0.98141 | -0.35792 | 0.98074 | -0.37112 | 10.6833
64 | -0.027377 | -0.0068856 | 0.027388 | 0.0068922 | 1.0609e-05 | 6.5814e-06 | 0.041461 | 0.041461 | 0.041461 | 0.98276 | -0.33157 | 0.98318 | -0.32347 | 11.3905
65 | 0.025629 | 0.0064296 | -0.02562 | -0.0064244 | 8.4602e-06 | 5.2264e-06 | 0.038887 | 0.038887 | 0.038887 | 0.98074 | -0.37112 | 0.98038 | -0.37805 | 10.6833
66 | 0.0004587 | 0.00011494 | -0.0004587 | -0.00011496 | 2.8515e-10 | -1.9872e-08 | 0.00069378 | 0.00069378 | 0.00069378 | 0.9838 | -0.31135 | 0.9838 | -0.31136 | 0.1906
67 | -0.0023071 | -0.00057822 | 0.0023072 | 0.00057798 | 1.1596e-07 | -2.3908e-07 | 0.0035149 | 0.0035147 | 0.0035149 | 0.97672 | -0.44788 | 0.97678 | -0.44682 | 0.96562
68 | -0.011233 | -0.0028163 | 0.011234 | 0.0028168 | 9.8209e-07 | 5.1515e-07 | 0.017058 | 0.017058 | 0.017058 | 0.9799 | -0.38746 | 0.98 | -0.38563 | 4.6864
69 | 0.011233 | 0.0028163 | -0.01123 | -0.0028144 | 3.5594e-06 | 1.8673e-06 | 0.017058 | 0.017059 | 0.017059 | 0.9799 | -0.38746 | 0.97957 | -0.39411 | 4.6864
70 | -0.011234 | -0.0028168 | 0.011235 | 0.002817 | 3.0324e-07 | 1.5906e-07 | 0.017058 | 0.017058 | 0.017058 | 0.98 | -0.38563 | 0.98003 | -0.38506 | 4.6864
71 | 0.017572 | 0.0044073 | -0.017566 | -0.0044038 | 5.8687e-06 | 3.4787e-06 | 0.026672 | 0.026672 | 0.026672 | 0.98038 | -0.37805 | 0.98003 | -0.38506 | 7.3275
72 | -0.0028958 | -0.00072576 | 0.0028959 | 0.00072566 | 8.7323e-08 | -9.8389e-08 | 0.004379 | 0.0043789 | 0.004379 | 0.98403 | -0.30692 | 0.98406 | -0.30629 | 1.203
73 | -0.065051 | -0.016303 | 0.065067 | 0.016314 | 1.633e-05 | 1.0394e-05 | 0.098365 | 0.098365 | 0.098365 | 0.98406 | -0.30629 | 0.98433 | -0.30102 | 27.0234
74 | -0.1918 | -0.048973 | 0.19196 | 0.049074 | 0.00016012 | 0.0001014 | 0.28735 | 0.28735 | 0.28735 | 0.99432 | -0.10784 | 0.99523 | -0.090585 | 19.7353
75 | -0.19692 | -0.050319 | 0.19704 | 0.050395 | 0.00012091 | 7.6612e-05 | 0.29477 | 0.29477 | 0.29477 | 0.99523 | -0.090585 | 0.9959 | -0.077896 | 20.2452
76 | -0.37953 | -0.096813 | 0.3802 | 0.097243 | 0.00067298 | 0.00042955 | 0.56767 | 0.56767 | 0.56767 | 0.9959 | -0.077896 | 0.99783 | -0.04125 | 38.9884
77 | 0.18248 | 0.046418 | -0.1824 | -0.046362 | 8.7618e-05 | 5.5423e-05 | 0.2729 | 0.2729 | 0.2729 | 0.9959 | -0.077896 | 0.99538 | -0.087865 | 18.7432
78 | -0.42324 | -0.10803 | 0.42332 | 0.10808 | 7.9788e-05 | 5.0953e-05 | 0.63185 | 0.63185 | 0.63185 | 0.99783 | -0.04125 | 0.99803 | -0.037349 | 43.3964
79 | 0.1824 | 0.046362 | -0.18227 | -0.046282 | 0.00012708 | 8.0386e-05 | 0.2729 | 0.2729 | 0.2729 | 0.99538 | -0.087865 | 0.99462 | -0.10234 | 18.7433
80 | -0.48186 | -0.12275 | 0.48273 | 0.12331 | 0.00086996 | 0.00055583 | 0.71914 | 0.71914 | 0.71914 | 0.99803 | -0.037349 | 1 | 0 | 49.3913
81 | 0.17991 | 0.045691 | -0.1799 | -0.045686 | 7.1178e-06 | 4.5011e-06 | 0.26937 | 0.26937 | 0.26937 | 0.99462 | -0.10234 | 0.99457 | -0.10317 | 18.5008
82 | 0.048395 | 0.012147 | -0.048348 | -0.012117 | 4.7094e-05 | 2.9823e-05 | 0.072019 | 0.072019 | 0.072019 | 1 | 0 | 0.99894 | -0.020425 | 19.7854
83 | 0.16027 | 0.04055 | -0.16026 | -0.04054 | 1.687e-05 | 1.0637e-05 | 0.24081 | 0.24081 | 0.24081 | 0.99091 | -0.17343 | 0.9908 | -0.17562 | 16.5393
84 | -0.16027 | -0.04055 | 0.16039 | 0.040622 | 0.00011382 | 7.1763e-05 | 0.24081 | 0.24081 | 0.24081 | 0.99091 | -0.17343 | 0.99168 | -0.15864 | 16.5393
85 | 0.0027733 | 0.00069473 | -0.0027731 | -0.00069499 | 1.9436e-07 | -2.6038e-07 | 0.0041649 | 0.004165 | 0.004165 | 0.9908 | -0.17562 | 0.99072 | -0.17709 | 1.1442
86 | 0.15748 | 0.039845 | -0.15743 | -0.039812 | 5.2755e-05 | 3.3246e-05 | 0.23665 | 0.23665 | 0.23665 | 0.9908 | -0.17562 | 0.99044 | -0.18261 | 16.2533
87 | -0.16169 | -0.040949 | 0.16171 | 0.040959 | 1.5097e-05 | 9.521e-06 | 0.24277 | 0.24277 | 0.24277 | 0.99168 | -0.15864 | 0.99178 | -0.1567 | 16.6737
88 | 0.17732 | 0.045039 | -0.17724 | -0.044985 | 8.554e-05 | 5.4074e-05 | 0.26551 | 0.26551 | 0.26551 | 0.99457 | -0.10317 | 0.99405 | -0.11319 | 18.2356
89 | 0.17109 | 0.043412 | -0.17106 | -0.043391 | 3.2543e-05 | 2.0554e-05 | 0.25644 | 0.25644 | 0.25644 | 0.99351 | -0.12359 | 0.9933 | -0.12754 | 17.6127
90 | -0.17461 | -0.044294 | 0.1747 | 0.044349 | 8.7323e-05 | 5.5182e-05 | 0.26171 | 0.26171 | 0.26171 | 0.99351 | -0.12359 | 0.99405 | -0.11319 | 17.9747
91 | 0.16923 | 0.042933 | -0.16918 | -0.042898 | 5.4344e-05 | 3.4314e-05 | 0.2537 | 0.2537 | 0.2537 | 0.9933 | -0.12754 | 0.99295 | -0.13422 | 17.4245
92 | 0.16728 | 0.042424 | -0.16721 | -0.04238 | 6.8265e-05 | 4.3091e-05 | 0.25086 | 0.25086 | 0.25086 | 0.99295 | -0.13422 | 0.99251 | -0.14272 | 17.2295
93 | 0.16611 | 0.042105 | -0.16607 | -0.042078 | 4.2607e-05 | 2.689e-05 | 0.24921 | 0.24921 | 0.24921 | 0.99251 | -0.14272 | 0.99223 | -0.14806 | 17.1161
94 | 0.1648 | 0.04176 | -0.16479 | -0.041753 | 1.0619e-05 | 6.7007e-06 | 0.24731 | 0.24731 | 0.24731 | 0.99223 | -0.14806 | 0.99216 | -0.1494 | 16.9855
95 | 0.1634 | 0.041405 | -0.16335 | -0.041369 | 5.7295e-05 | 3.6144e-05 | 0.24523 | 0.24523 | 0.24523 | 0.99216 | -0.1494 | 0.99178 | -0.1567 | 16.8426
96 | 0.15603 | 0.03946 | -0.15598 | -0.039428 | 5.1268e-05 | 3.23e-05 | 0.23454 | 0.23454 | 0.23454 | 0.99044 | -0.18261 | 0.99008 | -0.18946 | 16.1084
97 | 0.15415 | 0.038969 | -0.15408 | -0.038929 | 6.4679e-05 | 4.0734e-05 | 0.23179 | 0.23179 | 0.23179 | 0.99008 | -0.18946 | 0.98963 | -0.19821 | 15.9197
98 | -0.14912 | -0.037617 | 0.14919 | 0.037665 | 7.6112e-05 | 4.7886e-05 | 0.22459 | 0.22459 | 0.22459 | 0.98836 | -0.22276 | 0.98891 | -0.2121 | 15.4252
99 | 0.14797 | 0.037329 | -0.14794 | -0.037314 | 2.2964e-05 | 1.4444e-05 | 0.22286 | 0.22286 | 0.22286 | 0.98836 | -0.22276 | 0.98819 | -0.226 | 15.3062
100 | -0.15093 | -0.038099 | 0.15095 | 0.038117 | 2.8075e-05 | 1.767e-05 | 0.2272 | 0.2272 | 0.2272 | 0.98891 | -0.2121 | 0.98911 | -0.20822 | 15.6041
101 | 0.14383 | 0.036282 | -0.14366 | -0.036177 | 0.00016476 | 0.00010497 | 0.21666 | 0.21666 | 0.21666 | 0.98819 | -0.226 | 0.98696 | -0.24995 | 29.7605
102 | -0.15263 | -0.038537 | 0.15268 | 0.038566 | 4.6332e-05 | 2.9171e-05 | 0.22972 | 0.22972 | 0.22972 | 0.98911 | -0.20822 | 0.98944 | -0.20188 | 15.7772
103 | 0.10006 | 0.025218 | -0.099816 | -0.025063 | 0.00024384 | 0.00015569 | 0.15091 | 0.15091 | 0.15091 | 0.98696 | -0.24995 | 0.98433 | -0.30102 | 41.4586
104 | 0.033909 | 0.0085293 | -0.033881 | -0.0085118 | 2.8012e-05 | 1.7563e-05 | 0.051135 | 0.051135 | 0.051135 | 0.98696 | -0.24995 | 0.98606 | -0.26726 | 14.048
105 | 0.0096922 | 0.0024295 | -0.0096885 | -0.0024278 | 3.6648e-06 | 1.7609e-06 | 0.014613 | 0.014613 | 0.014613 | 0.98696 | -0.24995 | 0.98655 | -0.25789 | 4.0146
106 | -0.15268 | -0.038566 | 0.1527 | 0.038583 | 2.6883e-05 | 1.6926e-05 | 0.22972 | 0.22972 | 0.22972 | 0.98944 | -0.20188 | 0.98963 | -0.19821 | 15.7772
107 | 0.034749 | 0.008749 | -0.03474 | -0.0087432 | 9.1676e-06 | 5.7548e-06 | 0.052544 | 0.052544 | 0.052544 | 0.98433 | -0.30102 | 0.98405 | -0.30654 | 14.4352
108 | 0.033341 | 0.0083766 | -0.033333 | -0.0083715 | 8.1217e-06 | 5.0888e-06 | 0.050321 | 0.050321 | 0.050321 | 0.98606 | -0.26726 | 0.9858 | -0.27237 | 13.8243
109 | 0.008394 | 0.0021033 | -0.0083939 | -0.0021033 | 1.7391e-08 | 7.4361e-09 | 0.012661 | 0.012661 | 0.012661 | 0.98655 | -0.25789 | 0.98655 | -0.25794 | 3.4782
110 | 0.02914 | 0.00734 | -0.029127 | -0.0073316 | 1.3378e-05 | 8.329e-06 | 0.044078 | 0.044078 | 0.044078 | 0.98405 | -0.30654 | 0.98355 | -0.31615 | 12.1093
111 | 0.031839 | 0.0079971 | -0.031834 | -0.0079935 | 5.7827e-06 | 3.6158e-06 | 0.048066 | 0.048066 | 0.048066 | 0.9858 | -0.27237 | 0.98561 | -0.27617 | 13.2049
112 | 0.0063867 | 0.0016002 | -0.0063855 | -0.0015999 | 1.1309e-06 | 3.0889e-07 | 0.0096329 | 0.009633 | 0.009633 | 0.98655 | -0.25794 | 0.98635 | -0.26165 | 2.6464
113 | 0.027398 | 0.0068982 | -0.027388 | -0.0068922 | 9.5795e-06 | 5.9423e-06 | 0.041461 | 0.041461 | 0.041461 | 0.98355 | -0.31615 | 0.98318 | -0.32347 | 11.3904
114 | 0.031002 | 0.0077851 | -0.030986 | -0.0077752 | 1.5846e-05 | 9.8958e-06 | 0.04681 | 0.046811 | 0.046811 | 0.98561 | -0.27617 | 0.98506 | -0.28689 | 12.86
115 | 0.0063855 | 0.0015999 | -0.006385 | -0.0015998 | 5.1673e-07 | 1.4119e-07 | 0.009633 | 0.0096331 | 0.0096331 | 0.98635 | -0.26165 | 0.98627 | -0.26335 | 2.6465
116 | 0.030536 | 0.0076623 | -0.030528 | -0.0076576 | 7.4946e-06 | 4.677e-06 | 0.04613 | 0.04613 | 0.04613 | 0.98506 | -0.28689 | 0.98479 | -0.29204 | 12.6731
117 | 0.0032318 | 0.00080947 | -0.0032317 | -0.00080956 | 1.1577e-07 | -9.0628e-08 | 0.0048831 | 0.0048831 | 0.0048831 | 0.98479 | -0.29204 | 0.98475 | -0.29279 | 1.3415
118 | 0.0023909 | 0.00059885 | -0.0023909 | -0.00059891 | 2.9546e-08 | -5.7889e-08 | 0.0036127 | 0.0036127 | 0.0036127 | 0.98475 | -0.29279 | 0.98474 | -0.29305 | 0.99251
119 | 0.0015087 | 0.00037779 | -0.0015086 | -0.00037798 | 3.2569e-08 | -1.9177e-07 | 0.0022796 | 0.0022797 | 0.0022797 | 0.98474 | -0.29305 | 0.98472 | -0.29351 | 0.62628
120 | 0.00088972 | 0.00022287 | -0.00088971 | -0.00022296 | 4.8609e-09 | -8.8119e-08 | 0.0013444 | 0.0013444 | 0.0013444 | 0.98472 | -0.29351 | 0.98471 | -0.29362 | 0.36935
121 | 0.0045429 | 0.0011381 | -0.004542 | -0.0011382 | 8.6568e-07 | -7.2943e-08 | 0.0068538 | 0.0068541 | 0.0068541 | 0.98627 | -0.26335 | 0.98606 | -0.26735 | 1.883
122 | 0.0041044 | 0.0010285 | -0.004104 | -0.0010286 | 3.2241e-07 | -7.9521e-08 | 0.0061936 | 0.0061937 | 0.0061937 | 0.98606 | -0.26735 | 0.98598 | -0.269 | 1.7016
123 | 0.00043105 | 0.000108 | -0.00043105 | -0.00010803 | 3.2223e-10 | -2.5558e-08 | 0.00065135 | 0.00065136 | 0.00065136 | 0.98471 | -0.29362 | 0.98471 | -0.29364 | 0.17895

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61251 | 0.15544

## res_load
| p_mw | q_mvar
0 | 0.0079371 | 0.0019892
1 | 0.0024412 | 0.00061183
2 | 0.0024745 | 0.00062016
3 | 0.0092897 | 0.0023282
4 | 0.0092958 | 0.0023297
5 | 0.0020461 | 0.00051279
6 | 0.0069471 | 0.0017411
7 | 0.0054905 | 0.001376
8 | 0.0048231 | 0.0012088
9 | 0.019299 | 0.0048369
10 | 0.0029793 | 0.00074667
11 | 0.008686 | 0.0021769
12 | 0.0022357 | 0.00056031
13 | 0.001162 | 0.00029123
14 | 0.0021104 | 0.00052891
15 | 0.0056065 | 0.0014051
16 | 0.0011136 | 0.0002791
17 | 0.0017405 | 0.00043621
18 | 0.0084994 | 0.0021301
19 | 0.0040672 | 0.0010193
20 | 0.070063 | 0.017559
21 | 0.00081504 | 0.00020427
22 | 0.0026118 | 0.00065458
23 | 0.0054949 | 0.0013771
24 | 0.0016077 | 0.00040292
25 | 0.0012088 | 0.00030297
26 | 0.0013491 | 0.00033812
27 | 0.001498 | 0.00037543
28 | 0.0087211 | 0.0021857
29 | 0.0017305 | 0.0004337
30 | 0.00062847 | 0.00015751
31 | 0.00045595 | 0.00011427
32 | 0.00079569 | 0.00019942
33 | 0.00045518 | 0.00011408
34 | 0.00046676 | 0.00011698
35 | 0.00063542 | 0.00015925
36 | 0.0017003 | 0.00042614
37 | 0.0011933 | 0.00029907
38 | 0.0023071 | 0.00057822
39 | 0.00068178 | 0.00017087
40 | 0.01123 | 0.0028144
41 | 0.0080482 | 0.0020171
42 | 0.0063316 | 0.0015868
43 | 0.0028958 | 0.00072576
44 | 0.062155 | 0.015578
45 | 0.0027522 | 0.00068977
46 | 0.0019518 | 0.00048918
47 | 0.0049663 | 0.0012447
48 | 0.043038 | 0.010786
49 | 0.058545 | 0.014673
50 | 0.0023594 | 0.00059133
51 | 0.079732 | 0.019983
52 | 0.0013042 | 0.00032687
53 | 0.0025815 | 0.00064699
54 | 0.0035195 | 0.00088208
55 | 0.0018294 | 0.0004585
56 | 0.0025376 | 0.00063598
57 | 0.0018947 | 0.00047487
58 | 0.0011009 | 0.00027592
59 | 0.0012677 | 0.00031772
60 | 0.0013879 | 0.00034784
61 | 0.001639 | 0.00041077
62 | 0.0027731 | 0.00069499
63 | 0.001404 | 0.00035188
64 | 0.0018286 | 0.00045829
65 | 0.0011508 | 0.00028842
66 | 0.0017309 | 0.00043382
67 | 0.0041191 | 0.0010324
68 | 0.001675 | 0.0004198
69 | 0.00053954 | 0.00013522
70 | 0.0012945 | 0.00032444
71 | 0.0013802 | 0.00034592
72 | 0.0055991 | 0.0014033
73 | 0.0014937 | 0.00037435
74 | 0.0020073 | 0.00050307
75 | 0.048348 | 0.012117
76 | 0.0017295 | 0.00043346
77 | 0.00083156 | 0.00020841
78 | 0.0004587 | 0.00011496
79 | 0.00045057 | 0.00011292
80 | 0.00084075 | 0.00021071
81 | 0.00088226 | 0.00022112
82 | 0.00061891 | 0.00015511
83 | 0.0018421 | 0.00046168
84 | 0.00043765 | 0.00010969
85 | 0.004104 | 0.0010286
86 | 0.00045867 | 0.00011495
87 | 0.00043105 | 0.00010803
88 | 0.00057106 | 0.00014312

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1