## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-13_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_115-13_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_115-13_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_115-13_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_115-13_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_115-13_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_115-13_0_5_node_203 | 0.4 | n |  | TRUE
7 | bus_LV_115-13_0_5_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_115-13_0_5_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_115-13_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_115-13_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_115-13_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_115-13_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_115-13_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_115-13_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_115-13_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_115-13_0_5_node_152 | 0.4 | n |  | TRUE
17 | bus_LV_115-13_0_5_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_115-13_0_5_node_157 | 0.4 | n |  | TRUE
19 | bus_LV_115-13_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_115-13_0_5_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_115-13_0_5_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_115-13_0_5_node_158 | 0.4 | n |  | TRUE
23 | bus_LV_115-13_0_5_node_85 | 0.4 | n |  | TRUE
24 | bus_LV_115-13_0_5_node_83 | 0.4 | n |  | TRUE
25 | bus_LV_115-13_0_5_node_88 | 0.4 | n |  | TRUE
26 | bus_LV_115-13_0_5_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_115-13_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_115-13_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_115-13_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_115-13_0_5_node_84 | 0.4 | n |  | TRUE
31 | bus_LV_115-13_0_5_node_151 | 0.4 | n |  | TRUE
32 | bus_LV_115-13_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_115-13_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_115-13_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_115-13_0_5_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_115-13_0_5_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_115-13_0_5_node_156 | 0.4 | n |  | TRUE
38 | bus_LV_115-13_0_5_node_76 | 0.4 | n |  | TRUE
39 | bus_LV_115-13_0_5_node_155 | 0.4 | n |  | TRUE
40 | bus_LV_115-13_0_5_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_115-13_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_115-13_0_5_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_115-13_0_5_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_115-13_0_5_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_115-13_0_5_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_115-13_0_5_node_170 | 0.4 | n |  | TRUE
47 | bus_LV_115-13_0_5_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_115-13_0_5_node_172 | 0.4 | n |  | TRUE
49 | bus_LV_115-13_0_5_node_168 | 0.4 | n |  | TRUE
50 | bus_LV_115-13_0_5_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_115-13_0_5_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_115-13_0_5_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_115-13_0_5_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_115-13_0_5_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_115-13_0_5_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_115-13_0_5_node_75 | 0.4 | n |  | TRUE
57 | bus_LV_115-13_0_5_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_115-13_0_5_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_115-13_0_5_node_78 | 0.4 | n |  | TRUE
60 | bus_LV_115-13_0_5_node_79 | 0.4 | n |  | TRUE
61 | bus_LV_115-13_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_115-13_0_5_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_115-13_0_5_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_115-13_0_5_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_115-13_0_5_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_115-13_0_5_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_115-13_0_5_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_115-13_0_5_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_115-13_0_5_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_115-13_0_5_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_115-13_0_5_node_185 | 0.4 | n |  | TRUE
72 | bus_LV_115-13_0_5_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_115-13_0_5_node_167 | 0.4 | n |  | TRUE
74 | bus_LV_115-13_0_5_node_166 | 0.4 | n |  | TRUE
75 | bus_LV_115-13_0_5_node_186 | 0.4 | n |  | TRUE
76 | bus_LV_115-13_0_5_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_115-13_0_5_node_165 | 0.4 | n |  | TRUE
78 | bus_LV_115-13_0_5_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_115-13_0_5_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_115-13_0_5_node_49 | 0.4 | n |  | TRUE
81 | bus_LV_115-13_0_5_node_50 | 0.4 | n |  | TRUE
82 | bus_LV_115-13_0_5_node_161 | 0.4 | n |  | TRUE
83 | bus_LV_115-13_0_5_node_160 | 0.4 | n |  | TRUE
84 | bus_LV_115-13_0_5_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_115-13_0_5_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_115-13_0_5_node_58 | 0.4 | n |  | TRUE
87 | bus_LV_115-13_0_5_node_59 | 0.4 | n |  | TRUE
88 | bus_LV_115-13_0_5_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_115-13_0_5_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_115-13_0_5_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_115-13_0_5_node_63 | 0.4 | n |  | TRUE
92 | bus_LV_115-13_0_5_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_115-13_0_5_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_115-13_0_5_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_115-13_0_5_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_115-13_0_5_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_115-13_0_5_node_159 | 0.4 | n |  | TRUE
98 | bus_LV_115-13_0_5_node_70 | 0.4 | n |  | TRUE
99 | bus_LV_115-13_0_5_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_115-13_0_5_node_72 | 0.4 | n |  | TRUE
101 | bus_LV_115-13_0_5_node_73 | 0.4 | n |  | TRUE
102 | bus_LV_115-13_0_5_node_187 | 0.4 | n |  | TRUE
103 | bus_LV_115-13_0_5_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_115-13_0_5_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_115-13_0_5_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_115-13_0_5_node_201 | 0.4 | n |  | TRUE
107 | bus_LV_115-13_0_5_node_202 | 0.4 | n |  | TRUE
108 | bus_LV_115-13_0_5_node_125 | 0.4 | n |  | TRUE
109 | bus_LV_115-13_0_5_node_128 | 0.4 | n |  | TRUE
110 | bus_LV_115-13_0_5_node_129 | 0.4 | n |  | TRUE
111 | bus_LV_115-13_0_5_node_164 | 0.4 | n |  | TRUE
112 | bus_LV_115-13_0_5_node_163 | 0.4 | n |  | TRUE
113 | bus_LV_115-13_0_5_node_169 | 0.4 | n |  | TRUE
114 | bus_LV_115-13_0_5_node_171 | 0.4 | n |  | TRUE
115 | bus_LV_115-13_0_5_node_173 | 0.4 | n |  | TRUE
116 | bus_LV_115-13_0_5_node_177 | 0.4 | n |  | TRUE
117 | bus_LV_115-13_0_5_node_181 | 0.4 | n |  | TRUE
118 | bus_LV_115-13_0_5_node_178 | 0.4 | n |  | TRUE
119 | bus_LV_115-13_0_5_node_175 | 0.4 | n |  | TRUE
120 | bus_LV_115-13_0_5_node_193 | 0.4 | n |  | TRUE
121 | bus_LV_115-13_0_5_node_179 | 0.4 | n |  | TRUE
122 | bus_LV_115-13_0_5_node_174 | 0.4 | n |  | TRUE
123 | bus_LV_115-13_0_5_node_176 | 0.4 | n |  | TRUE
124 | bus_LV_115-13_0_5_node_180 | 0.4 | n |  | TRUE
125 | bus_LV_115-13_0_5_node_188 | 0.4 | n |  | TRUE
126 | bus_LV_115-13_0_5_node_184 | 0.4 | n |  | TRUE
127 | bus_LV_115-13_0_5_node_189 | 0.4 | n |  | TRUE
128 | bus_LV_115-13_0_5_node_183 | 0.4 | n |  | TRUE
129 | bus_LV_115-13_0_5_node_192 | 0.4 | n |  | TRUE
130 | bus_LV_115-13_0_5_node_182 | 0.4 | n |  | TRUE
131 | bus_LV_115-13_0_5_node_190 | 0.4 | n |  | TRUE
132 | bus_LV_115-13_0_5_node_191 | 0.4 | n |  | TRUE
133 | bus_LV_115-13_0_5_node_194 | 0.4 | n |  | TRUE
134 | bus_LV_115-13_0_5_node_198 | 0.4 | n |  | TRUE
135 | bus_LV_115-13_0_5_node_199 | 0.4 | n |  | TRUE
136 | bus_LV_115-13_0_5_node_200 | 0.4 | n |  | TRUE
137 | bus_MV_356_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-13_0_5_load_0 | 0 | 0.00023002 | 5.7648e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-13_0_5_load_1 | 1 | 0.00013059 | 3.273e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-13_0_5_load_3 | 3 | 0.00014181 | 3.5542e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-13_0_5_load_5 | 5 | 0.00013539 | 3.3933e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-13_0_5_load_203 | 6 | 0.005474 | 0.0013719 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-13_0_5_load_24 | 7 | 0.00079128 | 0.00019831 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-13_0_5_load_6 | 9 | 0.0011026 | 0.00027634 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-13_0_5_load_10 | 12 | 0.00084562 | 0.00021193 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-13_0_5_load_11 | 13 | 0.017169 | 0.0043029 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-13_0_5_load_9 | 15 | 4.7215e-05 | 1.1833e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-13_0_5_load_157 | 18 | 0.0080289 | 0.0020122 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-13_0_5_load_158 | 22 | 0.00031376 | 7.8635e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-13_0_5_load_85 | 23 | 0.0050605 | 0.0012683 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-13_0_5_load_83 | 24 | 0.000138 | 3.4587e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-13_0_5_load_14 | 27 | 0.00036496 | 9.1467e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-13_0_5_load_18 | 28 | 0.00042213 | 0.0001058 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-13_0_5_load_151 | 31 | 0.0041233 | 0.0010334 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-13_0_5_load_19 | 32 | 0.0074259 | 0.0018611 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-13_0_5_load_20 | 33 | 0.0022971 | 0.0005757 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-13_0_5_load_22 | 35 | 0.0016827 | 0.00042173 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-13_0_5_load_23 | 36 | 0.0028413 | 0.00071209 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-13_0_5_load_156 | 37 | 0.0043665 | 0.0010944 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-13_0_5_load_155 | 39 | 0.0043655 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-13_0_5_load_26 | 41 | 0.002824 | 0.00070776 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-13_0_5_load_27 | 42 | 0.0027944 | 0.00070033 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-13_0_5_load_29 | 43 | 0.0030448 | 0.00076311 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-13_0_5_load_31 | 44 | 0.0019238 | 0.00048214 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-13_0_5_load_32 | 45 | 0.0017188 | 0.00043078 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-13_0_5_load_57 | 47 | 0.0017207 | 0.00043124 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-13_0_5_load_172 | 48 | 0.0036203 | 0.00090733 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-13_0_5_load_168 | 49 | 0.003618 | 0.00090675 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-13_0_5_load_55 | 50 | 0.0017195 | 0.00043095 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-13_0_5_load_33 | 51 | 0.0023464 | 0.00058807 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-13_0_5_load_38 | 55 | 0.003117 | 0.0007812 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-13_0_5_load_75 | 56 | 0.0026465 | 0.00066327 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-13_0_5_load_39 | 57 | 0.0060689 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-13_0_5_load_51 | 58 | 0.0031197 | 0.00078187 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-13_0_5_load_78 | 59 | 0.0034044 | 0.00085321 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-13_0_5_load_79 | 60 | 0.0069273 | 0.0017362 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-13_0_5_load_69 | 63 | 0.0092088 | 0.0023079 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-13_0_5_load_41 | 65 | 0.012172 | 0.0030506 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-13_0_5_load_42 | 66 | 0.0022034 | 0.00055222 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-13_0_5_load_44 | 68 | 0.0022044 | 0.00055246 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-13_0_5_load_185 | 71 | 0.0022014 | 0.00055172 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-13_0_5_load_53 | 72 | 0.012557 | 0.0031471 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-13_0_5_load_166 | 74 | 0.011984 | 0.0030034 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_115-13_0_5_load_186 | 75 | 0.0022026 | 0.00055201 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_115-13_0_5_load_52 | 76 | 0.0037517 | 0.00094026 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_115-13_0_5_load_47 | 78 | 0.0025522 | 0.00063963 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_115-13_0_5_load_48 | 79 | 0.0016827 | 0.00042172 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_115-13_0_5_load_49 | 80 | 0.0031215 | 0.00078232 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_115-13_0_5_load_50 | 81 | 0.0016837 | 0.00042196 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_115-13_0_5_load_161 | 82 | 0.0011449 | 0.00028694 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_115-13_0_5_load_160 | 83 | 0.0011567 | 0.00028989 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_115-13_0_5_load_54 | 84 | 0.002492 | 0.00062455 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_115-13_0_5_load_56 | 85 | 0.0025199 | 0.00063155 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_115-13_0_5_load_58 | 86 | 0.0047431 | 0.0011887 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_115-13_0_5_load_59 | 87 | 0.0015236 | 0.00038185 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_115-13_0_5_load_60 | 88 | 0.001648 | 0.00041303 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_115-13_0_5_load_61 | 89 | 0.0011753 | 0.00029455 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_115-13_0_5_load_62 | 90 | 0.0020663 | 0.00051786 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_115-13_0_5_load_81 | 92 | 0.0024654 | 0.00061789 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_115-13_0_5_load_66 | 93 | 0.010328 | 0.0025884 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_115-13_0_5_load_80 | 94 | 0.0021269 | 0.00053306 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_115-13_0_5_load_64 | 95 | 0.0027836 | 0.00069764 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_115-13_0_5_load_65 | 96 | 0.011784 | 0.0029534 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_115-13_0_5_load_159 | 97 | 0.0015737 | 0.0003944 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_115-13_0_5_load_70 | 98 | 0.0098181 | 0.0024606 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_115-13_0_5_load_71 | 99 | 0.0022035 | 0.00055225 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_115-13_0_5_load_72 | 100 | 0.0022026 | 0.00055201 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_115-13_0_5_load_73 | 101 | 0.0022014 | 0.00055172 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_115-13_0_5_load_187 | 102 | 0.0022055 | 0.00055276 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_115-13_0_5_load_82 | 103 | 0.083563 | 0.020943 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_115-13_0_5_load_90 | 105 | 0.00077304 | 0.00019374 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_115-13_0_5_load_201 | 106 | 0.010936 | 0.0027408 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_115-13_0_5_load_202 | 107 | 0.00048921 | 0.00012261 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_115-13_0_5_load_125 | 108 | 0.00055483 | 0.00013905 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_115-13_0_5_load_163 | 112 | 0.0092078 | 0.0023077 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_115-13_0_5_load_169 | 113 | 0.0036212 | 0.00090757 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_115-13_0_5_load_171 | 114 | 0.0019227 | 0.00048188 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_115-13_0_5_load_177 | 116 | 0.00091769 | 0.00023 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_115-13_0_5_load_181 | 117 | 0.00095996 | 0.00024059 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_115-13_0_5_load_178 | 118 | 0.00091769 | 0.00023 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_115-13_0_5_load_175 | 119 | 0.00091769 | 0.00022999 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_115-13_0_5_load_193 | 120 | 0.001925 | 0.00048246 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_115-13_0_5_load_179 | 121 | 0.00096079 | 0.0002408 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_115-13_0_5_load_174 | 122 | 0.0036203 | 0.00090733 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_115-13_0_5_load_176 | 123 | 0.00091769 | 0.00022999 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_115-13_0_5_load_188 | 125 | 0.0012948 | 0.00032451 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_115-13_0_5_load_184 | 126 | 0.0012068 | 0.00030246 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_115-13_0_5_load_189 | 127 | 0.0012079 | 0.00030274 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_115-13_0_5_load_183 | 128 | 0.0012948 | 0.00032452 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_115-13_0_5_load_192 | 129 | 0.00096024 | 0.00024066 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_115-13_0_5_load_182 | 130 | 0.0012068 | 0.00030246 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_115-13_0_5_load_190 | 131 | 0.0012947 | 0.00032449 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_115-13_0_5_load_191 | 132 | 0.0023543 | 0.00059005 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_115-13_0_5_load_194 | 133 | 0.0043396 | 0.0010876 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_115-13_0_5_load_198 | 134 | 6.5277e-05 | 1.636e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_115-13_0_5_load_200 | 136 | 0.0026073 | 0.00065345 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 130 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-13_0_5_line_0 |  | 0 | 1 | 0.039331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-13_0_5_line_1 |  | 0 | 2 | 0.043782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-13_0_5_line_2 |  | 1 | 3 | 0.012608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-13_0_5_line_3 |  | 2 | 4 | 0.029542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-13_0_5_line_4 |  | 3 | 5 | 0.028216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-13_0_5_line_5 |  | 4 | 6 | 0.065319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-13_0_5_line_6 |  | 5 | 7 | 0.055421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-13_0_5_line_7 |  | 7 | 8 | 0.012003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-13_0_5_line_8 |  | 8 | 29 | 0.013644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-13_0_5_line_9 |  | 9 | 10 | 0.047203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-13_0_5_line_10 |  | 9 | 11 | 0.011654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-13_0_5_line_11 |  | 10 | 12 | 0.033454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-13_0_5_line_12 |  | 10 | 13 | 0.036719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-13_0_5_line_13 |  | 11 | 14 | 0.031358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_115-13_0_5_line_14 |  | 12 | 17 | 0.1481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-13_0_5_line_15 |  | 13 | 18 | 0.012743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-13_0_5_line_16 |  | 14 | 19 | 0.075759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-13_0_5_line_17 |  | 14 | 20 | 0.017348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-13_0_5_line_18 |  | 14 | 21 | 0.018875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_115-13_0_5_line_19 |  | 14 | 22 | 0.03487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-13_0_5_line_20 |  | 15 | 16 | 0.055836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-13_0_5_line_21 |  | 16 | 25 | 0.01031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-13_0_5_line_22 |  | 17 | 26 | 0.030583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_115-13_0_5_line_23 |  | 19 | 23 | 0.033013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-13_0_5_line_24 |  | 19 | 24 | 0.18941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-13_0_5_line_25 |  | 20 | 27 | 0.031288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-13_0_5_line_26 |  | 21 | 28 | 0.059776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-13_0_5_line_27 |  | 22 | 29 | 0.0016231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-13_0_5_line_28 |  | 24 | 30 | 0.0050431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-13_0_5_line_29 |  | 25 | 106 | 0.084243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-13_0_5_line_30 |  | 25 | 30 | 0.10756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-13_0_5_line_31 |  | 26 | 44 | 0.033269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_115-13_0_5_line_32 |  | 26 | 41 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-13_0_5_line_33 |  | 28 | 31 | 0.23434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_115-13_0_5_line_34 |  | 30 | 104 | 0.021433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-13_0_5_line_35 |  | 31 | 110 | 0.037416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-13_0_5_line_36 |  | 32 | 33 | 0.009402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_115-13_0_5_line_37 |  | 32 | 34 | 0.030195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_115-13_0_5_line_38 |  | 33 | 35 | 0.018909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_115-13_0_5_line_39 |  | 34 | 36 | 0.03581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_115-13_0_5_line_40 |  | 35 | 37 | 0.020119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_115-13_0_5_line_41 |  | 36 | 38 | 0.037227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_115-13_0_5_line_42 |  | 37 | 39 | 0.015239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_115-13_0_5_line_43 |  | 38 | 40 | 0.012177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_115-13_0_5_line_44 |  | 39 | 91 | 0.012931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_115-13_0_5_line_45 |  | 40 | 97 | 0.015727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_115-13_0_5_line_46 |  | 40 | 96 | 0.014516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_115-13_0_5_line_47 |  | 41 | 42 | 0.0016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_115-13_0_5_line_48 |  | 42 | 43 | 0.019507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_115-13_0_5_line_49 |  | 43 | 45 | 0.0071744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-13_0_5_line_50 |  | 44 | 46 | 0.029926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_115-13_0_5_line_51 |  | 45 | 47 | 2.7189e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-13_0_5_line_52 |  | 46 | 48 | 0.020812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_115-13_0_5_line_53 |  | 46 | 49 | 0.017536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_115-13_0_5_line_54 |  | 47 | 50 | 2.9507e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-13_0_5_line_55 |  | 48 | 73 | 0.064657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_115-13_0_5_line_56 |  | 49 | 113 | 0.00018085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_115-13_0_5_line_57 |  | 50 | 84 | 0.014306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-13_0_5_line_58 |  | 51 | 52 | 0.059484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-13_0_5_line_59 |  | 51 | 53 | 0.015968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-13_0_5_line_60 |  | 52 | 54 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_115-13_0_5_line_61 |  | 53 | 55 | 0.0060726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_115-13_0_5_line_62 |  | 54 | 56 | 0.03455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_115-13_0_5_line_63 |  | 55 | 57 | 0.026393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_115-13_0_5_line_64 |  | 56 | 58 | 0.01986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_115-13_0_5_line_65 |  | 57 | 61 | 0.030185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_115-13_0_5_line_66 |  | 58 | 80 | 0.010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_115-13_0_5_line_67 |  | 59 | 60 | 0.0027036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_115-13_0_5_line_68 |  | 60 | 61 | 0.018041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_115-13_0_5_line_69 |  | 62 | 63 | 0.021367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_115-13_0_5_line_70 |  | 62 | 64 | 0.06237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_115-13_0_5_line_71 |  | 63 | 69 | 0.0062049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_115-13_0_5_line_72 |  | 64 | 93 | 0.02671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_115-13_0_5_line_73 |  | 64 | 90 | 0.018209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_115-13_0_5_line_74 |  | 65 | 66 | 0.0050928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_115-13_0_5_line_75 |  | 65 | 67 | 0.023205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_115-13_0_5_line_76 |  | 66 | 68 | 0.0039317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_115-13_0_5_line_77 |  | 67 | 69 | 0.03463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_115-13_0_5_line_78 |  | 67 | 70 | 0.021221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_115-13_0_5_line_79 |  | 68 | 71 | 0.0039302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_115-13_0_5_line_80 |  | 69 | 72 | 0.024878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_115-13_0_5_line_81 |  | 70 | 73 | 0.025841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_115-13_0_5_line_82 |  | 70 | 74 | 0.026865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_115-13_0_5_line_83 |  | 71 | 75 | 0.0039295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_115-13_0_5_line_84 |  | 72 | 76 | 0.040461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_115-13_0_5_line_85 |  | 74 | 77 | 0.022619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_115-13_0_5_line_86 |  | 75 | 102 | 0.0039332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_115-13_0_5_line_87 |  | 77 | 111 | 0.060072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_115-13_0_5_line_88 |  | 78 | 79 | 0.019047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_115-13_0_5_line_89 |  | 78 | 80 | 0.00144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_115-13_0_5_line_90 |  | 79 | 81 | 0.00035006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_115-13_0_5_line_91 |  | 81 | 82 | 0.0003468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_115-13_0_5_line_92 |  | 82 | 83 | 0.014339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_115-13_0_5_line_93 |  | 83 | 97 | 0.0063366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_115-13_0_5_line_94 |  | 84 | 85 | 0.016548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_115-13_0_5_line_95 |  | 85 | 86 | 0.0038066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_115-13_0_5_line_96 |  | 87 | 88 | 0.018513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_115-13_0_5_line_97 |  | 87 | 89 | 0.0061606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_115-13_0_5_line_98 |  | 88 | 90 | 0.0091916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_115-13_0_5_line_99 |  | 91 | 92 | 0.032348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_115-13_0_5_line_100 |  | 92 | 94 | 0.0021976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_115-13_0_5_line_101 |  | 93 | 95 | 0.02925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_115-13_0_5_line_102 |  | 94 | 103 | 0.092525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_115-13_0_5_line_103 |  | 95 | 96 | 0.015813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_115-13_0_5_line_104 |  | 98 | 99 | 0.0031989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_115-13_0_5_line_105 |  | 98 | 100 | 0.00073281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_115-13_0_5_line_106 |  | 99 | 101 | 0.0039304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_115-13_0_5_line_107 |  | 101 | 102 | 0.0039315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_115-13_0_5_line_108 |  | 104 | 105 | 0.074389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_115-13_0_5_line_109 |  | 106 | 107 | 0.009958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_115-13_0_5_line_110 |  | 107 | 134 | 0.18556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_115-13_0_5_line_111 |  | 108 | 109 | 0.068753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_115-13_0_5_line_112 |  | 109 | 110 | 0.048511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_115-13_0_5_line_113 |  | 111 | 112 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_115-13_0_5_line_114 |  | 113 | 114 | 0.00036211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_115-13_0_5_line_115 |  | 114 | 115 | 0.01749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_115-13_0_5_line_116 |  | 115 | 116 | 0.014723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_115-13_0_5_line_117 |  | 115 | 117 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_115-13_0_5_line_118 |  | 115 | 118 | 0.010427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_115-13_0_5_line_119 |  | 116 | 119 | 0.0063512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_115-13_0_5_line_120 |  | 117 | 120 | 0.0035225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_115-13_0_5_line_121 |  | 118 | 121 | 0.00095585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_115-13_0_5_line_122 |  | 119 | 122 | 0.0058106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_115-13_0_5_line_123 |  | 120 | 129 | 0.0029094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_115-13_0_5_line_124 |  | 121 | 124 | 0.018589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_115-13_0_5_line_125 |  | 122 | 123 | 0.00054062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_115-13_0_5_line_126 |  | 124 | 125 | 0.0053098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_115-13_0_5_line_127 |  | 124 | 126 | 0.0044246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_115-13_0_5_line_128 |  | 125 | 127 | 0.0135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_115-13_0_5_line_129 |  | 126 | 128 | 0.014179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_115-13_0_5_line_130 |  | 127 | 131 | 0.0097738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_115-13_0_5_line_131 |  | 128 | 130 | 0.0097706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_115-13_0_5_line_132 |  | 129 | 133 | 0.0023182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_115-13_0_5_line_133 |  | 131 | 132 | 0.004423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_115-13_0_5_line_134 |  | 134 | 135 | 0.060469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_115-13_0_5_line_135 |  | 135 | 136 | 0.091783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-13_0_5_trafo_182 | 0.63 MVA 20/0.4 kV | 137 | 130 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2700326.3059 | 1239672.3472 | 2700364.7493 | 1239664.0363
1 | 2700283.5121 | 1239681.5987 | 2700326.3059 | 1239672.3472
2 | 2700364.7493 | 1239664.0363 | 2700377.073 | 1239661.372
3 | 2700254.5636 | 1239687.8925 | 2700283.5121 | 1239681.5987
4 | 2700404.6521 | 1239655.4098 | 2700377.073 | 1239661.372
5 | 2700254.5636 | 1239687.8925 | 2700262.7782 | 1239726.8385 | 2700287.4028 | 1239733.793
6 | 2700404.6521 | 1239655.4098 | 2700421.5637 | 1239651.7537 | 2700458.7388 | 1239643.3236
7 | 2700470.4141 | 1239640.5382 | 2700461.8996 | 1239642.6068 | 2700458.7388 | 1239643.3236
8 | 2700470.4141 | 1239640.5382 | 2700483.7919 | 1239643.4112
9 | 2700568.113 | 1239708.844 | 2700542.0943 | 1239669.4589
10 | 2700535.6706 | 1239659.7351 | 2700542.0943 | 1239669.4589
11 | 2700568.113 | 1239708.844 | 2700584.8774 | 1239731.0226 | 2700588.4575 | 1239735.3963
12 | 2700568.113 | 1239708.844 | 2700542.2948 | 1239734.954
13 | 2700518.674 | 1239633.3829 | 2700525.3073 | 1239643.6808 | 2700535.6706 | 1239659.7351
14 | 2700685.167 | 1239847.5222 | 2700620.7371 | 1239774.8302 | 2700588.4575 | 1239735.3963
15 | 2700533.3348 | 1239744.0152 | 2700542.2948 | 1239734.954
16 | 2700518.674 | 1239633.3829 | 2700528.8644 | 1239627.9401 | 2700535.7986 | 1239623.6098 | 2700541.508 | 1239621.0267 | 2700549.6508 | 1239618.5739 | 2700553.9488 | 1239616.256 | 2700568.6708 | 1239603.6402 | 2700575.9 | 1239593.9553 | 2700577.8741 | 1239591.2867 | 2700579.0421 | 1239590.2168
17 | 2700504.6216 | 1239632.3776 | 2700508.7301 | 1239630.9683 | 2700515.5488 | 1239628.5374 | 2700518.674 | 1239633.3829
18 | 2700518.674 | 1239633.3829 | 2700515.5488 | 1239628.5374 | 2700527.384 | 1239622.9001
19 | 2700518.674 | 1239633.3829 | 2700512.1124 | 1239635.8181 | 2700501.0535 | 1239639.834 | 2700493.8187 | 1239642.2689 | 2700487.9353 | 1239643.0699 | 2700485.4096 | 1239643.278
20 | 2700777.0539 | 1239559.8399 | 2700731.5936 | 1239592.2595
21 | 2700777.0539 | 1239559.8399 | 2700785.6977 | 1239554.1823
22 | 2700662.5186 | 1239868.1427 | 2700685.167 | 1239847.5222
23 | 2700579.0421 | 1239590.2168 | 2700584.1661 | 1239589.1472 | 2700592.4894 | 1239587.6537 | 2700597.9657 | 1239587.6687 | 2700600.9934 | 1239588.8876 | 2700602.6831 | 1239590.0616 | 2700605.7675 | 1239594.1836 | 2700608.0073 | 1239596.8125
24 | 2700579.0421 | 1239590.2168 | 2700660.1425 | 1239516.4238 | 2700680.41 | 1239498.8874 | 2700701.2697 | 1239484.3523 | 2700719.7536 | 1239476.0929 | 2700726.677 | 1239473.8183
25 | 2700504.6216 | 1239632.3776 | 2700501.4927 | 1239623.7291 | 2700499.7345 | 1239619.9076 | 2700497.4375 | 1239617.0777 | 2700494.7526 | 1239613.9298 | 2700491.8079 | 1239611.8229 | 2700488.9247 | 1239611.0068 | 2700485.4563 | 1239611.3458
26 | 2700527.384 | 1239622.9001 | 2700527.0413 | 1239579.2834 | 2700515.2821 | 1239568.2026
27 | 2700483.7919 | 1239643.4112 | 2700485.4096 | 1239643.278
28 | 2700731.4682 | 1239472.2442 | 2700726.677 | 1239473.8183
29 | 2700785.6977 | 1239554.1823 | 2700782.8681 | 1239570.2465 | 2700812.4052 | 1239621.5314 | 2700821.138 | 1239621.0037
30 | 2700731.4682 | 1239472.2442 | 2700735.928 | 1239471.0968 | 2700737.068 | 1239470.7826 | 2700785.7542 | 1239527.6964 | 2700785.0281 | 1239529.4744 | 2700784.4073 | 1239531.2874 | 2700783.9373 | 1239542.9216 | 2700785.6977 | 1239554.1823
31 | 2700662.5186 | 1239868.1427 | 2700637.4238 | 1239889.9853
32 | 2700662.5186 | 1239868.1427 | 2700650.815 | 1239854.2157
33 | 2700515.2821 | 1239568.2026 | 2700360.6435 | 1239392.1313
34 | 2700731.4682 | 1239472.2442 | 2700724.1926 | 1239467.7063 | 2700730.7586 | 1239465.4715 | 2700736.4163 | 1239463.7217
35 | 2700327.2724 | 1239409.0533 | 2700360.6435 | 1239392.1313
36 | 2700296.5694 | 1239824.2727 | 2700305.8 | 1239826.0597
37 | 2700266.9244 | 1239818.5337 | 2700296.5694 | 1239824.2727
38 | 2700324.4257 | 1239829.1982 | 2700320.3554 | 1239828.8774 | 2700305.8 | 1239826.0597
39 | 2700266.9244 | 1239818.5337 | 2700273.9509 | 1239828.4043 | 2700279.6372 | 1239836.1173 | 2700288.4168 | 1239847.1645
40 | 2700324.4257 | 1239829.1982 | 2700344.4823 | 1239830.7786
41 | 2700306.6884 | 1239878.4731 | 2700306.0036 | 1239872.0011 | 2700305.6477 | 1239870.2382 | 2700305.2689 | 1239868.9308 | 2700304.4634 | 1239867.3604 | 2700301.4935 | 1239863.6185 | 2700288.4168 | 1239847.1645
42 | 2700359.4447 | 1239833.6322 | 2700345.5098 | 1239830.8596 | 2700344.4823 | 1239830.7786
43 | 2700318.5041 | 1239881.5529 | 2700306.6884 | 1239878.4731
44 | 2700372.2704 | 1239834.4813 | 2700364.688 | 1239834.6755 | 2700359.4447 | 1239833.6322
45 | 2700318.5041 | 1239881.5529 | 2700318.6583 | 1239887.1931 | 2700318.8049 | 1239889.7086 | 2700319.1872 | 1239892.595 | 2700320.019 | 1239896.6344 | 2700320.1599 | 1239897.144
46 | 2700318.5041 | 1239881.5529 | 2700332.5081 | 1239885.3749
47 | 2700650.815 | 1239854.2157 | 2700649.7776 | 1239852.9812
48 | 2700637.228 | 1239838.0474 | 2700649.7776 | 1239852.9812
49 | 2700632.6123 | 1239832.5549 | 2700637.228 | 1239838.0474
50 | 2700614.8506 | 1239909.633 | 2700637.4238 | 1239889.9853
51 | 2700632.5948 | 1239832.534 | 2700632.6123 | 1239832.5549
52 | 2700614.8506 | 1239909.633 | 2700599.4565 | 1239923.639
53 | 2700614.8506 | 1239909.633 | 2700603.1238 | 1239896.5953
54 | 2700632.5759 | 1239832.5114 | 2700632.5948 | 1239832.534
55 | 2700559.9267 | 1239972.7061 | 2700563.339 | 1239960.1543 | 2700569.5432 | 1239950.6744 | 2700586.4872 | 1239935.4387 | 2700599.4565 | 1239923.639
56 | 2700603.1238 | 1239896.5953 | 2700603.0028 | 1239896.4608
57 | 2700632.5759 | 1239832.5114 | 2700623.3723 | 1239821.5594
58 | 2700353.6838 | 1240021.5204 | 2700369.5925 | 1240017.364 | 2700368.4659 | 1239983.3635 | 2700370.0247 | 1239981.0881 | 2700369.7021 | 1239974.8324
59 | 2700368.88 | 1239958.8852 | 2700369.7021 | 1239974.8324
60 | 2700348.0623 | 1240000.5984 | 2700353.6838 | 1240021.5204
61 | 2700368.88 | 1239958.8852 | 2700369.5267 | 1239952.8471
62 | 2700348.0623 | 1240000.5984 | 2700343.1462 | 1239980.4556 | 2700339.4375 | 1239967.147
63 | 2700369.5267 | 1239952.8471 | 2700369.5267 | 1239952.8471 | 2700372.4016 | 1239944.3115 | 2700375.1283 | 1239940.9661 | 2700379.1098 | 1239938.5538 | 2700383.5716 | 1239936.8168 | 2700385.0797 | 1239933.5176
64 | 2700339.4375 | 1239967.147 | 2700337.3273 | 1239959.5747 | 2700334.1546 | 1239948.0021
65 | 2700413.095 | 1239944.7554 | 2700385.0797 | 1239933.5176
66 | 2700331.2756 | 1239937.5008 | 2700334.1546 | 1239948.0021
67 | 2700406.4862 | 1239961.5419 | 2700405.4958 | 1239964.0576
68 | 2700413.095 | 1239944.7554 | 2700406.4862 | 1239961.5419
69 | 2700458.545 | 1239931.4141 | 2700478.2894 | 1239939.5814
70 | 2700400.603 | 1239907.905 | 2700458.545 | 1239931.4141
71 | 2700484.0231 | 1239941.9532 | 2700478.2894 | 1239939.5814
72 | 2700400.603 | 1239907.905 | 2700375.562 | 1239898.6113
73 | 2700400.603 | 1239907.905 | 2700405.9441 | 1239895.3302 | 2700406.6144 | 1239890.8327
74 | 2700537.4222 | 1239936.6209 | 2700533.5854 | 1239939.9698
75 | 2700516.1033 | 1239955.2285 | 2700533.5854 | 1239939.9698
76 | 2700537.4222 | 1239936.6209 | 2700540.3844 | 1239934.0355
77 | 2700484.0231 | 1239941.9532 | 2700516.1033 | 1239955.2285
78 | 2700535.7598 | 1239963.3675 | 2700516.1033 | 1239955.2285
79 | 2700540.3844 | 1239934.0355 | 2700543.3453 | 1239931.4511
80 | 2700484.0231 | 1239941.9532 | 2700502.2768 | 1239925.0502
81 | 2700559.9267 | 1239972.7061 | 2700535.7598 | 1239963.3675
82 | 2700535.7598 | 1239963.3675 | 2700533.6751 | 1239969.0032 | 2700530.5857 | 1239967.8611 | 2700522.5094 | 1239983.4566
83 | 2700543.3453 | 1239931.4511 | 2700546.3058 | 1239928.8671
84 | 2700533.0067 | 1239899.36 | 2700509.5082 | 1239920.8129 | 2700505.839 | 1239921.7515 | 2700502.2768 | 1239925.0502
85 | 2700512.108 | 1240003.5421 | 2700522.5094 | 1239983.4566
86 | 2700546.3058 | 1239928.8671 | 2700549.269 | 1239926.2808
87 | 2700464.9271 | 1240002.098 | 2700492.8902 | 1240014.1582 | 2700504.1085 | 1240018.9962 | 2700512.108 | 1240003.5421
88 | 2700330.8949 | 1239936.112 | 2700326.6906 | 1239920.7766 | 2700325.8526 | 1239917.7443
89 | 2700330.8949 | 1239936.112 | 2700331.2756 | 1239937.5008
90 | 2700325.7594 | 1239917.4069 | 2700325.8526 | 1239917.7443
91 | 2700325.667 | 1239917.0726 | 2700325.7594 | 1239917.4069
92 | 2700321.8477 | 1239903.2518 | 2700325.667 | 1239917.0726
93 | 2700320.1599 | 1239897.144 | 2700321.8477 | 1239903.2518
94 | 2700612.7264 | 1239808.8909 | 2700623.3723 | 1239821.5594
95 | 2700610.2774 | 1239805.9767 | 2700612.7264 | 1239808.8909
96 | 2700404.8331 | 1239863.8343 | 2700408.6831 | 1239876.9515 | 2700407.9692 | 1239881.7415
97 | 2700404.8331 | 1239863.8343 | 2700403.0981 | 1239857.923
98 | 2700406.6144 | 1239890.8327 | 2700407.9692 | 1239881.7415
99 | 2700372.2704 | 1239834.4813 | 2700375.0532 | 1239829.1576 | 2700397.7914 | 1239815.8597
100 | 2700399.6884 | 1239814.7502 | 2700397.7914 | 1239815.8597
101 | 2700375.562 | 1239898.6113 | 2700371.754 | 1239897.198 | 2700358.8707 | 1239892.8436 | 2700347.7496 | 1239889.5862
102 | 2700477.7734 | 1239766.5363 | 2700452.3372 | 1239788.7784 | 2700444.0569 | 1239792.6634 | 2700408.0562 | 1239809.8565 | 2700399.6884 | 1239814.7502
103 | 2700332.5081 | 1239885.3749 | 2700345.1723 | 1239888.8313 | 2700347.7496 | 1239889.5862
104 | 2700555.1921 | 1239921.111 | 2700557.6021 | 1239919.0074
105 | 2700558.1542 | 1239918.5256 | 2700557.6021 | 1239919.0074
106 | 2700552.231 | 1239923.6955 | 2700555.1921 | 1239921.111
107 | 2700549.269 | 1239926.2808 | 2700552.231 | 1239923.6955
108 | 2700736.4163 | 1239463.7217 | 2700723.2945 | 1239429.7066 | 2700720.9308 | 1239427.2424 | 2700716.701 | 1239425.0912 | 2700711.1884 | 1239424.9754 | 2700707.2853 | 1239425.8543 | 2700689.2806 | 1239435.1364
109 | 2700831.0778 | 1239620.4031 | 2700821.138 | 1239621.0037
110 | 2700831.0778 | 1239620.4031 | 2701009.7045 | 1239670.6412
111 | 2700356.5739 | 1239381.5275 | 2700417.7886 | 1239350.2279
112 | 2700327.2724 | 1239409.0533 | 2700322.7986 | 1239400.2933 | 2700326.6924 | 1239397.7238 | 2700333.8386 | 1239393.3857 | 2700340.323 | 1239389.7147 | 2700347.3061 | 1239386.0744 | 2700356.5739 | 1239381.5275
113 | 2700464.9271 | 1240002.098 | 2700453.5589 | 1239997.1983
114 | 2700603.0028 | 1239896.4608 | 2700602.7607 | 1239896.1916
115 | 2700591.0643 | 1239883.1876 | 2700602.7607 | 1239896.1916
116 | 2700591.0643 | 1239883.1876 | 2700579.9291 | 1239892.8202
117 | 2700591.0643 | 1239883.1876 | 2700602.2548 | 1239873.5118
118 | 2700591.0643 | 1239883.1876 | 2700584.0933 | 1239875.433
119 | 2700579.9291 | 1239892.8202 | 2700575.1257 | 1239896.9754
120 | 2700602.2548 | 1239873.5118 | 2700604.9194 | 1239871.2079
121 | 2700583.4543 | 1239874.7221 | 2700584.0933 | 1239875.433
122 | 2700570.7311 | 1239900.7768 | 2700575.1257 | 1239896.9754
123 | 2700607.1201 | 1239869.305 | 2700604.9194 | 1239871.2079
124 | 2700571.0271 | 1239860.8979 | 2700583.4543 | 1239874.7221
125 | 2700570.7311 | 1239900.7768 | 2700570.3223 | 1239901.1305
126 | 2700571.0271 | 1239860.8979 | 2700575.0193 | 1239857.3969
127 | 2700571.0271 | 1239860.8979 | 2700567.7103 | 1239863.8265
128 | 2700575.0193 | 1239857.3969 | 2700585.1691 | 1239848.4957
129 | 2700557.0818 | 1239873.2108 | 2700567.7103 | 1239863.8265
130 | 2700585.1691 | 1239848.4957 | 2700592.5174 | 1239842.0514
131 | 2700549.7576 | 1239879.6777 | 2700557.0818 | 1239873.2108
132 | 2700608.8737 | 1239867.7888 | 2700607.1201 | 1239869.305
133 | 2700595.8428 | 1239839.1351 | 2700592.5174 | 1239842.0514
134 | 2701068.4509 | 1239656.8665 | 2701061.6314 | 1239659.7749 | 2701029.3254 | 1239666.8416 | 2701009.7045 | 1239670.6412
135 | 2701068.4509 | 1239656.8665 | 2701080.1458 | 1239651.5059 | 2701101.9714 | 1239635.7989 | 2701145.1131 | 1239606.7172

## bus_geodata
| x | y | coords
0 | 2700326.3059 | 1239672.3472
1 | 2700364.7493 | 1239664.0363
2 | 2700283.5121 | 1239681.5987
3 | 2700377.073 | 1239661.372
4 | 2700254.5636 | 1239687.8925
5 | 2700404.6521 | 1239655.4098
6 | 2700287.4028 | 1239733.793
7 | 2700458.7388 | 1239643.3236
8 | 2700470.4141 | 1239640.5382
9 | 2700542.0943 | 1239669.4589
10 | 2700568.113 | 1239708.844
11 | 2700535.6706 | 1239659.7351
12 | 2700588.4575 | 1239735.3963
13 | 2700542.2948 | 1239734.954
14 | 2700518.674 | 1239633.3829
15 | 2700731.5936 | 1239592.2595
16 | 2700777.0539 | 1239559.8399
17 | 2700685.167 | 1239847.5222
18 | 2700533.3348 | 1239744.0152
19 | 2700579.0421 | 1239590.2168
20 | 2700504.6216 | 1239632.3776
21 | 2700527.384 | 1239622.9001
22 | 2700485.4096 | 1239643.278
23 | 2700608.0073 | 1239596.8125
24 | 2700726.677 | 1239473.8183
25 | 2700785.6977 | 1239554.1823
26 | 2700662.5186 | 1239868.1427
27 | 2700485.4563 | 1239611.3458
28 | 2700515.2821 | 1239568.2026
29 | 2700483.7919 | 1239643.4112
30 | 2700731.4682 | 1239472.2442
31 | 2700360.6435 | 1239392.1313
32 | 2700296.5694 | 1239824.2727
33 | 2700305.8 | 1239826.0597
34 | 2700266.9244 | 1239818.5337
35 | 2700324.4257 | 1239829.1982
36 | 2700288.4168 | 1239847.1645
37 | 2700344.4823 | 1239830.7786
38 | 2700306.6884 | 1239878.4731
39 | 2700359.4447 | 1239833.6322
40 | 2700318.5041 | 1239881.5529
41 | 2700650.815 | 1239854.2157
42 | 2700649.7776 | 1239852.9812
43 | 2700637.228 | 1239838.0474
44 | 2700637.4238 | 1239889.9853
45 | 2700632.6123 | 1239832.5549
46 | 2700614.8506 | 1239909.633
47 | 2700632.5948 | 1239832.534
48 | 2700599.4565 | 1239923.639
49 | 2700603.1238 | 1239896.5953
50 | 2700632.5759 | 1239832.5114
51 | 2700369.7021 | 1239974.8324
52 | 2700353.6838 | 1240021.5204
53 | 2700368.88 | 1239958.8852
54 | 2700348.0623 | 1240000.5984
55 | 2700369.5267 | 1239952.8471
56 | 2700339.4375 | 1239967.147
57 | 2700385.0797 | 1239933.5176
58 | 2700334.1546 | 1239948.0021
59 | 2700405.4958 | 1239964.0576
60 | 2700406.4862 | 1239961.5419
61 | 2700413.095 | 1239944.7554
62 | 2700458.545 | 1239931.4141
63 | 2700478.2894 | 1239939.5814
64 | 2700400.603 | 1239907.905
65 | 2700533.5854 | 1239939.9698
66 | 2700537.4222 | 1239936.6209
67 | 2700516.1033 | 1239955.2285
68 | 2700540.3844 | 1239934.0355
69 | 2700484.0231 | 1239941.9532
70 | 2700535.7598 | 1239963.3675
71 | 2700543.3453 | 1239931.4511
72 | 2700502.2768 | 1239925.0502
73 | 2700559.9267 | 1239972.7061
74 | 2700522.5094 | 1239983.4566
75 | 2700546.3058 | 1239928.8671
76 | 2700533.0067 | 1239899.36
77 | 2700512.108 | 1240003.5421
78 | 2700330.8949 | 1239936.112
79 | 2700325.8526 | 1239917.7443
80 | 2700331.2756 | 1239937.5008
81 | 2700325.7594 | 1239917.4069
82 | 2700325.667 | 1239917.0726
83 | 2700321.8477 | 1239903.2518
84 | 2700623.3723 | 1239821.5594
85 | 2700612.7264 | 1239808.8909
86 | 2700610.2774 | 1239805.9767
87 | 2700404.8331 | 1239863.8343
88 | 2700407.9692 | 1239881.7415
89 | 2700403.0981 | 1239857.923
90 | 2700406.6144 | 1239890.8327
91 | 2700372.2704 | 1239834.4813
92 | 2700397.7914 | 1239815.8597
93 | 2700375.562 | 1239898.6113
94 | 2700399.6884 | 1239814.7502
95 | 2700347.7496 | 1239889.5862
96 | 2700332.5081 | 1239885.3749
97 | 2700320.1599 | 1239897.144
98 | 2700557.6021 | 1239919.0074
99 | 2700555.1921 | 1239921.111
100 | 2700558.1542 | 1239918.5256
101 | 2700552.231 | 1239923.6955
102 | 2700549.269 | 1239926.2808
103 | 2700477.7734 | 1239766.5363
104 | 2700736.4163 | 1239463.7217
105 | 2700689.2806 | 1239435.1364
106 | 2700821.138 | 1239621.0037
107 | 2700831.0778 | 1239620.4031
108 | 2700417.7886 | 1239350.2279
109 | 2700356.5739 | 1239381.5275
110 | 2700327.2724 | 1239409.0533
111 | 2700464.9271 | 1240002.098
112 | 2700453.5589 | 1239997.1983
113 | 2700603.0028 | 1239896.4608
114 | 2700602.7607 | 1239896.1916
115 | 2700591.0643 | 1239883.1876
116 | 2700579.9291 | 1239892.8202
117 | 2700602.2548 | 1239873.5118
118 | 2700584.0933 | 1239875.433
119 | 2700575.1257 | 1239896.9754
120 | 2700604.9194 | 1239871.2079
121 | 2700583.4543 | 1239874.7221
122 | 2700570.7311 | 1239900.7768
123 | 2700570.3223 | 1239901.1305
124 | 2700571.0271 | 1239860.8979
125 | 2700575.0193 | 1239857.3969
126 | 2700567.7103 | 1239863.8265
127 | 2700585.1691 | 1239848.4957
128 | 2700557.0818 | 1239873.2108
129 | 2700607.1201 | 1239869.305
130 | 2700549.7576 | 1239879.6777
131 | 2700592.5174 | 1239842.0514
132 | 2700595.8428 | 1239839.1351
133 | 2700608.8737 | 1239867.7888
134 | 2701009.7045 | 1239670.6412
135 | 2701068.4509 | 1239656.8665
136 | 2701145.1131 | 1239606.7172
137 | 2700547.599 | 1239881.5836

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97785 | -0.42603 | 0.00023002 | 5.7648e-05
1 | 0.97806 | -0.42194 | 0.00013059 | 3.273e-05
2 | 0.97763 | -0.4304 | 0 | 0
3 | 0.97813 | -0.4206 | 0.00014181 | 3.5542e-05
4 | 0.97748 | -0.43335 | 0 | 0
5 | 0.97829 | -0.41752 | 0.00013539 | 3.3933e-05
6 | 0.97715 | -0.43988 | 0.005474 | 0.0013719
7 | 0.9786 | -0.41135 | 0.00079128 | 0.00019831
8 | 0.97868 | -0.40984 | 0 | 0
9 | 0.98032 | -0.37766 | 0.0011026 | 0.00027634
10 | 0.98181 | -0.34863 | 0 | 0
11 | 0.97997 | -0.38461 | 0 | 0
12 | 0.98364 | -0.31291 | 0.00084562 | 0.00021193
13 | 0.98095 | -0.36538 | 0.017169 | 0.0043029
14 | 0.97901 | -0.40333 | 0 | 0
15 | 0.97344 | -0.51279 | 4.7215e-05 | 1.1833e-05
16 | 0.97344 | -0.51274 | 0 | 0
17 | 0.99188 | -0.15414 | 0 | 0
18 | 0.98086 | -0.36723 | 0.0080289 | 0.0020122
19 | 0.97759 | -0.43113 | 0 | 0
20 | 0.979 | -0.40345 | 0 | 0
21 | 0.97892 | -0.40509 | 0 | 0
22 | 0.97878 | -0.40792 | 0.00031376 | 7.8635e-05
23 | 0.97743 | -0.43418 | 0.0050605 | 0.0012683
24 | 0.97493 | -0.48337 | 0.000138 | 3.4587e-05
25 | 0.97344 | -0.51273 | 0 | 0
26 | 0.99231 | -0.14602 | 0 | 0
27 | 0.97899 | -0.40365 | 0.00036496 | 9.1467e-05
28 | 0.97864 | -0.41065 | 0.00042213 | 0.0001058
29 | 0.97876 | -0.40812 | 0 | 0
30 | 0.97486 | -0.48475 | 0 | 0
31 | 0.97762 | -0.43066 | 0.0041233 | 0.0010334
32 | 0.97742 | -0.43374 | 0.0074259 | 0.0018611
33 | 0.97724 | -0.4372 | 0.0022971 | 0.0005757
34 | 0.97803 | -0.42181 | 0 | 0
35 | 0.9769 | -0.444 | 0.0016827 | 0.00042173
36 | 0.97875 | -0.40768 | 0.0028413 | 0.00071209
37 | 0.97653 | -0.45113 | 0.0043665 | 0.0010944
38 | 0.97952 | -0.39263 | 0 | 0
39 | 0.97627 | -0.45628 | 0.0043655 | 0.0010941
40 | 0.97978 | -0.38772 | 0 | 0
41 | 0.99191 | -0.15361 | 0.002824 | 0.00070776
42 | 0.99188 | -0.15421 | 0.0027944 | 0.00070033
43 | 0.99156 | -0.16041 | 0.0030448 | 0.00076311
44 | 0.99295 | -0.13372 | 0.0019238 | 0.00048214
45 | 0.99146 | -0.16231 | 0.0017188 | 0.00043078
46 | 0.99342 | -0.12467 | 0 | 0
47 | 0.99146 | -0.16232 | 0.0017207 | 0.00043124
48 | 0.99237 | -0.14477 | 0.0036203 | 0.00090733
49 | 0.99459 | -0.10249 | 0.003618 | 0.00090675
50 | 0.99146 | -0.16232 | 0.0017195 | 0.00043095
51 | 0.97471 | -0.48716 | 0.0023464 | 0.00058807
52 | 0.97592 | -0.46333 | 0 | 0
53 | 0.97442 | -0.49288 | 0 | 0
54 | 0.97636 | -0.45466 | 0 | 0
55 | 0.97431 | -0.49506 | 0.003117 | 0.0007812
56 | 0.97706 | -0.44086 | 0.0026465 | 0.00066327
57 | 0.9739 | -0.50301 | 0.0060689 | 0.001521
58 | 0.97752 | -0.43197 | 0.0031197 | 0.00078187
59 | 0.97343 | -0.51234 | 0.0034044 | 0.00085321
60 | 0.97344 | -0.51217 | 0.0069273 | 0.0017362
61 | 0.97361 | -0.50875 | 0 | 0
62 | 0.98458 | -0.29453 | 0 | 0
63 | 0.9853 | -0.28047 | 0.0092088 | 0.0023079
64 | 0.98245 | -0.33568 | 0 | 0
65 | 0.98602 | -0.26677 | 0.012172 | 0.0030506
66 | 0.98589 | -0.26927 | 0.0022034 | 0.00055222
67 | 0.98687 | -0.2503 | 0 | 0
68 | 0.9858 | -0.27105 | 0.0022044 | 0.00055246
69 | 0.98553 | -0.27619 | 0 | 0
70 | 0.98785 | -0.23147 | 0 | 0
71 | 0.98572 | -0.27268 | 0.0022014 | 0.00055172
72 | 0.98515 | -0.28348 | 0.012557 | 0.0031471
73 | 0.98914 | -0.20663 | 0 | 0
74 | 0.98732 | -0.24164 | 0.011984 | 0.0030034
75 | 0.98564 | -0.27414 | 0.0022026 | 0.00055201
76 | 0.98501 | -0.2862 | 0.0037517 | 0.00094026
77 | 0.98713 | -0.24537 | 0 | 0
78 | 0.97784 | -0.42568 | 0.0025522 | 0.00063963
79 | 0.97843 | -0.41412 | 0.0016827 | 0.00042172
80 | 0.9778 | -0.42649 | 0.0031215 | 0.00078232
81 | 0.97844 | -0.4139 | 0.0016837 | 0.00042196
82 | 0.97845 | -0.41366 | 0.0011449 | 0.00028694
83 | 0.97895 | -0.4038 | 0.0011567 | 0.00028989
84 | 0.99134 | -0.1648 | 0.002492 | 0.00062455
85 | 0.99123 | -0.16693 | 0.0025199 | 0.00063155
86 | 0.99121 | -0.16725 | 0.0047431 | 0.0011887
87 | 0.98226 | -0.33941 | 0.0015236 | 0.00038185
88 | 0.98231 | -0.33851 | 0.001648 | 0.00041303
89 | 0.98225 | -0.33954 | 0.0011753 | 0.00029455
90 | 0.98234 | -0.33778 | 0.0020663 | 0.00051786
91 | 0.97606 | -0.46045 | 0 | 0
92 | 0.97552 | -0.4709 | 0.0024654 | 0.00061789
93 | 0.98157 | -0.35273 | 0.010328 | 0.0025884
94 | 0.97549 | -0.47159 | 0.0021269 | 0.00053306
95 | 0.98067 | -0.37035 | 0.0027836 | 0.00069764
96 | 0.98019 | -0.37972 | 0.011784 | 0.0029534
97 | 0.97918 | -0.3993 | 0.0015737 | 0.0003944
98 | 0.98543 | -0.27831 | 0.0098181 | 0.0024606
99 | 0.98547 | -0.27762 | 0.0022035 | 0.00055225
100 | 0.98543 | -0.27834 | 0.0022026 | 0.00055201
101 | 0.98552 | -0.27662 | 0.0022014 | 0.00055172
102 | 0.98558 | -0.27546 | 0.0022055 | 0.00055276
103 | 0.97188 | -0.54266 | 0.083563 | 0.020943
104 | 0.97484 | -0.48505 | 0 | 0
105 | 0.97479 | -0.48611 | 0.00077304 | 0.00019374
106 | 0.97233 | -0.53462 | 0.010936 | 0.0027408
107 | 0.9723 | -0.5352 | 0.00048921 | 0.00012261
108 | 0.97754 | -0.43223 | 0.00055483 | 0.00013905
109 | 0.97758 | -0.43153 | 0 | 0
110 | 0.9776 | -0.43104 | 0 | 0
111 | 0.98662 | -0.25527 | 0 | 0
112 | 0.98652 | -0.25731 | 0.0092078 | 0.0023077
113 | 0.9946 | -0.10226 | 0.0036212 | 0.00090757
114 | 0.99462 | -0.10179 | 0.0019227 | 0.00048188
115 | 0.99581 | -0.079153 | 0 | 0
116 | 0.99573 | -0.080802 | 0.00091769 | 0.00023
117 | 0.9957 | -0.081281 | 0.00095996 | 0.00024059
118 | 0.99655 | -0.06515 | 0.00091769 | 0.00023
119 | 0.9957 | -0.081412 | 0.00091769 | 0.00022999
120 | 0.99568 | -0.081729 | 0.001925 | 0.00048246
121 | 0.99662 | -0.063864 | 0.00096079 | 0.0002408
122 | 0.99567 | -0.081875 | 0.0036203 | 0.00090733
123 | 0.99567 | -0.081884 | 0.00091769 | 0.00022999
124 | 0.99794 | -0.038833 | 0 | 0
125 | 0.99791 | -0.039405 | 0.0012948 | 0.00032451
126 | 0.99826 | -0.03279 | 0.0012068 | 0.00030246
127 | 0.99785 | -0.040553 | 0.0012079 | 0.00030274
128 | 0.99929 | -0.01339 | 0.0012948 | 0.00032452
129 | 0.99567 | -0.082 | 0.00096024 | 0.00024066
130 | 1 | 0 | -0.40129 | -0.1028
131 | 0.99782 | -0.041177 | 0.0012947 | 0.00032449
132 | 0.99781 | -0.04136 | 0.0023543 | 0.00059005
133 | 0.99566 | -0.082177 | 0.0043396 | 0.0010876
134 | 0.97184 | -0.54437 | 6.5277e-05 | 1.636e-05
135 | 0.9717 | -0.54729 | 0 | 0
136 | 0.97147 | -0.55171 | 0.0026073 | 0.00065345
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0057077 | -0.0014301 | 0.0057088 | 0.0014304 | 1.1126e-06 | 2.1856e-07 | 0.0086853 | 0.0086852 | 0.0086853 | 0.97785 | -0.42603 | 0.97806 | -0.42194 | 2.3861
1 | 0.0054777 | 0.0013725 | -0.0054765 | -0.0013723 | 1.1407e-06 | 1.8096e-07 | 0.0083353 | 0.0083355 | 0.0083355 | 0.97785 | -0.42603 | 0.97763 | -0.4304 | 2.29
2 | -0.0058394 | -0.0014631 | 0.0058398 | 0.0014632 | 3.7316e-07 | 8.0574e-08 | 0.0088838 | 0.0088838 | 0.0088838 | 0.97806 | -0.42194 | 0.97813 | -0.4206 | 2.4406
3 | 0.0054765 | 0.0013723 | -0.0054757 | -0.0013722 | 7.6974e-07 | 1.2226e-07 | 0.0083355 | 0.0083356 | 0.0083356 | 0.97763 | -0.4304 | 0.97748 | -0.43335 | 2.29
4 | -0.0059816 | -0.0014987 | 0.0059824 | 0.0014989 | 8.7612e-07 | 2.065e-07 | 0.0090995 | 0.0090994 | 0.0090995 | 0.97813 | -0.4206 | 0.97829 | -0.41752 | 2.4999
5 | 0.0054757 | 0.0013722 | -0.005474 | -0.0013719 | 1.702e-06 | 2.7079e-07 | 0.0083356 | 0.0083359 | 0.0083359 | 0.97748 | -0.43335 | 0.97715 | -0.43988 | 2.2901
6 | -0.0061178 | -0.0015329 | 0.0061196 | 0.0015333 | 1.7995e-06 | 4.5562e-07 | 0.0093053 | 0.0093051 | 0.0093053 | 0.97829 | -0.41752 | 0.9786 | -0.41135 | 2.5564
7 | -0.0069109 | -0.0017316 | 0.0069114 | 0.0017318 | 4.9704e-07 | 1.6729e-07 | 0.010508 | 0.010508 | 0.010508 | 0.9786 | -0.41135 | 0.97868 | -0.40984 | 2.8869
8 | -0.0069114 | -0.0017318 | 0.006912 | 0.001732 | 5.6497e-07 | 1.9012e-07 | 0.010508 | 0.010508 | 0.010508 | 0.97868 | -0.40984 | 0.97876 | -0.40812 | 2.8869
9 | -0.03406 | -0.0085746 | 0.034108 | 0.0086043 | 4.7338e-05 | 2.97e-05 | 0.051714 | 0.051713 | 0.051714 | 0.98032 | -0.37766 | 0.98181 | -0.34863 | 14.207
10 | 0.032958 | 0.0082983 | -0.032947 | -0.0082914 | 1.0943e-05 | 6.8567e-06 | 0.05004 | 0.05004 | 0.05004 | 0.98032 | -0.37766 | 0.97997 | -0.38461 | 13.7473
11 | -0.059326 | -0.014932 | 0.059428 | 0.014997 | 0.00010147 | 6.4518e-05 | 0.089937 | 0.089936 | 0.089937 | 0.98181 | -0.34863 | 0.98364 | -0.31291 | 24.7078
12 | 0.025218 | 0.0063278 | -0.025198 | -0.0063154 | 2.0118e-05 | 1.2411e-05 | 0.038223 | 0.038223 | 0.038223 | 0.98181 | -0.34863 | 0.98095 | -0.36538 | 10.5009
13 | 0.032947 | 0.0082914 | -0.032917 | -0.008273 | 2.9445e-05 | 1.845e-05 | 0.05004 | 0.05004 | 0.05004 | 0.97997 | -0.38461 | 0.97901 | -0.40333 | 13.7473
14 | -0.060273 | -0.015209 | 0.060735 | 0.015502 | 0.00046207 | 0.00029383 | 0.091216 | 0.091215 | 0.091216 | 0.98364 | -0.31291 | 0.99188 | -0.15414 | 25.0592
15 | 0.0080296 | 0.0020125 | -0.0080289 | -0.0020122 | 7.0895e-07 | 2.9287e-07 | 0.01218 | 0.01218 | 0.01218 | 0.98095 | -0.36538 | 0.98086 | -0.36723 | 3.3462
16 | 0.020219 | 0.0050945 | -0.020192 | -0.0050783 | 2.6847e-05 | 1.6231e-05 | 0.03074 | 0.030741 | 0.030741 | 0.97901 | -0.40333 | 0.97759 | -0.43113 | 8.4453
17 | 0.00036496 | 9.0859e-05 | -0.00036496 | -9.1076e-05 | 2.0006e-09 | -2.1686e-07 | 0.0005545 | 0.00055457 | 0.00055457 | 0.97901 | -0.40333 | 0.979 | -0.40345 | 0.15236
18 | 0.0051065 | 0.0012764 | -0.0051061 | -0.0012763 | 4.2626e-07 | 3.5489e-08 | 0.0077603 | 0.0077603 | 0.0077603 | 0.97901 | -0.40333 | 0.97892 | -0.40509 | 2.132
19 | 0.0072274 | 0.0018112 | -0.0072258 | -0.0018106 | 1.5779e-06 | 5.7152e-07 | 0.010985 | 0.010985 | 0.010985 | 0.97901 | -0.40333 | 0.97878 | -0.40792 | 3.0179
20 | -4.7215e-05 | -1.1833e-05 | 4.7215e-05 | 1.1139e-05 | 1.087e-10 | -6.9406e-07 | 7.2174e-05 | 7.1931e-05 | 7.2174e-05 | 0.97344 | -0.51279 | 0.97344 | -0.51274 | 0.019828
21 | -4.7215e-05 | -1.1139e-05 | 4.7215e-05 | 1.1011e-05 | 1.9983e-11 | -1.2816e-07 | 7.1931e-05 | 7.1887e-05 | 7.1931e-05 | 0.97344 | -0.51274 | 0.97344 | -0.51273 | 0.019761
22 | -0.060735 | -0.015502 | 0.060759 | 0.015516 | 2.3855e-05 | 1.3688e-05 | 0.091215 | 0.091214 | 0.091215 | 0.99188 | -0.15414 | 0.99231 | -0.14602 | 6.2648
23 | 0.0050613 | 0.0012683 | -0.0050605 | -0.0012683 | 7.3475e-07 | 5.6391e-08 | 0.0077038 | 0.007704 | 0.007704 | 0.97759 | -0.43113 | 0.97743 | -0.43418 | 2.1165
24 | 0.01513 | 0.0038099 | -0.015093 | -0.0037882 | 3.7696e-05 | 2.1757e-05 | 0.023037 | 0.023038 | 0.023038 | 0.97759 | -0.43113 | 0.97493 | -0.48337 | 6.3291
25 | 0.00036496 | 9.1076e-05 | -0.00036496 | -9.1467e-05 | 3.6094e-09 | -3.9111e-07 | 0.00055457 | 0.00055472 | 0.00055472 | 0.979 | -0.40345 | 0.97899 | -0.40365 | 0.15239
26 | 0.0051061 | 0.0012763 | -0.0051047 | -0.0012762 | 1.35e-06 | 1.1272e-07 | 0.0077603 | 0.0077606 | 0.0077606 | 0.97892 | -0.40509 | 0.97864 | -0.41065 | 2.132
27 | 0.006912 | 0.001732 | -0.006912 | -0.001732 | 6.721e-08 | 2.2615e-08 | 0.010508 | 0.010508 | 0.010508 | 0.97878 | -0.40792 | 0.97876 | -0.40812 | 2.8869
28 | 0.014955 | 0.0037536 | -0.014954 | -0.003753 | 9.8544e-07 | 5.678e-07 | 0.022827 | 0.022827 | 0.022827 | 0.97493 | -0.48337 | 0.97486 | -0.48475 | 6.2712
29 | 0.014115 | 0.0035387 | -0.0141 | -0.0035303 | 1.4707e-05 | 8.3663e-06 | 0.021576 | 0.021577 | 0.021577 | 0.97344 | -0.51273 | 0.97233 | -0.53462 | 5.9276
30 | -0.014162 | -0.0035497 | 0.014181 | 0.0035604 | 1.8903e-05 | 1.0759e-05 | 0.021648 | 0.021648 | 0.021648 | 0.97344 | -0.51273 | 0.97486 | -0.48475 | 5.9473
31 | -0.084354 | -0.021435 | 0.084404 | 0.021466 | 4.9988e-05 | 3.0272e-05 | 0.1266 | 0.1266 | 0.1266 | 0.99231 | -0.14602 | 0.99295 | -0.13372 | 8.6949
32 | 0.023595 | 0.0059193 | -0.023586 | -0.0059141 | 8.5412e-06 | 5.2314e-06 | 0.035384 | 0.035384 | 0.035384 | 0.99231 | -0.14602 | 0.99191 | -0.15361 | 9.7209
33 | 0.0046826 | 0.0011704 | -0.0046781 | -0.0011705 | 4.454e-06 | -9.0794e-08 | 0.0071188 | 0.0071198 | 0.0071198 | 0.97864 | -0.41065 | 0.97762 | -0.43066 | 1.956
34 | 0.00077309 | 0.00019258 | -0.00077308 | -0.00019284 | 1.1185e-08 | -2.6006e-07 | 0.0011796 | 0.0011797 | 0.0011797 | 0.97486 | -0.48475 | 0.97484 | -0.48505 | 0.3241
35 | 0.00055488 | 0.00013714 | -0.00055487 | -0.0001376 | 9.9939e-09 | -4.6275e-07 | 0.00084388 | 0.00084404 | 0.00084404 | 0.97762 | -0.43066 | 0.9776 | -0.43104 | 0.23188
36 | 0.10132 | 0.025561 | -0.1013 | -0.025551 | 1.6791e-05 | 1.0157e-05 | 0.15431 | 0.15431 | 0.15431 | 0.97742 | -0.43374 | 0.97724 | -0.4372 | 8.4786
37 | -0.10875 | -0.027422 | 0.10881 | 0.02746 | 6.2116e-05 | 3.7861e-05 | 0.16562 | 0.16561 | 0.16562 | 0.97742 | -0.43374 | 0.97803 | -0.42181 | 9.0997
38 | 0.099007 | 0.024975 | -0.098975 | -0.024955 | 3.2255e-05 | 1.9459e-05 | 0.15081 | 0.15081 | 0.15081 | 0.97724 | -0.4372 | 0.9769 | -0.444 | 8.2864
39 | -0.10881 | -0.02746 | 0.10888 | 0.027505 | 7.3664e-05 | 4.4897e-05 | 0.16561 | 0.16561 | 0.16561 | 0.97803 | -0.42181 | 0.97875 | -0.40768 | 9.0997
40 | 0.097292 | 0.024534 | -0.097259 | -0.024514 | 3.3163e-05 | 1.9965e-05 | 0.14825 | 0.14825 | 0.14825 | 0.9769 | -0.444 | 0.97653 | -0.45113 | 8.1456
41 | -0.11172 | -0.028217 | 0.1118 | 0.028266 | 8.0627e-05 | 4.926e-05 | 0.16993 | 0.16993 | 0.16993 | 0.97875 | -0.40768 | 0.97952 | -0.39263 | 9.337
42 | 0.092892 | 0.023419 | -0.092869 | -0.023406 | 2.2915e-05 | 1.3712e-05 | 0.1416 | 0.1416 | 0.1416 | 0.97653 | -0.45113 | 0.97627 | -0.45628 | 7.7801
43 | -0.1118 | -0.028266 | 0.11183 | 0.028282 | 2.6373e-05 | 1.6112e-05 | 0.16993 | 0.16993 | 0.16993 | 0.97952 | -0.39263 | 0.97978 | -0.38772 | 9.3369
44 | 0.088504 | 0.022312 | -0.088486 | -0.022301 | 1.766e-05 | 1.0494e-05 | 0.13494 | 0.13494 | 0.13494 | 0.97627 | -0.45628 | 0.97606 | -0.46045 | 7.4145
45 | 0.040699 | 0.010256 | -0.040676 | -0.010242 | 2.2546e-05 | 1.4232e-05 | 0.061831 | 0.061831 | 0.061831 | 0.97978 | -0.38772 | 0.97918 | -0.3993 | 16.9865
46 | -0.15253 | -0.038538 | 0.15259 | 0.038575 | 5.8479e-05 | 3.6512e-05 | 0.23176 | 0.23176 | 0.23176 | 0.97978 | -0.38772 | 0.98019 | -0.37972 | 12.7342
47 | 0.020762 | 0.0052063 | -0.020762 | -0.005206 | 5.8668e-07 | 3.5466e-07 | 0.031148 | 0.031148 | 0.031148 | 0.99191 | -0.15361 | 0.99188 | -0.15421 | 8.5571
48 | 0.017967 | 0.0045056 | -0.017962 | -0.0045025 | 5.3151e-06 | 3.15e-06 | 0.026956 | 0.026956 | 0.026956 | 0.99188 | -0.15421 | 0.99156 | -0.16041 | 7.4054
49 | 0.014917 | 0.0037394 | -0.014916 | -0.0037386 | 1.3483e-06 | 7.7038e-07 | 0.022386 | 0.022386 | 0.022386 | 0.99156 | -0.16041 | 0.99146 | -0.16231 | 6.1501
50 | -0.086328 | -0.021948 | 0.086365 | 0.02197 | 3.7629e-05 | 2.2146e-05 | 0.12948 | 0.12948 | 0.12948 | 0.99295 | -0.13372 | 0.99342 | -0.12467 | 7.1143
51 | 0.013197 | 0.0033078 | -0.013197 | -0.0033078 | 3.9989e-09 | 2.2065e-09 | 0.019807 | 0.019807 | 0.019807 | 0.99146 | -0.16231 | 0.99146 | -0.16232 | 5.4414
52 | 0.27669 | 0.070765 | -0.27643 | -0.070595 | 0.00026878 | 0.00017067 | 0.41496 | 0.41496 | 0.41496 | 0.99342 | -0.12467 | 0.99237 | -0.14477 | 22.8
53 | -0.36306 | -0.092735 | 0.36345 | 0.092984 | 0.00038984 | 0.00024836 | 0.54444 | 0.54444 | 0.54444 | 0.99342 | -0.12467 | 0.99459 | -0.10249 | 29.9142
54 | 0.011476 | 0.0028766 | -0.011476 | -0.0028766 | 3.2853e-09 | 1.7258e-09 | 0.017224 | 0.017224 | 0.017224 | 0.99146 | -0.16232 | 0.99146 | -0.16232 | 4.7319
55 | 0.27281 | 0.069687 | -0.27199 | -0.069171 | 0.00081331 | 0.00051635 | 0.40953 | 0.40953 | 0.40953 | 0.99237 | -0.14477 | 0.98914 | -0.20663 | 22.5018
56 | -0.36707 | -0.09389 | 0.36707 | 0.093893 | 4.1009e-06 | 2.6128e-06 | 0.54985 | 0.54985 | 0.54985 | 0.99459 | -0.10249 | 0.9946 | -0.10226 | 30.2116
57 | 0.0097569 | 0.0024456 | -0.0097558 | -0.0024451 | 1.1504e-06 | 5.5177e-07 | 0.014644 | 0.014644 | 0.014644 | 0.99146 | -0.16232 | 0.99134 | -0.1648 | 4.023
58 | -0.021882 | -0.00549 | 0.021907 | 0.0055052 | 2.4896e-05 | 1.5191e-05 | 0.033408 | 0.033408 | 0.033408 | 0.97471 | -0.48716 | 0.97592 | -0.46333 | 9.178
59 | 0.019536 | 0.0049019 | -0.01953 | -0.0048987 | 5.3269e-06 | 3.2103e-06 | 0.029826 | 0.029826 | 0.029826 | 0.97471 | -0.48716 | 0.97442 | -0.49288 | 8.1939
60 | -0.021907 | -0.0055052 | 0.021916 | 0.0055107 | 9.0661e-06 | 5.5315e-06 | 0.033408 | 0.033408 | 0.033408 | 0.97592 | -0.46333 | 0.97636 | -0.45466 | 9.1779
61 | 0.01953 | 0.0048987 | -0.019528 | -0.0048975 | 2.0258e-06 | 1.2209e-06 | 0.029826 | 0.029826 | 0.029826 | 0.97442 | -0.49288 | 0.97431 | -0.49506 | 8.1939
62 | -0.021916 | -0.0055107 | 0.021931 | 0.0055195 | 1.446e-05 | 8.8219e-06 | 0.033408 | 0.033407 | 0.033408 | 0.97636 | -0.45466 | 0.97706 | -0.44086 | 9.1779
63 | 0.016411 | 0.0041163 | -0.016405 | -0.0041126 | 6.2184e-06 | 3.6512e-06 | 0.025065 | 0.025066 | 0.025066 | 0.97431 | -0.49506 | 0.9739 | -0.50301 | 6.8861
64 | -0.024577 | -0.0061828 | 0.024587 | 0.0061892 | 1.0439e-05 | 6.4319e-06 | 0.037438 | 0.037438 | 0.037438 | 0.97706 | -0.44086 | 0.97752 | -0.43197 | 10.2851
65 | 0.010336 | 0.0025916 | -0.010333 | -0.0025902 | 2.8233e-06 | 1.4314e-06 | 0.015793 | 0.015793 | 0.015793 | 0.9739 | -0.50301 | 0.97361 | -0.50875 | 4.3388
66 | -0.027707 | -0.0069711 | 0.027714 | 0.0069756 | 7.2672e-06 | 4.5145e-06 | 0.042187 | 0.042187 | 0.042187 | 0.97752 | -0.43197 | 0.9778 | -0.42649 | 11.5898
67 | -0.0034044 | -0.00085321 | 0.0034044 | 0.0008532 | 2.7456e-08 | -1.6038e-08 | 0.005204 | 0.005204 | 0.005204 | 0.97343 | -0.51234 | 0.97344 | -0.51217 | 1.4297
68 | -0.010332 | -0.0025893 | 0.010333 | 0.0025902 | 1.6874e-06 | 8.5563e-07 | 0.015793 | 0.015793 | 0.015793 | 0.97344 | -0.51217 | 0.97361 | -0.50875 | 4.3388
69 | -0.18462 | -0.046877 | 0.18475 | 0.046956 | 0.00012496 | 7.8614e-05 | 0.27924 | 0.27924 | 0.27924 | 0.98458 | -0.29453 | 0.9853 | -0.28047 | 15.3431
70 | 0.18462 | 0.046877 | -0.18426 | -0.046648 | 0.00036476 | 0.00022949 | 0.27924 | 0.27925 | 0.27925 | 0.98458 | -0.29453 | 0.98245 | -0.33568 | 15.3431
71 | -0.19396 | -0.049264 | 0.194 | 0.049289 | 3.9992e-05 | 2.52e-05 | 0.29315 | 0.29315 | 0.29315 | 0.9853 | -0.28047 | 0.98553 | -0.27619 | 16.1072
72 | 0.17784 | 0.045041 | -0.1777 | -0.044949 | 0.00014553 | 9.1449e-05 | 0.26953 | 0.26953 | 0.26953 | 0.98245 | -0.33568 | 0.98157 | -0.35273 | 14.8094
73 | 0.0064141 | 0.0016072 | -0.0064134 | -0.001607 | 6.4443e-07 | 1.8188e-07 | 0.0097146 | 0.0097147 | 0.0097147 | 0.98245 | -0.33568 | 0.98234 | -0.33778 | 2.6689
74 | 0.027455 | 0.006885 | -0.027451 | -0.0068829 | 3.2786e-06 | 2.0334e-06 | 0.041433 | 0.041434 | 0.041434 | 0.98602 | -0.26677 | 0.98589 | -0.26927 | 11.3828
75 | -0.039626 | -0.0099355 | 0.039658 | 0.0099551 | 3.112e-05 | 1.9621e-05 | 0.059802 | 0.059802 | 0.059802 | 0.98602 | -0.26677 | 0.98687 | -0.2503 | 16.4292
76 | 0.025248 | 0.0063307 | -0.025246 | -0.0063294 | 2.1411e-06 | 1.3202e-06 | 0.038108 | 0.038108 | 0.038108 | 0.98589 | -0.26927 | 0.9858 | -0.27105 | 10.4692
77 | 0.21057 | 0.053545 | -0.21031 | -0.053379 | 0.00026229 | 0.00016565 | 0.31778 | 0.31778 | 0.31778 | 0.98687 | -0.2503 | 0.98553 | -0.27619 | 17.4607
78 | -0.25023 | -0.0635 | 0.25046 | 0.063644 | 0.00022691 | 0.00014387 | 0.37759 | 0.37758 | 0.37759 | 0.98687 | -0.2503 | 0.98785 | -0.23147 | 20.7464
79 | 0.023041 | 0.0057769 | -0.02304 | -0.0057758 | 1.7829e-06 | 1.0909e-06 | 0.034781 | 0.034781 | 0.034781 | 0.9858 | -0.27105 | 0.98572 | -0.27268 | 9.5551
80 | 0.016315 | 0.0040905 | -0.016309 | -0.0040872 | 5.6613e-06 | 3.3064e-06 | 0.024634 | 0.024634 | 0.024634 | 0.98553 | -0.27619 | 0.98515 | -0.28348 | 6.7676
81 | -0.27167 | -0.068965 | 0.27199 | 0.069171 | 0.00032505 | 0.00020638 | 0.40953 | 0.40953 | 0.40953 | 0.98785 | -0.23147 | 0.98914 | -0.20663 | 22.5018
82 | 0.021209 | 0.0053205 | -0.021198 | -0.0053143 | 1.0283e-05 | 6.2376e-06 | 0.031949 | 0.031949 | 0.031949 | 0.98785 | -0.23147 | 0.98732 | -0.24164 | 8.7772
83 | 0.020838 | 0.0052241 | -0.020837 | -0.0052232 | 1.4582e-06 | 8.8316e-07 | 0.031457 | 0.031457 | 0.031457 | 0.98572 | -0.27268 | 0.98564 | -0.27414 | 8.6422
84 | 0.0037522 | 0.00094006 | -0.0037517 | -0.00094026 | 4.8734e-07 | -2.032e-07 | 0.0056673 | 0.0056675 | 0.0056675 | 0.98515 | -0.28348 | 0.98501 | -0.2862 | 1.557
85 | 0.0092147 | 0.0023109 | -0.009213 | -0.0023101 | 1.636e-06 | 7.5786e-07 | 0.013888 | 0.013888 | 0.013888 | 0.98732 | -0.24164 | 0.98713 | -0.24537 | 3.8155
86 | 0.018634 | 0.0046712 | -0.018633 | -0.0046705 | 1.1673e-06 | 6.9696e-07 | 0.028132 | 0.028132 | 0.028132 | 0.98564 | -0.27414 | 0.98558 | -0.27546 | 7.7287
87 | 0.009213 | 0.0023101 | -0.0092087 | -0.0023081 | 4.3452e-06 | 2.0133e-06 | 0.013888 | 0.013889 | 0.013889 | 0.98713 | -0.24537 | 0.98662 | -0.25527 | 3.8155
88 | -0.033389 | -0.0083983 | 0.033408 | 0.0084099 | 1.8448e-05 | 1.1568e-05 | 0.050821 | 0.050821 | 0.050821 | 0.97784 | -0.42568 | 0.97843 | -0.41412 | 13.9617
89 | 0.030837 | 0.0077587 | -0.030836 | -0.007758 | 1.1897e-06 | 7.4331e-07 | 0.046937 | 0.046937 | 0.046937 | 0.97784 | -0.42568 | 0.9778 | -0.42649 | 12.8948
90 | -0.03509 | -0.0088316 | 0.035091 | 0.0088318 | 3.7405e-07 | 2.3499e-07 | 0.05338 | 0.05338 | 0.05338 | 0.97843 | -0.41412 | 0.97844 | -0.4139 | 14.6648
91 | -0.036774 | -0.0092538 | 0.036775 | 0.0092541 | 4.0697e-07 | 2.561e-07 | 0.05594 | 0.05594 | 0.05594 | 0.97844 | -0.4139 | 0.97845 | -0.41366 | 15.3682
92 | -0.03792 | -0.009541 | 0.037938 | 0.0095523 | 1.789e-05 | 1.127e-05 | 0.057681 | 0.057681 | 0.057681 | 0.97845 | -0.41366 | 0.97895 | -0.4038 | 15.8465
93 | -0.039094 | -0.0098422 | 0.039103 | 0.0098475 | 8.3954e-06 | 5.2934e-06 | 0.059439 | 0.059439 | 0.059439 | 0.97895 | -0.4038 | 0.97918 | -0.3993 | 16.3295
94 | 0.0072638 | 0.0018205 | -0.0072631 | -0.0018203 | 7.3769e-07 | 2.588e-07 | 0.010903 | 0.010903 | 0.010903 | 0.99134 | -0.1648 | 0.99123 | -0.16693 | 2.9954
95 | 0.0047432 | 0.0011887 | -0.0047431 | -0.0011887 | 7.2373e-08 | -2.7483e-09 | 0.0071204 | 0.0071204 | 0.0071204 | 0.99123 | -0.16693 | 0.99121 | -0.16725 | 1.9561
96 | -0.0026989 | -0.00067632 | 0.002699 | 0.00067616 | 1.1605e-07 | -1.6008e-07 | 0.0040885 | 0.0040884 | 0.0040885 | 0.98226 | -0.33941 | 0.98231 | -0.33851 | 1.1232
97 | 0.0011753 | 0.00029448 | -0.0011753 | -0.00029455 | 7.3231e-09 | -7.3294e-08 | 0.0017804 | 0.0017804 | 0.0017804 | 0.98226 | -0.33941 | 0.98225 | -0.33954 | 0.48913
98 | -0.004347 | -0.0010892 | 0.0043472 | 0.0010892 | 1.4946e-07 | -2.0712e-08 | 0.0065848 | 0.0065848 | 0.0065848 | 0.98231 | -0.33851 | 0.98234 | -0.33778 | 1.809
99 | 0.088486 | 0.022301 | -0.088442 | -0.022275 | 4.4179e-05 | 2.6254e-05 | 0.13494 | 0.13494 | 0.13494 | 0.97606 | -0.46045 | 0.97552 | -0.4709 | 7.4145
100 | 0.085976 | 0.021657 | -0.085974 | -0.021655 | 2.8365e-06 | 1.6782e-06 | 0.13118 | 0.13118 | 0.13118 | 0.97552 | -0.4709 | 0.97549 | -0.47159 | 7.2079
101 | 0.16737 | 0.042361 | -0.16723 | -0.042272 | 0.00014139 | 8.8643e-05 | 0.25387 | 0.25388 | 0.25388 | 0.98157 | -0.35273 | 0.98067 | -0.37035 | 13.9492
102 | 0.083847 | 0.021122 | -0.083563 | -0.020943 | 0.00028397 | 0.00017944 | 0.12794 | 0.12794 | 0.12794 | 0.97549 | -0.47159 | 0.97188 | -0.54266 | 17.5742
103 | 0.16445 | 0.041574 | -0.16437 | -0.041528 | 7.3917e-05 | 4.631e-05 | 0.24965 | 0.24965 | 0.24965 | 0.98067 | -0.37035 | 0.98019 | -0.37972 | 13.7171
104 | -0.012021 | -0.0030127 | 0.012021 | 0.0030129 | 3.9523e-07 | 2.1219e-07 | 0.018151 | 0.018151 | 0.018151 | 0.98543 | -0.27831 | 0.98547 | -0.27762 | 4.9866
105 | 0.0022026 | 0.00055201 | -0.0022026 | -0.00055201 | 3.0399e-09 | -7.3904e-09 | 0.0033259 | 0.0033259 | 0.0033259 | 0.98543 | -0.27831 | 0.98543 | -0.27834 | 0.91371
106 | -0.014225 | -0.0035651 | 0.014225 | 0.0035655 | 6.7996e-07 | 3.8509e-07 | 0.021479 | 0.021479 | 0.021479 | 0.98547 | -0.27762 | 0.98552 | -0.27662 | 5.9007
107 | -0.016427 | -0.0041172 | 0.016428 | 0.0041178 | 9.0694e-07 | 5.3034e-07 | 0.024802 | 0.024802 | 0.024802 | 0.98552 | -0.27662 | 0.98558 | -0.27546 | 6.8139
108 | 0.00077308 | 0.00019284 | -0.00077304 | -0.00019374 | 3.8834e-08 | -9.0255e-07 | 0.0011797 | 0.00118 | 0.00118 | 0.97484 | -0.48505 | 0.97479 | -0.48611 | 0.32419
109 | 0.003164 | 0.00078949 | -0.0031639 | -0.00078956 | 8.7504e-08 | -6.7507e-08 | 0.0048407 | 0.0048408 | 0.0048408 | 0.97233 | -0.53462 | 0.9723 | -0.5352 | 1.3299
110 | 0.0026747 | 0.00066695 | -0.0026735 | -0.00066851 | 1.1654e-06 | -1.5544e-06 | 0.0040921 | 0.0040929 | 0.0040929 | 0.9723 | -0.5352 | 0.97184 | -0.54437 | 1.1244
111 | -0.00055483 | -0.00013905 | 0.00055485 | 0.0001382 | 1.8384e-08 | -8.5019e-07 | 0.00084457 | 0.00084426 | 0.00084457 | 0.97754 | -0.43223 | 0.97758 | -0.43153 | 0.23202
112 | -0.00055485 | -0.0001382 | 0.00055487 | 0.0001376 | 1.2963e-08 | -5.9992e-07 | 0.00084426 | 0.00084404 | 0.00084426 | 0.97758 | -0.43153 | 0.9776 | -0.43104 | 0.23194
113 | 0.0092087 | 0.0023081 | -0.0092078 | -0.0023077 | 8.9544e-07 | 4.1501e-07 | 0.013889 | 0.013889 | 0.013889 | 0.98662 | -0.25527 | 0.98652 | -0.25731 | 3.8155
114 | -0.37069 | -0.094801 | 0.3707 | 0.094806 | 8.3736e-06 | 5.3356e-06 | 0.55527 | 0.55527 | 0.55527 | 0.9946 | -0.10226 | 0.99462 | -0.10179 | 30.5093
115 | -0.37262 | -0.095288 | 0.37303 | 0.095548 | 0.00040865 | 0.0002604 | 0.55815 | 0.55815 | 0.55815 | 0.99462 | -0.10179 | 0.99581 | -0.079153 | 30.6673
116 | 0.0063741 | 0.0015974 | -0.0063736 | -0.0015973 | 5.0089e-07 | 1.2904e-07 | 0.0095246 | 0.0095247 | 0.0095247 | 0.99581 | -0.079153 | 0.99573 | -0.080802 | 2.6167
117 | 0.0081859 | 0.0020517 | -0.0081851 | -0.0020514 | 8.3005e-07 | 3.3879e-07 | 0.012232 | 0.012232 | 0.012232 | 0.99581 | -0.079153 | 0.9957 | -0.081281 | 3.3605
118 | -0.38759 | -0.099197 | 0.38786 | 0.099365 | 0.00026299 | 0.00016764 | 0.5799 | 0.5799 | 0.5799 | 0.99581 | -0.079153 | 0.99655 | -0.06515 | 31.8627
119 | 0.0054559 | 0.0013673 | -0.0054558 | -0.0013673 | 1.5833e-07 | 1.8719e-08 | 0.0081533 | 0.0081533 | 0.0081533 | 0.99573 | -0.080802 | 0.9957 | -0.081412 | 2.2399
120 | 0.0072251 | 0.0018108 | -0.007225 | -0.0018107 | 1.54e-07 | 5.2747e-08 | 0.010797 | 0.010798 | 0.010798 | 0.9957 | -0.081281 | 0.99568 | -0.081729 | 2.9663
121 | -0.38877 | -0.099595 | 0.3888 | 0.09961 | 2.4222e-05 | 1.544e-05 | 0.58127 | 0.58127 | 0.58127 | 0.99655 | -0.06515 | 0.99662 | -0.063864 | 31.938
122 | 0.0045381 | 0.0011373 | -0.004538 | -0.0011373 | 1.0022e-07 | -1.1434e-08 | 0.0067819 | 0.0067819 | 0.0067819 | 0.9957 | -0.081412 | 0.99567 | -0.081875 | 1.8632
123 | 0.0052999 | 0.0013283 | -0.0052999 | -0.0013283 | 6.8445e-08 | 5.9657e-09 | 0.0079206 | 0.0079206 | 0.0079206 | 0.99568 | -0.081729 | 0.99567 | -0.082 | 2.176
124 | -0.38976 | -0.099851 | 0.39023 | 0.10015 | 0.00047338 | 0.00030175 | 0.58271 | 0.58271 | 0.58271 | 0.99662 | -0.063864 | 0.99794 | -0.038833 | 32.0168
125 | 0.00091769 | 0.00022999 | -0.00091769 | -0.00022999 | 3.8124e-10 | -6.7872e-09 | 0.0013715 | 0.0013715 | 0.0013715 | 0.99567 | -0.081875 | 0.99567 | -0.081884 | 0.37678
126 | 0.0061524 | 0.0015417 | -0.0061522 | -0.0015417 | 1.6757e-07 | 3.7871e-08 | 0.0091736 | 0.0091736 | 0.0091736 | 0.99794 | -0.038833 | 0.99791 | -0.039405 | 2.5202
127 | -0.39638 | -0.10169 | 0.3965 | 0.10177 | 0.00011625 | 7.4113e-05 | 0.59188 | 0.59188 | 0.59188 | 0.99794 | -0.038833 | 0.99826 | -0.03279 | 32.5208
128 | 0.0048574 | 0.0012172 | -0.0048571 | -0.0012172 | 2.6558e-07 | -6.391e-09 | 0.0072429 | 0.007243 | 0.007243 | 0.99791 | -0.039405 | 0.99785 | -0.040553 | 1.9898
129 | -0.39771 | -0.10207 | 0.39808 | 0.10231 | 0.0003748 | 0.00023894 | 0.59368 | 0.59368 | 0.59368 | 0.99826 | -0.03279 | 0.99929 | -0.01339 | 32.6197
130 | 0.0036492 | 0.00091443 | -0.003649 | -0.00091449 | 1.0853e-07 | -5.821e-08 | 0.0054416 | 0.0054417 | 0.0054417 | 0.99785 | -0.040553 | 0.99782 | -0.041177 | 1.495
131 | -0.39938 | -0.10263 | 0.39964 | 0.1028 | 0.00025996 | 0.00016573 | 0.59561 | 0.59561 | 0.59561 | 0.99929 | -0.01339 | 1 | 0 | 32.7256
132 | 0.0043396 | 0.0010876 | -0.0043396 | -0.0010876 | 3.6565e-08 | -6.7477e-09 | 0.0064855 | 0.0064855 | 0.0064855 | 0.99567 | -0.082 | 0.99566 | -0.082177 | 1.7817
133 | 0.0023543 | 0.00059 | -0.0023543 | -0.00059005 | 2.0445e-08 | -4.4688e-08 | 0.0035109 | 0.0035109 | 0.0035109 | 0.99782 | -0.041177 | 0.99781 | -0.04136 | 0.96455
134 | 0.0026082 | 0.00065215 | -0.0026079 | -0.00065267 | 3.6156e-07 | -5.1775e-07 | 0.003993 | 0.0039932 | 0.0039932 | 0.97184 | -0.54437 | 0.9717 | -0.54729 | 1.097
135 | 0.0026079 | 0.00065267 | -0.0026073 | -0.00065345 | 5.4889e-07 | -7.8538e-07 | 0.0039932 | 0.0039936 | 0.0039936 | 0.9717 | -0.54729 | 0.97147 | -0.55171 | 1.0972

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40249 | 0.1031

## res_load
| p_mw | q_mvar
0 | 0.00023002 | 5.7648e-05
1 | 0.00013059 | 3.273e-05
2 | 0.00014181 | 3.5542e-05
3 | 0.00013539 | 3.3933e-05
4 | 0.005474 | 0.0013719
5 | 0.00079128 | 0.00019831
6 | 0.0011026 | 0.00027634
7 | 0.00084562 | 0.00021193
8 | 0.017169 | 0.0043029
9 | 4.7215e-05 | 1.1833e-05
10 | 0.0080289 | 0.0020122
11 | 0.00031376 | 7.8635e-05
12 | 0.0050605 | 0.0012683
13 | 0.000138 | 3.4587e-05
14 | 0.00036496 | 9.1467e-05
15 | 0.00042213 | 0.0001058
16 | 0.0041233 | 0.0010334
17 | 0.0074259 | 0.0018611
18 | 0.0022971 | 0.0005757
19 | 0.0016827 | 0.00042173
20 | 0.0028413 | 0.00071209
21 | 0.0043665 | 0.0010944
22 | 0.0043655 | 0.0010941
23 | 0.002824 | 0.00070776
24 | 0.0027944 | 0.00070033
25 | 0.0030448 | 0.00076311
26 | 0.0019238 | 0.00048214
27 | 0.0017188 | 0.00043078
28 | 0.0017207 | 0.00043124
29 | 0.0036203 | 0.00090733
30 | 0.003618 | 0.00090675
31 | 0.0017195 | 0.00043095
32 | 0.0023464 | 0.00058807
33 | 0.003117 | 0.0007812
34 | 0.0026465 | 0.00066327
35 | 0.0060689 | 0.001521
36 | 0.0031197 | 0.00078187
37 | 0.0034044 | 0.00085321
38 | 0.0069273 | 0.0017362
39 | 0.0092088 | 0.0023079
40 | 0.012172 | 0.0030506
41 | 0.0022034 | 0.00055222
42 | 0.0022044 | 0.00055246
43 | 0.0022014 | 0.00055172
44 | 0.012557 | 0.0031471
45 | 0.011984 | 0.0030034
46 | 0.0022026 | 0.00055201
47 | 0.0037517 | 0.00094026
48 | 0.0025522 | 0.00063963
49 | 0.0016827 | 0.00042172
50 | 0.0031215 | 0.00078232
51 | 0.0016837 | 0.00042196
52 | 0.0011449 | 0.00028694
53 | 0.0011567 | 0.00028989
54 | 0.002492 | 0.00062455
55 | 0.0025199 | 0.00063155
56 | 0.0047431 | 0.0011887
57 | 0.0015236 | 0.00038185
58 | 0.001648 | 0.00041303
59 | 0.0011753 | 0.00029455
60 | 0.0020663 | 0.00051786
61 | 0.0024654 | 0.00061789
62 | 0.010328 | 0.0025884
63 | 0.0021269 | 0.00053306
64 | 0.0027836 | 0.00069764
65 | 0.011784 | 0.0029534
66 | 0.0015737 | 0.0003944
67 | 0.0098181 | 0.0024606
68 | 0.0022035 | 0.00055225
69 | 0.0022026 | 0.00055201
70 | 0.0022014 | 0.00055172
71 | 0.0022055 | 0.00055276
72 | 0.083563 | 0.020943
73 | 0.00077304 | 0.00019374
74 | 0.010936 | 0.0027408
75 | 0.00048921 | 0.00012261
76 | 0.00055483 | 0.00013905
77 | 0.0092078 | 0.0023077
78 | 0.0036212 | 0.00090757
79 | 0.0019227 | 0.00048188
80 | 0.00091769 | 0.00023
81 | 0.00095996 | 0.00024059
82 | 0.00091769 | 0.00023
83 | 0.00091769 | 0.00022999
84 | 0.001925 | 0.00048246
85 | 0.00096079 | 0.0002408
86 | 0.0036203 | 0.00090733
87 | 0.00091769 | 0.00022999
88 | 0.0012948 | 0.00032451
89 | 0.0012068 | 0.00030246
90 | 0.0012079 | 0.00030274
91 | 0.0012948 | 0.00032452
92 | 0.00096024 | 0.00024066
93 | 0.0012068 | 0.00030246
94 | 0.0012947 | 0.00032449
95 | 0.0023543 | 0.00059005
96 | 0.0043396 | 0.0010876
97 | 6.5277e-05 | 1.636e-05
98 | 0.0026073 | 0.00065345

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1