## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-13_1_2_node_130 | 0.4 | n |  | TRUE
1 | bus_LV_115-13_1_2_node_118 | 0.4 | n |  | TRUE
2 | bus_LV_115-13_1_2_node_131 | 0.4 | n |  | TRUE
3 | bus_LV_115-13_1_2_node_132 | 0.4 | n |  | TRUE
4 | bus_LV_115-13_1_2_node_145 | 0.4 | n |  | TRUE
5 | bus_LV_115-13_1_2_node_133 | 0.4 | n |  | TRUE
6 | bus_LV_115-13_1_2_node_134 | 0.4 | n |  | TRUE
7 | bus_LV_115-13_1_2_node_135 | 0.4 | n |  | TRUE
8 | bus_LV_115-13_1_2_node_136 | 0.4 | n |  | TRUE
9 | bus_LV_115-13_1_2_node_101 | 0.4 | n |  | TRUE
10 | bus_LV_115-13_1_2_node_150 | 0.4 | n |  | TRUE
11 | bus_LV_115-13_1_2_node_137 | 0.4 | n |  | TRUE
12 | bus_LV_115-13_1_2_node_123 | 0.4 | n |  | TRUE
13 | bus_LV_115-13_1_2_node_138 | 0.4 | n |  | TRUE
14 | bus_LV_115-13_1_2_node_89 | 0.4 | n |  | TRUE
15 | bus_LV_115-13_1_2_node_139 | 0.4 | n |  | TRUE
16 | bus_LV_115-13_1_2_node_143 | 0.4 | n |  | TRUE
17 | bus_LV_115-13_1_2_node_148 | 0.4 | n |  | TRUE
18 | bus_LV_115-13_1_2_node_140 | 0.4 | n |  | TRUE
19 | bus_LV_115-13_1_2_node_195 | 0.4 | n |  | TRUE
20 | bus_LV_115-13_1_2_node_142 | 0.4 | n |  | TRUE
21 | bus_LV_115-13_1_2_node_144 | 0.4 | n |  | TRUE
22 | bus_LV_115-13_1_2_node_146 | 0.4 | n |  | TRUE
23 | bus_LV_115-13_1_2_node_147 | 0.4 | n |  | TRUE
24 | bus_LV_115-13_1_2_node_149 | 0.4 | n |  | TRUE
25 | bus_LV_115-13_1_2_node_153 | 0.4 | n |  | TRUE
26 | bus_LV_115-13_1_2_node_110 | 0.4 | n |  | TRUE
27 | bus_LV_115-13_1_2_node_154 | 0.4 | n |  | TRUE
28 | bus_LV_115-13_1_2_node_124 | 0.4 | n |  | TRUE
29 | bus_LV_115-13_1_2_node_196 | 0.4 | n |  | TRUE
30 | bus_LV_115-13_1_2_node_197 | 0.4 | n |  | TRUE
31 | bus_LV_115-13_1_2_node_204 | 0.4 | n |  | TRUE
32 | bus_LV_115-13_1_2_node_119 | 0.4 | n |  | TRUE
33 | bus_LV_115-13_1_2_node_91 | 0.4 | n |  | TRUE
34 | bus_LV_115-13_1_2_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_115-13_1_2_node_93 | 0.4 | n |  | TRUE
36 | bus_LV_115-13_1_2_node_94 | 0.4 | n |  | TRUE
37 | bus_LV_115-13_1_2_node_95 | 0.4 | n |  | TRUE
38 | bus_LV_115-13_1_2_node_96 | 0.4 | n |  | TRUE
39 | bus_LV_115-13_1_2_node_113 | 0.4 | n |  | TRUE
40 | bus_LV_115-13_1_2_node_97 | 0.4 | n |  | TRUE
41 | bus_LV_115-13_1_2_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_115-13_1_2_node_99 | 0.4 | n |  | TRUE
43 | bus_LV_115-13_1_2_node_100 | 0.4 | n |  | TRUE
44 | bus_LV_115-13_1_2_node_102 | 0.4 | n |  | TRUE
45 | bus_LV_115-13_1_2_node_103 | 0.4 | n |  | TRUE
46 | bus_LV_115-13_1_2_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_115-13_1_2_node_105 | 0.4 | n |  | TRUE
48 | bus_LV_115-13_1_2_node_106 | 0.4 | n |  | TRUE
49 | bus_LV_115-13_1_2_node_114 | 0.4 | n |  | TRUE
50 | bus_LV_115-13_1_2_node_115 | 0.4 | n |  | TRUE
51 | bus_LV_115-13_1_2_node_107 | 0.4 | n |  | TRUE
52 | bus_LV_115-13_1_2_node_108 | 0.4 | n |  | TRUE
53 | bus_LV_115-13_1_2_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_115-13_1_2_node_117 | 0.4 | n |  | TRUE
55 | bus_LV_115-13_1_2_node_112 | 0.4 | n |  | TRUE
56 | bus_LV_115-13_1_2_node_116 | 0.4 | n |  | TRUE
57 | bus_LV_115-13_1_2_node_120 | 0.4 | n |  | TRUE
58 | bus_LV_115-13_1_2_node_121 | 0.4 | n |  | TRUE
59 | bus_LV_115-13_1_2_node_122 | 0.4 | n |  | TRUE
60 | bus_LV_115-13_1_2_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_115-13_1_2_node_126 | 0.4 | n |  | TRUE
62 | bus_MV_356_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-13_1_2_load_130 | 0 | 0.0034015 | 0.00085248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-13_1_2_load_131 | 2 | 0.00078158 | 0.00019588 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-13_1_2_load_132 | 3 | 0.0014057 | 0.00035229 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-13_1_2_load_145 | 4 | 0.00078178 | 0.00019593 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-13_1_2_load_133 | 5 | 0.00056883 | 0.00014256 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-13_1_2_load_134 | 6 | 0.0012877 | 0.00032272 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-13_1_2_load_135 | 7 | 0.00082475 | 0.0002067 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-13_1_2_load_136 | 8 | 0.00044739 | 0.00011213 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-13_1_2_load_101 | 9 | 0.00083664 | 0.00020968 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-13_1_2_load_150 | 10 | 0.00045488 | 0.000114 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-13_1_2_load_137 | 11 | 4.7828e-05 | 1.1987e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-13_1_2_load_138 | 13 | 0.00080296 | 0.00020124 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-13_1_2_load_148 | 17 | 0.00044946 | 0.00011265 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-13_1_2_load_195 | 19 | 7.818e-05 | 1.9594e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-13_1_2_load_142 | 20 | 0.0046497 | 0.0011653 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-13_1_2_load_144 | 21 | 0.0035726 | 0.00089538 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-13_1_2_load_146 | 22 | 0.00047305 | 0.00011856 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-13_1_2_load_147 | 23 | 0.0012176 | 0.00030517 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-13_1_2_load_149 | 24 | 0.0011188 | 0.00028039 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-13_1_2_load_153 | 25 | 0.005363 | 0.0013441 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-13_1_2_load_154 | 27 | 0.00018939 | 4.7464e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-13_1_2_load_196 | 29 | 9.7014e-05 | 2.4314e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-13_1_2_load_197 | 30 | 0.00022224 | 5.5698e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-13_1_2_load_204 | 31 | 0.0047594 | 0.0011928 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-13_1_2_load_91 | 33 | 0.0037768 | 0.00094655 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-13_1_2_load_92 | 34 | 0.0051917 | 0.0013012 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-13_1_2_load_93 | 35 | 0.0030468 | 0.00076361 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-13_1_2_load_94 | 36 | 0.0046641 | 0.0011689 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-13_1_2_load_95 | 37 | 0.0029982 | 0.00075142 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-13_1_2_load_96 | 38 | 0.0071926 | 0.0018026 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-13_1_2_load_97 | 40 | 0.00067877 | 0.00017012 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-13_1_2_load_98 | 41 | 0.0022179 | 0.00055586 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-13_1_2_load_99 | 42 | 0.00045725 | 0.0001146 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-13_1_2_load_100 | 43 | 0.0014519 | 0.00036388 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-13_1_2_load_102 | 44 | 0.0047249 | 0.0011842 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-13_1_2_load_103 | 45 | 0.068712 | 0.017221 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-13_1_2_load_105 | 47 | 0.004185 | 0.0010489 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-13_1_2_load_114 | 49 | 0.013428 | 0.0033654 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-13_1_2_load_115 | 50 | 0.037517 | 0.0094025 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-13_1_2_load_107 | 51 | 0.0064169 | 0.0016082 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-13_1_2_load_117 | 54 | 0.0070362 | 0.0017634 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-13_1_2_load_112 | 55 | 0.0023144 | 0.00058004 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-13_1_2_load_116 | 56 | 0.0053119 | 0.0013313 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-13_1_2_load_120 | 57 | 0.00021619 | 5.4183e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-13_1_2_load_127 | 60 | 0.00042464 | 0.00010643 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-13_1_2_load_126 | 61 | 0.00057875 | 0.00014505 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-13_1_2_line_0 |  | 0 | 1 | 0.0087719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-13_1_2_line_1 |  | 0 | 2 | 0.011148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-13_1_2_line_2 |  | 1 | 48 | 0.16528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-13_1_2_line_3 |  | 2 | 3 | 0.004935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-13_1_2_line_4 |  | 3 | 4 | 0.0017604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-13_1_2_line_5 |  | 4 | 22 | 0.025946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-13_1_2_line_6 |  | 5 | 6 | 0.0031341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-13_1_2_line_7 |  | 5 | 7 | 0.0014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-13_1_2_line_8 |  | 6 | 8 | 0.0085644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-13_1_2_line_9 |  | 7 | 9 | 0.013192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-13_1_2_line_10 |  | 8 | 10 | 0.00078104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-13_1_2_line_11 |  | 9 | 42 | 0.037859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-13_1_2_line_12 |  | 10 | 24 | 0.00032003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-13_1_2_line_13 |  | 11 | 12 | 0.092799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_115-13_1_2_line_14 |  | 11 | 13 | 0.14574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-13_1_2_line_15 |  | 12 | 15 | 0.065355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-13_1_2_line_16 |  | 12 | 58 | 0.1421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-13_1_2_line_17 |  | 13 | 14 | 0.12718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-13_1_2_line_18 |  | 14 | 18 | 0.032878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_115-13_1_2_line_19 |  | 15 | 16 | 0.12322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-13_1_2_line_20 |  | 15 | 17 | 0.062658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-13_1_2_line_21 |  | 16 | 21 | 0.031508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-13_1_2_line_22 |  | 16 | 20 | 0.0064282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_115-13_1_2_line_23 |  | 17 | 23 | 0.0042239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-13_1_2_line_24 |  | 18 | 19 | 0.12234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-13_1_2_line_25 |  | 19 | 29 | 0.013297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-13_1_2_line_26 |  | 23 | 24 | 0.011717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-13_1_2_line_27 |  | 25 | 26 | 0.005372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-13_1_2_line_28 |  | 26 | 43 | 0.015719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-13_1_2_line_29 |  | 26 | 52 | 0.008415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-13_1_2_line_30 |  | 27 | 28 | 0.011554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-13_1_2_line_31 |  | 28 | 60 | 0.019445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_115-13_1_2_line_32 |  | 28 | 59 | 0.14785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-13_1_2_line_33 |  | 29 | 30 | 0.0070192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_115-13_1_2_line_34 |  | 31 | 32 | 0.025908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-13_1_2_line_35 |  | 32 | 48 | 0.021782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-13_1_2_line_36 |  | 33 | 34 | 0.012865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_115-13_1_2_line_37 |  | 33 | 35 | 0.030982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_115-13_1_2_line_38 |  | 34 | 36 | 0.032049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_115-13_1_2_line_39 |  | 35 | 37 | 0.0088407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_115-13_1_2_line_40 |  | 36 | 38 | 0.020394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_115-13_1_2_line_41 |  | 37 | 39 | 0.016288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_115-13_1_2_line_42 |  | 39 | 53 | 0.01057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_115-13_1_2_line_43 |  | 39 | 55 | 0.015828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_115-13_1_2_line_44 |  | 40 | 41 | 0.0093269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_115-13_1_2_line_45 |  | 40 | 42 | 0.0028528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_115-13_1_2_line_46 |  | 41 | 43 | 0.0024388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_115-13_1_2_line_47 |  | 44 | 45 | 0.0012678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_115-13_1_2_line_48 |  | 44 | 46 | 0.046702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_115-13_1_2_line_49 |  | 46 | 47 | 0.011981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-13_1_2_line_50 |  | 46 | 48 | 0.018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_115-13_1_2_line_51 |  | 47 | 49 | 0.024941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-13_1_2_line_52 |  | 48 | 50 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_115-13_1_2_line_53 |  | 50 | 56 | 0.020825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_115-13_1_2_line_54 |  | 51 | 52 | 0.014894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-13_1_2_line_55 |  | 52 | 53 | 0.061172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_115-13_1_2_line_56 |  | 53 | 54 | 0.0066341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_115-13_1_2_line_57 |  | 54 | 56 | 0.0065441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-13_1_2_line_58 |  | 57 | 58 | 0.0054434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-13_1_2_line_59 |  | 57 | 59 | 0.11096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-13_1_2_line_60 |  | 60 | 61 | 0.00056519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-13_1_2_trafo_116 | 0.63 MVA 20/0.4 kV | 62 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34
0 | 2700662.9091 | 1238646.5216 | 2700664.2291 | 1238642.7411 | 2700665.6081 | 1238639.4954 | 2700666.122 | 1238638.3658
1 | 2700666.122 | 1238638.3658 | 2700670.7384 | 1238628.2185
2 | 2700662.9091 | 1238646.5216 | 2700662.2298 | 1238649.101 | 2700661.7304 | 1238651.7834 | 2700661.3869 | 1238654.1905 | 2700660.4849 | 1238660.9804 | 2700659.5632 | 1238669.827 | 2700659.2985 | 1238672.9471 | 2700659.1794 | 1238675.5026 | 2700659.2013 | 1238678.672 | 2700659.3943 | 1238681.5664 | 2700659.7511 | 1238684.1744 | 2700660.3377 | 1238687.0532 | 2700661.1492 | 1238690.5029 | 2700662.1893 | 1238693.8564 | 2700663.5952 | 1238697.95 | 2700666.5303 | 1238705.9947 | 2700671.4156 | 1238719.4878 | 2700673.2548 | 1238725.2344 | 2700674.791 | 1238730.5645 | 2700675.6879 | 1238734.327 | 2700676.47 | 1238738.6213 | 2700676.7586 | 1238741.673 | 2700676.865 | 1238744.766 | 2700676.7546 | 1238748.6004 | 2700676.3785 | 1238752.9306 | 2700675.8835 | 1238757.5813 | 2700672.911 | 1238775.3777 | 2700672.4485 | 1238779.006 | 2700672.1851 | 1238782.493 | 2700672.1591 | 1238785.8062 | 2700672.3406 | 1238788.4891 | 2700672.6447 | 1238791.074 | 2700673.1414 | 1238793.9068 | 2700674.0063 | 1238799.1143 | 2700675.5 | 1238808.2799
3 | 2700672.8299 | 1238623.7489 | 2700671.612 | 1238626.2983 | 2700670.7384 | 1238628.2185
4 | 2700672.8299 | 1238623.7489 | 2700673.5887 | 1238622.1604
5 | 2700673.5887 | 1238622.1604 | 2700674.0358 | 1238621.2244 | 2700675.7529 | 1238618.1178 | 2700678.1281 | 1238614.5776 | 2700681.8276 | 1238609.6699 | 2700688.7796 | 1238601.2098
6 | 2700742.5052 | 1238961.6981 | 2700743.5998 | 1238964.6348
7 | 2700742.5052 | 1238961.6981 | 2700741.9845 | 1238960.3012
8 | 2700743.5998 | 1238964.6348 | 2700745.8175 | 1238970.5844 | 2700746.6667 | 1238972.63
9 | 2700741.9845 | 1238960.3012 | 2700741.563 | 1238959.1702 | 2700740.2777 | 1238955.5568 | 2700739.2674 | 1238952.2372 | 2700738.349 | 1238948.8523 | 2700738.1055 | 1238947.7048
10 | 2700746.9662 | 1238973.3513 | 2700746.6667 | 1238972.63
11 | 2700738.1055 | 1238947.7048 | 2700737.8446 | 1238946.4753 | 2700737.4725 | 1238944.334 | 2700737.2771 | 1238942.4738 | 2700737.2455 | 1238940.7719 | 2700737.3271 | 1238938.6384 | 2700740.2843 | 1238911.946 | 2700740.3986 | 1238910.0841
12 | 2700747.0889 | 1238973.6469 | 2700746.9662 | 1238973.3513
13 | 2700748.6184 | 1239092.5579 | 2700750.4982 | 1239095.4586 | 2700751.6849 | 1239097.3024 | 2700792.521 | 1239167.6265 | 2700795.4748 | 1239172.6511
14 | 2700795.4748 | 1239172.6511 | 2700826.1284 | 1239224.7961 | 2700827.9325 | 1239228.5851 | 2700828.6226 | 1239231.1543 | 2700828.9148 | 1239234.4396 | 2700828.4416 | 1239237.356 | 2700827.2944 | 1239239.8717 | 2700825.7959 | 1239242.1369 | 2700823.7739 | 1239244.4933 | 2700814.5361 | 1239253.9214 | 2700810.9878 | 1239257.9531 | 2700808.9184 | 1239260.8757 | 2700807.2363 | 1239264.1497 | 2700806.0994 | 1239267.3995 | 2700805.2938 | 1239271.6224 | 2700805.062 | 1239276.8113 | 2700805.3158 | 1239281.0188 | 2700805.9855 | 1239284.7885 | 2700807.1925 | 1239288.99 | 2700808.9673 | 1239292.723 | 2700811.959 | 1239297.8554 | 2700813.361 | 1239299.6783
15 | 2700788.1749 | 1239040.4784 | 2700761.6286 | 1239076.6109 | 2700748.6184 | 1239092.5579
16 | 2700653.8988 | 1239198.6544 | 2700683.3492 | 1239163.8383 | 2700692.7337 | 1239152.9002 | 2700718.3175 | 1239124.4014 | 2700748.6184 | 1239092.5579
17 | 2700894.4932 | 1239397.2884 | 2700887.5983 | 1239388.5979 | 2700876.2384 | 1239372.4593 | 2700867.9243 | 1239360.9316 | 2700860.3345 | 1239350.8394 | 2700854.1902 | 1239343.3849 | 2700847.4556 | 1239335.9427 | 2700826.6773 | 1239314.9183 | 2700820.4582 | 1239308.2966 | 2700815.4079 | 1239302.3396 | 2700813.361 | 1239299.6783
18 | 2700894.4932 | 1239397.2884 | 2700898.2046 | 1239392.5589 | 2700899.631 | 1239390.5261 | 2700900.9572 | 1239388.1579 | 2700909.9842 | 1239368.4408
19 | 2700890.6479 | 1238974.7686 | 2700884.4246 | 1238976.3863 | 2700878.3548 | 1238978.318 | 2700871.3828 | 1238980.8126 | 2700864.2066 | 1238983.7485 | 2700857.2749 | 1238986.9888 | 2700848.0433 | 1238992.0136 | 2700838.7783 | 1238997.6717 | 2700826.4888 | 1239005.9137 | 2700816.9518 | 1239013.3352 | 2700801.4123 | 1239026.7483 | 2700788.1749 | 1239040.4784
20 | 2700788.1749 | 1239040.4784 | 2700781.8431 | 1239032.4538 | 2700778.7341 | 1239027.9865 | 2700761.6113 | 1238999.2186 | 2700754.6327 | 1238988.2919 | 2700754.3562 | 1238987.8166
21 | 2700890.6479 | 1238974.7686 | 2700901.7131 | 1239004.279
22 | 2700890.6479 | 1238974.7686 | 2700896.9051 | 1238973.296
23 | 2700752.2336 | 1238984.1648 | 2700752.2732 | 1238984.2376 | 2700754.3562 | 1238987.8166
24 | 2700909.9842 | 1239368.4408 | 2700952.2849 | 1239270.6521 | 2700961.5313 | 1239257.8452
25 | 2700961.5313 | 1239257.8452 | 2700969.315 | 1239247.0643
26 | 2700752.2336 | 1238984.1648 | 2700750.0577 | 1238980.1636 | 2700747.7144 | 1238975.1534 | 2700747.0889 | 1238973.6469
27 | 2700743.3801 | 1238880.2078 | 2700737.9977 | 1238879.9719
28 | 2700737.9977 | 1238879.9719 | 2700738.676 | 1238881.9071 | 2700739.1028 | 1238883.9492 | 2700739.3969 | 1238886.2337 | 2700740.1064 | 1238895.4858
29 | 2700733.7788 | 1238872.6948 | 2700736.2029 | 1238876.5166 | 2700737.1279 | 1238878.178 | 2700737.9977 | 1238879.9719
30 | 2700455.9984 | 1239168.6138 | 2700461.6834 | 1239158.555
31 | 2700455.9984 | 1239168.6138 | 2700446.2539 | 1239185.4406
32 | 2700561.9685 | 1239268.9169 | 2700533.2157 | 1239234.5039 | 2700505.8114 | 1239200.8478 | 2700497.6704 | 1239192.437 | 2700494.1812 | 1239189.4201 | 2700490.7041 | 1239187.0261 | 2700486.5401 | 1239184.5426 | 2700455.9984 | 1239168.6138
33 | 2700973.4237 | 1239241.3734 | 2700969.315 | 1239247.0643
34 | 2700684.8175 | 1238792.8484 | 2700707.2877 | 1238779.8417
35 | 2700675.5 | 1238808.2799 | 2700674.0063 | 1238799.1143 | 2700684.8175 | 1238792.8484
36 | 2700787.2275 | 1238819.7847 | 2700790.8455 | 1238820.4457 | 2700794.0642 | 1238821.1341 | 2700797.0009 | 1238821.9402 | 2700799.6696 | 1238822.9418 | 2700799.6696 | 1238822.9418
37 | 2700787.2275 | 1238819.7847 | 2700773.1296 | 1238817.2092 | 2700756.694 | 1238814.5393
38 | 2700799.6696 | 1238822.9418 | 2700802.5302 | 1238824.2246 | 2700805.1663 | 1238825.8039 | 2700808.0243 | 1238828.132 | 2700809.9746 | 1238830.4446 | 2700811.732 | 1238832.9875 | 2700814.5376 | 1238838.3948 | 2700816.5545 | 1238842.1318 | 2700818.1566 | 1238844.4608 | 2700820.0798 | 1238846.5951
39 | 2700756.694 | 1238814.5393 | 2700755.7774 | 1238814.3904 | 2700750.6225 | 1238813.6691 | 2700747.9297 | 1238813.3925
40 | 2700835.4588 | 1238859.9769 | 2700833.2576 | 1238858.2165 | 2700830.2515 | 1238855.708 | 2700827.2835 | 1238853.1779 | 2700824.7266 | 1238850.9439 | 2700822.4917 | 1238848.9044 | 2700820.0798 | 1238846.5951 | 2700820.0798 | 1238846.5951
41 | 2700731.6648 | 1238812.7246 | 2700738.9266 | 1238812.7811 | 2700745.4342 | 1238813.1362 | 2700747.9297 | 1238813.3925
42 | 2700731.6648 | 1238812.7246 | 2700721.079 | 1238813.2899
43 | 2700731.6648 | 1238812.7246 | 2700732.0646 | 1238808.3391 | 2700732.5282 | 1238803.3099 | 2700732.5944 | 1238802.5326 | 2700733.1041 | 1238796.9623
44 | 2700740.544 | 1238907.2351 | 2700740.5966 | 1238906.0246 | 2700740.5614 | 1238902.7549 | 2700740.3941 | 1238899.2383 | 2700740.2928 | 1238897.9175
45 | 2700740.544 | 1238907.2351 | 2700740.4725 | 1238908.8802 | 2700740.3986 | 1238910.0841
46 | 2700740.1064 | 1238895.4858 | 2700740.2928 | 1238897.9175
47 | 2700657.3769 | 1238849.4571 | 2700658.182 | 1238850.4364
48 | 2700657.6923 | 1238805.0978 | 2700652.0195 | 1238842.9415 | 2700657.3769 | 1238849.4571
49 | 2700657.6923 | 1238805.0978 | 2700645.8887 | 1238803.0411
50 | 2700657.6923 | 1238805.0978 | 2700675.5 | 1238808.2799
51 | 2700621.2458 | 1238799.2785 | 2700623.0341 | 1238799.3951 | 2700629.9794 | 1238800.269 | 2700645.8887 | 1238803.0411
52 | 2700675.5 | 1238808.2799 | 2700687.2778 | 1238810.2375
53 | 2700687.2778 | 1238810.2375 | 2700697.7774 | 1238811.9826 | 2700704.9219 | 1238812.7043 | 2700707.9133 | 1238812.937
54 | 2700733.7788 | 1238872.6948 | 2700732.9495 | 1238876.0944 | 2700731.5754 | 1238879.0511 | 2700729.5618 | 1238881.7968 | 2700726.8124 | 1238884.6635 | 2700726.2522 | 1238885.1736
55 | 2700721.079 | 1238813.2899 | 2700721.398 | 1238819.4555 | 2700721.9165 | 1238826.3473 | 2700722.674 | 1238832.9763 | 2700723.679 | 1238838.8423 | 2700724.9271 | 1238844.6456 | 2700726.108 | 1238849.0579 | 2700727.2373 | 1238852.9466 | 2700733.2224 | 1238868.4822 | 2700733.6786 | 1238870.5804 | 2700733.7788 | 1238872.6948
56 | 2700721.079 | 1238813.2899 | 2700714.4449 | 1238813.2672
57 | 2700714.4449 | 1238813.2672 | 2700712.0541 | 1238813.259 | 2700707.9133 | 1238812.937
58 | 2700653.8988 | 1239198.6544 | 2700650.1579 | 1239202.6086
59 | 2700561.9685 | 1239268.9169 | 2700597.7605 | 1239247.2956 | 2700606.2406 | 1239241.9352 | 2700613.1231 | 1239237.1148 | 2700620.0263 | 1239231.9612 | 2700626.1436 | 1239226.7609 | 2700633.0547 | 1239220.2508 | 2700643.0069 | 1239210.1674 | 2700650.1579 | 1239202.6086
60 | 2700446.2539 | 1239185.4406 | 2700445.9706 | 1239185.9297

## bus_geodata
| x | y | coords
0 | 2700666.122 | 1238638.3658
1 | 2700662.9091 | 1238646.5216
2 | 2700670.7384 | 1238628.2185
3 | 2700672.8299 | 1238623.7489
4 | 2700673.5887 | 1238622.1604
5 | 2700742.5052 | 1238961.6981
6 | 2700743.5998 | 1238964.6348
7 | 2700741.9845 | 1238960.3012
8 | 2700746.6667 | 1238972.63
9 | 2700738.1055 | 1238947.7048
10 | 2700746.9662 | 1238973.3513
11 | 2700795.4748 | 1239172.6511
12 | 2700748.6184 | 1239092.5579
13 | 2700813.361 | 1239299.6783
14 | 2700894.4932 | 1239397.2884
15 | 2700788.1749 | 1239040.4784
16 | 2700890.6479 | 1238974.7686
17 | 2700754.3562 | 1238987.8166
18 | 2700909.9842 | 1239368.4408
19 | 2700961.5313 | 1239257.8452
20 | 2700896.9051 | 1238973.296
21 | 2700901.7131 | 1239004.279
22 | 2700688.7796 | 1238601.2098
23 | 2700752.2336 | 1238984.1648
24 | 2700747.0889 | 1238973.6469
25 | 2700743.3801 | 1238880.2078
26 | 2700737.9977 | 1238879.9719
27 | 2700461.6834 | 1239158.555
28 | 2700455.9984 | 1239168.6138
29 | 2700969.315 | 1239247.0643
30 | 2700973.4237 | 1239241.3734
31 | 2700707.2877 | 1238779.8417
32 | 2700684.8175 | 1238792.8484
33 | 2700787.2275 | 1238819.7847
34 | 2700799.6696 | 1238822.9418
35 | 2700756.694 | 1238814.5393
36 | 2700820.0798 | 1238846.5951
37 | 2700747.9297 | 1238813.3925
38 | 2700835.4588 | 1238859.9769
39 | 2700731.6648 | 1238812.7246
40 | 2700740.544 | 1238907.2351
41 | 2700740.2928 | 1238897.9175
42 | 2700740.3986 | 1238910.0841
43 | 2700740.1064 | 1238895.4858
44 | 2700657.3769 | 1238849.4571
45 | 2700658.182 | 1238850.4364
46 | 2700657.6923 | 1238805.0978
47 | 2700645.8887 | 1238803.0411
48 | 2700675.5 | 1238808.2799
49 | 2700621.2458 | 1238799.2785
50 | 2700687.2778 | 1238810.2375
51 | 2700726.2522 | 1238885.1736
52 | 2700733.7788 | 1238872.6948
53 | 2700721.079 | 1238813.2899
54 | 2700714.4449 | 1238813.2672
55 | 2700733.1041 | 1238796.9622
56 | 2700707.9133 | 1238812.937
57 | 2700650.1579 | 1239202.6086
58 | 2700653.8988 | 1239198.6544
59 | 2700561.9685 | 1239268.9169
60 | 2700446.2539 | 1239185.4406
61 | 2700445.9706 | 1239185.9297
62 | 2700721.079 | 1238813.2899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99513 | -0.093474 | 0.0034015 | 0.00085248
1 | 0.99519 | -0.092418 | 0 | 0
2 | 0.9951 | -0.09415 | 0.00078158 | 0.00019588
3 | 0.99508 | -0.094381 | 0.0014057 | 0.00035229
4 | 0.99508 | -0.09442 | 0.00078178 | 0.00019593
5 | 0.9956 | -0.084643 | 0.00056883 | 0.00014256
6 | 0.99556 | -0.085519 | 0.0012877 | 0.00032272
7 | 0.99563 | -0.084211 | 0.00082475 | 0.0002067
8 | 0.99545 | -0.08772 | 0.00044739 | 0.00011213
9 | 0.99583 | -0.080201 | 0.00083664 | 0.00020968
10 | 0.99544 | -0.087915 | 0.00045488 | 0.000114
11 | 0.99437 | -0.10865 | 4.7828e-05 | 1.1987e-05
12 | 0.99447 | -0.10658 | 0 | 0
13 | 0.99421 | -0.11176 | 0.00080296 | 0.00020124
14 | 0.99416 | -0.11267 | 0 | 0
15 | 0.99463 | -0.10348 | 0 | 0
16 | 0.99371 | -0.12135 | 0 | 0
17 | 0.99525 | -0.091432 | 0.00044946 | 0.00011265
18 | 0.99415 | -0.11291 | 0 | 0
19 | 0.99411 | -0.11377 | 7.818e-05 | 1.9594e-05
20 | 0.99368 | -0.12188 | 0.0046497 | 0.0011653
21 | 0.99361 | -0.12334 | 0.0035726 | 0.00089538
22 | 0.99507 | -0.094636 | 0.00047305 | 0.00011856
23 | 0.9953 | -0.090587 | 0.0012176 | 0.00030517
24 | 0.99543 | -0.087992 | 0.0011188 | 0.00028039
25 | 0.99702 | -0.057323 | 0.005363 | 0.0013441
26 | 0.99704 | -0.056818 | 0 | 0
27 | 0.994 | -0.11578 | 0.00018939 | 4.7464e-05
28 | 0.994 | -0.11574 | 0 | 0
29 | 0.9941 | -0.11384 | 9.7014e-05 | 2.4314e-05
30 | 0.9941 | -0.11387 | 0.00022224 | 5.5698e-05
31 | 0.99601 | -0.076508 | 0.0047594 | 0.0011928
32 | 0.99612 | -0.074341 | 0 | 0
33 | 0.99774 | -0.043513 | 0.0037768 | 0.00094655
34 | 0.99754 | -0.047355 | 0.0051917 | 0.0013012
35 | 0.99832 | -0.032222 | 0.0030468 | 0.00076361
36 | 0.99719 | -0.054013 | 0.0046641 | 0.0011689
37 | 0.99851 | -0.028531 | 0.0029982 | 0.00075142
38 | 0.99706 | -0.056585 | 0.0071926 | 0.0018026
39 | 0.99891 | -0.020882 | 0 | 0
40 | 0.99651 | -0.067214 | 0.00067877 | 0.00017012
41 | 0.99667 | -0.064061 | 0.0022179 | 0.00055586
42 | 0.99646 | -0.068145 | 0.00045725 | 0.0001146
43 | 0.99672 | -0.063142 | 0.0014519 | 0.00036388
44 | 0.99158 | -0.16201 | 0.0047249 | 0.0011842
45 | 0.9915 | -0.16356 | 0.068712 | 0.017221
46 | 0.99471 | -0.10141 | 0 | 0
47 | 0.99452 | -0.10513 | 0.004185 | 0.0010489
48 | 0.99622 | -0.07252 | 0 | 0
49 | 0.99422 | -0.11103 | 0.013428 | 0.0033654
50 | 0.99734 | -0.051017 | 0.037517 | 0.0094025
51 | 0.99717 | -0.054319 | 0.0064169 | 0.0016082
52 | 0.99726 | -0.052643 | 0 | 0
53 | 0.99919 | -0.015495 | 0 | 0
54 | 0.99958 | -0.0080956 | 0.0070362 | 0.0017634
55 | 0.99888 | -0.021522 | 0.0023144 | 0.00058004
56 | 1 | 0 | -0.21372 | -0.053519
57 | 0.99428 | -0.11027 | 0.00021619 | 5.4183e-05
58 | 0.99429 | -0.11014 | 0 | 0
59 | 0.99416 | -0.11262 | 0 | 0
60 | 0.99399 | -0.11609 | 0.00042464 | 0.00010643
61 | 0.99399 | -0.11609 | 0.00057875 | 0.00014505
62 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0068437 | -0.0017147 | 0.006844 | 0.0017148 | 3.4446e-07 | 1.0649e-07 | 0.010233 | 0.010233 | 0.010233 | 0.99513 | -0.093474 | 0.99519 | -0.092418 | 2.8113
1 | 0.0034422 | 0.00086219 | -0.0034421 | -0.00086226 | 1.1075e-07 | -7.395e-08 | 0.005147 | 0.005147 | 0.005147 | 0.99513 | -0.093474 | 0.9951 | -0.09415 | 1.414
2 | -0.006844 | -0.0017148 | 0.0068505 | 0.0017168 | 6.4897e-06 | 2.0037e-06 | 0.010233 | 0.010232 | 0.010233 | 0.99519 | -0.092418 | 0.99622 | -0.07252 | 2.8113
3 | 0.0026605 | 0.00066638 | -0.0026605 | -0.00066643 | 2.9289e-08 | -4.5364e-08 | 0.0039783 | 0.0039783 | 0.0039783 | 0.9951 | -0.09415 | 0.99508 | -0.094381 | 1.0929
4 | 0.0012548 | 0.00031414 | -0.0012548 | -0.00031416 | 2.324e-09 | -2.1381e-08 | 0.0018763 | 0.0018763 | 0.0018763 | 0.99508 | -0.094381 | 0.99508 | -0.09442 | 0.51548
5 | 0.00047305 | 0.00011822 | -0.00047305 | -0.00011856 | 4.868e-09 | -3.3393e-07 | 0.00070727 | 0.00070739 | 0.00070739 | 0.99508 | -0.09442 | 0.99507 | -0.094636 | 0.19434
6 | 0.015875 | 0.0039693 | -0.015874 | -0.0039689 | 6.6141e-07 | 3.8255e-07 | 0.023723 | 0.023723 | 0.023723 | 0.9956 | -0.084643 | 0.99556 | -0.085519 | 6.5172
7 | -0.016443 | -0.0041118 | 0.016444 | 0.004112 | 3.3756e-07 | 1.9665e-07 | 0.024573 | 0.024573 | 0.024573 | 0.9956 | -0.084643 | 0.99563 | -0.084211 | 6.7508
8 | 0.014586 | 0.0036462 | -0.014585 | -0.0036453 | 1.526e-06 | 8.6532e-07 | 0.021798 | 0.021798 | 0.021798 | 0.99556 | -0.085519 | 0.99545 | -0.08772 | 5.9885
9 | -0.017269 | -0.0043187 | 0.017272 | 0.0043207 | 3.2944e-06 | 1.9368e-06 | 0.025806 | 0.025805 | 0.025806 | 0.99563 | -0.084211 | 0.99583 | -0.080201 | 7.0894
10 | 0.014137 | 0.0035332 | -0.014137 | -0.0035331 | 1.3076e-07 | 7.3534e-08 | 0.021129 | 0.021129 | 0.021129 | 0.99545 | -0.08772 | 0.99544 | -0.087915 | 5.8048
11 | -0.018108 | -0.0045304 | 0.018119 | 0.0045365 | 1.0392e-05 | 6.1582e-06 | 0.027056 | 0.027055 | 0.027056 | 0.99583 | -0.080201 | 0.99646 | -0.068145 | 7.4329
12 | 0.013682 | 0.0034191 | -0.013682 | -0.0034191 | 5.0187e-08 | 2.7959e-08 | 0.020449 | 0.020449 | 0.020449 | 0.99544 | -0.087915 | 0.99543 | -0.087992 | 5.618
13 | -0.0012484 | -0.00030716 | 0.0012486 | 0.00030603 | 1.2117e-07 | -1.1264e-06 | 0.0018662 | 0.0018658 | 0.0018662 | 0.99437 | -0.10865 | 0.99447 | -0.10658 | 0.51269
14 | 0.0012006 | 0.00029517 | -0.0012004 | -0.00029695 | 1.7608e-07 | -1.7775e-06 | 0.0017946 | 0.0017953 | 0.0017953 | 0.99437 | -0.10865 | 0.99421 | -0.11176 | 0.49321
15 | -0.0026581 | -0.00065384 | 0.0026585 | 0.00065324 | 3.8682e-07 | -6.0053e-07 | 0.0039729 | 0.0039727 | 0.0039729 | 0.99447 | -0.10658 | 0.99463 | -0.10348 | 1.0915
16 | 0.0014095 | 0.00034781 | -0.0014093 | -0.0003495 | 2.3667e-07 | -1.6919e-06 | 0.0021072 | 0.0021078 | 0.0021078 | 0.99447 | -0.10658 | 0.99429 | -0.11014 | 0.57907
17 | 0.00039747 | 9.5705e-05 | -0.00039745 | -9.7344e-05 | 1.6817e-08 | -1.6384e-06 | 0.00059353 | 0.0005941 | 0.0005941 | 0.99421 | -0.11176 | 0.99416 | -0.11267 | 0.16321
18 | 0.00039745 | 9.7344e-05 | -0.00039745 | -9.7767e-05 | 4.3527e-09 | -4.2353e-07 | 0.0005941 | 0.00059424 | 0.00059424 | 0.99416 | -0.11267 | 0.99415 | -0.11291 | 0.16325
19 | 0.0082297 | 0.0020634 | -0.0082227 | -0.0020605 | 7.0048e-06 | 2.8854e-06 | 0.012312 | 0.012313 | 0.012313 | 0.99463 | -0.10348 | 0.99371 | -0.12135 | 3.3827
20 | -0.010888 | -0.0027166 | 0.010894 | 0.0027198 | 6.2312e-06 | 3.1742e-06 | 0.016285 | 0.016285 | 0.016285 | 0.99463 | -0.10348 | 0.99525 | -0.091432 | 4.4739
21 | 0.0035729 | 0.00089519 | -0.0035726 | -0.00089538 | 3.3822e-07 | -1.9168e-07 | 0.0053502 | 0.0053503 | 0.0053503 | 0.99371 | -0.12135 | 0.99361 | -0.12334 | 1.4699
22 | 0.0046498 | 0.0011653 | -0.0046497 | -0.0011653 | 1.1686e-07 | -8.4794e-09 | 0.0069628 | 0.0069628 | 0.0069628 | 0.99371 | -0.12135 | 0.99368 | -0.12188 | 1.9129
23 | -0.011344 | -0.0028324 | 0.011344 | 0.0028327 | 4.5543e-07 | 2.3659e-07 | 0.016957 | 0.016957 | 0.016957 | 0.99525 | -0.091432 | 0.9953 | -0.090587 | 4.6584
24 | 0.00039745 | 9.7767e-05 | -0.00039743 | -9.9343e-05 | 1.6216e-08 | -1.5759e-06 | 0.00059424 | 0.0005948 | 0.0005948 | 0.99415 | -0.11291 | 0.99411 | -0.11377 | 0.16341
25 | 0.00031925 | 7.9749e-05 | -0.00031925 | -7.9921e-05 | 1.1384e-09 | -1.7167e-07 | 0.00047778 | 0.00047784 | 0.00047784 | 0.99411 | -0.11377 | 0.9941 | -0.11384 | 0.13127
26 | -0.012562 | -0.0031378 | 0.012564 | 0.0031387 | 1.5492e-06 | 8.3918e-07 | 0.018777 | 0.018777 | 0.018777 | 0.9953 | -0.090587 | 0.99543 | -0.087992 | 5.1585
27 | -0.005363 | -0.0013441 | 0.0053631 | 0.0013441 | 1.2906e-07 | 1.2538e-08 | 0.0080041 | 0.008004 | 0.0080041 | 0.99702 | -0.057323 | 0.99704 | -0.056818 | 2.1989
28 | 0.022936 | 0.005748 | -0.022929 | -0.0057438 | 6.9071e-06 | 4.2156e-06 | 0.034231 | 0.034231 | 0.034231 | 0.99704 | -0.056818 | 0.99672 | -0.063142 | 9.404
29 | -0.028299 | -0.0070921 | 0.028305 | 0.0070956 | 5.6289e-06 | 3.4927e-06 | 0.042235 | 0.042235 | 0.042235 | 0.99704 | -0.056818 | 0.99726 | -0.052643 | 11.6029
30 | -0.00018939 | -4.7464e-05 | 0.00018939 | 4.7315e-05 | 3.4819e-10 | -1.4955e-07 | 0.00028351 | 0.00028346 | 0.00028351 | 0.994 | -0.11578 | 0.994 | -0.11574 | 0.077887
31 | 0.0010034 | 0.00025122 | -0.0010034 | -0.00025147 | 1.6451e-08 | -2.4152e-07 | 0.001502 | 0.0015021 | 0.0015021 | 0.994 | -0.11574 | 0.99399 | -0.11609 | 0.41266
32 | -0.0011928 | -0.00029854 | 0.001193 | 0.00029674 | 1.7669e-07 | -1.8038e-06 | 0.0017855 | 0.0017848 | 0.0017855 | 0.994 | -0.11574 | 0.99416 | -0.11262 | 0.49051
33 | 0.00022224 | 5.5607e-05 | -0.00022224 | -5.5698e-05 | 2.9123e-10 | -9.0817e-08 | 0.00033262 | 0.00033265 | 0.00033265 | 0.9941 | -0.11384 | 0.9941 | -0.11387 | 0.091389
34 | -0.0047594 | -0.0011928 | 0.0047599 | 0.0011928 | 4.912e-07 | -2.2856e-08 | 0.0071105 | 0.0071104 | 0.0071105 | 0.99601 | -0.076508 | 0.99612 | -0.074341 | 1.9534
35 | -0.0047599 | -0.0011928 | 0.0047604 | 0.0011928 | 4.1297e-07 | -1.9283e-08 | 0.0071104 | 0.0071103 | 0.0071104 | 0.99612 | -0.074341 | 0.99622 | -0.07252 | 1.9534
36 | 0.017056 | 0.0042769 | -0.017053 | -0.004275 | 3.1219e-06 | 1.83e-06 | 0.025438 | 0.025438 | 0.025438 | 0.99774 | -0.043513 | 0.99754 | -0.047355 | 6.9886
37 | -0.020833 | -0.0052234 | 0.020844 | 0.0052302 | 1.1216e-05 | 6.7736e-06 | 0.031071 | 0.031071 | 0.031071 | 0.99774 | -0.043513 | 0.99832 | -0.032222 | 8.536
38 | 0.011861 | 0.0029739 | -0.011858 | -0.0029719 | 3.7626e-06 | 1.9898e-06 | 0.017694 | 0.017694 | 0.017694 | 0.99754 | -0.047355 | 0.99719 | -0.054013 | 4.861
39 | -0.023891 | -0.0059938 | 0.023895 | 0.0059964 | 4.2045e-06 | 2.5753e-06 | 0.035612 | 0.035612 | 0.035612 | 0.99832 | -0.032222 | 0.99851 | -0.028531 | 9.7836
40 | 0.0071935 | 0.0018029 | -0.0071926 | -0.0018026 | 8.812e-07 | 2.9795e-07 | 0.010734 | 0.010734 | 0.010734 | 0.99719 | -0.054013 | 0.99706 | -0.056585 | 2.949
41 | -0.026893 | -0.0067478 | 0.026903 | 0.0067539 | 9.8119e-06 | 6.0665e-06 | 0.04008 | 0.04008 | 0.04008 | 0.99851 | -0.028531 | 0.99891 | -0.020882 | 11.011
42 | -0.029218 | -0.0073337 | 0.029225 | 0.0073384 | 7.5099e-06 | 4.668e-06 | 0.043528 | 0.043528 | 0.043528 | 0.99891 | -0.020882 | 0.99919 | -0.015495 | 11.9581
43 | 0.0023145 | 0.00057988 | -0.0023144 | -0.00058004 | 7.0551e-08 | -1.6204e-07 | 0.0034476 | 0.0034477 | 0.0034477 | 0.99891 | -0.020882 | 0.99888 | -0.021522 | 0.94717
44 | -0.019256 | -0.0048217 | 0.019259 | 0.0048234 | 2.8913e-06 | 1.7289e-06 | 0.028752 | 0.028752 | 0.028752 | 0.99651 | -0.067214 | 0.99667 | -0.064061 | 7.8988
45 | 0.018577 | 0.0046516 | -0.018576 | -0.0046511 | 8.2312e-07 | 4.8963e-07 | 0.027738 | 0.027738 | 0.027738 | 0.99651 | -0.067214 | 0.99646 | -0.068145 | 7.6204
46 | -0.021477 | -0.0053793 | 0.021477 | 0.0053799 | 9.4019e-07 | 5.6994e-07 | 0.032063 | 0.032063 | 0.032063 | 0.99667 | -0.064061 | 0.99672 | -0.063142 | 8.8085
47 | 0.068717 | 0.017224 | -0.068712 | -0.017221 | 5.0556e-06 | 3.2192e-06 | 0.10312 | 0.10312 | 0.10312 | 0.99158 | -0.16201 | 0.9915 | -0.16356 | 28.33
48 | -0.073442 | -0.018408 | 0.073655 | 0.018544 | 0.00021273 | 0.00013554 | 0.11021 | 0.11021 | 0.11021 | 0.99158 | -0.16201 | 0.99471 | -0.10141 | 30.2779
49 | 0.01762 | 0.0044181 | -0.017617 | -0.0044163 | 3.1217e-06 | 1.8424e-06 | 0.026359 | 0.026359 | 0.026359 | 0.99471 | -0.10141 | 0.99452 | -0.10513 | 7.2414
50 | -0.091274 | -0.022962 | 0.091401 | 0.023042 | 0.00012616 | 8.051e-05 | 0.13657 | 0.13657 | 0.13657 | 0.99471 | -0.10141 | 0.99622 | -0.07252 | 37.5193
51 | 0.013432 | 0.0033675 | -0.013428 | -0.0033654 | 3.7776e-06 | 2.0941e-06 | 0.020097 | 0.020097 | 0.020097 | 0.99452 | -0.10513 | 0.99422 | -0.11103 | 5.5212
52 | -0.10301 | -0.025952 | 0.10312 | 0.02602 | 0.00010606 | 6.7724e-05 | 0.15391 | 0.15391 | 0.15391 | 0.99622 | -0.07252 | 0.99734 | -0.051017 | 42.2837
53 | -0.14063 | -0.035422 | 0.14098 | 0.035642 | 0.00034402 | 0.0002199 | 0.20989 | 0.20989 | 0.20989 | 0.99734 | -0.051017 | 1 | 0 | 57.6612
54 | -0.0064169 | -0.0016082 | 0.0064174 | 0.0016084 | 5.1212e-07 | 1.3344e-07 | 0.0095755 | 0.0095754 | 0.0095755 | 0.99717 | -0.054319 | 0.99726 | -0.052643 | 2.6306
55 | -0.034722 | -0.0087039 | 0.034784 | 0.0087425 | 6.1576e-05 | 3.8609e-05 | 0.05181 | 0.05181 | 0.05181 | 0.99726 | -0.052643 | 0.99919 | -0.015495 | 14.2335
56 | -0.064009 | -0.016081 | 0.064032 | 0.016095 | 2.2612e-05 | 1.4385e-05 | 0.095337 | 0.095337 | 0.095337 | 0.99919 | -0.015495 | 0.99958 | -0.0080956 | 26.1916
57 | -0.071068 | -0.017859 | 0.071095 | 0.017876 | 2.7476e-05 | 1.7499e-05 | 0.10581 | 0.10581 | 0.10581 | 0.99958 | -0.0080956 | 1 | 0 | 29.0691
58 | -0.0014093 | -0.00034956 | 0.0014093 | 0.0003495 | 9.0692e-09 | -6.4796e-08 | 0.0021078 | 0.0021078 | 0.0021078 | 0.99428 | -0.11027 | 0.99429 | -0.11014 | 0.57907
59 | 0.0011931 | 0.00029538 | -0.001193 | -0.00029674 | 1.3251e-07 | -1.3542e-06 | 0.0017843 | 0.0017848 | 0.0017848 | 0.99428 | -0.11027 | 0.99416 | -0.11262 | 0.49033
60 | 0.00057875 | 0.00014504 | -0.00057875 | -0.00014505 | 1.5917e-10 | -7.2244e-09 | 0.00086639 | 0.0008664 | 0.0008664 | 0.99399 | -0.11609 | 0.99399 | -0.11609 | 0.23802

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.21904 | 0.05485

## res_load
| p_mw | q_mvar
0 | 0.0034015 | 0.00085248
1 | 0.00078158 | 0.00019588
2 | 0.0014057 | 0.00035229
3 | 0.00078178 | 0.00019593
4 | 0.00056883 | 0.00014256
5 | 0.0012877 | 0.00032272
6 | 0.00082475 | 0.0002067
7 | 0.00044739 | 0.00011213
8 | 0.00083664 | 0.00020968
9 | 0.00045488 | 0.000114
10 | 4.7828e-05 | 1.1987e-05
11 | 0.00080296 | 0.00020124
12 | 0.00044946 | 0.00011265
13 | 7.818e-05 | 1.9594e-05
14 | 0.0046497 | 0.0011653
15 | 0.0035726 | 0.00089538
16 | 0.00047305 | 0.00011856
17 | 0.0012176 | 0.00030517
18 | 0.0011188 | 0.00028039
19 | 0.005363 | 0.0013441
20 | 0.00018939 | 4.7464e-05
21 | 9.7014e-05 | 2.4314e-05
22 | 0.00022224 | 5.5698e-05
23 | 0.0047594 | 0.0011928
24 | 0.0037768 | 0.00094655
25 | 0.0051917 | 0.0013012
26 | 0.0030468 | 0.00076361
27 | 0.0046641 | 0.0011689
28 | 0.0029982 | 0.00075142
29 | 0.0071926 | 0.0018026
30 | 0.00067877 | 0.00017012
31 | 0.0022179 | 0.00055586
32 | 0.00045725 | 0.0001146
33 | 0.0014519 | 0.00036388
34 | 0.0047249 | 0.0011842
35 | 0.068712 | 0.017221
36 | 0.004185 | 0.0010489
37 | 0.013428 | 0.0033654
38 | 0.037517 | 0.0094025
39 | 0.0064169 | 0.0016082
40 | 0.0070362 | 0.0017634
41 | 0.0023144 | 0.00058004
42 | 0.0053119 | 0.0013313
43 | 0.00021619 | 5.4183e-05
44 | 0.00042464 | 0.00010643
45 | 0.00057875 | 0.00014505

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1