## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_115-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_115-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_115-15_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_115-15_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_115-15_0_2_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_115-15_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_115-15_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_115-15_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_115-15_0_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_115-15_0_2_node_286 | 0.4 | n |  | TRUE
11 | bus_LV_115-15_0_2_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_115-15_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_115-15_0_2_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_115-15_0_2_node_284 | 0.4 | n |  | TRUE
15 | bus_LV_115-15_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_115-15_0_2_node_265 | 0.4 | n |  | TRUE
17 | bus_LV_115-15_0_2_node_264 | 0.4 | n |  | TRUE
18 | bus_LV_115-15_0_2_node_295 | 0.4 | n |  | TRUE
19 | bus_LV_115-15_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_115-15_0_2_node_202 | 0.4 | n |  | TRUE
21 | bus_LV_115-15_0_2_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_115-15_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_115-15_0_2_node_244 | 0.4 | n |  | TRUE
24 | bus_LV_115-15_0_2_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_115-15_0_2_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_115-15_0_2_node_203 | 0.4 | n |  | TRUE
27 | bus_LV_115-15_0_2_node_278 | 0.4 | n |  | TRUE
28 | bus_LV_115-15_0_2_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_115-15_0_2_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_115-15_0_2_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_115-15_0_2_node_155 | 0.4 | n |  | TRUE
32 | bus_LV_115-15_0_2_node_165 | 0.4 | n |  | TRUE
33 | bus_LV_115-15_0_2_node_166 | 0.4 | n |  | TRUE
34 | bus_LV_115-15_0_2_node_213 | 0.4 | n |  | TRUE
35 | bus_LV_115-15_0_2_node_300 | 0.4 | n |  | TRUE
36 | bus_LV_115-15_0_2_node_195 | 0.4 | n |  | TRUE
37 | bus_LV_115-15_0_2_node_196 | 0.4 | n |  | TRUE
38 | bus_LV_115-15_0_2_node_197 | 0.4 | n |  | TRUE
39 | bus_LV_115-15_0_2_node_198 | 0.4 | n |  | TRUE
40 | bus_LV_115-15_0_2_node_200 | 0.4 | n |  | TRUE
41 | bus_LV_115-15_0_2_node_201 | 0.4 | n |  | TRUE
42 | bus_LV_115-15_0_2_node_208 | 0.4 | n |  | TRUE
43 | bus_LV_115-15_0_2_node_206 | 0.4 | n |  | TRUE
44 | bus_LV_115-15_0_2_node_207 | 0.4 | n |  | TRUE
45 | bus_LV_115-15_0_2_node_210 | 0.4 | n |  | TRUE
46 | bus_LV_115-15_0_2_node_211 | 0.4 | n |  | TRUE
47 | bus_LV_115-15_0_2_node_215 | 0.4 | n |  | TRUE
48 | bus_LV_115-15_0_2_node_223 | 0.4 | n |  | TRUE
49 | bus_LV_115-15_0_2_node_216 | 0.4 | n |  | TRUE
50 | bus_LV_115-15_0_2_node_217 | 0.4 | n |  | TRUE
51 | bus_LV_115-15_0_2_node_218 | 0.4 | n |  | TRUE
52 | bus_LV_115-15_0_2_node_219 | 0.4 | n |  | TRUE
53 | bus_LV_115-15_0_2_node_220 | 0.4 | n |  | TRUE
54 | bus_LV_115-15_0_2_node_254 | 0.4 | n |  | TRUE
55 | bus_LV_115-15_0_2_node_221 | 0.4 | n |  | TRUE
56 | bus_LV_115-15_0_2_node_222 | 0.4 | n |  | TRUE
57 | bus_LV_115-15_0_2_node_224 | 0.4 | n |  | TRUE
58 | bus_LV_115-15_0_2_node_263 | 0.4 | n |  | TRUE
59 | bus_LV_115-15_0_2_node_225 | 0.4 | n |  | TRUE
60 | bus_LV_115-15_0_2_node_226 | 0.4 | n |  | TRUE
61 | bus_LV_115-15_0_2_node_227 | 0.4 | n |  | TRUE
62 | bus_LV_115-15_0_2_node_228 | 0.4 | n |  | TRUE
63 | bus_LV_115-15_0_2_node_230 | 0.4 | n |  | TRUE
64 | bus_LV_115-15_0_2_node_229 | 0.4 | n |  | TRUE
65 | bus_LV_115-15_0_2_node_240 | 0.4 | n |  | TRUE
66 | bus_LV_115-15_0_2_node_246 | 0.4 | n |  | TRUE
67 | bus_LV_115-15_0_2_node_231 | 0.4 | n |  | TRUE
68 | bus_LV_115-15_0_2_node_232 | 0.4 | n |  | TRUE
69 | bus_LV_115-15_0_2_node_262 | 0.4 | n |  | TRUE
70 | bus_LV_115-15_0_2_node_260 | 0.4 | n |  | TRUE
71 | bus_LV_115-15_0_2_node_290 | 0.4 | n |  | TRUE
72 | bus_LV_115-15_0_2_node_233 | 0.4 | n |  | TRUE
73 | bus_LV_115-15_0_2_node_234 | 0.4 | n |  | TRUE
74 | bus_LV_115-15_0_2_node_235 | 0.4 | n |  | TRUE
75 | bus_LV_115-15_0_2_node_236 | 0.4 | n |  | TRUE
76 | bus_LV_115-15_0_2_node_237 | 0.4 | n |  | TRUE
77 | bus_LV_115-15_0_2_node_248 | 0.4 | n |  | TRUE
78 | bus_LV_115-15_0_2_node_268 | 0.4 | n |  | TRUE
79 | bus_LV_115-15_0_2_node_238 | 0.4 | n |  | TRUE
80 | bus_LV_115-15_0_2_node_239 | 0.4 | n |  | TRUE
81 | bus_LV_115-15_0_2_node_241 | 0.4 | n |  | TRUE
82 | bus_LV_115-15_0_2_node_266 | 0.4 | n |  | TRUE
83 | bus_LV_115-15_0_2_node_267 | 0.4 | n |  | TRUE
84 | bus_LV_115-15_0_2_node_261 | 0.4 | n |  | TRUE
85 | bus_LV_115-15_0_2_node_242 | 0.4 | n |  | TRUE
86 | bus_LV_115-15_0_2_node_243 | 0.4 | n |  | TRUE
87 | bus_LV_115-15_0_2_node_247 | 0.4 | n |  | TRUE
88 | bus_LV_115-15_0_2_node_249 | 0.4 | n |  | TRUE
89 | bus_LV_115-15_0_2_node_250 | 0.4 | n |  | TRUE
90 | bus_LV_115-15_0_2_node_255 | 0.4 | n |  | TRUE
91 | bus_LV_115-15_0_2_node_288 | 0.4 | n |  | TRUE
92 | bus_LV_115-15_0_2_node_251 | 0.4 | n |  | TRUE
93 | bus_LV_115-15_0_2_node_252 | 0.4 | n |  | TRUE
94 | bus_LV_115-15_0_2_node_253 | 0.4 | n |  | TRUE
95 | bus_LV_115-15_0_2_node_272 | 0.4 | n |  | TRUE
96 | bus_LV_115-15_0_2_node_256 | 0.4 | n |  | TRUE
97 | bus_LV_115-15_0_2_node_257 | 0.4 | n |  | TRUE
98 | bus_LV_115-15_0_2_node_258 | 0.4 | n |  | TRUE
99 | bus_LV_115-15_0_2_node_259 | 0.4 | n |  | TRUE
100 | bus_LV_115-15_0_2_node_270 | 0.4 | n |  | TRUE
101 | bus_LV_115-15_0_2_node_293 | 0.4 | n |  | TRUE
102 | bus_LV_115-15_0_2_node_291 | 0.4 | n |  | TRUE
103 | bus_LV_115-15_0_2_node_296 | 0.4 | n |  | TRUE
104 | bus_LV_115-15_0_2_node_269 | 0.4 | n |  | TRUE
105 | bus_LV_115-15_0_2_node_273 | 0.4 | n |  | TRUE
106 | bus_LV_115-15_0_2_node_274 | 0.4 | n |  | TRUE
107 | bus_LV_115-15_0_2_node_275 | 0.4 | n |  | TRUE
108 | bus_LV_115-15_0_2_node_276 | 0.4 | n |  | TRUE
109 | bus_LV_115-15_0_2_node_289 | 0.4 | n |  | TRUE
110 | bus_LV_115-15_0_2_node_294 | 0.4 | n |  | TRUE
111 | bus_LV_115-15_0_2_node_277 | 0.4 | n |  | TRUE
112 | bus_LV_115-15_0_2_node_285 | 0.4 | n |  | TRUE
113 | bus_LV_115-15_0_2_node_287 | 0.4 | n |  | TRUE
114 | bus_LV_115-15_0_2_node_292 | 0.4 | n |  | TRUE
115 | bus_LV_115-15_0_2_node_297 | 0.4 | n |  | TRUE
116 | bus_LV_115-15_0_2_node_299 | 0.4 | n |  | TRUE
117 | bus_LV_115-15_0_2_node_298 | 0.4 | n |  | TRUE
118 | bus_LV_115-15_0_2_node_308 | 0.4 | n |  | TRUE
119 | bus_MV_357_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-15_0_2_load_0 | 0 | 0.0056551 | 0.0014173 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-15_0_2_load_1 | 1 | 0.0010824 | 0.00027129 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-15_0_2_load_21 | 5 | 0.0039883 | 0.00099956 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-15_0_2_load_8 | 6 | 0.0071362 | 0.0017885 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-15_0_2_load_6 | 7 | 0.0032104 | 0.00080461 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-15_0_2_load_9 | 9 | 0.0040116 | 0.0010054 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-15_0_2_load_17 | 11 | 0.003334 | 0.00083558 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-15_0_2_load_284 | 14 | 0.0058757 | 0.0014726 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-15_0_2_load_264 | 17 | 0.0052159 | 0.0013072 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-15_0_2_load_295 | 18 | 0.0075571 | 0.001894 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-15_0_2_load_20 | 21 | 0.002416 | 0.0006055 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-15_0_2_load_244 | 23 | 0.0028611 | 0.00071705 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-15_0_2_load_203 | 26 | 0.0052006 | 0.0013034 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-15_0_2_load_278 | 27 | 0.00067617 | 0.00016946 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-15_0_2_load_18 | 28 | 0.0038666 | 0.00096906 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-15_0_2_load_19 | 29 | 0.002416 | 0.0006055 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-15_0_2_load_22 | 30 | 0.0015017 | 0.00037636 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-15_0_2_load_165 | 32 | 0.010999 | 0.0027565 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-15_0_2_load_166 | 33 | 0.0010543 | 0.00026422 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-15_0_2_load_195 | 36 | 0.0071324 | 0.0017875 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-15_0_2_load_196 | 37 | 0.0027511 | 0.00068949 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-15_0_2_load_197 | 38 | 0.0023487 | 0.00058863 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-15_0_2_load_198 | 39 | 0.0010127 | 0.00025382 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-15_0_2_load_200 | 40 | 0.0004658 | 0.00011674 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-15_0_2_load_208 | 42 | 0.00089224 | 0.00022362 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-15_0_2_load_206 | 43 | 0.0032858 | 0.00082349 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-15_0_2_load_207 | 44 | 0.0046146 | 0.0011565 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-15_0_2_load_210 | 45 | 0.0062451 | 0.0015652 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-15_0_2_load_211 | 46 | 0.0068626 | 0.0017199 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-15_0_2_load_215 | 47 | 0.0023006 | 0.0005766 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-15_0_2_load_216 | 49 | 0.0026036 | 0.00065253 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-15_0_2_load_217 | 50 | 0.0012919 | 0.00032378 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-15_0_2_load_218 | 51 | 0.0018851 | 0.00047245 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-15_0_2_load_219 | 52 | 0.0013864 | 0.00034745 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-15_0_2_load_220 | 53 | 0.0014867 | 0.00037261 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-15_0_2_load_254 | 54 | 0.0017021 | 0.00042658 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-15_0_2_load_221 | 55 | 0.0024511 | 0.0006143 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-15_0_2_load_222 | 56 | 0.0035473 | 0.00088903 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-15_0_2_load_224 | 57 | 0.0012923 | 0.00032389 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-15_0_2_load_263 | 58 | 0.0014346 | 0.00035955 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-15_0_2_load_225 | 59 | 0.0020001 | 0.00050126 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-15_0_2_load_226 | 60 | 0.0022695 | 0.00056879 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-15_0_2_load_227 | 61 | 0.0019272 | 0.00048301 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-15_0_2_load_228 | 62 | 0.0016925 | 0.00042418 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-15_0_2_load_240 | 65 | 0.0017926 | 0.00044927 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-15_0_2_load_246 | 66 | 0.0028319 | 0.00070973 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_115-15_0_2_load_232 | 68 | 0.0025696 | 0.00064401 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_115-15_0_2_load_262 | 69 | 0.0032483 | 0.0008141 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_115-15_0_2_load_260 | 70 | 0.0021985 | 0.00055101 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_115-15_0_2_load_233 | 72 | 0.001237 | 0.00031001 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_115-15_0_2_load_234 | 73 | 0.001803 | 0.00045188 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_115-15_0_2_load_235 | 74 | 0.00092832 | 0.00023266 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_115-15_0_2_load_236 | 75 | 0.0018582 | 0.0004657 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_115-15_0_2_load_237 | 76 | 0.0030682 | 0.00076896 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_115-15_0_2_load_248 | 77 | 0.0039945 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_115-15_0_2_load_238 | 79 | 0.001975 | 0.00049498 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_115-15_0_2_load_239 | 80 | 0.0023295 | 0.00058383 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_115-15_0_2_load_266 | 82 | 0.0013351 | 0.00033461 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_115-15_0_2_load_267 | 83 | 0.0013949 | 0.00034959 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_115-15_0_2_load_261 | 84 | 0.0018451 | 0.00046242 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_115-15_0_2_load_242 | 85 | 0.0039974 | 0.0010018 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_115-15_0_2_load_243 | 86 | 0.0006642 | 0.00016647 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_115-15_0_2_load_247 | 87 | 0.0017928 | 0.00044932 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_115-15_0_2_load_249 | 88 | 0.0019198 | 0.00048114 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_115-15_0_2_load_288 | 91 | 0.0026091 | 0.00065391 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_115-15_0_2_load_251 | 92 | 0.0041955 | 0.0010515 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_115-15_0_2_load_252 | 93 | 0.0041949 | 0.0010513 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_115-15_0_2_load_272 | 95 | 0.0014841 | 0.00037194 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_115-15_0_2_load_256 | 96 | 0.004173 | 0.0010459 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_115-15_0_2_load_257 | 97 | 0.0011165 | 0.00027981 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_115-15_0_2_load_258 | 98 | 0.0011157 | 0.00027962 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_115-15_0_2_load_270 | 100 | 0.0037729 | 0.00094559 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_115-15_0_2_load_293 | 101 | 0.0028058 | 0.00070319 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_115-15_0_2_load_291 | 102 | 0.0013774 | 0.00034522 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_115-15_0_2_load_296 | 103 | 0.0012264 | 0.00030738 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_115-15_0_2_load_269 | 104 | 0.0048163 | 0.0012071 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_115-15_0_2_load_273 | 105 | 0.0020264 | 0.00050786 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_115-15_0_2_load_275 | 107 | 0.0018369 | 0.00046036 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_115-15_0_2_load_276 | 108 | 0.00060456 | 0.00015152 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_115-15_0_2_load_289 | 109 | 0.0011045 | 0.00027681 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_115-15_0_2_load_294 | 110 | 0.0020587 | 0.00051597 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_115-15_0_2_load_277 | 111 | 0.0015786 | 0.00039564 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_115-15_0_2_load_292 | 114 | 0.0041111 | 0.0010303 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_115-15_0_2_load_297 | 115 | 0.0022736 | 0.00056982 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_115-15_0_2_load_299 | 116 | 0.0012263 | 0.00030735 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_115-15_0_2_load_298 | 117 | 0.0012264 | 0.00030738 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_115-15_0_2_load_308 | 118 | 0.00045132 | 0.00011311 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-15_0_2_line_0 |  | 0 | 1 | 0.016099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-15_0_2_line_1 |  | 0 | 2 | 0.02058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-15_0_2_line_2 |  | 1 | 3 | 0.0085945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-15_0_2_line_3 |  | 2 | 4 | 0.011959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-15_0_2_line_4 |  | 3 | 5 | 0.0090907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-15_0_2_line_5 |  | 4 | 6 | 0.025383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-15_0_2_line_6 |  | 4 | 7 | 0.039559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-15_0_2_line_7 |  | 5 | 30 | 0.0030266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-15_0_2_line_8 |  | 6 | 10 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-15_0_2_line_9 |  | 7 | 8 | 0.022293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-15_0_2_line_10 |  | 8 | 9 | 0.026039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-15_0_2_line_11 |  | 9 | 11 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-15_0_2_line_12 |  | 10 | 112 | 0.032199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-15_0_2_line_13 |  | 11 | 28 | 0.0066828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_115-15_0_2_line_14 |  | 12 | 13 | 0.007917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-15_0_2_line_15 |  | 12 | 14 | 0.015516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-15_0_2_line_16 |  | 13 | 18 | 0.0024139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-15_0_2_line_17 |  | 14 | 112 | 0.022587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-15_0_2_line_18 |  | 15 | 16 | 0.018618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_115-15_0_2_line_19 |  | 15 | 17 | 0.021256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-15_0_2_line_20 |  | 16 | 101 | 0.020693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-15_0_2_line_21 |  | 16 | 102 | 0.020962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-15_0_2_line_22 |  | 17 | 22 | 0.011688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_115-15_0_2_line_23 |  | 19 | 20 | 0.1593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-15_0_2_line_24 |  | 19 | 21 | 0.013415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-15_0_2_line_25 |  | 20 | 42 | 0.017486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-15_0_2_line_26 |  | 20 | 25 | 0.072436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-15_0_2_line_27 |  | 20 | 41 | 0.10188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-15_0_2_line_28 |  | 21 | 29 | 0.018236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-15_0_2_line_29 |  | 22 | 23 | 0.040165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-15_0_2_line_30 |  | 23 | 86 | 0.046704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-15_0_2_line_31 |  | 24 | 25 | 0.14711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_115-15_0_2_line_32 |  | 24 | 26 | 0.045509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-15_0_2_line_33 |  | 25 | 27 | 0.017356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_115-15_0_2_line_34 |  | 27 | 111 | 0.0063278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-15_0_2_line_35 |  | 28 | 29 | 0.023603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-15_0_2_line_36 |  | 31 | 32 | 0.022183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_115-15_0_2_line_37 |  | 31 | 33 | 0.017984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_115-15_0_2_line_38 |  | 32 | 34 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_115-15_0_2_line_39 |  | 33 | 35 | 0.018086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_115-15_0_2_line_40 |  | 34 | 47 | 0.016676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_115-15_0_2_line_41 |  | 34 | 46 | 0.016788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_115-15_0_2_line_42 |  | 35 | 118 | 0.011739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_115-15_0_2_line_43 |  | 35 | 99 | 0.003949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_115-15_0_2_line_44 |  | 36 | 37 | 0.0059716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_115-15_0_2_line_45 |  | 36 | 38 | 0.013324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_115-15_0_2_line_46 |  | 37 | 39 | 0.0049145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_115-15_0_2_line_47 |  | 39 | 40 | 0.076013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_115-15_0_2_line_48 |  | 40 | 41 | 0.033983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_115-15_0_2_line_49 |  | 42 | 43 | 0.016912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-15_0_2_line_50 |  | 43 | 44 | 0.0033401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_115-15_0_2_line_51 |  | 45 | 46 | 0.0097905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-15_0_2_line_52 |  | 47 | 48 | 0.013985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_115-15_0_2_line_53 |  | 48 | 57 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_115-15_0_2_line_54 |  | 48 | 55 | 0.0084713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-15_0_2_line_55 |  | 49 | 50 | 0.0011871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_115-15_0_2_line_56 |  | 49 | 51 | 0.021849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_115-15_0_2_line_57 |  | 50 | 52 | 0.012328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-15_0_2_line_58 |  | 51 | 53 | 0.0082842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-15_0_2_line_59 |  | 52 | 54 | 0.013005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-15_0_2_line_60 |  | 54 | 90 | 0.019297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_115-15_0_2_line_61 |  | 55 | 56 | 0.019049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_115-15_0_2_line_62 |  | 57 | 58 | 0.013121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_115-15_0_2_line_63 |  | 58 | 90 | 0.014073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_115-15_0_2_line_64 |  | 59 | 60 | 0.02727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_115-15_0_2_line_65 |  | 59 | 61 | 0.0020496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_115-15_0_2_line_66 |  | 60 | 62 | 0.017337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_115-15_0_2_line_67 |  | 62 | 63 | 0.04451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_115-15_0_2_line_68 |  | 63 | 67 | 0.007781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_115-15_0_2_line_69 |  | 63 | 68 | 0.020209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_115-15_0_2_line_70 |  | 64 | 65 | 0.015776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_115-15_0_2_line_71 |  | 64 | 66 | 0.016348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_115-15_0_2_line_72 |  | 65 | 79 | 0.0015188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_115-15_0_2_line_73 |  | 66 | 87 | 0.00094314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_115-15_0_2_line_74 |  | 67 | 69 | 0.018559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_115-15_0_2_line_75 |  | 67 | 70 | 0.0089308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_115-15_0_2_line_76 |  | 68 | 71 | 0.0014634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_115-15_0_2_line_77 |  | 70 | 84 | 0.025534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_115-15_0_2_line_78 |  | 71 | 101 | 0.014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_115-15_0_2_line_79 |  | 71 | 109 | 0.021284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_115-15_0_2_line_80 |  | 72 | 73 | 0.017598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_115-15_0_2_line_81 |  | 72 | 74 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_115-15_0_2_line_82 |  | 73 | 75 | 0.007984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_115-15_0_2_line_83 |  | 74 | 76 | 0.013944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_115-15_0_2_line_84 |  | 75 | 77 | 0.00071204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_115-15_0_2_line_85 |  | 76 | 78 | 0.020761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_115-15_0_2_line_86 |  | 77 | 88 | 0.028118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_115-15_0_2_line_87 |  | 78 | 94 | 0.017628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_115-15_0_2_line_88 |  | 79 | 80 | 0.026603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_115-15_0_2_line_89 |  | 80 | 81 | 0.018007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_115-15_0_2_line_90 |  | 81 | 82 | 0.020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_115-15_0_2_line_91 |  | 81 | 83 | 0.018489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_115-15_0_2_line_92 |  | 81 | 84 | 0.020856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_115-15_0_2_line_93 |  | 82 | 91 | 0.0076752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_115-15_0_2_line_94 |  | 83 | 103 | 0.012447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_115-15_0_2_line_95 |  | 85 | 86 | 0.050361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_115-15_0_2_line_96 |  | 88 | 89 | 0.012775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_115-15_0_2_line_97 |  | 89 | 90 | 0.02361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_115-15_0_2_line_98 |  | 89 | 91 | 0.013895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_115-15_0_2_line_99 |  | 92 | 93 | 0.0003285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_115-15_0_2_line_100 |  | 93 | 94 | 0.033655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_115-15_0_2_line_101 |  | 94 | 95 | 0.0096963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_115-15_0_2_line_102 |  | 96 | 97 | 0.00021997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_115-15_0_2_line_103 |  | 96 | 98 | 0.0063459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_115-15_0_2_line_104 |  | 97 | 99 | 0.049172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_115-15_0_2_line_105 |  | 99 | 100 | 0.031553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_115-15_0_2_line_106 |  | 100 | 104 | 0.042805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_115-15_0_2_line_107 |  | 102 | 114 | 0.042993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_115-15_0_2_line_108 |  | 103 | 115 | 0.0043876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_115-15_0_2_line_109 |  | 105 | 106 | 0.0099494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_115-15_0_2_line_110 |  | 106 | 107 | 0.01725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_115-15_0_2_line_111 |  | 106 | 108 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_115-15_0_2_line_112 |  | 107 | 109 | 0.00047586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_115-15_0_2_line_113 |  | 108 | 110 | 0.012913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_115-15_0_2_line_114 |  | 112 | 113 | 0.008065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_115-15_0_2_line_115 |  | 113 | 114 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_115-15_0_2_line_116 |  | 115 | 116 | 0.0014267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_115-15_0_2_line_117 |  | 116 | 117 | 0.0058142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-15_0_2_trafo_293 | 0.63 MVA 20/0.4 kV | 119 | 101 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2701365.5237 | 1240624.3939 | 2701354.597 | 1240612.5702
1 | 2701379.4915 | 1240639.5083 | 2701365.5237 | 1240624.3939
2 | 2701348.7639 | 1240606.2583 | 2701354.597 | 1240612.5702
3 | 2701379.4915 | 1240639.5083 | 2701388.4978 | 1240631.6117
4 | 2701348.7639 | 1240606.2583 | 2701342.5969 | 1240599.5793
5 | 2701388.4978 | 1240631.6117 | 2701405.3214 | 1240650.618
6 | 2701388.4978 | 1240631.6117 | 2701418.2277 | 1240605.5146
7 | 2701340.5437 | 1240597.3556 | 2701342.5969 | 1240599.5793
8 | 2701421.3076 | 1240668.6782 | 2701405.3214 | 1240650.618
9 | 2701434.9818 | 1240590.8078 | 2701418.2277 | 1240605.5146
10 | 2701434.9818 | 1240590.8078 | 2701416.8669 | 1240572.1027
11 | 2701416.8669 | 1240572.1027 | 2701402.668 | 1240557.4414 | 2701402.668 | 1240557.4414
12 | 2701446.4531 | 1240649.293 | 2701439.9355 | 1240651.4055 | 2701421.3076 | 1240668.6782
13 | 2701402.668 | 1240557.4414 | 2701406.8731 | 1240552.2474
14 | 2701455.3854 | 1240611.2387 | 2701447.4448 | 1240611.203
15 | 2701447.4448 | 1240611.203 | 2701447.041 | 1240626.7134
16 | 2701455.3854 | 1240611.2387 | 2701455.2967 | 1240613.651
17 | 2701446.4531 | 1240649.293 | 2701447.041 | 1240626.7134
18 | 2701499.4097 | 1240584.7154 | 2701485.4643 | 1240584.6658 | 2701480.7409 | 1240584.4627
19 | 2701480.7409 | 1240584.4627 | 2701481.6782 | 1240570.3457 | 2701480.8981 | 1240563.2803
20 | 2701499.4097 | 1240584.7154 | 2701520.1024 | 1240584.6626
21 | 2701499.4097 | 1240584.7154 | 2701498.9826 | 1240605.6734
22 | 2701479.6154 | 1240551.6628 | 2701480.8981 | 1240563.2803
23 | 2701390.122 | 1240381.2479 | 2701395.7838 | 1240389.3953 | 2701392.5487 | 1240392.8204 | 2701391.9446 | 1240396.7465 | 2701393.88 | 1240399.4482 | 2701432.4051 | 1240452.2244 | 2701441.267 | 1240465.6194 | 2701448.1371 | 1240479.6142 | 2701449.2993 | 1240488.6076 | 2701448.5523 | 1240519.9077
24 | 2701448.5523 | 1240519.9077 | 2701438.9616 | 1240519.9438 | 2701436.1179 | 1240522.5003
25 | 2701390.122 | 1240381.2479 | 2701376.2175 | 1240391.8513
26 | 2701390.122 | 1240381.2479 | 2701395.7838 | 1240389.3953 | 2701416.1442 | 1240416.3859 | 2701433.1595 | 1240439.5054
27 | 2701390.122 | 1240381.2479 | 2701374.4455 | 1240359.4302 | 2701330.5988 | 1240298.4462
28 | 2701436.1179 | 1240522.5003 | 2701422.5569 | 1240534.6919
29 | 2701479.6154 | 1240551.6628 | 2701509.25 | 1240524.5513
30 | 2701543.7092 | 1240493.0259 | 2701509.25 | 1240524.5513
31 | 2701433.1595 | 1240439.5054 | 2701438.3991 | 1240446.2445 | 2701457.0253 | 1240472.8943 | 2701464.8733 | 1240422.6344 | 2701474.2938 | 1240375.9597 | 2701475.7897 | 1240368.5352
32 | 2701475.7897 | 1240368.5352 | 2701443.3371 | 1240363.132 | 2701442.0492 | 1240360.1633 | 2701443.8248 | 1240350.9595
33 | 2701433.1595 | 1240439.5054 | 2701440.7228 | 1240433.7524 | 2701445.0327 | 1240427.1877 | 2701445.0327 | 1240427.1877
34 | 2701451.3478 | 1240427.5888 | 2701445.0327 | 1240427.1877
35 | 2701406.8731 | 1240552.2474 | 2701417.1238 | 1240539.5858 | 2701421.1796 | 1240535.93 | 2701422.5569 | 1240534.6919
36 | 2701672.3122 | 1240737.6355 | 2701658.4262 | 1240722.2192 | 2701657.3452 | 1240721.2749
37 | 2701672.3122 | 1240737.6355 | 2701684.2829 | 1240724.2139
38 | 2701647.6367 | 1240712.7939 | 2701657.3452 | 1240721.2749
39 | 2701696.7858 | 1240711.1566 | 2701689.1917 | 1240718.7101 | 2701684.2829 | 1240724.2139
40 | 2701647.6367 | 1240712.7939 | 2701635.7898 | 1240701.0579
41 | 2701647.6367 | 1240712.7939 | 2701634.6144 | 1240723.3893
42 | 2701696.7858 | 1240711.1566 | 2701704.7865 | 1240719.7471
43 | 2701699.5791 | 1240708.3579 | 2701696.7858 | 1240711.1566
44 | 2701238.4698 | 1240349.8522 | 2701242.8031 | 1240353.961
45 | 2701228.2054 | 1240341.8291 | 2701230.2949 | 1240344.8706 | 2701236.9358 | 1240348.3977 | 2701238.4698 | 1240349.8522
46 | 2701246.3693 | 1240357.3425 | 2701242.8031 | 1240353.961
47 | 2701246.3693 | 1240357.3425 | 2701248.6509 | 1240359.5059 | 2701251.1897 | 1240360.5389 | 2701256.5424 | 1240358.006 | 2701263.259 | 1240351.3377 | 2701266.177 | 1240340.7905 | 2701270.4131 | 1240334.9917 | 2701275.5263 | 1240330.0974 | 2701295.4048 | 1240318.9057 | 2701301.2198 | 1240315.5253
48 | 2701330.5988 | 1240298.4462 | 2701301.2198 | 1240315.5253
49 | 2701376.2175 | 1240391.8513 | 2701362.7694 | 1240402.1066
50 | 2701362.7694 | 1240402.1066 | 2701360.1134 | 1240404.1319
51 | 2701627.0201 | 1240729.5684 | 2701634.6144 | 1240723.3893
52 | 2701625.8546 | 1240691.2156 | 2701635.7898 | 1240701.0579
53 | 2701625.8546 | 1240691.2156 | 2701630.5089 | 1240682.2106 | 2701630.8795 | 1240674.224
54 | 2701625.8546 | 1240691.2156 | 2701621.049 | 1240698.1919
55 | 2701671.452 | 1240630.9681 | 2701670.4097 | 1240631.5362
56 | 2701671.452 | 1240630.9681 | 2701690.6365 | 1240620.5114
57 | 2701659.5853 | 1240637.4361 | 2701670.4097 | 1240631.5362
58 | 2701690.6365 | 1240620.5114 | 2701697.9104 | 1240616.5468
59 | 2701659.5853 | 1240637.4361 | 2701658.8055 | 1240637.8611 | 2701647.2273 | 1240641.4328
60 | 2701628.7882 | 1240647.121 | 2701647.2273 | 1240641.4328
61 | 2701621.049 | 1240698.1919 | 2701619.8361 | 1240699.9526 | 2701606.8423 | 1240710.7758
62 | 2701630.8795 | 1240674.224 | 2701630.9404 | 1240672.9109 | 2701629.9585 | 1240661.145
63 | 2701628.7882 | 1240647.121 | 2701629.9585 | 1240661.145
64 | 2701571.568 | 1240506.723 | 2701551.761 | 1240525.4673
65 | 2701571.568 | 1240506.723 | 2701573.0567 | 1240505.3141
66 | 2701548.4939 | 1240541.4257 | 2701547.6778 | 1240538.7278 | 2701547.5265 | 1240532.5427 | 2701550.4474 | 1240526.7105 | 2701551.761 | 1240525.4673
67 | 2701556.1439 | 1240584.9414 | 2701555.0219 | 1240563.0054 | 2701548.4939 | 1240541.4257
68 | 2701556.1439 | 1240584.9414 | 2701563.9469 | 1240585.0638
69 | 2701556.1439 | 1240584.9414 | 2701535.9368 | 1240584.6473
70 | 2701605.0219 | 1240522.352 | 2701609.3288 | 1240537.5288
71 | 2701605.0219 | 1240522.352 | 2701618.7106 | 1240513.4142
72 | 2701609.7434 | 1240538.9899 | 2701609.3288 | 1240537.5288
73 | 2701619.5004 | 1240512.8986 | 2701618.7106 | 1240513.4142
74 | 2701563.9469 | 1240585.0638 | 2701563.546 | 1240603.6156
75 | 2701563.9469 | 1240585.0638 | 2701572.8764 | 1240585.214
76 | 2701534.4736 | 1240584.626 | 2701535.9368 | 1240584.6473
77 | 2701572.8764 | 1240585.214 | 2701598.4063 | 1240585.6433
78 | 2701534.4736 | 1240584.626 | 2701520.1024 | 1240584.6626
79 | 2701534.4736 | 1240584.626 | 2701534.5302 | 1240605.9099
80 | 2701573.4217 | 1240665.082 | 2701586.0463 | 1240652.8221
81 | 2701573.4217 | 1240665.082 | 2701563.1565 | 1240675.0505
82 | 2701591.774 | 1240647.2599 | 2701586.0463 | 1240652.8221
83 | 2701553.1533 | 1240684.7648 | 2701563.1565 | 1240675.0505
84 | 2701591.774 | 1240647.2599 | 2701592.2848 | 1240646.7638
85 | 2701534.7527 | 1240692.9248 | 2701548.2117 | 1240689.5635 | 2701553.1533 | 1240684.7648
86 | 2701592.2848 | 1240646.7638 | 2701612.4562 | 1240627.1752
87 | 2701534.7527 | 1240692.9248 | 2701534.7065 | 1240675.2994
88 | 2701609.7434 | 1240538.9899 | 2701610.7423 | 1240542.5098 | 2701615.3788 | 1240564.9804
89 | 2701619.0176 | 1240582.6154 | 2701615.3788 | 1240564.9804
90 | 2701619.0176 | 1240582.6154 | 2701621.7319 | 1240602.5046
91 | 2701619.0176 | 1240582.6154 | 2701636.6228 | 1240576.968 | 2701636.6228 | 1240576.968
92 | 2701619.0176 | 1240582.6154 | 2701600.0274 | 1240585.6705 | 2701598.4063 | 1240585.6433
93 | 2701622.7697 | 1240610.1094 | 2701621.7319 | 1240602.5046
94 | 2701636.6228 | 1240576.968 | 2701647.4304 | 1240572.116 | 2701647.9341 | 1240571.7889
95 | 2701580.8664 | 1240459.0323 | 2701543.7092 | 1240493.0259
96 | 2701624.6486 | 1240623.8767 | 2701613.2148 | 1240626.4385 | 2701612.4562 | 1240627.1752
97 | 2701628.7882 | 1240647.121 | 2701624.6486 | 1240623.8767
98 | 2701624.6486 | 1240623.8767 | 2701622.7697 | 1240610.1094
99 | 2701500.7232 | 1240675.2131 | 2701501.0517 | 1240675.2139
100 | 2701534.7065 | 1240675.2994 | 2701501.0517 | 1240675.2139
101 | 2701534.7065 | 1240675.2994 | 2701534.6823 | 1240665.6031
102 | 2701736.9498 | 1240676.4727 | 2701737.1268 | 1240676.3422
103 | 2701737.1268 | 1240676.3422 | 2701742.2345 | 1240672.5762
104 | 2701699.5791 | 1240708.3579 | 2701707.5407 | 1240700.5439 | 2701717.9205 | 1240691.5148 | 2701733.8092 | 1240678.7884 | 2701736.9498 | 1240676.4727
105 | 2701699.5791 | 1240708.3579 | 2701693.1388 | 1240701.1087 | 2701692.8737 | 1240696.2782 | 2701700.825 | 1240681.2319
106 | 2701720.5281 | 1240643.2379 | 2701717.1284 | 1240650.3808 | 2701700.825 | 1240681.2319
107 | 2701498.9826 | 1240605.6734 | 2701498.8439 | 1240612.4825 | 2701494.2159 | 1240623.5007 | 2701484.0251 | 1240632.0998 | 2701474.5928 | 1240637.5576
108 | 2701651.6138 | 1240569.3991 | 2701647.9341 | 1240571.7889
109 | 2701534.5773 | 1240623.6354 | 2701534.6022 | 1240633.5848
110 | 2701534.5773 | 1240623.6354 | 2701534.5314 | 1240606.3858
111 | 2701534.5773 | 1240623.6354 | 2701522.8502 | 1240623.6411
112 | 2701534.5314 | 1240606.3858 | 2701534.5302 | 1240605.9099
113 | 2701509.9369 | 1240623.6474 | 2701522.8502 | 1240623.6411
114 | 2701454.0845 | 1240646.6214 | 2701446.4531 | 1240649.293
115 | 2701454.0845 | 1240646.6214 | 2701468.1598 | 1240641.2801 | 2701474.5928 | 1240637.5576
116 | 2701651.6138 | 1240569.3991 | 2701652.8103 | 1240568.6221
117 | 2701657.6865 | 1240565.4553 | 2701652.8103 | 1240568.6221

## bus_geodata
| x | y | coords
0 | 2701365.5237 | 1240624.3939
1 | 2701354.597 | 1240612.5702
2 | 2701379.4915 | 1240639.5083
3 | 2701348.7639 | 1240606.2583
4 | 2701388.4978 | 1240631.6117
5 | 2701342.5969 | 1240599.5793
6 | 2701405.3214 | 1240650.618
7 | 2701418.2277 | 1240605.5146
8 | 2701434.9818 | 1240590.8078
9 | 2701416.8669 | 1240572.1027
10 | 2701421.3076 | 1240668.6782
11 | 2701402.6681 | 1240557.4414
12 | 2701447.4448 | 1240611.203
13 | 2701455.3854 | 1240611.2387
14 | 2701447.041 | 1240626.7134
15 | 2701480.7409 | 1240584.4627
16 | 2701499.4097 | 1240584.7154
17 | 2701480.8981 | 1240563.2803
18 | 2701455.2967 | 1240613.651
19 | 2701448.5523 | 1240519.9077
20 | 2701390.122 | 1240381.2479
21 | 2701436.1179 | 1240522.5003
22 | 2701479.6154 | 1240551.6628
23 | 2701509.25 | 1240524.5513
24 | 2701475.7897 | 1240368.5352
25 | 2701433.1595 | 1240439.5054
26 | 2701443.8248 | 1240350.9595
27 | 2701445.0327 | 1240427.1877
28 | 2701406.8731 | 1240552.2474
29 | 2701422.5569 | 1240534.6919
30 | 2701340.5437 | 1240597.3556
31 | 2701672.3122 | 1240737.6355
32 | 2701657.3452 | 1240721.2749
33 | 2701684.2829 | 1240724.2139
34 | 2701647.6367 | 1240712.7939
35 | 2701696.7858 | 1240711.1566
36 | 2701238.4698 | 1240349.8522
37 | 2701242.8031 | 1240353.961
38 | 2701228.2054 | 1240341.8291
39 | 2701246.3693 | 1240357.3425
40 | 2701301.2198 | 1240315.5253
41 | 2701330.5988 | 1240298.4462
42 | 2701376.2175 | 1240391.8513
43 | 2701362.7694 | 1240402.1066
44 | 2701360.1134 | 1240404.1319
45 | 2701627.0201 | 1240729.5684
46 | 2701634.6144 | 1240723.3893
47 | 2701635.7898 | 1240701.0579
48 | 2701625.8546 | 1240691.2156
49 | 2701671.452 | 1240630.9681
50 | 2701670.4097 | 1240631.5362
51 | 2701690.6365 | 1240620.5114
52 | 2701659.5853 | 1240637.4361
53 | 2701697.9104 | 1240616.5468
54 | 2701647.2273 | 1240641.4328
55 | 2701621.049 | 1240698.1919
56 | 2701606.8423 | 1240710.7757
57 | 2701630.8795 | 1240674.224
58 | 2701629.9585 | 1240661.145
59 | 2701571.568 | 1240506.723
60 | 2701551.761 | 1240525.4673
61 | 2701573.0567 | 1240505.3142
62 | 2701548.4939 | 1240541.4257
63 | 2701556.1439 | 1240584.9414
64 | 2701605.0219 | 1240522.352
65 | 2701609.3288 | 1240537.5288
66 | 2701618.7106 | 1240513.4142
67 | 2701563.9469 | 1240585.0638
68 | 2701535.9368 | 1240584.6473
69 | 2701563.546 | 1240603.6156
70 | 2701572.8764 | 1240585.214
71 | 2701534.4736 | 1240584.626
72 | 2701573.4217 | 1240665.082
73 | 2701586.0463 | 1240652.8221
74 | 2701563.1565 | 1240675.0505
75 | 2701591.774 | 1240647.2599
76 | 2701553.1533 | 1240684.7648
77 | 2701592.2848 | 1240646.7639
78 | 2701534.7527 | 1240692.9248
79 | 2701609.7434 | 1240538.9899
80 | 2701615.3788 | 1240564.9804
81 | 2701619.0176 | 1240582.6154
82 | 2701621.7319 | 1240602.5046
83 | 2701636.6228 | 1240576.968
84 | 2701598.4063 | 1240585.6433
85 | 2701580.8664 | 1240459.0323
86 | 2701543.7092 | 1240493.0259
87 | 2701619.5004 | 1240512.8986
88 | 2701612.4563 | 1240627.1752
89 | 2701624.6486 | 1240623.8767
90 | 2701628.7882 | 1240647.121
91 | 2701622.7697 | 1240610.1094
92 | 2701500.7232 | 1240675.2131
93 | 2701501.0517 | 1240675.2139
94 | 2701534.7065 | 1240675.2994
95 | 2701534.6823 | 1240665.6031
96 | 2701737.1268 | 1240676.3422
97 | 2701736.9498 | 1240676.4727
98 | 2701742.2345 | 1240672.5762
99 | 2701699.5791 | 1240708.3579
100 | 2701700.825 | 1240681.2319
101 | 2701520.1024 | 1240584.6626
102 | 2701498.9826 | 1240605.6734
103 | 2701647.9341 | 1240571.7889
104 | 2701720.5281 | 1240643.2379
105 | 2701534.6022 | 1240633.5848
106 | 2701534.5773 | 1240623.6354
107 | 2701534.5314 | 1240606.3858
108 | 2701522.8502 | 1240623.6411
109 | 2701534.5302 | 1240605.9099
110 | 2701509.9369 | 1240623.6474
111 | 2701451.3478 | 1240427.5888
112 | 2701446.4531 | 1240649.293
113 | 2701454.0845 | 1240646.6214
114 | 2701474.5928 | 1240637.5576
115 | 2701651.6138 | 1240569.3991
116 | 2701652.8103 | 1240568.6221
117 | 2701657.6865 | 1240565.4553
118 | 2701704.7865 | 1240719.7471
119 | 2701534.4736 | 1240584.626

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98525 | -0.28204 | 0.0056551 | 0.0014173
1 | 0.98515 | -0.28394 | 0.0010824 | 0.00027129
2 | 0.98548 | -0.27752 | 0 | 0
3 | 0.98511 | -0.28478 | 0 | 0
4 | 0.98562 | -0.27489 | 0 | 0
5 | 0.98506 | -0.28568 | 0.0039883 | 0.00099956
6 | 0.98706 | -0.24694 | 0.0071362 | 0.0017885
7 | 0.98381 | -0.30991 | 0.0032104 | 0.00080461
8 | 0.98285 | -0.3284 | 0 | 0
9 | 0.98174 | -0.35005 | 0.0040116 | 0.0010054
10 | 0.9886 | -0.21738 | 0 | 0
11 | 0.98094 | -0.36557 | 0.003334 | 0.00083558
12 | 0.99026 | -0.18554 | 0 | 0
13 | 0.9902 | -0.1866 | 0 | 0
14 | 0.99037 | -0.18346 | 0.0058757 | 0.0014726
15 | 0.99787 | -0.04039 | 0 | 0
16 | 0.99808 | -0.036237 | 0 | 0
17 | 0.99762 | -0.045132 | 0.0052159 | 0.0013072
18 | 0.99019 | -0.18693 | 0.0075571 | 0.001894
19 | 0.97901 | -0.4032 | 0 | 0
20 | 0.97456 | -0.49044 | 0 | 0
21 | 0.97939 | -0.39589 | 0.002416 | 0.0006055
22 | 0.99754 | -0.046673 | 0 | 0
23 | 0.99727 | -0.05197 | 0.0028611 | 0.00071705
24 | 0.97335 | -0.51444 | 0 | 0
25 | 0.97406 | -0.50037 | 0 | 0
26 | 0.97313 | -0.5188 | 0.0052006 | 0.0013034
27 | 0.97402 | -0.50109 | 0.00067617 | 0.00016946
28 | 0.9807 | -0.37026 | 0.0038666 | 0.00096906
29 | 0.97994 | -0.38516 | 0.002416 | 0.0006055
30 | 0.98506 | -0.28576 | 0.0015017 | 0.00037636
31 | 0.98057 | -0.37433 | 0 | 0
32 | 0.98091 | -0.3677 | 0.010999 | 0.0027565
33 | 0.98029 | -0.37971 | 0.0010543 | 0.00026422
34 | 0.98123 | -0.36127 | 0 | 0
35 | 0.98004 | -0.38478 | 0 | 0
36 | 0.97178 | -0.54542 | 0.0071324 | 0.0017875
37 | 0.97183 | -0.54437 | 0.0027511 | 0.00068949
38 | 0.97175 | -0.54599 | 0.0023487 | 0.00058863
39 | 0.97189 | -0.54326 | 0.0010127 | 0.00025382
40 | 0.97283 | -0.5247 | 0.0004658 | 0.00011674
41 | 0.97326 | -0.51612 | 0 | 0
42 | 0.97442 | -0.49326 | 0.00089224 | 0.00022362
43 | 0.9743 | -0.49572 | 0.0032858 | 0.00082349
44 | 0.97428 | -0.496 | 0.0046146 | 0.0011565
45 | 0.98098 | -0.36637 | 0.0062451 | 0.0015652
46 | 0.98103 | -0.36526 | 0.0068626 | 0.0017199
47 | 0.98186 | -0.34902 | 0.0023006 | 0.0005766
48 | 0.98242 | -0.33818 | 0 | 0
49 | 0.98414 | -0.30459 | 0.0026036 | 0.00065253
50 | 0.98415 | -0.30446 | 0.0012919 | 0.00032378
51 | 0.98407 | -0.30591 | 0.0018851 | 0.00047245
52 | 0.98423 | -0.30285 | 0.0013864 | 0.00034745
53 | 0.98406 | -0.30613 | 0.0014867 | 0.00037261
54 | 0.98433 | -0.30082 | 0.0017021 | 0.00042658
55 | 0.98237 | -0.3391 | 0.0024511 | 0.0006143
56 | 0.98231 | -0.34032 | 0.0035473 | 0.00088903
57 | 0.98324 | -0.32217 | 0.0012923 | 0.00032389
58 | 0.98384 | -0.3103 | 0.0014346 | 0.00035955
59 | 0.99523 | -0.090752 | 0.0020001 | 0.00050126
60 | 0.99533 | -0.088867 | 0.0022695 | 0.00056879
61 | 0.99523 | -0.090821 | 0.0019272 | 0.00048301
62 | 0.99543 | -0.086977 | 0.0016925 | 0.00042418
63 | 0.99575 | -0.0808 | 0 | 0
64 | 0.98884 | -0.21354 | 0 | 0
65 | 0.9889 | -0.21224 | 0.0017926 | 0.00044927
66 | 0.98877 | -0.21489 | 0.0028319 | 0.00070973
67 | 0.99492 | -0.096681 | 0 | 0
68 | 0.99806 | -0.036888 | 0.0025696 | 0.00064401
69 | 0.99486 | -0.097742 | 0.0032483 | 0.0008141
70 | 0.99399 | -0.11443 | 0.0021985 | 0.00055101
71 | 0.99823 | -0.03365 | 0 | 0
72 | 0.98461 | -0.29554 | 0.001237 | 0.00031001
73 | 0.98485 | -0.29076 | 0.001803 | 0.00045188
74 | 0.98442 | -0.29911 | 0.00092832 | 0.00023266
75 | 0.98498 | -0.28833 | 0.0018582 | 0.0004657
76 | 0.98426 | -0.30235 | 0.0030682 | 0.00076896
77 | 0.98499 | -0.28809 | 0.0039945 | 0.0010011
78 | 0.98407 | -0.30604 | 0 | 0
79 | 0.98891 | -0.21207 | 0.001975 | 0.00049498
80 | 0.98912 | -0.20809 | 0.0023295 | 0.00058383
81 | 0.98929 | -0.20465 | 0 | 0
82 | 0.98761 | -0.23711 | 0.0013351 | 0.00033461
83 | 0.98917 | -0.20707 | 0.0013949 | 0.00034959
84 | 0.99138 | -0.16436 | 0.0018451 | 0.00046242
85 | 0.99689 | -0.059319 | 0.0039974 | 0.0010018
86 | 0.99707 | -0.055788 | 0.0006642 | 0.00016647
87 | 0.98876 | -0.21492 | 0.0017928 | 0.00044932
88 | 0.98558 | -0.2766 | 0.0019198 | 0.00048114
89 | 0.98587 | -0.27094 | 0 | 0
90 | 0.98452 | -0.29723 | 0 | 0
91 | 0.98698 | -0.24936 | 0.0026091 | 0.00065391
92 | 0.98365 | -0.31429 | 0.0041955 | 0.0010515
93 | 0.98365 | -0.31426 | 0.0041949 | 0.0010513
94 | 0.98391 | -0.30918 | 0 | 0
95 | 0.9839 | -0.30944 | 0.0014841 | 0.00037194
96 | 0.97969 | -0.3916 | 0.004173 | 0.0010459
97 | 0.97969 | -0.39158 | 0.0011165 | 0.00027981
98 | 0.97968 | -0.39173 | 0.0011157 | 0.00027962
99 | 0.97998 | -0.38586 | 0 | 0
100 | 0.97973 | -0.39078 | 0.0037729 | 0.00094559
101 | 1 | 0 | -0.23925 | -0.060799
102 | 0.99639 | -0.068397 | 0.0013774 | 0.00034522
103 | 0.9891 | -0.20839 | 0.0012264 | 0.00030738
104 | 0.97954 | -0.39452 | 0.0048163 | 0.0012071
105 | 0.99798 | -0.038315 | 0.0020264 | 0.00050786
106 | 0.998 | -0.037962 | 0 | 0
107 | 0.99808 | -0.036546 | 0.0018369 | 0.00046036
108 | 0.99797 | -0.038509 | 0.00060456 | 0.00015152
109 | 0.99808 | -0.036492 | 0.0011045 | 0.00027681
110 | 0.99795 | -0.038974 | 0.0020587 | 0.00051597
111 | 0.97402 | -0.50127 | 0.0015786 | 0.00039564
112 | 0.99064 | -0.17807 | 0 | 0
113 | 0.99126 | -0.16632 | 0 | 0
114 | 0.99296 | -0.13365 | 0.0041111 | 0.0010303
115 | 0.98908 | -0.20876 | 0.0022736 | 0.00056982
116 | 0.98908 | -0.20882 | 0.0012263 | 0.00030735
117 | 0.98907 | -0.20895 | 0.0012264 | 0.00030738
118 | 0.98003 | -0.38488 | 0.00045132 | 0.00011311
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0065735 | 0.0016474 | -0.0065729 | -0.0016472 | 5.9506e-07 | 1.7583e-07 | 0.0099279 | 0.0099279 | 0.0099279 | 0.98525 | -0.28204 | 0.98515 | -0.28394 | 2.7275
1 | -0.012229 | -0.0030647 | 0.012231 | 0.0030661 | 2.6324e-06 | 1.4226e-06 | 0.018469 | 0.018469 | 0.018469 | 0.98525 | -0.28204 | 0.98548 | -0.27752 | 5.0738
2 | 0.0054904 | 0.001376 | -0.0054902 | -0.0013759 | 2.2165e-07 | 3.2432e-08 | 0.008293 | 0.008293 | 0.008293 | 0.98515 | -0.28394 | 0.98511 | -0.28478 | 2.2783
3 | -0.012231 | -0.0030661 | 0.012233 | 0.003067 | 1.5297e-06 | 8.2659e-07 | 0.018469 | 0.018469 | 0.018469 | 0.98548 | -0.27752 | 0.98562 | -0.27489 | 5.0738
4 | 0.0054902 | 0.0013759 | -0.00549 | -0.0013759 | 2.3445e-07 | 3.4317e-08 | 0.008293 | 0.008293 | 0.008293 | 0.98511 | -0.28478 | 0.98506 | -0.28568 | 2.2783
5 | -0.061882 | -0.015669 | 0.061965 | 0.015722 | 8.3182e-05 | 5.2912e-05 | 0.093483 | 0.093483 | 0.093483 | 0.98562 | -0.27489 | 0.98706 | -0.24694 | 25.6821
6 | 0.049649 | 0.012602 | -0.049566 | -0.012549 | 8.3477e-05 | 5.2922e-05 | 0.075014 | 0.075014 | 0.075014 | 0.98562 | -0.27489 | 0.98381 | -0.30991 | 20.6083
7 | 0.0015017 | 0.00037633 | -0.0015017 | -0.00037636 | 5.8404e-09 | -3.4792e-08 | 0.0022684 | 0.0022684 | 0.0022684 | 0.98506 | -0.28568 | 0.98506 | -0.28576 | 0.6232
8 | -0.069102 | -0.01751 | 0.0692 | 0.017573 | 9.828e-05 | 6.2591e-05 | 0.10424 | 0.10424 | 0.10424 | 0.98706 | -0.24694 | 0.9886 | -0.21738 | 28.6375
9 | 0.046356 | 0.011745 | -0.046314 | -0.011718 | 4.115e-05 | 2.6053e-05 | 0.070159 | 0.070159 | 0.070159 | 0.98381 | -0.30991 | 0.98285 | -0.3284 | 19.2744
10 | 0.046314 | 0.011718 | -0.046266 | -0.011688 | 4.8064e-05 | 3.0431e-05 | 0.070159 | 0.070159 | 0.070159 | 0.98285 | -0.3284 | 0.98174 | -0.35005 | 19.2744
11 | 0.042255 | 0.010683 | -0.042223 | -0.010663 | 3.1427e-05 | 1.9855e-05 | 0.064079 | 0.064079 | 0.064079 | 0.98174 | -0.35005 | 0.98094 | -0.36557 | 17.604
12 | -0.0692 | -0.017573 | 0.069331 | 0.017657 | 0.0001312 | 8.3557e-05 | 0.10424 | 0.10424 | 0.10424 | 0.9886 | -0.21738 | 0.99064 | -0.17807 | 28.6375
13 | 0.038889 | 0.0098272 | -0.038881 | -0.0098217 | 8.7299e-06 | 5.5028e-06 | 0.059021 | 0.059021 | 0.059021 | 0.98094 | -0.36557 | 0.9807 | -0.37026 | 16.2146
14 | 0.0075576 | 0.0018942 | -0.0075572 | -0.001894 | 3.8289e-07 | 1.4321e-07 | 0.011356 | 0.011356 | 0.011356 | 0.99026 | -0.18554 | 0.9902 | -0.1866 | 3.1199
15 | -0.0075576 | -0.0018942 | 0.0075583 | 0.0018944 | 7.5038e-07 | 2.8062e-07 | 0.011356 | 0.011356 | 0.011356 | 0.99026 | -0.18554 | 0.99037 | -0.18346 | 3.1199
16 | 0.0075572 | 0.001894 | -0.0075571 | -0.001894 | 1.1674e-07 | 4.3666e-08 | 0.011356 | 0.011356 | 0.011356 | 0.9902 | -0.1866 | 0.99019 | -0.18693 | 3.1199
17 | -0.013434 | -0.003367 | 0.013437 | 0.003369 | 3.4509e-06 | 1.9178e-06 | 0.020185 | 0.020184 | 0.020185 | 0.99037 | -0.18346 | 0.99064 | -0.17807 | 5.5452
18 | -0.012745 | -0.0031947 | 0.012748 | 0.0031961 | 2.522e-06 | 1.3708e-06 | 0.019006 | 0.019006 | 0.019006 | 0.99787 | -0.04039 | 0.99808 | -0.036237 | 5.2214
19 | 0.012745 | 0.0031947 | -0.012742 | -0.0031932 | 2.8794e-06 | 1.5652e-06 | 0.019006 | 0.019006 | 0.019006 | 0.99787 | -0.04039 | 0.99762 | -0.045132 | 5.2214
20 | -0.1016 | -0.025974 | 0.10177 | 0.026088 | 0.00017845 | 0.00011394 | 0.15165 | 0.15165 | 0.15165 | 0.99808 | -0.036237 | 1 | 0 | 41.6615
21 | 0.088848 | 0.022778 | -0.088709 | -0.02269 | 0.0001383 | 8.8241e-05 | 0.13264 | 0.13264 | 0.13264 | 0.99808 | -0.036237 | 0.99639 | -0.068397 | 36.4401
22 | 0.0075266 | 0.001886 | -0.0075261 | -0.0018857 | 5.5239e-07 | 2.0093e-07 | 0.011226 | 0.011226 | 0.011226 | 0.99762 | -0.045132 | 0.99754 | -0.046673 | 3.0842
23 | 0.03013 | 0.0076089 | -0.030004 | -0.0075306 | 0.00012539 | 7.8258e-05 | 0.045815 | 0.045816 | 0.045816 | 0.97901 | -0.4032 | 0.97456 | -0.49044 | 12.5869
24 | -0.03013 | -0.0076089 | 0.03014 | 0.0076155 | 1.0559e-05 | 6.5892e-06 | 0.045815 | 0.045815 | 0.045815 | 0.97901 | -0.4032 | 0.97939 | -0.39589 | 12.5867
25 | 0.0087948 | 0.0022046 | -0.0087936 | -0.002204 | 1.1825e-06 | 5.3892e-07 | 0.013428 | 0.013429 | 0.013429 | 0.97456 | -0.49044 | 0.97442 | -0.49326 | 3.6892
26 | 0.0074635 | 0.0018701 | -0.00746 | -0.0018688 | 3.5276e-06 | 1.3555e-06 | 0.011396 | 0.011396 | 0.011396 | 0.97456 | -0.49044 | 0.97406 | -0.50037 | 3.1307
27 | 0.013746 | 0.0034559 | -0.013729 | -0.0034464 | 1.6836e-05 | 9.5071e-06 | 0.020992 | 0.020993 | 0.020993 | 0.97456 | -0.49044 | 0.97326 | -0.51612 | 5.7672
28 | -0.032556 | -0.008221 | 0.032573 | 0.0082314 | 1.6746e-05 | 1.0488e-05 | 0.049486 | 0.049486 | 0.049486 | 0.97939 | -0.39589 | 0.97994 | -0.38516 | 13.5951
29 | 0.0075261 | 0.0018857 | -0.0075242 | -0.0018851 | 1.8983e-06 | 6.907e-07 | 0.011226 | 0.011227 | 0.011227 | 0.99754 | -0.046673 | 0.99727 | -0.05197 | 3.0842
30 | 0.0046631 | 0.001168 | -0.0046622 | -0.0011681 | 8.4783e-07 | -6.6653e-08 | 0.0069575 | 0.0069577 | 0.0069577 | 0.99727 | -0.05197 | 0.99707 | -0.055788 | 1.9115
31 | -0.0052016 | -0.0013035 | 0.0052051 | 0.0013039 | 3.4881e-06 | 4.0257e-07 | 0.007952 | 0.0079513 | 0.007952 | 0.97335 | -0.51444 | 0.97406 | -0.50037 | 2.1846
32 | 0.0052016 | 0.0013035 | -0.0052006 | -0.0013034 | 1.0792e-06 | 1.2516e-07 | 0.007952 | 0.0079522 | 0.0079522 | 0.97335 | -0.51444 | 0.97313 | -0.5188 | 2.1847
33 | 0.0022549 | 0.00056487 | -0.0022548 | -0.00056504 | 7.7224e-08 | -1.666e-07 | 0.0034446 | 0.0034447 | 0.0034447 | 0.97406 | -0.50037 | 0.97402 | -0.50109 | 0.94633
34 | 0.0015786 | 0.00039557 | -0.0015786 | -0.00039564 | 1.3802e-08 | -6.9926e-08 | 0.0024117 | 0.0024117 | 0.0024117 | 0.97402 | -0.50109 | 0.97402 | -0.50127 | 0.66255
35 | 0.035014 | 0.0088527 | -0.034989 | -0.0088369 | 2.5008e-05 | 1.5708e-05 | 0.053154 | 0.053155 | 0.053155 | 0.9807 | -0.37026 | 0.97994 | -0.38516 | 14.6029
36 | -0.016513 | -0.0041416 | 0.016519 | 0.0041446 | 5.2243e-06 | 3.0636e-06 | 0.02506 | 0.02506 | 0.02506 | 0.98057 | -0.37433 | 0.98091 | -0.3677 | 6.8847
37 | 0.016513 | 0.0041416 | -0.016509 | -0.0041391 | 4.2354e-06 | 2.4839e-06 | 0.02506 | 0.02506 | 0.02506 | 0.98057 | -0.37433 | 0.98029 | -0.37971 | 6.8847
38 | -0.027517 | -0.0069011 | 0.027526 | 0.0069063 | 8.4241e-06 | 5.2286e-06 | 0.041745 | 0.041745 | 0.041745 | 0.98091 | -0.3677 | 0.98123 | -0.36127 | 11.4683
39 | 0.015455 | 0.0038749 | -0.015451 | -0.0038727 | 3.7327e-06 | 2.161e-06 | 0.02346 | 0.02346 | 0.02346 | 0.98029 | -0.37971 | 0.98004 | -0.38478 | 6.4451
40 | -0.040636 | -0.010193 | 0.04066 | 0.010208 | 2.375e-05 | 1.4989e-05 | 0.061627 | 0.061627 | 0.061627 | 0.98123 | -0.36127 | 0.98186 | -0.34902 | 16.9304
41 | 0.013111 | 0.0032866 | -0.013108 | -0.0032852 | 2.4886e-06 | 1.3807e-06 | 0.019882 | 0.019882 | 0.019882 | 0.98123 | -0.36127 | 0.98103 | -0.36526 | 5.4621
42 | 0.00045132 | 0.00011296 | -0.00045132 | -0.00011311 | 2.067e-09 | -1.466e-07 | 0.0006852 | 0.00068526 | 0.00068526 | 0.98004 | -0.38478 | 0.98003 | -0.38488 | 0.18826
43 | 0.015 | 0.0037597 | -0.014999 | -0.0037593 | 7.6812e-07 | 4.4184e-07 | 0.022775 | 0.022775 | 0.022775 | 0.98004 | -0.38478 | 0.97998 | -0.38586 | 6.2568
44 | -0.0094811 | -0.0023761 | 0.0094816 | 0.0023763 | 4.7197e-07 | 2.2807e-07 | 0.014518 | 0.014518 | 0.014518 | 0.97178 | -0.54542 | 0.97183 | -0.54437 | 3.9884
45 | 0.0023487 | 0.00058851 | -0.0023487 | -0.00058863 | 6.4625e-08 | -1.237e-07 | 0.0035964 | 0.0035965 | 0.0035965 | 0.97178 | -0.54542 | 0.97175 | -0.54599 | 0.98804
46 | -0.012233 | -0.0030658 | 0.012233 | 0.0030661 | 6.4652e-07 | 3.5288e-07 | 0.01873 | 0.01873 | 0.01873 | 0.97183 | -0.54437 | 0.97189 | -0.54326 | 5.1456
47 | -0.013246 | -0.0033199 | 0.013258 | 0.0033265 | 1.1724e-05 | 6.5604e-06 | 0.020281 | 0.02028 | 0.020281 | 0.97189 | -0.54326 | 0.97283 | -0.5247 | 5.5716
48 | -0.013724 | -0.0034432 | 0.013729 | 0.0034464 | 5.6159e-06 | 3.1721e-06 | 0.020993 | 0.020993 | 0.020993 | 0.97283 | -0.5247 | 0.97326 | -0.51612 | 5.7672
49 | 0.0079014 | 0.0019804 | -0.0079005 | -0.00198 | 9.2335e-07 | 3.803e-07 | 0.012066 | 0.012066 | 0.012066 | 0.97442 | -0.49326 | 0.9743 | -0.49572 | 3.3149
50 | 0.0046147 | 0.0011565 | -0.0046146 | -0.0011565 | 6.2216e-08 | -1.7768e-09 | 0.0070479 | 0.0070479 | 0.0070479 | 0.9743 | -0.49572 | 0.97428 | -0.496 | 1.9362
51 | -0.0062451 | -0.0015652 | 0.0062455 | 0.0015653 | 3.2947e-07 | 8.7251e-08 | 0.0094731 | 0.009473 | 0.0094731 | 0.98098 | -0.36637 | 0.98103 | -0.36526 | 2.6025
52 | -0.042961 | -0.010785 | 0.042983 | 0.010799 | 2.2235e-05 | 1.4053e-05 | 0.065113 | 0.065113 | 0.065113 | 0.98186 | -0.34902 | 0.98242 | -0.33818 | 17.8882
53 | -0.048982 | -0.012302 | 0.049019 | 0.012326 | 3.7435e-05 | 2.3728e-05 | 0.074199 | 0.074199 | 0.074199 | 0.98242 | -0.33818 | 0.98324 | -0.32217 | 20.3844
54 | 0.0059988 | 0.0015033 | -0.0059986 | -0.0015032 | 2.6226e-07 | 6.059e-08 | 0.0090861 | 0.0090861 | 0.0090861 | 0.98242 | -0.33818 | 0.98237 | -0.3391 | 2.4962
55 | -0.0059757 | -0.0014974 | 0.0059758 | 0.0014974 | 3.634e-08 | 8.1738e-09 | 0.0090352 | 0.0090352 | 0.0090352 | 0.98414 | -0.30459 | 0.98415 | -0.30446 | 2.4822
56 | 0.0033721 | 0.00084483 | -0.0033719 | -0.00084497 | 2.1299e-07 | -1.4129e-07 | 0.0050985 | 0.0050986 | 0.0050986 | 0.98414 | -0.30459 | 0.98407 | -0.30591 | 1.4007
57 | -0.0072677 | -0.0018212 | 0.0072682 | 0.0018214 | 5.582e-07 | 2.0059e-07 | 0.010988 | 0.010988 | 0.010988 | 0.98415 | -0.30446 | 0.98423 | -0.30285 | 3.0188
58 | 0.0014868 | 0.00037252 | -0.0014867 | -0.00037261 | 1.5701e-08 | -9.5199e-08 | 0.0022481 | 0.0022481 | 0.0022481 | 0.98407 | -0.30591 | 0.98406 | -0.30613 | 0.61762
59 | -0.0086546 | -0.0021688 | 0.0086554 | 0.0021692 | 8.3491e-07 | 3.6905e-07 | 0.013084 | 0.013084 | 0.013084 | 0.98423 | -0.30285 | 0.98433 | -0.30082 | 3.5946
60 | -0.010358 | -0.0025958 | 0.010359 | 0.0025967 | 1.774e-06 | 8.9002e-07 | 0.015657 | 0.015657 | 0.015657 | 0.98433 | -0.30082 | 0.98452 | -0.29723 | 4.3015
61 | 0.0035475 | 0.00088892 | -0.0035473 | -0.00088903 | 2.0626e-07 | -1.0916e-07 | 0.0053734 | 0.0053735 | 0.0053735 | 0.98237 | -0.3391 | 0.98231 | -0.34032 | 1.4762
62 | -0.050311 | -0.012649 | 0.05034 | 0.012668 | 2.8537e-05 | 1.8097e-05 | 0.076155 | 0.076155 | 0.076155 | 0.98324 | -0.32217 | 0.98384 | -0.3103 | 20.9217
63 | -0.051775 | -0.013027 | 0.051807 | 0.013048 | 3.2375e-05 | 2.0541e-05 | 0.078325 | 0.078325 | 0.078325 | 0.98384 | -0.3103 | 0.98452 | -0.29723 | 21.5178
64 | -0.0039273 | -0.00098425 | 0.0039276 | 0.00098412 | 3.5258e-07 | -1.2875e-07 | 0.0058718 | 0.0058717 | 0.0058718 | 0.99523 | -0.090752 | 0.99533 | -0.088867 | 1.6131
65 | 0.0019272 | 0.00048298 | -0.0019272 | -0.00048301 | 6.3817e-09 | -2.255e-08 | 0.0028815 | 0.0028815 | 0.0028815 | 0.99523 | -0.090752 | 0.99523 | -0.090821 | 0.79161
66 | -0.0061971 | -0.0015529 | 0.0061977 | 0.001553 | 5.5803e-07 | 1.3179e-07 | 0.0092646 | 0.0092645 | 0.0092646 | 0.99533 | -0.088867 | 0.99543 | -0.086977 | 2.5452
67 | -0.0078902 | -0.0019772 | 0.0078925 | 0.0019781 | 2.3219e-06 | 9.0723e-07 | 0.011795 | 0.011794 | 0.011795 | 0.99543 | -0.086977 | 0.99575 | -0.0808 | 3.2403
68 | 0.11722 | 0.029853 | -0.11713 | -0.029796 | 8.9712e-05 | 5.7314e-05 | 0.17534 | 0.17534 | 0.17534 | 0.99575 | -0.0808 | 0.99492 | -0.096681 | 48.1715
69 | -0.12512 | -0.031831 | 0.12538 | 0.032001 | 0.0002654 | 0.00016959 | 0.18714 | 0.18714 | 0.18714 | 0.99575 | -0.0808 | 0.99806 | -0.036888 | 51.4117
70 | -0.004625 | -0.001159 | 0.0046253 | 0.001159 | 2.8655e-07 | -1.8994e-08 | 0.0069597 | 0.0069596 | 0.0069597 | 0.98884 | -0.21354 | 0.9889 | -0.21224 | 1.912
71 | 0.004625 | 0.001159 | -0.0046247 | -0.001159 | 2.9695e-07 | -1.965e-08 | 0.0069597 | 0.0069598 | 0.0069598 | 0.98884 | -0.21354 | 0.98877 | -0.21489 | 1.912
72 | -0.0064179 | -0.0016083 | 0.0064179 | 0.0016083 | 5.3114e-08 | 1.4507e-08 | 0.009657 | 0.009657 | 0.009657 | 0.9889 | -0.21224 | 0.98891 | -0.21207 | 2.653
73 | 0.0017928 | 0.00044931 | -0.0017928 | -0.00044932 | 2.5746e-09 | -1.0449e-08 | 0.002698 | 0.002698 | 0.002698 | 0.98877 | -0.21489 | 0.98876 | -0.21492 | 0.74122
74 | 0.0032485 | 0.00081396 | -0.0032483 | -0.0008141 | 1.6428e-07 | -1.3586e-07 | 0.0048584 | 0.0048585 | 0.0048585 | 0.99492 | -0.096681 | 0.99486 | -0.097742 | 1.3347
75 | 0.11389 | 0.028982 | -0.11379 | -0.02892 | 9.7342e-05 | 6.2183e-05 | 0.17049 | 0.17049 | 0.17049 | 0.99492 | -0.096681 | 0.99399 | -0.11443 | 46.8368
76 | -0.12795 | -0.032645 | 0.12797 | 0.032658 | 2.0014e-05 | 1.279e-05 | 0.19097 | 0.19097 | 0.19097 | 0.99806 | -0.036888 | 0.99823 | -0.03365 | 52.4641
77 | 0.11159 | 0.028369 | -0.11132 | -0.028198 | 0.00026766 | 0.00017097 | 0.16719 | 0.16719 | 0.16719 | 0.99399 | -0.11443 | 0.99138 | -0.16436 | 45.9326
78 | -0.1356 | -0.03457 | 0.13582 | 0.034711 | 0.00022066 | 0.00014103 | 0.20235 | 0.20235 | 0.20235 | 0.99823 | -0.03365 | 1 | 0 | 55.5897
79 | 0.0076325 | 0.0019125 | -0.0076315 | -0.0019121 | 1.0332e-06 | 3.8303e-07 | 0.011377 | 0.011377 | 0.011377 | 0.99823 | -0.03365 | 0.99808 | -0.036492 | 3.1257
80 | -0.015118 | -0.0037912 | 0.015121 | 0.0037931 | 3.4449e-06 | 1.9809e-06 | 0.022848 | 0.022848 | 0.022848 | 0.98461 | -0.29554 | 0.98485 | -0.29076 | 6.2768
81 | 0.013881 | 0.0034812 | -0.013878 | -0.0034798 | 2.3615e-06 | 1.3294e-06 | 0.020978 | 0.020978 | 0.020978 | 0.98461 | -0.29554 | 0.98442 | -0.29911 | 5.7633
82 | -0.016924 | -0.004245 | 0.016926 | 0.0042462 | 1.9578e-06 | 1.1514e-06 | 0.025572 | 0.025572 | 0.025572 | 0.98485 | -0.29076 | 0.98498 | -0.28833 | 7.0252
83 | 0.01295 | 0.0032472 | -0.012948 | -0.0032461 | 2.0037e-06 | 1.1051e-06 | 0.019575 | 0.019575 | 0.019575 | 0.98442 | -0.29911 | 0.98426 | -0.30235 | 5.3778
84 | -0.018784 | -0.0047119 | 0.018784 | 0.004712 | 2.1504e-07 | 1.2856e-07 | 0.028379 | 0.028379 | 0.028379 | 0.98498 | -0.28833 | 0.98499 | -0.28809 | 7.7964
85 | 0.0098797 | 0.0024771 | -0.009878 | -0.0024763 | 1.7369e-06 | 8.4783e-07 | 0.014937 | 0.014937 | 0.014937 | 0.98426 | -0.30235 | 0.98407 | -0.30604 | 4.1035
86 | -0.022779 | -0.0057131 | 0.022791 | 0.0057208 | 1.2487e-05 | 7.6337e-06 | 0.034413 | 0.034413 | 0.034413 | 0.98499 | -0.28809 | 0.98558 | -0.2766 | 9.4542
87 | 0.009878 | 0.0024763 | -0.0098765 | -0.0024755 | 1.4749e-06 | 7.1999e-07 | 0.014937 | 0.014937 | 0.014937 | 0.98407 | -0.30604 | 0.98391 | -0.30918 | 4.1035
88 | -0.0083929 | -0.0021033 | 0.0083945 | 0.0021039 | 1.591e-06 | 6.7686e-07 | 0.012629 | 0.012629 | 0.012629 | 0.98891 | -0.21207 | 0.98912 | -0.20809 | 3.4694
89 | -0.010724 | -0.0026878 | 0.010726 | 0.0026887 | 1.7575e-06 | 8.9364e-07 | 0.016133 | 0.016133 | 0.016133 | 0.98912 | -0.20809 | 0.98929 | -0.20465 | 4.4322
90 | 0.091191 | 0.02307 | -0.091049 | -0.022979 | 0.00014178 | 9.048e-05 | 0.13724 | 0.13724 | 0.13724 | 0.98929 | -0.20465 | 0.98761 | -0.23711 | 37.7029
91 | 0.0073491 | 0.0018418 | -0.0073482 | -0.0018415 | 8.4718e-07 | 3.0483e-07 | 0.011054 | 0.011054 | 0.011054 | 0.98929 | -0.20465 | 0.98917 | -0.20707 | 3.0368
92 | -0.10927 | -0.0276 | 0.10948 | 0.027736 | 0.00021144 | 0.00013506 | 0.16443 | 0.16443 | 0.16443 | 0.98929 | -0.20465 | 0.99138 | -0.16436 | 45.1718
93 | 0.089714 | 0.022645 | -0.089661 | -0.022611 | 5.2632e-05 | 3.3586e-05 | 0.13523 | 0.13523 | 0.13523 | 0.98761 | -0.23711 | 0.98698 | -0.24936 | 37.1503
94 | 0.0059533 | 0.0014919 | -0.005953 | -0.0014918 | 3.7437e-07 | 7.9827e-08 | 0.0089556 | 0.0089557 | 0.0089557 | 0.98917 | -0.20707 | 0.9891 | -0.20839 | 2.4604
95 | -0.0039974 | -0.0010018 | 0.003998 | 0.0010016 | 6.7232e-07 | -2.2643e-07 | 0.0059667 | 0.0059665 | 0.0059667 | 0.99689 | -0.059319 | 0.99707 | -0.055788 | 1.6392
96 | -0.024711 | -0.0062019 | 0.024718 | 0.006206 | 6.6691e-06 | 4.1054e-06 | 0.037312 | 0.037312 | 0.037312 | 0.98558 | -0.2766 | 0.98587 | -0.27094 | 10.2505
97 | 0.062244 | 0.015694 | -0.062166 | -0.015644 | 7.8202e-05 | 4.9748e-05 | 0.093982 | 0.093982 | 0.093982 | 0.98587 | -0.27094 | 0.98452 | -0.29723 | 25.8192
98 | -0.086962 | -0.0219 | 0.087052 | 0.021957 | 8.9821e-05 | 5.7308e-05 | 0.13129 | 0.13129 | 0.13129 | 0.98587 | -0.27094 | 0.98698 | -0.24936 | 36.0696
99 | -0.0041955 | -0.0010515 | 0.0041955 | 0.0010515 | 4.9625e-09 | -9.9418e-10 | 0.0063467 | 0.0063467 | 0.0063467 | 0.98365 | -0.31429 | 0.98365 | -0.31426 | 1.7436
100 | -0.0083904 | -0.0021028 | 0.0083924 | 0.0021037 | 2.0332e-06 | 8.7391e-07 | 0.012693 | 0.012692 | 0.012693 | 0.98365 | -0.31426 | 0.98391 | -0.30918 | 3.487
101 | 0.0014841 | 0.00037183 | -0.0014841 | -0.00037194 | 1.8317e-08 | -1.1142e-07 | 0.0022444 | 0.0022445 | 0.0022445 | 0.98391 | -0.30918 | 0.9839 | -0.30944 | 0.61661
102 | -0.0052888 | -0.0013254 | 0.0052888 | 0.0013254 | 5.3226e-09 | 6.3727e-10 | 0.0080329 | 0.0080329 | 0.0080329 | 0.97969 | -0.3916 | 0.97969 | -0.39158 | 2.2068
103 | 0.0011157 | 0.00027955 | -0.0011157 | -0.00027962 | 6.8339e-09 | -7.5532e-08 | 0.0016946 | 0.0016946 | 0.0016946 | 0.97969 | -0.3916 | 0.97968 | -0.39173 | 0.46556
104 | -0.0064052 | -0.0016052 | 0.006407 | 0.0016057 | 1.7452e-06 | 4.9758e-07 | 0.0097287 | 0.0097285 | 0.0097287 | 0.97969 | -0.39158 | 0.97998 | -0.38586 | 2.6727
105 | 0.0085921 | 0.0021536 | -0.0085901 | -0.0021527 | 2.014e-06 | 8.915e-07 | 0.013046 | 0.013047 | 0.013047 | 0.97998 | -0.38586 | 0.97973 | -0.39078 | 3.5842
106 | 0.0048171 | 0.0012071 | -0.0048163 | -0.0012071 | 8.5921e-07 | 1.097e-08 | 0.0073162 | 0.0073164 | 0.0073164 | 0.97973 | -0.39078 | 0.97954 | -0.39452 | 2.01
107 | 0.087332 | 0.022344 | -0.087057 | -0.022169 | 0.00027492 | 0.00017539 | 0.13059 | 0.13059 | 0.13059 | 0.99639 | -0.068397 | 0.99296 | -0.13365 | 35.8751
108 | 0.0047265 | 0.0011845 | -0.0047264 | -0.0011845 | 8.3189e-08 | -3.0716e-09 | 0.0071106 | 0.0071106 | 0.0071106 | 0.9891 | -0.20839 | 0.98908 | -0.20876 | 1.9535
109 | -0.0020264 | -0.00050786 | 0.0020264 | 0.00050775 | 3.4059e-08 | -1.0821e-07 | 0.0030214 | 0.0030213 | 0.0030214 | 0.99798 | -0.038315 | 0.998 | -0.037962 | 0.83004
110 | -0.0046898 | -0.001175 | 0.0046901 | 0.001175 | 3.1627e-07 | -2.3005e-08 | 0.0069924 | 0.0069923 | 0.0069924 | 0.998 | -0.037962 | 0.99808 | -0.036546 | 1.921
111 | 0.0026634 | 0.00066724 | -0.0026633 | -0.00066735 | 6.9349e-08 | -1.0885e-07 | 0.003971 | 0.0039711 | 0.0039711 | 0.998 | -0.037962 | 0.99797 | -0.038509 | 1.091
112 | -0.006527 | -0.0016353 | 0.006527 | 0.0016353 | 1.6897e-08 | 4.5952e-09 | 0.0097308 | 0.0097308 | 0.0097308 | 0.99808 | -0.036546 | 0.99808 | -0.036492 | 2.6733
113 | 0.0020588 | 0.00051583 | -0.0020587 | -0.00051597 | 4.5631e-08 | -1.3952e-07 | 0.0030697 | 0.0030697 | 0.0030697 | 0.99797 | -0.038509 | 0.99795 | -0.038974 | 0.84333
114 | -0.082769 | -0.021026 | 0.082815 | 0.021055 | 4.6822e-05 | 2.9862e-05 | 0.12442 | 0.12442 | 0.12442 | 0.99064 | -0.17807 | 0.99126 | -0.16632 | 34.1826
115 | -0.082815 | -0.021055 | 0.082946 | 0.021139 | 0.00013055 | 8.3262e-05 | 0.12442 | 0.12442 | 0.12442 | 0.99126 | -0.16632 | 0.99296 | -0.13365 | 34.1826
116 | 0.0024528 | 0.00061465 | -0.0024528 | -0.00061466 | 7.2851e-09 | -1.3648e-08 | 0.0036901 | 0.0036901 | 0.0036901 | 0.98908 | -0.20876 | 0.98908 | -0.20882 | 1.0138
117 | 0.0012265 | 0.00030731 | -0.0012264 | -0.00030738 | 7.423e-09 | -6.987e-08 | 0.0018451 | 0.0018451 | 0.0018451 | 0.98908 | -0.20882 | 0.98907 | -0.20895 | 0.50691

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24205 | 0.061503

## res_load
| p_mw | q_mvar
0 | 0.0056551 | 0.0014173
1 | 0.0010824 | 0.00027129
2 | 0.0039883 | 0.00099956
3 | 0.0071362 | 0.0017885
4 | 0.0032104 | 0.00080461
5 | 0.0040116 | 0.0010054
6 | 0.003334 | 0.00083558
7 | 0.0058757 | 0.0014726
8 | 0.0052159 | 0.0013072
9 | 0.0075571 | 0.001894
10 | 0.002416 | 0.0006055
11 | 0.0028611 | 0.00071705
12 | 0.0052006 | 0.0013034
13 | 0.00067617 | 0.00016946
14 | 0.0038666 | 0.00096906
15 | 0.002416 | 0.0006055
16 | 0.0015017 | 0.00037636
17 | 0.010999 | 0.0027565
18 | 0.0010543 | 0.00026422
19 | 0.0071324 | 0.0017875
20 | 0.0027511 | 0.00068949
21 | 0.0023487 | 0.00058863
22 | 0.0010127 | 0.00025382
23 | 0.0004658 | 0.00011674
24 | 0.00089224 | 0.00022362
25 | 0.0032858 | 0.00082349
26 | 0.0046146 | 0.0011565
27 | 0.0062451 | 0.0015652
28 | 0.0068626 | 0.0017199
29 | 0.0023006 | 0.0005766
30 | 0.0026036 | 0.00065253
31 | 0.0012919 | 0.00032378
32 | 0.0018851 | 0.00047245
33 | 0.0013864 | 0.00034745
34 | 0.0014867 | 0.00037261
35 | 0.0017021 | 0.00042658
36 | 0.0024511 | 0.0006143
37 | 0.0035473 | 0.00088903
38 | 0.0012923 | 0.00032389
39 | 0.0014346 | 0.00035955
40 | 0.0020001 | 0.00050126
41 | 0.0022695 | 0.00056879
42 | 0.0019272 | 0.00048301
43 | 0.0016925 | 0.00042418
44 | 0.0017926 | 0.00044927
45 | 0.0028319 | 0.00070973
46 | 0.0025696 | 0.00064401
47 | 0.0032483 | 0.0008141
48 | 0.0021985 | 0.00055101
49 | 0.001237 | 0.00031001
50 | 0.001803 | 0.00045188
51 | 0.00092832 | 0.00023266
52 | 0.0018582 | 0.0004657
53 | 0.0030682 | 0.00076896
54 | 0.0039945 | 0.0010011
55 | 0.001975 | 0.00049498
56 | 0.0023295 | 0.00058383
57 | 0.0013351 | 0.00033461
58 | 0.0013949 | 0.00034959
59 | 0.0018451 | 0.00046242
60 | 0.0039974 | 0.0010018
61 | 0.0006642 | 0.00016647
62 | 0.0017928 | 0.00044932
63 | 0.0019198 | 0.00048114
64 | 0.0026091 | 0.00065391
65 | 0.0041955 | 0.0010515
66 | 0.0041949 | 0.0010513
67 | 0.0014841 | 0.00037194
68 | 0.004173 | 0.0010459
69 | 0.0011165 | 0.00027981
70 | 0.0011157 | 0.00027962
71 | 0.0037729 | 0.00094559
72 | 0.0028058 | 0.00070319
73 | 0.0013774 | 0.00034522
74 | 0.0012264 | 0.00030738
75 | 0.0048163 | 0.0012071
76 | 0.0020264 | 0.00050786
77 | 0.0018369 | 0.00046036
78 | 0.00060456 | 0.00015152
79 | 0.0011045 | 0.00027681
80 | 0.0020587 | 0.00051597
81 | 0.0015786 | 0.00039564
82 | 0.0041111 | 0.0010303
83 | 0.0022736 | 0.00056982
84 | 0.0012263 | 0.00030735
85 | 0.0012264 | 0.00030738
86 | 0.00045132 | 0.00011311

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1