## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-16_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_115-16_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_115-16_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_115-16_0_6_node_44 | 0.4 | n |  | TRUE
4 | bus_LV_115-16_0_6_node_60 | 0.4 | n |  | TRUE
5 | bus_LV_115-16_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_115-16_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_115-16_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_115-16_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_115-16_0_6_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_115-16_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_115-16_0_6_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_115-16_0_6_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_115-16_0_6_node_136 | 0.4 | n |  | TRUE
14 | bus_LV_115-16_0_6_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_115-16_0_6_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_115-16_0_6_node_123 | 0.4 | n |  | TRUE
17 | bus_LV_115-16_0_6_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_115-16_0_6_node_112 | 0.4 | n |  | TRUE
19 | bus_LV_115-16_0_6_node_110 | 0.4 | n |  | TRUE
20 | bus_LV_115-16_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_115-16_0_6_node_100 | 0.4 | n |  | TRUE
22 | bus_LV_115-16_0_6_node_113 | 0.4 | n |  | TRUE
23 | bus_LV_115-16_0_6_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_115-16_0_6_node_124 | 0.4 | n |  | TRUE
25 | bus_LV_115-16_0_6_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_115-16_0_6_node_137 | 0.4 | n |  | TRUE
27 | bus_LV_115-16_0_6_node_133 | 0.4 | n |  | TRUE
28 | bus_LV_115-16_0_6_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_115-16_0_6_node_122 | 0.4 | n |  | TRUE
30 | bus_LV_115-16_0_6_node_141 | 0.4 | n |  | TRUE
31 | bus_LV_115-16_0_6_node_140 | 0.4 | n |  | TRUE
32 | bus_LV_115-16_0_6_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_115-16_0_6_node_106 | 0.4 | n |  | TRUE
34 | bus_LV_115-16_0_6_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_115-16_0_6_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_115-16_0_6_node_111 | 0.4 | n |  | TRUE
37 | bus_LV_115-16_0_6_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_115-16_0_6_node_129 | 0.4 | n |  | TRUE
39 | bus_LV_115-16_0_6_node_139 | 0.4 | n |  | TRUE
40 | bus_LV_115-16_0_6_node_138 | 0.4 | n |  | TRUE
41 | bus_LV_115-16_0_6_node_105 | 0.4 | n |  | TRUE
42 | bus_LV_115-16_0_6_node_98 | 0.4 | n |  | TRUE
43 | bus_LV_115-16_0_6_node_90 | 0.4 | n |  | TRUE
44 | bus_LV_115-16_0_6_node_99 | 0.4 | n |  | TRUE
45 | bus_LV_115-16_0_6_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_115-16_0_6_node_97 | 0.4 | n |  | TRUE
47 | bus_LV_115-16_0_6_node_14 | 0.4 | n |  | TRUE
48 | bus_LV_115-16_0_6_node_15 | 0.4 | n |  | TRUE
49 | bus_LV_115-16_0_6_node_16 | 0.4 | n |  | TRUE
50 | bus_LV_115-16_0_6_node_17 | 0.4 | n |  | TRUE
51 | bus_LV_115-16_0_6_node_19 | 0.4 | n |  | TRUE
52 | bus_LV_115-16_0_6_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_115-16_0_6_node_21 | 0.4 | n |  | TRUE
54 | bus_LV_115-16_0_6_node_18 | 0.4 | n |  | TRUE
55 | bus_LV_115-16_0_6_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_115-16_0_6_node_64 | 0.4 | n |  | TRUE
57 | bus_LV_115-16_0_6_node_20 | 0.4 | n |  | TRUE
58 | bus_LV_115-16_0_6_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_115-16_0_6_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_115-16_0_6_node_23 | 0.4 | n |  | TRUE
61 | bus_LV_115-16_0_6_node_119 | 0.4 | n |  | TRUE
62 | bus_LV_115-16_0_6_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_115-16_0_6_node_128 | 0.4 | n |  | TRUE
64 | bus_LV_115-16_0_6_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_115-16_0_6_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_115-16_0_6_node_125 | 0.4 | n |  | TRUE
67 | bus_LV_115-16_0_6_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_115-16_0_6_node_32 | 0.4 | n |  | TRUE
69 | bus_LV_115-16_0_6_node_117 | 0.4 | n |  | TRUE
70 | bus_LV_115-16_0_6_node_118 | 0.4 | n |  | TRUE
71 | bus_LV_115-16_0_6_node_114 | 0.4 | n |  | TRUE
72 | bus_LV_115-16_0_6_node_28 | 0.4 | n |  | TRUE
73 | bus_LV_115-16_0_6_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_115-16_0_6_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_115-16_0_6_node_25 | 0.4 | n |  | TRUE
76 | bus_LV_115-16_0_6_node_26 | 0.4 | n |  | TRUE
77 | bus_LV_115-16_0_6_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_115-16_0_6_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_115-16_0_6_node_120 | 0.4 | n |  | TRUE
80 | bus_LV_115-16_0_6_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_115-16_0_6_node_33 | 0.4 | n |  | TRUE
82 | bus_LV_115-16_0_6_node_34 | 0.4 | n |  | TRUE
83 | bus_LV_115-16_0_6_node_35 | 0.4 | n |  | TRUE
84 | bus_LV_115-16_0_6_node_36 | 0.4 | n |  | TRUE
85 | bus_LV_115-16_0_6_node_37 | 0.4 | n |  | TRUE
86 | bus_LV_115-16_0_6_node_45 | 0.4 | n |  | TRUE
87 | bus_LV_115-16_0_6_node_63 | 0.4 | n |  | TRUE
88 | bus_LV_115-16_0_6_node_39 | 0.4 | n |  | TRUE
89 | bus_LV_115-16_0_6_node_41 | 0.4 | n |  | TRUE
90 | bus_LV_115-16_0_6_node_43 | 0.4 | n |  | TRUE
91 | bus_LV_115-16_0_6_node_61 | 0.4 | n |  | TRUE
92 | bus_LV_115-16_0_6_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_115-16_0_6_node_51 | 0.4 | n |  | TRUE
94 | bus_LV_115-16_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_115-16_0_6_node_62 | 0.4 | n |  | TRUE
96 | bus_LV_115-16_0_6_node_47 | 0.4 | n |  | TRUE
97 | bus_LV_115-16_0_6_node_50 | 0.4 | n |  | TRUE
98 | bus_LV_115-16_0_6_node_54 | 0.4 | n |  | TRUE
99 | bus_LV_115-16_0_6_node_104 | 0.4 | n |  | TRUE
100 | bus_LV_115-16_0_6_node_77 | 0.4 | n |  | TRUE
101 | bus_LV_115-16_0_6_node_127 | 0.4 | n |  | TRUE
102 | bus_LV_115-16_0_6_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_115-16_0_6_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_115-16_0_6_node_68 | 0.4 | n |  | TRUE
105 | bus_LV_115-16_0_6_node_69 | 0.4 | n |  | TRUE
106 | bus_LV_115-16_0_6_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_115-16_0_6_node_78 | 0.4 | n |  | TRUE
108 | bus_LV_115-16_0_6_node_84 | 0.4 | n |  | TRUE
109 | bus_LV_115-16_0_6_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_115-16_0_6_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_115-16_0_6_node_81 | 0.4 | n |  | TRUE
112 | bus_LV_115-16_0_6_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_115-16_0_6_node_73 | 0.4 | n |  | TRUE
114 | bus_LV_115-16_0_6_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_115-16_0_6_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_115-16_0_6_node_76 | 0.4 | n |  | TRUE
117 | bus_LV_115-16_0_6_node_83 | 0.4 | n |  | TRUE
118 | bus_LV_115-16_0_6_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_115-16_0_6_node_85 | 0.4 | n |  | TRUE
120 | bus_LV_115-16_0_6_node_80 | 0.4 | n |  | TRUE
121 | bus_LV_115-16_0_6_node_86 | 0.4 | n |  | TRUE
122 | bus_LV_115-16_0_6_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_115-16_0_6_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_115-16_0_6_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_115-16_0_6_node_91 | 0.4 | n |  | TRUE
126 | bus_LV_115-16_0_6_node_87 | 0.4 | n |  | TRUE
127 | bus_LV_115-16_0_6_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_115-16_0_6_node_95 | 0.4 | n |  | TRUE
129 | bus_LV_115-16_0_6_node_93 | 0.4 | n |  | TRUE
130 | bus_LV_115-16_0_6_node_96 | 0.4 | n |  | TRUE
131 | bus_LV_115-16_0_6_node_101 | 0.4 | n |  | TRUE
132 | bus_LV_115-16_0_6_node_103 | 0.4 | n |  | TRUE
133 | bus_LV_115-16_0_6_node_134 | 0.4 | n |  | TRUE
134 | bus_LV_115-16_0_6_node_126 | 0.4 | n |  | TRUE
135 | bus_LV_115-16_0_6_node_116 | 0.4 | n |  | TRUE
136 | bus_LV_115-16_0_6_node_132 | 0.4 | n |  | TRUE
137 | bus_LV_115-16_0_6_node_131 | 0.4 | n |  | TRUE
138 | bus_MV_357_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-16_0_6_load_0 | 0 | 0.0043394 | 0.0010876 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-16_0_6_load_1 | 1 | 0.0027569 | 0.00069094 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-16_0_6_load_3 | 2 | 0.0027877 | 0.00069868 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-16_0_6_load_44 | 3 | 0.0021442 | 0.00053738 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-16_0_6_load_60 | 4 | 0.0021442 | 0.00053738 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-16_0_6_load_4 | 5 | 0.0061918 | 0.0015518 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-16_0_6_load_9 | 10 | 0.0022209 | 0.0005566 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-16_0_6_load_29 | 12 | 0.020779 | 0.0052078 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-16_0_6_load_136 | 13 | 0.007655 | 0.0019185 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-16_0_6_load_135 | 14 | 0.0071318 | 0.0017874 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-16_0_6_load_38 | 15 | 0.003782 | 0.00094786 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-16_0_6_load_110 | 19 | 0.0091106 | 0.0022833 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-16_0_6_load_113 | 22 | 0.038925 | 0.0097554 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-16_0_6_load_31 | 23 | 0.012331 | 0.0030905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-16_0_6_load_124 | 24 | 0.015571 | 0.0039024 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-16_0_6_load_30 | 25 | 0.0049145 | 0.0012317 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-16_0_6_load_137 | 26 | 0.005774 | 0.0014471 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-16_0_6_load_133 | 27 | 0.0068826 | 0.0017249 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-16_0_6_load_27 | 28 | 0.0040645 | 0.0010187 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-16_0_6_load_122 | 29 | 0.0043033 | 0.0010785 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-16_0_6_load_141 | 30 | 0.0022249 | 0.0005576 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-16_0_6_load_140 | 31 | 0.0022215 | 0.00055676 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-16_0_6_load_106 | 33 | 0.002598 | 0.00065112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-16_0_6_load_57 | 37 | 0.023897 | 0.0059892 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-16_0_6_load_129 | 38 | 0.0062475 | 0.0015658 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-16_0_6_load_139 | 39 | 0.0023179 | 0.00058093 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-16_0_6_load_138 | 40 | 0.0062907 | 0.0015766 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-16_0_6_load_105 | 41 | 0.022882 | 0.0057348 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-16_0_6_load_88 | 45 | 0.013795 | 0.0034574 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-16_0_6_load_97 | 46 | 0.0087266 | 0.0021871 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-16_0_6_load_14 | 47 | 0.0055795 | 0.0013984 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-16_0_6_load_17 | 50 | 0.013234 | 0.0033168 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-16_0_6_load_24 | 52 | 0.011852 | 0.0029703 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-16_0_6_load_64 | 56 | 0.0012331 | 0.00030905 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-16_0_6_load_46 | 59 | 0.012757 | 0.0031972 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-16_0_6_load_119 | 61 | 0.00016275 | 4.079e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-16_0_6_load_130 | 62 | 0.001636 | 0.00041003 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-16_0_6_load_128 | 63 | 0.0016669 | 0.00041777 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-16_0_6_load_56 | 64 | 0.0027461 | 0.00068825 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-16_0_6_load_125 | 66 | 0.0011413 | 0.00028604 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-16_0_6_load_40 | 67 | 0.001065 | 0.00026693 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-16_0_6_load_117 | 69 | 0.00059324 | 0.00014868 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-16_0_6_load_114 | 71 | 0.0014615 | 0.00036629 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-16_0_6_load_52 | 74 | 0.00057025 | 0.00014292 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-16_0_6_load_25 | 75 | 0.0054503 | 0.001366 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-16_0_6_load_26 | 76 | 0.0045945 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_115-16_0_6_load_121 | 77 | 0.00029328 | 7.3504e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_115-16_0_6_load_53 | 78 | 0.0044876 | 0.0011247 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_115-16_0_6_load_120 | 79 | 0.00036565 | 9.164e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_115-16_0_6_load_115 | 80 | 0.0006572 | 0.00016471 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_115-16_0_6_load_33 | 81 | 0.00030738 | 7.7038e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_115-16_0_6_load_34 | 82 | 0.001995 | 0.00049998 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_115-16_0_6_load_35 | 83 | 0.00060448 | 0.0001515 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_115-16_0_6_load_37 | 85 | 0.00032992 | 8.2685e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_115-16_0_6_load_45 | 86 | 0.00030701 | 7.6944e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_115-16_0_6_load_63 | 87 | 0.0047951 | 0.0012018 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_115-16_0_6_load_39 | 88 | 0.0028431 | 0.00071254 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_115-16_0_6_load_41 | 89 | 0.00075026 | 0.00018803 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_115-16_0_6_load_43 | 90 | 0.0018486 | 0.0004633 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_115-16_0_6_load_61 | 91 | 0.013033 | 0.0032663 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_115-16_0_6_load_79 | 94 | 0.0021442 | 0.00053738 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_115-16_0_6_load_62 | 95 | 0.00045111 | 0.00011306 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_115-16_0_6_load_50 | 97 | 0.017033 | 0.0042689 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_115-16_0_6_load_54 | 98 | 0.0014513 | 0.00036373 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_115-16_0_6_load_104 | 99 | 0.011035 | 0.0027656 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_115-16_0_6_load_127 | 101 | 0.0023205 | 0.00058158 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_115-16_0_6_load_66 | 102 | 0.001924 | 0.00048219 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_115-16_0_6_load_67 | 103 | 0.00097384 | 0.00024407 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_115-16_0_6_load_69 | 105 | 0.00068488 | 0.00017165 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_115-16_0_6_load_71 | 106 | 0.0014317 | 0.00035881 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_115-16_0_6_load_78 | 107 | 0.002142 | 0.00053684 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_115-16_0_6_load_84 | 108 | 0.0026261 | 0.00065816 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_115-16_0_6_load_94 | 109 | 0.0018201 | 0.00045617 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_115-16_0_6_load_92 | 110 | 0.0053763 | 0.0013474 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_115-16_0_6_load_72 | 112 | 0.0024365 | 0.00061065 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_115-16_0_6_load_73 | 113 | 0.0015426 | 0.0003866 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_115-16_0_6_load_74 | 114 | 0.0008026 | 0.00020115 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_115-16_0_6_load_76 | 116 | 0.0026587 | 0.00066633 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_115-16_0_6_load_83 | 117 | 0.00086971 | 0.00021797 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_115-16_0_6_load_85 | 119 | 0.0011835 | 0.0002966 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_115-16_0_6_load_80 | 120 | 0.0028478 | 0.00071372 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_115-16_0_6_load_109 | 123 | 0.0061623 | 0.0015444 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_115-16_0_6_load_107 | 124 | 0.0046 | 0.0011529 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_115-16_0_6_load_87 | 126 | 0.0094978 | 0.0023804 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_115-16_0_6_load_89 | 127 | 0.0046033 | 0.0011537 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_115-16_0_6_load_95 | 128 | 0.0029521 | 0.00073987 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_115-16_0_6_load_93 | 129 | 0.0026909 | 0.00067441 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_115-16_0_6_load_96 | 130 | 0.0099341 | 0.0024897 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_115-16_0_6_load_101 | 131 | 0.0096271 | 0.0024128 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_115-16_0_6_load_103 | 132 | 0.00073249 | 0.00018358 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_115-16_0_6_load_134 | 133 | 0.0057042 | 0.0014296 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_115-16_0_6_load_126 | 134 | 0.012656 | 0.0031718 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_115-16_0_6_load_116 | 135 | 0.00015717 | 3.9391e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_115-16_0_6_load_132 | 136 | 0.0070165 | 0.0017585 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-16_0_6_line_0 |  | 0 | 1 | 0.011549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-16_0_6_line_1 |  | 1 | 2 | 0.013523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-16_0_6_line_2 |  | 2 | 3 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-16_0_6_line_3 |  | 3 | 4 | 0.0075994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-16_0_6_line_4 |  | 4 | 94 | 0.0076007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-16_0_6_line_5 |  | 5 | 6 | 0.0041028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-16_0_6_line_6 |  | 5 | 7 | 0.021796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-16_0_6_line_7 |  | 6 | 8 | 0.017164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-16_0_6_line_8 |  | 6 | 9 | 0.032736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-16_0_6_line_9 |  | 7 | 10 | 0.0017876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-16_0_6_line_10 |  | 7 | 11 | 0.06148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-16_0_6_line_11 |  | 8 | 12 | 0.053119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-16_0_6_line_12 |  | 9 | 13 | 0.026536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-16_0_6_line_13 |  | 9 | 14 | 0.020739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_115-16_0_6_line_14 |  | 11 | 15 | 0.017623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-16_0_6_line_15 |  | 11 | 16 | 0.045214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-16_0_6_line_16 |  | 12 | 25 | 0.018744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-16_0_6_line_17 |  | 13 | 26 | 8.3346e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-16_0_6_line_18 |  | 14 | 27 | 8.8674e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_115-16_0_6_line_19 |  | 15 | 28 | 0.019212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-16_0_6_line_20 |  | 16 | 29 | 0.018087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-16_0_6_line_21 |  | 17 | 18 | 0.017106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-16_0_6_line_22 |  | 17 | 19 | 0.01786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_115-16_0_6_line_23 |  | 18 | 39 | 0.023066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-16_0_6_line_24 |  | 18 | 40 | 0.017666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-16_0_6_line_25 |  | 20 | 21 | 0.021146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-16_0_6_line_26 |  | 20 | 22 | 0.02976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-16_0_6_line_27 |  | 21 | 41 | 0.041527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-16_0_6_line_28 |  | 21 | 42 | 0.021212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-16_0_6_line_29 |  | 23 | 24 | 0.0029899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-16_0_6_line_30 |  | 24 | 51 | 0.042468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-16_0_6_line_31 |  | 25 | 51 | 0.032008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_115-16_0_6_line_32 |  | 26 | 40 | 7.5829e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-16_0_6_line_33 |  | 27 | 137 | 0.018352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_115-16_0_6_line_34 |  | 28 | 76 | 0.0095457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-16_0_6_line_35 |  | 29 | 98 | 0.0037375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-16_0_6_line_36 |  | 30 | 31 | 0.0062088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_115-16_0_6_line_37 |  | 31 | 39 | 0.006337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_115-16_0_6_line_38 |  | 32 | 33 | 0.015527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_115-16_0_6_line_39 |  | 32 | 34 | 0.024249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_115-16_0_6_line_40 |  | 33 | 99 | 0.004996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_115-16_0_6_line_41 |  | 34 | 64 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_115-16_0_6_line_42 |  | 34 | 65 | 0.02288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_115-16_0_6_line_43 |  | 34 | 58 | 0.02818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_115-16_0_6_line_44 |  | 35 | 36 | 0.040977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_115-16_0_6_line_45 |  | 35 | 37 | 0.011463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_115-16_0_6_line_46 |  | 36 | 38 | 0.0063793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_115-16_0_6_line_47 |  | 37 | 64 | 0.02341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_115-16_0_6_line_48 |  | 38 | 133 | 0.0048246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_115-16_0_6_line_49 |  | 41 | 132 | 0.0073664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-16_0_6_line_50 |  | 42 | 131 | 0.019817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_115-16_0_6_line_51 |  | 42 | 130 | 0.016645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-16_0_6_line_52 |  | 43 | 44 | 0.024648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_115-16_0_6_line_53 |  | 43 | 45 | 0.035372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_115-16_0_6_line_54 |  | 44 | 46 | 0.027419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-16_0_6_line_55 |  | 46 | 130 | 0.037115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_115-16_0_6_line_56 |  | 47 | 48 | 0.019737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_115-16_0_6_line_57 |  | 47 | 49 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-16_0_6_line_58 |  | 48 | 50 | 0.025942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-16_0_6_line_59 |  | 48 | 51 | 0.046834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-16_0_6_line_60 |  | 49 | 52 | 0.0241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_115-16_0_6_line_61 |  | 50 | 53 | 0.041746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_115-16_0_6_line_62 |  | 53 | 60 | 0.30264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_115-16_0_6_line_63 |  | 54 | 55 | 0.012113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_115-16_0_6_line_64 |  | 54 | 56 | 0.024141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_115-16_0_6_line_65 |  | 55 | 62 | 0.010004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_115-16_0_6_line_66 |  | 55 | 63 | 0.0077426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_115-16_0_6_line_67 |  | 56 | 58 | 0.021306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_115-16_0_6_line_68 |  | 57 | 58 | 0.007902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_115-16_0_6_line_69 |  | 57 | 59 | 0.028077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_115-16_0_6_line_70 |  | 60 | 61 | 0.30132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_115-16_0_6_line_71 |  | 61 | 70 | 0.095257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_115-16_0_6_line_72 |  | 63 | 101 | 0.005329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_115-16_0_6_line_73 |  | 65 | 66 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_115-16_0_6_line_74 |  | 65 | 67 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_115-16_0_6_line_75 |  | 66 | 92 | 0.019036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_115-16_0_6_line_76 |  | 67 | 88 | 0.027972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_115-16_0_6_line_77 |  | 68 | 69 | 0.094484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_115-16_0_6_line_78 |  | 68 | 70 | 0.32076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_115-16_0_6_line_79 |  | 68 | 71 | 0.019844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_115-16_0_6_line_80 |  | 69 | 79 | 0.019159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_115-16_0_6_line_81 |  | 71 | 80 | 0.014689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_115-16_0_6_line_82 |  | 72 | 73 | 0.005077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_115-16_0_6_line_83 |  | 72 | 74 | 0.016032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_115-16_0_6_line_84 |  | 73 | 77 | 0.015686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_115-16_0_6_line_85 |  | 74 | 78 | 0.02161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_115-16_0_6_line_86 |  | 75 | 76 | 0.026397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_115-16_0_6_line_87 |  | 78 | 98 | 0.029645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_115-16_0_6_line_88 |  | 80 | 135 | 0.0069853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_115-16_0_6_line_89 |  | 81 | 82 | 0.020066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_115-16_0_6_line_90 |  | 81 | 83 | 0.0025559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_115-16_0_6_line_91 |  | 82 | 84 | 0.060965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_115-16_0_6_line_92 |  | 83 | 85 | 0.019232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_115-16_0_6_line_93 |  | 84 | 86 | 0.06379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_115-16_0_6_line_94 |  | 86 | 87 | 0.034098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_115-16_0_6_line_95 |  | 87 | 95 | 0.0018302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_115-16_0_6_line_96 |  | 88 | 89 | 0.004854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_115-16_0_6_line_97 |  | 89 | 90 | 0.0049171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_115-16_0_6_line_98 |  | 90 | 91 | 0.021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_115-16_0_6_line_99 |  | 91 | 93 | 0.011476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_115-16_0_6_line_100 |  | 92 | 104 | 0.00962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_115-16_0_6_line_101 |  | 93 | 95 | 0.0010817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_115-16_0_6_line_102 |  | 93 | 96 | 0.026735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_115-16_0_6_line_103 |  | 94 | 100 | 0.014167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_115-16_0_6_line_104 |  | 96 | 97 | 0.047535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_115-16_0_6_line_105 |  | 99 | 132 | 0.016319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_115-16_0_6_line_106 |  | 100 | 107 | 0.010641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_115-16_0_6_line_107 |  | 100 | 116 | 0.0039957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_115-16_0_6_line_108 |  | 101 | 134 | 0.013075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_115-16_0_6_line_109 |  | 102 | 103 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_115-16_0_6_line_110 |  | 102 | 104 | 0.019889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_115-16_0_6_line_111 |  | 103 | 105 | 0.0014871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_115-16_0_6_line_112 |  | 104 | 106 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_115-16_0_6_line_113 |  | 105 | 107 | 0.0057349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_115-16_0_6_line_114 |  | 106 | 108 | 0.0012276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_115-16_0_6_line_115 |  | 108 | 111 | 0.0098945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_115-16_0_6_line_116 |  | 109 | 110 | 0.010127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_115-16_0_6_line_117 |  | 110 | 129 | 0.0040791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_115-16_0_6_line_118 |  | 111 | 120 | 0.011238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_115-16_0_6_line_119 |  | 112 | 113 | 0.0041913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_115-16_0_6_line_120 |  | 112 | 114 | 0.0031938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_115-16_0_6_line_121 |  | 113 | 115 | 0.0072137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_115-16_0_6_line_122 |  | 114 | 116 | 0.01445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_115-16_0_6_line_123 |  | 115 | 117 | 0.015383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_115-16_0_6_line_124 |  | 118 | 119 | 0.0070041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_115-16_0_6_line_125 |  | 118 | 120 | 0.011244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_115-16_0_6_line_126 |  | 119 | 124 | 0.027314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_115-16_0_6_line_127 |  | 121 | 122 | 0.043766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_115-16_0_6_line_128 |  | 121 | 123 | 0.071537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_115-16_0_6_line_129 |  | 122 | 125 | 0.014932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_115-16_0_6_line_130 |  | 122 | 124 | 0.023759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_115-16_0_6_line_131 |  | 125 | 128 | 0.019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_115-16_0_6_line_132 |  | 125 | 127 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_115-16_0_6_line_133 |  | 126 | 127 | 0.0025866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_115-16_0_6_line_134 |  | 128 | 129 | 0.018208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_115-16_0_6_line_135 |  | 133 | 136 | 0.0051343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_115-16_0_6_line_136 |  | 136 | 137 | 0.017552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-16_0_6_trafo_58 | 0.63 MVA 20/0.4 kV | 138 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2701419.2429 | 1240958.4203 | 2701419.2429 | 1240958.4203 | 2701427.5119 | 1240950.3583
1 | 2701427.5119 | 1240950.3583 | 2701430.2945 | 1240947.6453 | 2701437.9553 | 1240941.7992
2 | 2701437.9553 | 1240941.7992 | 2701445.7576 | 1240935.845 | 2701452.5987 | 1240930.9948
3 | 2701458.7982 | 1240926.5996 | 2701452.5987 | 1240930.9948
4 | 2701464.9986 | 1240922.2036 | 2701458.7982 | 1240926.5996
5 | 2701402.3185 | 1240686.2895 | 2701405.3267 | 1240683.4996
6 | 2701421.3076 | 1240668.6782 | 2701405.3267 | 1240683.4996
7 | 2701389.7081 | 1240697.972 | 2701399.6212 | 1240688.7898 | 2701402.3185 | 1240686.2895
8 | 2701401.9179 | 1240719.0189 | 2701402.3185 | 1240686.2895
9 | 2701421.3076 | 1240668.6782 | 2701422.6184 | 1240667.4628
10 | 2701379.4915 | 1240639.5083 | 2701388.4978 | 1240631.6117 | 2701421.3076 | 1240668.6782
11 | 2701389.7081 | 1240697.972 | 2701366.5103 | 1240696.7861 | 2701344.8004 | 1240717.3325
12 | 2701401.9179 | 1240719.0189 | 2701403.3498 | 1240717.987 | 2701428.1197 | 1240718.2617
13 | 2701401.9179 | 1240719.0189 | 2701398.4702 | 1240718.9599 | 2701396.7782 | 1240720.1653 | 2701396.467 | 1240735.3754
14 | 2701379.4915 | 1240639.5083 | 2701366.8185 | 1240651.7549
15 | 2701379.4915 | 1240639.5083 | 2701348.7639 | 1240606.2583
16 | 2701344.8004 | 1240717.3325 | 2701331.5874 | 1240729.8374 | 2701331.3289 | 1240730.3254
17 | 2701428.2031 | 1240718.2627 | 2701428.1197 | 1240718.2617
18 | 2701396.467 | 1240735.3754 | 2701396.4652 | 1240735.464
19 | 2701366.8185 | 1240651.7549 | 2701358.3364 | 1240659.9516 | 2701352.8756 | 1240664.9705
20 | 2701348.7639 | 1240606.2583 | 2701335.8206 | 1240618.892
21 | 2701452.3812 | 1240727.1984 | 2701445.8641 | 1240728.8438 | 2701445.9434 | 1240718.4595
22 | 2701452.3812 | 1240727.1984 | 2701470.1801 | 1240725.7262
23 | 2701445.9434 | 1240718.4595 | 2701446.1134 | 1240695.394
24 | 2701445.9434 | 1240718.4595 | 2701428.2789 | 1240718.2635
25 | 2701528.3235 | 1240742.0191 | 2701524.3144 | 1240752.225 | 2701518.7608 | 1240760.7699
26 | 2701528.3235 | 1240742.0191 | 2701499.8002 | 1240733.5277
27 | 2701518.7608 | 1240760.7699 | 2701488.3319 | 1240789.0292
28 | 2701518.7608 | 1240760.7699 | 2701533.1962 | 1240776.351
29 | 2701379.3514 | 1240754.4728 | 2701377.1104 | 1240756.4521
30 | 2701342.446 | 1240756.4987 | 2701347.6486 | 1240757.8663 | 2701360.2619 | 1240767.6892 | 2701364.3836 | 1240767.6929 | 2701377.1104 | 1240756.4521
31 | 2701342.446 | 1240756.4987 | 2701329.6628 | 1240742.4475 | 2701328.313 | 1240736.0196 | 2701331.3289 | 1240730.3254
32 | 2701428.2789 | 1240718.2635 | 2701428.2031 | 1240718.2627
33 | 2701396.0897 | 1240753.8126 | 2701396.4652 | 1240735.464
34 | 2701345.8474 | 1240671.43 | 2701352.8756 | 1240664.9705
35 | 2701335.8206 | 1240618.892 | 2701334.612 | 1240620.0717 | 2701336.039 | 1240621.5416 | 2701336.039 | 1240621.5416
36 | 2701446.1601 | 1240689.0572 | 2701446.2058 | 1240682.8486
37 | 2701446.1601 | 1240689.0572 | 2701446.1134 | 1240695.394
38 | 2701453.7796 | 1240816.5685 | 2701466.0544 | 1240807.0604
39 | 2701453.7796 | 1240816.5685 | 2701454.3737 | 1240823.395 | 2701453.3321 | 1240830.7939 | 2701444.7816 | 1240825.7551
40 | 2701466.0544 | 1240807.0604 | 2701470.0041 | 1240804.001
41 | 2701444.7816 | 1240825.7551 | 2701447.7851 | 1240823.0377 | 2701448.709 | 1240819.8732 | 2701448.4288 | 1240811.0506 | 2701448.2321 | 1240809.1027
42 | 2701444.7816 | 1240825.7551 | 2701453.3321 | 1240830.7939 | 2701450.9589 | 1240843.5298
43 | 2701421.4967 | 1240825.268 | 2701426.3395 | 1240828.2085 | 2701429.0816 | 1240823.9743 | 2701434.0187 | 1240826.7052 | 2701436.7145 | 1240827.8299 | 2701439.6307 | 1240828.4469 | 2701442.4658 | 1240827.6169 | 2701444.7816 | 1240825.7551
44 | 2701428.9388 | 1240749.615 | 2701439.4786 | 1240749.773 | 2701439.1243 | 1240774.4747 | 2701444.8556 | 1240774.5505
45 | 2701444.8556 | 1240774.5505 | 2701444.5992 | 1240786.0104
46 | 2701428.9388 | 1240749.615 | 2701422.5601 | 1240749.5241
47 | 2701448.2321 | 1240809.1027 | 2701447.103 | 1240797.9179 | 2701444.5992 | 1240786.0104
48 | 2701422.5601 | 1240749.5241 | 2701417.736 | 1240749.4553
49 | 2701482.9051 | 1240794.0078 | 2701483.3025 | 1240793.7 | 2701488.3319 | 1240789.0292
50 | 2701518.9906 | 1240790.2075 | 2701533.1962 | 1240776.351
51 | 2701533.1962 | 1240776.351 | 2701545.0355 | 1240764.6516
52 | 2701603.2149 | 1240743.9908 | 2701594.2217 | 1240731.2382 | 2701593.0596 | 1240722.2559
53 | 2701603.2149 | 1240743.9908 | 2701600.618 | 1240745.9256 | 2701605.7812 | 1240753.1194 | 2701604.542 | 1240760.5595 | 2701592.1776 | 1240770.2934
54 | 2701593.0596 | 1240722.2559 | 2701572.8752 | 1240740.8141
55 | 2701545.0355 | 1240764.6516 | 2701558.183 | 1240751.6594 | 2701562.3089 | 1240750.5292 | 2701572.8752 | 1240740.8141
56 | 2701309.0763 | 1240758.4195 | 2701295.8104 | 1240773.0328
57 | 2701284.3463 | 1240781.4263 | 2701293.8379 | 1240775.2057 | 2701295.8104 | 1240773.0328
58 | 2701309.0763 | 1240758.4195 | 2701290.5842 | 1240740.2257
59 | 2701309.0763 | 1240758.4195 | 2701312.8008 | 1240754.2243 | 2701318.6095 | 1240747.9964 | 2701323.2737 | 1240752.5462 | 2701335.0746 | 1240763.4448 | 2701342.446 | 1240756.4987
60 | 2701284.3463 | 1240781.4263 | 2701267.1114 | 1240764.5805
61 | 2701263.4851 | 1240708.5035 | 2701275.2869 | 1240722.4599 | 2701286.7403 | 1240736.4438 | 2701290.5842 | 1240740.2257
62 | 2701053.2773 | 1240884.1671 | 2701132.1587 | 1240810.3539 | 2701196 | 1240740.5106 | 2701220.0351 | 1240708.1289 | 2701232.8594 | 1240688.7661 | 2701263.4851 | 1240708.5035
63 | 2701390.8085 | 1240790.6728 | 2701383.4964 | 1240800.3443
64 | 2701383.4964 | 1240800.3443 | 2701403.6006 | 1240813.7096
65 | 2701390.8085 | 1240790.6728 | 2701382.7287 | 1240784.7741
66 | 2701390.8085 | 1240790.6728 | 2701394.0534 | 1240786.2249 | 2701396.1257 | 1240785.383
67 | 2701421.4967 | 1240825.268 | 2701412.9215 | 1240819.9063 | 2701403.6006 | 1240813.7096
68 | 2701414.7627 | 1240829.4339 | 2701421.4967 | 1240825.268
69 | 2701414.7627 | 1240829.4339 | 2701391.6575 | 1240845.3866
70 | 2701053.2773 | 1240884.1671 | 2701027.7356 | 1240851.4629 | 2701017.825 | 1240838.3398 | 2701005.1943 | 1240842.3946 | 2700983.6719 | 1240847.6659 | 2700940.2369 | 1240853.1425 | 2700920.8535 | 1240851.823 | 2700811.4783 | 1240830.6819 | 2700778.8491 | 1240823.8077
71 | 2700685.6386 | 1240804.1705 | 2700778.8491 | 1240823.8077
72 | 2701401.0629 | 1240783.3774 | 2701396.1257 | 1240785.383
73 | 2701450.9589 | 1240843.5298 | 2701468.285 | 1240853.9065
74 | 2701450.9589 | 1240843.5298 | 2701449.1826 | 1240848.7813 | 2701442.6816 | 1240855.6866 | 2701442.6816 | 1240855.6866
75 | 2701484.6161 | 1240863.6872 | 2701468.285 | 1240853.9065
76 | 2701442.6816 | 1240855.6866 | 2701417.4598 | 1240867.7808
77 | 2700894.6106 | 1240662.8659 | 2700965.5823 | 1240626.3557 | 2700977.6458 | 1240618.0048
78 | 2700894.6106 | 1240662.8659 | 2700881.6407 | 1240667.727 | 2700820.3089 | 1240655.0644 | 2700791.5451 | 1240648.5043 | 2700763.5659 | 1240637.5988 | 2700711.2984 | 1240733.3739 | 2700698.2027 | 1240760.8171 | 2700689.1402 | 1240786.7944 | 2700685.6386 | 1240804.1705
79 | 2700894.6106 | 1240662.8659 | 2700892.867 | 1240643.099 | 2700892.867 | 1240643.099
80 | 2700977.6458 | 1240618.0048 | 2700987.5622 | 1240611.1402 | 2700991.9428 | 1240605.5548
81 | 2700892.867 | 1240643.099 | 2700886.6041 | 1240629.8122
82 | 2701283.0494 | 1240662.9246 | 2701286.4334 | 1240666.7186
83 | 2701286.4334 | 1240666.7186 | 2701298.3678 | 1240656.0142
84 | 2701283.0494 | 1240662.9246 | 2701271.695 | 1240673.7478
85 | 2701298.3678 | 1240656.0142 | 2701313.4537 | 1240642.4833 | 2701314.3153 | 1240641.4501
86 | 2701345.8474 | 1240671.43 | 2701326.4121 | 1240689.2926
87 | 2701314.3153 | 1240641.4501 | 2701318.5187 | 1240636.4095 | 2701323.907 | 1240633.1101 | 2701336.039 | 1240621.5416
88 | 2700883.6257 | 1240623.4936 | 2700886.6041 | 1240629.8122
89 | 2701338.8799 | 1240962.2503 | 2701351.9762 | 1240951.1993 | 2701350.4719 | 1240948.6852
90 | 2701349.1596 | 1240946.4919 | 2701350.4719 | 1240948.6852
91 | 2701293.2913 | 1240938.7548 | 2701298.3541 | 1240946.9697 | 2701320.9106 | 1240967.4926 | 2701325.5537 | 1240969.2843 | 2701330.7292 | 1240969.1281 | 2701338.8799 | 1240962.2503
92 | 2701339.2855 | 1240929.9887 | 2701349.1596 | 1240946.4919
93 | 2701293.2913 | 1240938.7548 | 2701341.3665 | 1240909.1082 | 2701347.6135 | 1240905.3146
94 | 2701347.6135 | 1240905.3146 | 2701376.7587 | 1240887.6155
95 | 2701376.7587 | 1240887.6155 | 2701378.323 | 1240886.6655
96 | 2701413.083 | 1240869.8795 | 2701417.4598 | 1240867.7808
97 | 2701408.6492 | 1240872.0056 | 2701413.083 | 1240869.8795
98 | 2701389.5958 | 1240881.1419 | 2701408.6492 | 1240872.0056
99 | 2701379.2476 | 1240886.104 | 2701389.5958 | 1240881.1419
100 | 2701484.6161 | 1240863.6872 | 2701492.9894 | 1240868.4673
101 | 2701379.2476 | 1240886.104 | 2701378.323 | 1240886.6655
102 | 2701359.6623 | 1240867.8445 | 2701379.2476 | 1240886.104
103 | 2701476.5555 | 1240914.0102 | 2701464.9986 | 1240922.2036
104 | 2701359.6623 | 1240867.8445 | 2701342.9947 | 1240852.3147 | 2701359.1671 | 1240833.5741
105 | 2701482.9051 | 1240794.0078 | 2701470.0041 | 1240804.001
106 | 2701476.5555 | 1240914.0102 | 2701476.1065 | 1240903.3784
107 | 2701476.5555 | 1240914.0102 | 2701480.4013 | 1240912.9261
108 | 2701413.1763 | 1240778.4567 | 2701413.1763 | 1240778.4567 | 2701401.0629 | 1240783.3774
109 | 2701479.8584 | 1240883.4059 | 2701475.4736 | 1240888.3943 | 2701475.8017 | 1240896.1628
110 | 2701492.9894 | 1240868.4673 | 2701479.8584 | 1240883.4059
111 | 2701475.8017 | 1240896.1628 | 2701475.8645 | 1240897.6486
112 | 2701492.9894 | 1240868.4673 | 2701503.7728 | 1240872.4992 | 2701504.9997 | 1240872.7626
113 | 2701476.1065 | 1240903.3784 | 2701475.8645 | 1240897.6486
114 | 2701504.9997 | 1240872.7626 | 2701506.1999 | 1240873.0203
115 | 2701515.874 | 1240875.097 | 2701506.1999 | 1240873.0203
116 | 2701516.1652 | 1240833.6118 | 2701508.5812 | 1240840.3235
117 | 2701516.1652 | 1240833.6118 | 2701519.2199 | 1240830.9085
118 | 2701515.874 | 1240875.097 | 2701526.8814 | 1240877.3642
119 | 2701497.4979 | 1240908.6659 | 2701501.6387 | 1240908.0168
120 | 2701497.4979 | 1240908.6659 | 2701494.3426 | 1240909.1604
121 | 2701508.7654 | 1240906.8998 | 2701501.6387 | 1240908.0168
122 | 2701480.4013 | 1240912.9261 | 2701493.0307 | 1240909.366 | 2701494.3426 | 1240909.1604
123 | 2701508.7654 | 1240906.8998 | 2701506.9535 | 1240893.4585 | 2701507.0139 | 1240891.6392
124 | 2701537.8946 | 1240879.6326 | 2701539.4376 | 1240872.8006
125 | 2701537.8946 | 1240879.6326 | 2701526.8814 | 1240877.3642
126 | 2701539.4376 | 1240872.8006 | 2701544.7845 | 1240849.1271 | 2701546.2692 | 1240846.4699
127 | 2701560.8346 | 1240828.2523 | 2701600.3878 | 1240847.2326
128 | 2701600.3878 | 1240847.2326 | 2701617.4181 | 1240810.2068 | 2701633.484 | 1240784.8958 | 2701633.9149 | 1240784.2175
129 | 2701560.8346 | 1240828.2523 | 2701556.2688 | 1240822.8256 | 2701551.1066 | 1240816.8995
130 | 2701560.8346 | 1240828.2523 | 2701552.914 | 1240834.5773 | 2701546.2692 | 1240846.4699
131 | 2701551.1066 | 1240816.8995 | 2701546.394 | 1240814.3058 | 2701540.259 | 1240815.7241 | 2701533.463 | 1240819.682
132 | 2701551.1066 | 1240816.8995 | 2701555.4383 | 1240811.2581 | 2701561.6212 | 1240803.1159
133 | 2701563.1854 | 1240801.056 | 2701561.6212 | 1240803.1159
134 | 2701519.2199 | 1240830.9085 | 2701528.9076 | 1240822.335 | 2701533.463 | 1240819.682
135 | 2701417.736 | 1240749.4553 | 2701412.6022 | 1240749.3821
136 | 2701396.0897 | 1240753.8126 | 2701405.4619 | 1240749.2803 | 2701412.6022 | 1240749.3821

## bus_geodata
| x | y | coords
0 | 2701419.2429 | 1240958.4203
1 | 2701427.5119 | 1240950.3583
2 | 2701437.9553 | 1240941.7992
3 | 2701452.5987 | 1240930.9948
4 | 2701458.7982 | 1240926.5996
5 | 2701405.3267 | 1240683.4996
6 | 2701402.3185 | 1240686.2895
7 | 2701421.3076 | 1240668.6782
8 | 2701389.7081 | 1240697.972
9 | 2701401.9179 | 1240719.0189
10 | 2701422.6184 | 1240667.4628
11 | 2701379.4915 | 1240639.5083
12 | 2701344.8004 | 1240717.3325
13 | 2701428.1197 | 1240718.2617
14 | 2701396.467 | 1240735.3754
15 | 2701366.8185 | 1240651.7549
16 | 2701348.7639 | 1240606.2583
17 | 2701452.3812 | 1240727.1984
18 | 2701445.9434 | 1240718.4595
19 | 2701470.1801 | 1240725.7262
20 | 2701528.3235 | 1240742.0191
21 | 2701518.7608 | 1240760.7699
22 | 2701499.8002 | 1240733.5277
23 | 2701379.3514 | 1240754.4728
24 | 2701377.1104 | 1240756.4521
25 | 2701331.3289 | 1240730.3254
26 | 2701428.2031 | 1240718.2627
27 | 2701396.4652 | 1240735.464
28 | 2701352.8756 | 1240664.9705
29 | 2701335.8206 | 1240618.892
30 | 2701446.2058 | 1240682.8486
31 | 2701446.1601 | 1240689.0572
32 | 2701453.7796 | 1240816.5685
33 | 2701466.0544 | 1240807.0604
34 | 2701444.7816 | 1240825.7551
35 | 2701444.8556 | 1240774.5505
36 | 2701428.9388 | 1240749.615
37 | 2701444.5991 | 1240786.0104
38 | 2701422.5601 | 1240749.5241
39 | 2701446.1134 | 1240695.394
40 | 2701428.2789 | 1240718.2635
41 | 2701488.3319 | 1240789.0292
42 | 2701533.1962 | 1240776.3509
43 | 2701603.2149 | 1240743.9908
44 | 2701593.0596 | 1240722.2559
45 | 2701592.1776 | 1240770.2934
46 | 2701572.8752 | 1240740.8141
47 | 2701295.8104 | 1240773.0328
48 | 2701309.0763 | 1240758.4195
49 | 2701284.3463 | 1240781.4263
50 | 2701290.5842 | 1240740.2257
51 | 2701342.446 | 1240756.4987
52 | 2701267.1114 | 1240764.5805
53 | 2701263.4851 | 1240708.5035
54 | 2701383.4964 | 1240800.3443
55 | 2701390.8085 | 1240790.6728
56 | 2701403.6006 | 1240813.7096
57 | 2701414.7627 | 1240829.4339
58 | 2701421.4967 | 1240825.268
59 | 2701391.6575 | 1240845.3866
60 | 2701053.2773 | 1240884.1671
61 | 2700778.8491 | 1240823.8077
62 | 2701382.7287 | 1240784.7741
63 | 2701396.1257 | 1240785.383
64 | 2701448.2321 | 1240809.1027
65 | 2701450.9589 | 1240843.5298
66 | 2701468.285 | 1240853.9065
67 | 2701442.6816 | 1240855.6866
68 | 2700894.6106 | 1240662.8659
69 | 2700977.6458 | 1240618.0048
70 | 2700685.6386 | 1240804.1705
71 | 2700892.867 | 1240643.099
72 | 2701286.4334 | 1240666.7186
73 | 2701283.0494 | 1240662.9246
74 | 2701298.3678 | 1240656.0142
75 | 2701326.4121 | 1240689.2926
76 | 2701345.8474 | 1240671.43
77 | 2701271.695 | 1240673.7478
78 | 2701314.3153 | 1240641.4501
79 | 2700991.9428 | 1240605.5548
80 | 2700886.6041 | 1240629.8122
81 | 2701350.4719 | 1240948.6852
82 | 2701338.8799 | 1240962.2503
83 | 2701349.1596 | 1240946.4919
84 | 2701293.2913 | 1240938.7548
85 | 2701339.2855 | 1240929.9887
86 | 2701347.6135 | 1240905.3146
87 | 2701376.7587 | 1240887.6155
88 | 2701417.4598 | 1240867.7808
89 | 2701413.0829 | 1240869.8795
90 | 2701408.6492 | 1240872.0056
91 | 2701389.5958 | 1240881.1419
92 | 2701484.6161 | 1240863.6872
93 | 2701379.2476 | 1240886.104
94 | 2701464.9986 | 1240922.2036
95 | 2701378.323 | 1240886.6655
96 | 2701359.6623 | 1240867.8445
97 | 2701359.1671 | 1240833.5741
98 | 2701336.039 | 1240621.5416
99 | 2701470.0041 | 1240804.001
100 | 2701476.5555 | 1240914.0102
101 | 2701401.0629 | 1240783.3774
102 | 2701479.8584 | 1240883.4059
103 | 2701475.8017 | 1240896.1628
104 | 2701492.9894 | 1240868.4673
105 | 2701475.8645 | 1240897.6486
106 | 2701504.9997 | 1240872.7626
107 | 2701476.1065 | 1240903.3784
108 | 2701506.1999 | 1240873.0203
109 | 2701508.5812 | 1240840.3235
110 | 2701516.1652 | 1240833.6118
111 | 2701515.874 | 1240875.097
112 | 2701497.4979 | 1240908.6659
113 | 2701501.6387 | 1240908.0168
114 | 2701494.3426 | 1240909.1604
115 | 2701508.7654 | 1240906.8998
116 | 2701480.4013 | 1240912.9261
117 | 2701507.0139 | 1240891.6392
118 | 2701537.8946 | 1240879.6326
119 | 2701539.4376 | 1240872.8006
120 | 2701526.8814 | 1240877.3642
121 | 2701600.3878 | 1240847.2326
122 | 2701560.8346 | 1240828.2524
123 | 2701633.9149 | 1240784.2175
124 | 2701546.2692 | 1240846.4699
125 | 2701551.1066 | 1240816.8995
126 | 2701563.1854 | 1240801.056
127 | 2701561.6212 | 1240803.1159
128 | 2701533.463 | 1240819.682
129 | 2701519.2199 | 1240830.9085
130 | 2701545.0355 | 1240764.6516
131 | 2701518.9906 | 1240790.2075
132 | 2701482.9051 | 1240794.0078
133 | 2701417.736 | 1240749.4553
134 | 2701413.1763 | 1240778.4567
135 | 2700883.6257 | 1240623.4936
136 | 2701412.6022 | 1240749.3821
137 | 2701396.0897 | 1240753.8126
138 | 2701439.4787 | 1240749.773

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98662 | -0.25709 | 0.0043394 | 0.0010876
1 | 0.98667 | -0.25619 | 0.0027569 | 0.00069094
2 | 0.98675 | -0.25448 | 0.0027877 | 0.00069868
3 | 0.98692 | -0.25126 | 0.0021442 | 0.00053738
4 | 0.987 | -0.24962 | 0.0021442 | 0.00053738
5 | 0.98923 | -0.20585 | 0.0061918 | 0.0015518
6 | 0.98937 | -0.20311 | 0 | 0
7 | 0.98861 | -0.21798 | 0 | 0
8 | 0.98798 | -0.22995 | 0 | 0
9 | 0.99316 | -0.13045 | 0 | 0
10 | 0.9886 | -0.21805 | 0.0022209 | 0.0005566
11 | 0.98697 | -0.24983 | 0 | 0
12 | 0.98367 | -0.31351 | 0.020779 | 0.0052078
13 | 0.99229 | -0.14716 | 0.007655 | 0.0019185
14 | 0.99469 | -0.10105 | 0.0071318 | 0.0017874
15 | 0.98668 | -0.25547 | 0.003782 | 0.00094786
16 | 0.98651 | -0.25882 | 0 | 0
17 | 0.99189 | -0.15496 | 0 | 0
18 | 0.99203 | -0.1522 | 0 | 0
19 | 0.99174 | -0.15784 | 0.0091106 | 0.0022833
20 | 0.98368 | -0.31394 | 0 | 0
21 | 0.98443 | -0.29913 | 0 | 0
22 | 0.98261 | -0.33483 | 0.038925 | 0.0097554
23 | 0.97954 | -0.3942 | 0.012331 | 0.0030905
24 | 0.97958 | -0.39353 | 0.015571 | 0.0039024
25 | 0.98251 | -0.33613 | 0.0049145 | 0.0012317
26 | 0.99229 | -0.1472 | 0.005774 | 0.0014471
27 | 0.9947 | -0.10096 | 0.0068826 | 0.0017249
28 | 0.98643 | -0.26033 | 0.0040645 | 0.0010187
29 | 0.98632 | -0.26242 | 0.0043033 | 0.0010785
30 | 0.99185 | -0.15571 | 0.0022249 | 0.0005576
31 | 0.99187 | -0.15546 | 0.0022215 | 0.00055676
32 | 0.99204 | -0.15187 | 0 | 0
33 | 0.99035 | -0.18444 | 0.002598 | 0.00065112
34 | 0.99469 | -0.10121 | 0 | 0
35 | 1 | 0 | -0.50101 | -0.1274
36 | 0.99757 | -0.046231 | 0 | 0
37 | 0.99895 | -0.019991 | 0.023897 | 0.0059892
38 | 0.99719 | -0.053448 | 0.0062475 | 0.0015658
39 | 0.99189 | -0.15496 | 0.0023179 | 0.00058093
40 | 0.99229 | -0.14723 | 0.0062907 | 0.0015766
41 | 0.98754 | -0.23881 | 0.022882 | 0.0057348
42 | 0.98361 | -0.3152 | 0 | 0
43 | 0.98168 | -0.35301 | 0 | 0
44 | 0.98199 | -0.34686 | 0 | 0
45 | 0.98123 | -0.36184 | 0.013795 | 0.0034574
46 | 0.98234 | -0.34002 | 0.0087266 | 0.0021871
47 | 0.97888 | -0.40728 | 0.0055795 | 0.0013984
48 | 0.9792 | -0.40103 | 0 | 0
49 | 0.97872 | -0.41036 | 0 | 0
50 | 0.9788 | -0.40889 | 0.013234 | 0.0033168
51 | 0.98068 | -0.37203 | 0 | 0
52 | 0.97846 | -0.41556 | 0.011852 | 0.0029703
53 | 0.97867 | -0.4115 | 0 | 0
54 | 0.99308 | -0.13238 | 0 | 0
55 | 0.99287 | -0.1363 | 0 | 0
56 | 0.99348 | -0.12459 | 0.0012331 | 0.00030905
57 | 0.99377 | -0.11903 | 0 | 0
58 | 0.99386 | -0.11725 | 0 | 0
59 | 0.99344 | -0.12535 | 0.012757 | 0.0031972
60 | 0.97771 | -0.43041 | 0 | 0
61 | 0.97676 | -0.44922 | 0.00016275 | 4.079e-05
62 | 0.99286 | -0.13659 | 0.001636 | 0.00041003
63 | 0.99276 | -0.13858 | 0.0016669 | 0.00041777
64 | 0.99697 | -0.057678 | 0.0027461 | 0.00068825
65 | 0.99211 | -0.15079 | 0 | 0
66 | 0.99067 | -0.17847 | 0.0011413 | 0.00028604
67 | 0.99148 | -0.16287 | 0.001065 | 0.00026693
68 | 0.97551 | -0.47393 | 0 | 0
69 | 0.97543 | -0.47559 | 0.00059324 | 0.00014868
70 | 0.97648 | -0.45488 | 0 | 0
71 | 0.97547 | -0.47476 | 0.0014615 | 0.00036629
72 | 0.98613 | -0.26614 | 0 | 0
73 | 0.98613 | -0.26617 | 0 | 0
74 | 0.98614 | -0.26606 | 0.00057025 | 0.00014292
75 | 0.98621 | -0.26462 | 0.0054503 | 0.001366
76 | 0.98634 | -0.26205 | 0.0045945 | 0.0011515
77 | 0.98613 | -0.26625 | 0.00029328 | 7.3504e-05
78 | 0.98615 | -0.26572 | 0.0044876 | 0.0011247
79 | 0.97542 | -0.47572 | 0.00036565 | 9.164e-05
80 | 0.97546 | -0.47497 | 0.0006572 | 0.00016471
81 | 0.98843 | -0.22216 | 0.00030738 | 7.7038e-05
82 | 0.98845 | -0.22171 | 0.001995 | 0.00049998
83 | 0.98843 | -0.2222 | 0.00060448 | 0.0001515
84 | 0.98863 | -0.21819 | 0 | 0
85 | 0.98842 | -0.22231 | 0.00032992 | 8.2685e-05
86 | 0.98882 | -0.2145 | 0.00030701 | 7.6944e-05
87 | 0.98893 | -0.21234 | 0.0047951 | 0.0012018
88 | 0.99035 | -0.18487 | 0.0028431 | 0.00071254
89 | 0.99016 | -0.18845 | 0.00075026 | 0.00018803
90 | 0.98998 | -0.192 | 0.0018486 | 0.0004633
91 | 0.98923 | -0.20662 | 0.013033 | 0.0032663
92 | 0.98934 | -0.20425 | 0 | 0
93 | 0.98895 | -0.2119 | 0 | 0
94 | 0.9871 | -0.24769 | 0.0021442 | 0.00053738
95 | 0.98895 | -0.21207 | 0.00045111 | 0.00011306
96 | 0.98854 | -0.22002 | 0 | 0
97 | 0.98779 | -0.23448 | 0.017033 | 0.0042689
98 | 0.9863 | -0.26288 | 0.0014513 | 0.00036373
99 | 0.98982 | -0.19472 | 0.011035 | 0.0027656
100 | 0.98732 | -0.24356 | 0 | 0
101 | 0.99268 | -0.13999 | 0.0023205 | 0.00058158
102 | 0.98811 | -0.22808 | 0.001924 | 0.00048219
103 | 0.98773 | -0.2354 | 0.00097384 | 0.00024407
104 | 0.98867 | -0.21731 | 0 | 0
105 | 0.9877 | -0.23613 | 0.00068488 | 0.00017165
106 | 0.98813 | -0.22774 | 0.0014317 | 0.00035881
107 | 0.98756 | -0.23887 | 0.002142 | 0.00053684
108 | 0.98808 | -0.22871 | 0.0026261 | 0.00065816
109 | 0.98413 | -0.3056 | 0.0018201 | 0.00045617
110 | 0.98414 | -0.30527 | 0.0053763 | 0.0013474
111 | 0.9877 | -0.23609 | 0 | 0
112 | 0.9872 | -0.24589 | 0.0024365 | 0.00061065
113 | 0.98719 | -0.24607 | 0.0015426 | 0.0003866
114 | 0.98721 | -0.24561 | 0.0008026 | 0.00020115
115 | 0.98718 | -0.24618 | 0 | 0
116 | 0.98729 | -0.24415 | 0.0026587 | 0.00066633
117 | 0.98717 | -0.24642 | 0.00086971 | 0.00021797
118 | 0.98686 | -0.2523 | 0 | 0
119 | 0.98661 | -0.25717 | 0.0011835 | 0.0002966
120 | 0.98727 | -0.24447 | 0.0028478 | 0.00071372
121 | 0.98469 | -0.29461 | 0 | 0
122 | 0.98494 | -0.28976 | 0 | 0
123 | 0.98428 | -0.30254 | 0.0061623 | 0.0015444
124 | 0.98566 | -0.27564 | 0.0046 | 0.0011529
125 | 0.98457 | -0.29699 | 0 | 0
126 | 0.98432 | -0.30183 | 0.0094978 | 0.0023804
127 | 0.98434 | -0.30139 | 0.0046033 | 0.0011537
128 | 0.98434 | -0.3015 | 0.0029521 | 0.00073987
129 | 0.98417 | -0.30474 | 0.0026909 | 0.00067441
130 | 0.98311 | -0.32494 | 0.0099341 | 0.0024897
131 | 0.98343 | -0.31863 | 0.0096271 | 0.0024128
132 | 0.98825 | -0.22514 | 0.00073249 | 0.00018358
133 | 0.99691 | -0.058734 | 0.0057042 | 0.0014296
134 | 0.99253 | -0.14292 | 0.012656 | 0.0031718
135 | 0.97546 | -0.475 | 0.00015717 | 3.9391e-05
136 | 0.99662 | -0.064191 | 0.0070165 | 0.0017585
137 | 0.99568 | -0.082148 | 0 | 0
138 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0043394 | -0.0010876 | 0.0043396 | 0.0010875 | 1.855e-07 | -2.8773e-08 | 0.0065447 | 0.0065446 | 0.0065447 | 0.98662 | -0.25709 | 0.98667 | -0.25619 | 1.798
1 | -0.0070965 | -0.0017785 | 0.007097 | 0.0017787 | 5.8083e-07 | 1.9901e-07 | 0.010702 | 0.010702 | 0.010702 | 0.98667 | -0.25619 | 0.98675 | -0.25448 | 2.9402
2 | -0.0098848 | -0.0024773 | 0.0098863 | 0.0024781 | 1.5165e-06 | 7.3804e-07 | 0.014906 | 0.014906 | 0.014906 | 0.98675 | -0.25448 | 0.98692 | -0.25126 | 4.0951
3 | -0.01203 | -0.0030155 | 0.012031 | 0.003016 | 9.3763e-07 | 5.0297e-07 | 0.018139 | 0.018139 | 0.018139 | 0.98692 | -0.25126 | 0.987 | -0.24962 | 4.9832
4 | -0.014176 | -0.0035533 | 0.014177 | 0.0035541 | 1.3018e-06 | 7.3602e-07 | 0.021371 | 0.021371 | 0.021371 | 0.987 | -0.24962 | 0.9871 | -0.24769 | 5.8713
5 | -0.037489 | -0.0094225 | 0.037494 | 0.0094256 | 4.8942e-06 | 3.0796e-06 | 0.056401 | 0.056401 | 0.056401 | 0.98923 | -0.20585 | 0.98937 | -0.20311 | 15.4947
6 | 0.031297 | 0.0078707 | -0.031279 | -0.0078594 | 1.8122e-05 | 1.1319e-05 | 0.047087 | 0.047087 | 0.047087 | 0.98923 | -0.20585 | 0.98861 | -0.21798 | 12.936
7 | 0.088407 | 0.022429 | -0.088293 | -0.022357 | 0.00011396 | 7.2715e-05 | 0.13306 | 0.13306 | 0.13306 | 0.98937 | -0.20311 | 0.98798 | -0.22995 | 36.5554
8 | -0.1259 | -0.031855 | 0.12634 | 0.032137 | 0.00044066 | 0.0002816 | 0.18946 | 0.18946 | 0.18946 | 0.98937 | -0.20311 | 0.99316 | -0.13045 | 52.05
9 | 0.0022209 | 0.00055659 | -0.0022209 | -0.0005566 | 7.4906e-09 | -1.8126e-08 | 0.0033428 | 0.0033428 | 0.0033428 | 0.98861 | -0.21798 | 0.9886 | -0.21805 | 0.91835
10 | 0.029058 | 0.0073028 | -0.029014 | -0.0072754 | 4.4117e-05 | 2.7448e-05 | 0.043744 | 0.043745 | 0.043745 | 0.98861 | -0.21798 | 0.98697 | -0.24983 | 12.0178
11 | 0.088293 | 0.022357 | -0.087941 | -0.022132 | 0.00035269 | 0.00022504 | 0.13306 | 0.13306 | 0.13306 | 0.98798 | -0.22995 | 0.98367 | -0.31351 | 36.5554
12 | 0.03563 | 0.0089422 | -0.035602 | -0.0089244 | 2.8364e-05 | 1.781e-05 | 0.053388 | 0.053388 | 0.053388 | 0.99316 | -0.13045 | 0.99229 | -0.14716 | 14.6671
13 | -0.16197 | -0.041079 | 0.1622 | 0.041225 | 0.00022933 | 0.00014623 | 0.24285 | 0.24285 | 0.24285 | 0.99316 | -0.13045 | 0.99469 | -0.10105 | 33.3585
14 | 0.017901 | 0.0044892 | -0.017896 | -0.0044863 | 4.814e-06 | 2.8558e-06 | 0.026989 | 0.026989 | 0.026989 | 0.98697 | -0.24983 | 0.98668 | -0.25547 | 7.4147
15 | 0.011113 | 0.0027862 | -0.011108 | -0.0027837 | 4.7601e-06 | 2.4689e-06 | 0.016755 | 0.016756 | 0.016756 | 0.98697 | -0.24983 | 0.98651 | -0.25882 | 4.6032
16 | 0.067161 | 0.016924 | -0.067089 | -0.016878 | 7.26e-05 | 4.6226e-05 | 0.10163 | 0.10163 | 0.10163 | 0.98367 | -0.31351 | 0.98251 | -0.33613 | 27.92
17 | 0.027947 | 0.0070058 | -0.027947 | -0.0070058 | 5.4895e-08 | 3.4056e-08 | 0.041909 | 0.041909 | 0.041909 | 0.99229 | -0.14716 | 0.99229 | -0.1472 | 11.5134
18 | -0.16933 | -0.043012 | 0.16933 | 0.043013 | 7.124e-07 | 4.5248e-07 | 0.25352 | 0.25352 | 0.25352 | 0.99469 | -0.10105 | 0.9947 | -0.10096 | 23.216
19 | 0.014114 | 0.0035384 | -0.014111 | -0.0035366 | 3.2643e-06 | 1.8438e-06 | 0.021286 | 0.021286 | 0.021286 | 0.98668 | -0.25547 | 0.98643 | -0.26033 | 5.8478
20 | 0.011108 | 0.0027837 | -0.011107 | -0.0027827 | 1.9042e-06 | 9.8782e-07 | 0.016756 | 0.016756 | 0.016756 | 0.98651 | -0.25882 | 0.98632 | -0.26242 | 4.6032
21 | -0.0091119 | -0.0022839 | 0.0091131 | 0.0022844 | 1.1986e-06 | 5.463e-07 | 0.01367 | 0.013669 | 0.01367 | 0.99189 | -0.15496 | 0.99203 | -0.1522 | 3.7554
22 | 0.0091119 | 0.0022839 | -0.0091106 | -0.0022833 | 1.2514e-06 | 5.7044e-07 | 0.01367 | 0.01367 | 0.01367 | 0.99189 | -0.15496 | 0.99174 | -0.15784 | 3.7554
23 | 0.0067653 | 0.0016955 | -0.0067644 | -0.0016952 | 8.9073e-07 | 2.723e-07 | 0.010148 | 0.010148 | 0.010148 | 0.99203 | -0.1522 | 0.99189 | -0.15496 | 2.7879
24 | -0.015878 | -0.0039799 | 0.015882 | 0.0039821 | 3.7578e-06 | 2.1769e-06 | 0.023817 | 0.023817 | 0.023817 | 0.99203 | -0.1522 | 0.99229 | -0.14723 | 6.5432
25 | -0.038963 | -0.0097799 | 0.038991 | 0.0097972 | 2.7553e-05 | 1.7365e-05 | 0.058946 | 0.058946 | 0.058946 | 0.98368 | -0.31394 | 0.98443 | -0.29913 | 16.1939
26 | 0.038963 | 0.0097799 | -0.038925 | -0.0097554 | 3.8777e-05 | 2.444e-05 | 0.058946 | 0.058946 | 0.058946 | 0.98368 | -0.31394 | 0.98261 | -0.33483 | 16.1939
27 | -0.081154 | -0.020393 | 0.081388 | 0.020542 | 0.0002344 | 0.00014949 | 0.12269 | 0.12269 | 0.12269 | 0.98443 | -0.29913 | 0.98754 | -0.23881 | 33.705
28 | 0.042163 | 0.010596 | -0.04213 | -0.010575 | 3.2318e-05 | 2.0414e-05 | 0.063741 | 0.063741 | 0.063741 | 0.98443 | -0.29913 | 0.98361 | -0.3152 | 17.5112
29 | -0.012331 | -0.0030905 | 0.012332 | 0.0030907 | 3.9343e-07 | 2.1416e-07 | 0.018732 | 0.018732 | 0.018732 | 0.97954 | -0.3942 | 0.97958 | -0.39353 | 5.1462
30 | -0.027903 | -0.0069932 | 0.027931 | 0.0070109 | 2.861e-05 | 1.7775e-05 | 0.042385 | 0.042385 | 0.042385 | 0.97958 | -0.39353 | 0.98068 | -0.37203 | 11.6443
31 | 0.062174 | 0.015646 | -0.062068 | -0.015578 | 0.00010648 | 6.7741e-05 | 0.094186 | 0.094186 | 0.094186 | 0.98251 | -0.33613 | 0.98068 | -0.37203 | 25.8753
32 | 0.022173 | 0.0055587 | -0.022173 | -0.0055587 | 3.144e-08 | 1.9141e-08 | 0.03325 | 0.03325 | 0.03325 | 0.99229 | -0.1472 | 0.99229 | -0.14723 | 9.1347
33 | -0.17622 | -0.044738 | 0.17638 | 0.044839 | 0.00015966 | 0.00010147 | 0.26381 | 0.26381 | 0.26381 | 0.9947 | -0.10096 | 0.99568 | -0.082148 | 24.1588
34 | 0.010046 | 0.0025179 | -0.010045 | -0.0025175 | 8.2211e-07 | 4.0431e-07 | 0.015155 | 0.015155 | 0.015155 | 0.98643 | -0.26033 | 0.98634 | -0.26205 | 4.1634
35 | 0.0068033 | 0.0017042 | -0.0068031 | -0.0017042 | 1.4764e-07 | 4.6789e-08 | 0.010263 | 0.010263 | 0.010263 | 0.98632 | -0.26242 | 0.9863 | -0.26288 | 2.8196
36 | -0.0022249 | -0.0005576 | 0.0022249 | 0.00055754 | 2.5939e-08 | -6.3533e-08 | 0.0033378 | 0.0033378 | 0.0033378 | 0.99185 | -0.15571 | 0.99187 | -0.15546 | 0.91698
37 | -0.0044464 | -0.0011143 | 0.0044465 | 0.0011143 | 1.0574e-07 | -1.4119e-08 | 0.0066705 | 0.0066705 | 0.0066705 | 0.99187 | -0.15546 | 0.99189 | -0.15496 | 1.8326
38 | 0.1191 | 0.030174 | -0.11891 | -0.030055 | 0.00018606 | 0.00011888 | 0.17876 | 0.17876 | 0.17876 | 0.99204 | -0.15187 | 0.99035 | -0.18444 | 49.1097
39 | -0.1191 | -0.030174 | 0.11939 | 0.03036 | 0.00029058 | 0.00018566 | 0.17876 | 0.17876 | 0.17876 | 0.99204 | -0.15187 | 0.99469 | -0.10121 | 49.1097
40 | 0.11632 | 0.029404 | -0.11626 | -0.029368 | 5.7282e-05 | 3.6596e-05 | 0.17486 | 0.17486 | 0.17486 | 0.99035 | -0.18444 | 0.98982 | -0.19472 | 48.0374
41 | -0.27524 | -0.069767 | 0.27581 | 0.070136 | 0.00057715 | 0.0003689 | 0.41202 | 0.41202 | 0.41202 | 0.99469 | -0.10121 | 0.99697 | -0.057678 | 56.5967
42 | 0.12353 | 0.031289 | -0.12323 | -0.031102 | 0.00029336 | 0.00018745 | 0.18491 | 0.18491 | 0.18491 | 0.99469 | -0.10121 | 0.99211 | -0.15079 | 50.799
43 | 0.032321 | 0.0081182 | -0.032296 | -0.0081028 | 2.4711e-05 | 1.5449e-05 | 0.048357 | 0.048357 | 0.048357 | 0.99469 | -0.10121 | 0.99386 | -0.11725 | 13.2849
44 | 0.1961 | 0.050073 | -0.19566 | -0.049795 | 0.00043711 | 0.00027814 | 0.29213 | 0.29213 | 0.29213 | 1 | 0 | 0.99757 | -0.046231 | 26.7515
45 | 0.30326 | 0.077324 | -0.30297 | -0.077137 | 0.00029237 | 0.00018667 | 0.45172 | 0.45172 | 0.45172 | 1 | 0 | 0.99895 | -0.019991 | 41.3662
46 | 0.19566 | 0.049795 | -0.19559 | -0.049752 | 6.805e-05 | 4.3302e-05 | 0.29213 | 0.29213 | 0.29213 | 0.99757 | -0.046231 | 0.99719 | -0.053448 | 26.7515
47 | 0.27907 | 0.071148 | -0.27856 | -0.070825 | 0.00050669 | 0.00032337 | 0.41612 | 0.41612 | 0.41612 | 0.99895 | -0.019991 | 0.99697 | -0.057678 | 38.1065
48 | 0.18935 | 0.048186 | -0.1893 | -0.048155 | 4.8233e-05 | 3.068e-05 | 0.2828 | 0.2828 | 0.2828 | 0.99719 | -0.053448 | 0.99691 | -0.058734 | 25.8978
49 | -0.10427 | -0.026277 | 0.10434 | 0.026321 | 6.8233e-05 | 4.3575e-05 | 0.15716 | 0.15716 | 0.15716 | 0.98754 | -0.23881 | 0.98825 | -0.22514 | 43.1771
50 | 0.0096286 | 0.0024135 | -0.0096271 | -0.0024128 | 1.5768e-06 | 7.5767e-07 | 0.014566 | 0.014567 | 0.014567 | 0.98361 | -0.3152 | 0.98343 | -0.31863 | 4.0018
51 | 0.032502 | 0.0081617 | -0.032486 | -0.0081522 | 1.5093e-05 | 9.4486e-06 | 0.049174 | 0.049175 | 0.049175 | 0.98361 | -0.3152 | 0.98311 | -0.32494 | 13.5095
52 | -0.013801 | -0.0034607 | 0.013805 | 0.003463 | 4.0452e-06 | 2.2772e-06 | 0.02092 | 0.02092 | 0.02092 | 0.98168 | -0.35301 | 0.98199 | -0.34686 | 5.7473
53 | 0.013801 | 0.0034607 | -0.013795 | -0.0034574 | 5.8053e-06 | 3.2684e-06 | 0.02092 | 0.02092 | 0.02092 | 0.98168 | -0.35301 | 0.98123 | -0.36184 | 5.7473
54 | -0.013805 | -0.003463 | 0.01381 | 0.0034655 | 4.5e-06 | 2.533e-06 | 0.02092 | 0.02092 | 0.02092 | 0.98199 | -0.34686 | 0.98234 | -0.34002 | 5.7473
55 | -0.022536 | -0.0056526 | 0.022552 | 0.0056625 | 1.6221e-05 | 9.9112e-06 | 0.034139 | 0.034139 | 0.034139 | 0.98234 | -0.34002 | 0.98311 | -0.32494 | 9.3788
56 | -0.017436 | -0.0043711 | 0.017441 | 0.0043742 | 5.1994e-06 | 3.0794e-06 | 0.026505 | 0.026505 | 0.026505 | 0.97888 | -0.40728 | 0.9792 | -0.40103 | 7.2816
57 | 0.011856 | 0.0029728 | -0.011854 | -0.0029719 | 1.7399e-06 | 9.3402e-07 | 0.018023 | 0.018023 | 0.018023 | 0.97888 | -0.40728 | 0.97872 | -0.41036 | 4.9515
58 | 0.016649 | 0.0041635 | -0.016642 | -0.0041598 | 6.2252e-06 | 3.6579e-06 | 0.025296 | 0.025297 | 0.025297 | 0.9792 | -0.40103 | 0.9788 | -0.40889 | 6.9496
59 | -0.03409 | -0.0085377 | 0.034137 | 0.0085673 | 4.7127e-05 | 2.9572e-05 | 0.051801 | 0.051801 | 0.051801 | 0.9792 | -0.40103 | 0.98068 | -0.37203 | 14.2311
60 | 0.011854 | 0.0029719 | -0.011852 | -0.0029703 | 2.9358e-06 | 1.5762e-06 | 0.018023 | 0.018024 | 0.018024 | 0.97872 | -0.41036 | 0.97846 | -0.41556 | 4.9515
61 | 0.003408 | 0.00084296 | -0.0034076 | -0.00084322 | 4.1958e-07 | -2.5609e-07 | 0.005177 | 0.0051772 | 0.0051772 | 0.9788 | -0.40889 | 0.97867 | -0.4115 | 1.4223
62 | 0.0034076 | 0.00084322 | -0.0034045 | -0.00084507 | 3.0427e-06 | -1.8518e-06 | 0.0051772 | 0.0051786 | 0.0051786 | 0.97867 | -0.4115 | 0.97771 | -0.43041 | 1.4227
63 | 0.018287 | 0.0045857 | -0.018284 | -0.0045837 | 3.4108e-06 | 2.0262e-06 | 0.027402 | 0.027402 | 0.027402 | 0.99308 | -0.13238 | 0.99287 | -0.1363 | 7.5281
64 | -0.018287 | -0.0045857 | 0.018294 | 0.0045897 | 6.7978e-06 | 4.0381e-06 | 0.027402 | 0.027402 | 0.027402 | 0.99308 | -0.13238 | 0.99348 | -0.12459 | 7.5281
65 | 0.0016361 | 0.00040991 | -0.001636 | -0.00041003 | 2.2554e-08 | -1.1494e-07 | 0.0024519 | 0.002452 | 0.002452 | 0.99287 | -0.1363 | 0.99286 | -0.13659 | 0.67361
66 | 0.016648 | 0.0041738 | -0.016646 | -0.0041727 | 1.8075e-06 | 1.0567e-06 | 0.02495 | 0.02495 | 0.02495 | 0.99287 | -0.1363 | 0.99276 | -0.13858 | 6.8545
67 | -0.019527 | -0.0048988 | 0.019534 | 0.0049029 | 6.8354e-06 | 4.0986e-06 | 0.029249 | 0.029249 | 0.029249 | 0.99348 | -0.12459 | 0.99386 | -0.11725 | 8.0355
68 | -0.012761 | -0.0031993 | 0.012762 | 0.0031999 | 1.0819e-06 | 5.9004e-07 | 0.019108 | 0.019108 | 0.019108 | 0.99377 | -0.11903 | 0.99386 | -0.11725 | 5.2494
69 | 0.012761 | 0.0031993 | -0.012757 | -0.0031972 | 3.8443e-06 | 2.0967e-06 | 0.019108 | 0.019108 | 0.019108 | 0.99377 | -0.11903 | 0.99344 | -0.12535 | 5.2495
70 | 0.0034045 | 0.00084507 | -0.0034015 | -0.00084691 | 3.031e-06 | -1.8353e-06 | 0.0051786 | 0.0051799 | 0.0051799 | 0.97771 | -0.43041 | 0.97676 | -0.44922 | 1.4231
71 | 0.0032388 | 0.00080612 | -0.0032379 | -0.00080675 | 8.6897e-07 | -6.358e-07 | 0.004932 | 0.0049324 | 0.0049324 | 0.97676 | -0.44922 | 0.97648 | -0.45488 | 1.3551
72 | 0.014979 | 0.0037549 | -0.014978 | -0.0037544 | 1.0074e-06 | 5.7581e-07 | 0.022452 | 0.022452 | 0.022452 | 0.99276 | -0.13858 | 0.99268 | -0.13999 | 6.1681
73 | 0.07773 | 0.019648 | -0.077627 | -0.019582 | 0.00010304 | 6.5685e-05 | 0.11664 | 0.11664 | 0.11664 | 0.99211 | -0.15079 | 0.99067 | -0.17847 | 32.0446
74 | 0.045503 | 0.011454 | -0.045477 | -0.011438 | 2.6262e-05 | 1.6614e-05 | 0.068266 | 0.068266 | 0.068266 | 0.99211 | -0.15079 | 0.99148 | -0.16287 | 18.7544
75 | 0.076485 | 0.019296 | -0.076391 | -0.019236 | 9.4288e-05 | 6.01e-05 | 0.11493 | 0.11493 | 0.11493 | 0.99067 | -0.17847 | 0.98934 | -0.20425 | 31.5737
76 | 0.044412 | 0.011171 | -0.044365 | -0.011141 | 4.6621e-05 | 2.9477e-05 | 0.066668 | 0.066668 | 0.066668 | 0.99148 | -0.16287 | 0.99035 | -0.18487 | 18.3153
77 | 0.00095897 | 0.00023895 | -0.00095889 | -0.00024008 | 7.5784e-08 | -1.131e-06 | 0.0014623 | 0.0014627 | 0.0014627 | 0.97551 | -0.47393 | 0.97543 | -0.47559 | 0.40184
78 | -0.003235 | -0.00080889 | 0.0032379 | 0.00080675 | 2.9272e-06 | -2.1351e-06 | 0.0049338 | 0.0049324 | 0.0049338 | 0.97551 | -0.47393 | 0.97648 | -0.45488 | 1.3554
79 | 0.002276 | 0.00056994 | -0.0022759 | -0.00057013 | 8.9683e-08 | -1.9033e-07 | 0.0034716 | 0.0034716 | 0.0034716 | 0.97551 | -0.47393 | 0.97547 | -0.47476 | 0.95375
80 | 0.00036565 | 9.1402e-05 | -0.00036565 | -9.164e-05 | 2.2351e-09 | -2.3772e-07 | 0.00055772 | 0.0005578 | 0.0005578 | 0.97543 | -0.47559 | 0.97542 | -0.47572 | 0.15324
81 | 0.00081439 | 0.00020384 | -0.00081438 | -0.00020402 | 8.5001e-09 | -1.7793e-07 | 0.0012422 | 0.0012423 | 0.0012423 | 0.97547 | -0.47476 | 0.97546 | -0.47497 | 0.34128
82 | 0.00029329 | 7.324e-05 | -0.00029329 | -7.3305e-05 | 3.7276e-10 | -6.4534e-08 | 0.00044246 | 0.00044248 | 0.00044248 | 0.98613 | -0.26614 | 0.98613 | -0.26617 | 0.12156
83 | -0.00029329 | -7.324e-05 | 0.00029329 | 7.3036e-05 | 1.1767e-09 | -2.0378e-07 | 0.00044246 | 0.00044238 | 0.00044246 | 0.98613 | -0.26614 | 0.98614 | -0.26606 | 0.12155
84 | 0.00029329 | 7.3305e-05 | -0.00029328 | -7.3504e-05 | 1.1519e-09 | -1.9939e-07 | 0.00044248 | 0.00044255 | 0.00044255 | 0.98613 | -0.26617 | 0.98613 | -0.26625 | 0.12158
85 | -0.00086354 | -0.00021595 | 0.00086355 | 0.00021569 | 1.3755e-08 | -2.6691e-07 | 0.0013029 | 0.0013028 | 0.0013029 | 0.98614 | -0.26606 | 0.98615 | -0.26572 | 0.35793
86 | -0.0054503 | -0.001366 | 0.005451 | 0.0013661 | 6.6942e-07 | 9.1556e-08 | 0.0082235 | 0.0082234 | 0.0082235 | 0.98621 | -0.26462 | 0.98634 | -0.26205 | 2.2592
87 | -0.0053511 | -0.0013404 | 0.0053518 | 0.0013405 | 7.247e-07 | 8.5528e-08 | 0.0080741 | 0.0080739 | 0.0080741 | 0.98615 | -0.26572 | 0.9863 | -0.26288 | 2.2182
88 | 0.00015717 | 3.9304e-05 | -0.00015717 | -3.9391e-05 | 1.5055e-10 | -8.7104e-08 | 0.00023973 | 0.00023976 | 0.00023976 | 0.97546 | -0.47497 | 0.97546 | -0.475 | 0.065868
89 | -0.0012418 | -0.00031094 | 0.0012418 | 0.0003107 | 2.6293e-08 | -2.4037e-07 | 0.0018693 | 0.0018692 | 0.0018693 | 0.98843 | -0.22216 | 0.98845 | -0.22171 | 0.51355
90 | 0.0009344 | 0.00023391 | -0.0009344 | -0.00023394 | 1.8964e-09 | -3.1547e-08 | 0.0014066 | 0.0014066 | 0.0014066 | 0.98843 | -0.22216 | 0.98843 | -0.2222 | 0.38643
91 | -0.0032368 | -0.00081069 | 0.0032373 | 0.00081025 | 5.4273e-07 | -4.3424e-07 | 0.0048725 | 0.0048722 | 0.0048725 | 0.98845 | -0.22171 | 0.98863 | -0.21819 | 1.3386
92 | 0.00032992 | 8.244e-05 | -0.00032992 | -8.2685e-05 | 1.7787e-09 | -2.4536e-07 | 0.00049659 | 0.00049667 | 0.00049667 | 0.98843 | -0.2222 | 0.98842 | -0.22231 | 0.13645
93 | -0.0032373 | -0.00081025 | 0.0032379 | 0.0008098 | 5.6781e-07 | -4.5472e-07 | 0.0048722 | 0.0048719 | 0.0048722 | 0.98863 | -0.21819 | 0.98882 | -0.2145 | 1.3385
94 | -0.0035449 | -0.00088674 | 0.0035453 | 0.00088654 | 3.6378e-07 | -2.0463e-07 | 0.0053339 | 0.0053337 | 0.0053339 | 0.98882 | -0.2145 | 0.98893 | -0.21234 | 1.4654
95 | -0.0083403 | -0.0020883 | 0.0083404 | 0.0020883 | 1.0807e-07 | 4.5685e-08 | 0.012549 | 0.012549 | 0.012549 | 0.98893 | -0.21234 | 0.98895 | -0.21207 | 3.4474
96 | 0.041522 | 0.010429 | -0.041515 | -0.010424 | 7.0868e-06 | 4.4731e-06 | 0.062396 | 0.062396 | 0.062396 | 0.99035 | -0.18487 | 0.99016 | -0.18845 | 17.1418
97 | 0.040765 | 0.010236 | -0.040758 | -0.010232 | 6.9218e-06 | 4.3667e-06 | 0.061269 | 0.061269 | 0.061269 | 0.99016 | -0.18845 | 0.98998 | -0.192 | 16.832
98 | 0.038909 | 0.0097685 | -0.038882 | -0.0097515 | 2.7109e-05 | 1.7078e-05 | 0.05849 | 0.05849 | 0.05849 | 0.98998 | -0.192 | 0.98923 | -0.20662 | 16.0687
99 | 0.02585 | 0.0064851 | -0.025843 | -0.0064811 | 6.5076e-06 | 4.0175e-06 | 0.038886 | 0.038886 | 0.038886 | 0.98923 | -0.20662 | 0.98895 | -0.2119 | 10.6829
100 | 0.076391 | 0.019236 | -0.076343 | -0.019205 | 4.765e-05 | 3.0372e-05 | 0.11493 | 0.11493 | 0.11493 | 0.98934 | -0.20425 | 0.98867 | -0.21731 | 31.5737
101 | 0.0087916 | 0.0022014 | -0.0087915 | -0.0022014 | 7.0975e-08 | 3.1544e-08 | 0.013227 | 0.013227 | 0.013227 | 0.98895 | -0.2119 | 0.98895 | -0.21207 | 3.6339
102 | 0.017051 | 0.0042797 | -0.017045 | -0.0042758 | 6.6004e-06 | 3.8814e-06 | 0.025658 | 0.025658 | 0.025658 | 0.98895 | -0.2119 | 0.98854 | -0.22002 | 7.049
103 | -0.016321 | -0.0040914 | 0.016324 | 0.0040933 | 3.2158e-06 | 1.877e-06 | 0.024604 | 0.024604 | 0.024604 | 0.9871 | -0.24769 | 0.98732 | -0.24356 | 6.7592
104 | 0.017045 | 0.0042758 | -0.017033 | -0.0042689 | 1.1736e-05 | 6.9019e-06 | 0.025658 | 0.025659 | 0.025659 | 0.98854 | -0.22002 | 0.98779 | -0.23448 | 7.0491
105 | 0.10522 | 0.026602 | -0.10507 | -0.026504 | 0.00015328 | 9.7893e-05 | 0.15827 | 0.15827 | 0.15827 | 0.98982 | -0.19472 | 0.98825 | -0.22514 | 43.48
106 | -0.024635 | -0.0061759 | 0.024641 | 0.0061793 | 5.5011e-06 | 3.3846e-06 | 0.037129 | 0.037129 | 0.037129 | 0.98732 | -0.24356 | 0.98756 | -0.23887 | 10.2003
107 | 0.0083108 | 0.0020826 | -0.0083106 | -0.0020825 | 2.3507e-07 | 9.935e-08 | 0.012525 | 0.012525 | 0.012525 | 0.98732 | -0.24356 | 0.98729 | -0.24415 | 3.4411
108 | 0.012657 | 0.0031728 | -0.012656 | -0.0031718 | 1.7651e-06 | 9.6064e-07 | 0.018974 | 0.018974 | 0.018974 | 0.99268 | -0.13999 | 0.99253 | -0.14292 | 5.2125
109 | 0.028456 | 0.0071407 | -0.028446 | -0.0071346 | 9.9293e-06 | 6.1701e-06 | 0.042855 | 0.042855 | 0.042855 | 0.98811 | -0.22808 | 0.98773 | -0.2354 | 11.7734
110 | -0.03038 | -0.0076229 | 0.030395 | 0.0076327 | 1.5613e-05 | 9.7373e-06 | 0.045753 | 0.045752 | 0.045753 | 0.98811 | -0.22808 | 0.98867 | -0.21731 | 12.5694
111 | 0.027472 | 0.0068905 | -0.027471 | -0.0068899 | 9.5527e-07 | 5.9234e-07 | 0.041388 | 0.041388 | 0.041388 | 0.98773 | -0.2354 | 0.9877 | -0.23613 | 11.3704
112 | 0.045948 | 0.011573 | -0.045925 | -0.011558 | 2.2911e-05 | 1.4499e-05 | 0.069176 | 0.069176 | 0.069176 | 0.98867 | -0.21731 | 0.98813 | -0.22774 | 19.0043
113 | 0.026786 | 0.0067183 | -0.026783 | -0.0067161 | 3.5025e-06 | 2.1682e-06 | 0.040356 | 0.040356 | 0.040356 | 0.9877 | -0.23613 | 0.98756 | -0.23887 | 11.0869
114 | 0.044494 | 0.011199 | -0.044491 | -0.011198 | 2.0678e-06 | 1.3077e-06 | 0.06702 | 0.06702 | 0.06702 | 0.98813 | -0.22774 | 0.98808 | -0.22871 | 18.412
115 | 0.041865 | 0.01054 | -0.041851 | -0.010531 | 1.4757e-05 | 9.3179e-06 | 0.063065 | 0.063065 | 0.063065 | 0.98808 | -0.22871 | 0.9877 | -0.23609 | 17.3256
116 | -0.0018201 | -0.00045617 | 0.0018202 | 0.00045606 | 2.8764e-08 | -1.1027e-07 | 0.0027521 | 0.002752 | 0.0027521 | 0.98413 | -0.3056 | 0.98414 | -0.30527 | 0.75607
117 | -0.0071965 | -0.0018035 | 0.0071966 | 0.0018035 | 1.811e-07 | 6.4073e-08 | 0.010881 | 0.010881 | 0.010881 | 0.98414 | -0.30527 | 0.98417 | -0.30474 | 2.9893
118 | 0.041851 | 0.010531 | -0.041834 | -0.01052 | 1.6761e-05 | 1.0584e-05 | 0.063065 | 0.063065 | 0.063065 | 0.9877 | -0.23609 | 0.98727 | -0.24447 | 17.3256
119 | 0.0024123 | 0.00060425 | -0.0024123 | -0.00060429 | 2.0779e-08 | -4.0289e-08 | 0.003636 | 0.003636 | 0.003636 | 0.9872 | -0.24589 | 0.98719 | -0.24607 | 0.9989
120 | -0.0048488 | -0.0012149 | 0.0048489 | 0.0012149 | 6.3975e-08 | 1.0898e-10 | 0.0073086 | 0.0073086 | 0.0073086 | 0.9872 | -0.24589 | 0.98721 | -0.24561 | 2.0079
121 | 0.00086973 | 0.00021769 | -0.00086972 | -0.00021778 | 4.6486e-09 | -8.9254e-08 | 0.0013109 | 0.0013109 | 0.0013109 | 0.98719 | -0.24607 | 0.98718 | -0.24618 | 0.36014
122 | -0.0056515 | -0.0014161 | 0.0056519 | 0.0014161 | 3.9318e-07 | 6.6873e-08 | 0.0085184 | 0.0085183 | 0.0085184 | 0.98721 | -0.24561 | 0.98729 | -0.24415 | 2.3402
123 | 0.00086972 | 0.00021778 | -0.00086971 | -0.00021797 | 9.9138e-09 | -1.9033e-07 | 0.0013109 | 0.001311 | 0.001311 | 0.98718 | -0.24618 | 0.98717 | -0.24642 | 0.36016
124 | 0.038972 | 0.0097971 | -0.038962 | -0.0097914 | 9.0727e-06 | 5.7171e-06 | 0.058773 | 0.058773 | 0.058773 | 0.98686 | -0.2523 | 0.98661 | -0.25717 | 16.1464
125 | -0.038972 | -0.0097971 | 0.038986 | 0.0098063 | 1.4565e-05 | 9.1781e-06 | 0.058773 | 0.058773 | 0.058773 | 0.98686 | -0.2523 | 0.98727 | -0.24447 | 16.1464
126 | 0.037779 | 0.0094948 | -0.037746 | -0.0094738 | 3.3264e-05 | 2.0941e-05 | 0.056988 | 0.056988 | 0.056988 | 0.98661 | -0.25717 | 0.98566 | -0.27564 | 15.6561
127 | -0.0061646 | -0.001545 | 0.006166 | 0.0015453 | 1.4242e-06 | 3.5464e-07 | 0.0093156 | 0.0093154 | 0.0093156 | 0.98469 | -0.29461 | 0.98494 | -0.28976 | 2.5592
128 | 0.0061646 | 0.001545 | -0.0061623 | -0.0015444 | 2.3281e-06 | 5.8036e-07 | 0.0093156 | 0.0093159 | 0.0093159 | 0.98469 | -0.29461 | 0.98428 | -0.30254 | 2.5593
129 | 0.026957 | 0.0067617 | -0.026948 | -0.0067559 | 9.2885e-06 | 5.7547e-06 | 0.040728 | 0.040729 | 0.040729 | 0.98494 | -0.28976 | 0.98457 | -0.29699 | 11.1892
130 | -0.033123 | -0.008307 | 0.033146 | 0.008321 | 2.2313e-05 | 1.3978e-05 | 0.050044 | 0.050044 | 0.050044 | 0.98494 | -0.28976 | 0.98566 | -0.27564 | 13.7483
131 | 0.012844 | 0.0032201 | -0.012841 | -0.0032186 | 2.7613e-06 | 1.5188e-06 | 0.019412 | 0.019412 | 0.019412 | 0.98457 | -0.29699 | 0.98434 | -0.3015 | 5.333
132 | 0.014104 | 0.0035358 | -0.014101 | -0.0035342 | 2.9541e-06 | 1.6702e-06 | 0.021317 | 0.021317 | 0.021317 | 0.98457 | -0.29699 | 0.98434 | -0.30139 | 5.8562
133 | -0.0094978 | -0.0023804 | 0.009498 | 0.0023805 | 1.9996e-07 | 9.5094e-08 | 0.014358 | 0.014358 | 0.014358 | 0.98432 | -0.30183 | 0.98434 | -0.30139 | 3.9445
134 | 0.0098891 | 0.0024787 | -0.0098875 | -0.002478 | 1.526e-06 | 7.4521e-07 | 0.014949 | 0.014949 | 0.014949 | 0.98434 | -0.3015 | 0.98417 | -0.30474 | 4.107
135 | 0.18359 | 0.046726 | -0.18355 | -0.046695 | 4.8285e-05 | 3.0702e-05 | 0.27429 | 0.27429 | 0.27429 | 0.99691 | -0.058734 | 0.99662 | -0.064191 | 25.1181
136 | 0.17653 | 0.044936 | -0.17638 | -0.044839 | 0.00015269 | 9.7039e-05 | 0.26381 | 0.26381 | 0.26381 | 0.99662 | -0.064191 | 0.99568 | -0.082148 | 24.1588

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50101 | 0.1274

## res_load
| p_mw | q_mvar
0 | 0.0043394 | 0.0010876
1 | 0.0027569 | 0.00069094
2 | 0.0027877 | 0.00069868
3 | 0.0021442 | 0.00053738
4 | 0.0021442 | 0.00053738
5 | 0.0061918 | 0.0015518
6 | 0.0022209 | 0.0005566
7 | 0.020779 | 0.0052078
8 | 0.007655 | 0.0019185
9 | 0.0071318 | 0.0017874
10 | 0.003782 | 0.00094786
11 | 0.0091106 | 0.0022833
12 | 0.038925 | 0.0097554
13 | 0.012331 | 0.0030905
14 | 0.015571 | 0.0039024
15 | 0.0049145 | 0.0012317
16 | 0.005774 | 0.0014471
17 | 0.0068826 | 0.0017249
18 | 0.0040645 | 0.0010187
19 | 0.0043033 | 0.0010785
20 | 0.0022249 | 0.0005576
21 | 0.0022215 | 0.00055676
22 | 0.002598 | 0.00065112
23 | 0.023897 | 0.0059892
24 | 0.0062475 | 0.0015658
25 | 0.0023179 | 0.00058093
26 | 0.0062907 | 0.0015766
27 | 0.022882 | 0.0057348
28 | 0.013795 | 0.0034574
29 | 0.0087266 | 0.0021871
30 | 0.0055795 | 0.0013984
31 | 0.013234 | 0.0033168
32 | 0.011852 | 0.0029703
33 | 0.0012331 | 0.00030905
34 | 0.012757 | 0.0031972
35 | 0.00016275 | 4.079e-05
36 | 0.001636 | 0.00041003
37 | 0.0016669 | 0.00041777
38 | 0.0027461 | 0.00068825
39 | 0.0011413 | 0.00028604
40 | 0.001065 | 0.00026693
41 | 0.00059324 | 0.00014868
42 | 0.0014615 | 0.00036629
43 | 0.00057025 | 0.00014292
44 | 0.0054503 | 0.001366
45 | 0.0045945 | 0.0011515
46 | 0.00029328 | 7.3504e-05
47 | 0.0044876 | 0.0011247
48 | 0.00036565 | 9.164e-05
49 | 0.0006572 | 0.00016471
50 | 0.00030738 | 7.7038e-05
51 | 0.001995 | 0.00049998
52 | 0.00060448 | 0.0001515
53 | 0.00032992 | 8.2685e-05
54 | 0.00030701 | 7.6944e-05
55 | 0.0047951 | 0.0012018
56 | 0.0028431 | 0.00071254
57 | 0.00075026 | 0.00018803
58 | 0.0018486 | 0.0004633
59 | 0.013033 | 0.0032663
60 | 0.0021442 | 0.00053738
61 | 0.00045111 | 0.00011306
62 | 0.017033 | 0.0042689
63 | 0.0014513 | 0.00036373
64 | 0.011035 | 0.0027656
65 | 0.0023205 | 0.00058158
66 | 0.001924 | 0.00048219
67 | 0.00097384 | 0.00024407
68 | 0.00068488 | 0.00017165
69 | 0.0014317 | 0.00035881
70 | 0.002142 | 0.00053684
71 | 0.0026261 | 0.00065816
72 | 0.0018201 | 0.00045617
73 | 0.0053763 | 0.0013474
74 | 0.0024365 | 0.00061065
75 | 0.0015426 | 0.0003866
76 | 0.0008026 | 0.00020115
77 | 0.0026587 | 0.00066633
78 | 0.00086971 | 0.00021797
79 | 0.0011835 | 0.0002966
80 | 0.0028478 | 0.00071372
81 | 0.0061623 | 0.0015444
82 | 0.0046 | 0.0011529
83 | 0.0094978 | 0.0023804
84 | 0.0046033 | 0.0011537
85 | 0.0029521 | 0.00073987
86 | 0.0026909 | 0.00067441
87 | 0.0099341 | 0.0024897
88 | 0.0096271 | 0.0024128
89 | 0.00073249 | 0.00018358
90 | 0.0057042 | 0.0014296
91 | 0.012656 | 0.0031718
92 | 0.00015717 | 3.9391e-05
93 | 0.0070165 | 0.0017585

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1