## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-3_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_115-3_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_115-3_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_115-3_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_115-3_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_115-3_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_115-3_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_115-3_0_2_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_115-3_0_2_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_115-3_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_115-3_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_115-3_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_115-3_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_115-3_0_2_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_115-3_0_2_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_115-3_0_2_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_115-3_0_2_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_115-3_0_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_115-3_0_2_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_115-3_0_2_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_115-3_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_115-3_0_2_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_115-3_0_2_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_115-3_0_2_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_115-3_0_2_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_115-3_0_2_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_115-3_0_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_115-3_0_2_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_115-3_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_115-3_0_2_node_82 | 0.4 | n |  | TRUE
30 | bus_LV_115-3_0_2_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_115-3_0_2_node_80 | 0.4 | n |  | TRUE
32 | bus_LV_115-3_0_2_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_115-3_0_2_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_115-3_0_2_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_115-3_0_2_node_253 | 0.4 | n |  | TRUE
36 | bus_LV_115-3_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_115-3_0_2_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_115-3_0_2_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_115-3_0_2_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_115-3_0_2_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_115-3_0_2_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_115-3_0_2_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_115-3_0_2_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_115-3_0_2_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_115-3_0_2_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_115-3_0_2_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_115-3_0_2_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_115-3_0_2_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_115-3_0_2_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_115-3_0_2_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_115-3_0_2_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_115-3_0_2_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_115-3_0_2_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_115-3_0_2_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_115-3_0_2_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_115-3_0_2_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_115-3_0_2_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_115-3_0_2_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_115-3_0_2_node_247 | 0.4 | n |  | TRUE
60 | bus_LV_115-3_0_2_node_204 | 0.4 | n |  | TRUE
61 | bus_LV_115-3_0_2_node_199 | 0.4 | n |  | TRUE
62 | bus_LV_115-3_0_2_node_162 | 0.4 | n |  | TRUE
63 | bus_LV_115-3_0_2_node_81 | 0.4 | n |  | TRUE
64 | bus_LV_115-3_0_2_node_83 | 0.4 | n |  | TRUE
65 | bus_LV_115-3_0_2_node_252 | 0.4 | n |  | TRUE
66 | bus_LV_115-3_0_2_node_250 | 0.4 | n |  | TRUE
67 | bus_LV_115-3_0_2_node_165 | 0.4 | n |  | TRUE
68 | bus_LV_115-3_0_2_node_166 | 0.4 | n |  | TRUE
69 | bus_LV_115-3_0_2_node_167 | 0.4 | n |  | TRUE
70 | bus_LV_115-3_0_2_node_168 | 0.4 | n |  | TRUE
71 | bus_LV_115-3_0_2_node_170 | 0.4 | n |  | TRUE
72 | bus_LV_115-3_0_2_node_171 | 0.4 | n |  | TRUE
73 | bus_LV_115-3_0_2_node_173 | 0.4 | n |  | TRUE
74 | bus_LV_115-3_0_2_node_210 | 0.4 | n |  | TRUE
75 | bus_LV_115-3_0_2_node_172 | 0.4 | n |  | TRUE
76 | bus_LV_115-3_0_2_node_268 | 0.4 | n |  | TRUE
77 | bus_LV_115-3_0_2_node_213 | 0.4 | n |  | TRUE
78 | bus_LV_115-3_0_2_node_214 | 0.4 | n |  | TRUE
79 | bus_LV_115-3_0_2_node_194 | 0.4 | n |  | TRUE
80 | bus_LV_115-3_0_2_node_196 | 0.4 | n |  | TRUE
81 | bus_LV_115-3_0_2_node_198 | 0.4 | n |  | TRUE
82 | bus_LV_115-3_0_2_node_212 | 0.4 | n |  | TRUE
83 | bus_LV_115-3_0_2_node_205 | 0.4 | n |  | TRUE
84 | bus_LV_115-3_0_2_node_206 | 0.4 | n |  | TRUE
85 | bus_LV_115-3_0_2_node_207 | 0.4 | n |  | TRUE
86 | bus_LV_115-3_0_2_node_242 | 0.4 | n |  | TRUE
87 | bus_LV_115-3_0_2_node_211 | 0.4 | n |  | TRUE
88 | bus_LV_115-3_0_2_node_215 | 0.4 | n |  | TRUE
89 | bus_LV_115-3_0_2_node_216 | 0.4 | n |  | TRUE
90 | bus_LV_115-3_0_2_node_260 | 0.4 | n |  | TRUE
91 | bus_LV_115-3_0_2_node_266 | 0.4 | n |  | TRUE
92 | bus_LV_115-3_0_2_node_265 | 0.4 | n |  | TRUE
93 | bus_LV_115-3_0_2_node_217 | 0.4 | n |  | TRUE
94 | bus_LV_115-3_0_2_node_218 | 0.4 | n |  | TRUE
95 | bus_LV_115-3_0_2_node_219 | 0.4 | n |  | TRUE
96 | bus_LV_115-3_0_2_node_220 | 0.4 | n |  | TRUE
97 | bus_LV_115-3_0_2_node_221 | 0.4 | n |  | TRUE
98 | bus_LV_115-3_0_2_node_222 | 0.4 | n |  | TRUE
99 | bus_LV_115-3_0_2_node_231 | 0.4 | n |  | TRUE
100 | bus_LV_115-3_0_2_node_223 | 0.4 | n |  | TRUE
101 | bus_LV_115-3_0_2_node_224 | 0.4 | n |  | TRUE
102 | bus_LV_115-3_0_2_node_225 | 0.4 | n |  | TRUE
103 | bus_LV_115-3_0_2_node_226 | 0.4 | n |  | TRUE
104 | bus_LV_115-3_0_2_node_228 | 0.4 | n |  | TRUE
105 | bus_LV_115-3_0_2_node_229 | 0.4 | n |  | TRUE
106 | bus_LV_115-3_0_2_node_230 | 0.4 | n |  | TRUE
107 | bus_LV_115-3_0_2_node_227 | 0.4 | n |  | TRUE
108 | bus_LV_115-3_0_2_node_235 | 0.4 | n |  | TRUE
109 | bus_LV_115-3_0_2_node_241 | 0.4 | n |  | TRUE
110 | bus_LV_115-3_0_2_node_238 | 0.4 | n |  | TRUE
111 | bus_LV_115-3_0_2_node_236 | 0.4 | n |  | TRUE
112 | bus_LV_115-3_0_2_node_232 | 0.4 | n |  | TRUE
113 | bus_LV_115-3_0_2_node_233 | 0.4 | n |  | TRUE
114 | bus_LV_115-3_0_2_node_234 | 0.4 | n |  | TRUE
115 | bus_LV_115-3_0_2_node_237 | 0.4 | n |  | TRUE
116 | bus_LV_115-3_0_2_node_239 | 0.4 | n |  | TRUE
117 | bus_LV_115-3_0_2_node_240 | 0.4 | n |  | TRUE
118 | bus_LV_115-3_0_2_node_259 | 0.4 | n |  | TRUE
119 | bus_LV_115-3_0_2_node_244 | 0.4 | n |  | TRUE
120 | bus_LV_115-3_0_2_node_245 | 0.4 | n |  | TRUE
121 | bus_LV_115-3_0_2_node_246 | 0.4 | n |  | TRUE
122 | bus_LV_115-3_0_2_node_248 | 0.4 | n |  | TRUE
123 | bus_LV_115-3_0_2_node_249 | 0.4 | n |  | TRUE
124 | bus_LV_115-3_0_2_node_256 | 0.4 | n |  | TRUE
125 | bus_LV_115-3_0_2_node_257 | 0.4 | n |  | TRUE
126 | bus_LV_115-3_0_2_node_251 | 0.4 | n |  | TRUE
127 | bus_LV_115-3_0_2_node_254 | 0.4 | n |  | TRUE
128 | bus_LV_115-3_0_2_node_255 | 0.4 | n |  | TRUE
129 | bus_LV_115-3_0_2_node_258 | 0.4 | n |  | TRUE
130 | bus_LV_115-3_0_2_node_283 | 0.4 | n |  | TRUE
131 | bus_LV_115-3_0_2_node_261 | 0.4 | n |  | TRUE
132 | bus_LV_115-3_0_2_node_262 | 0.4 | n |  | TRUE
133 | bus_LV_115-3_0_2_node_263 | 0.4 | n |  | TRUE
134 | bus_LV_115-3_0_2_node_264 | 0.4 | n |  | TRUE
135 | bus_LV_115-3_0_2_node_267 | 0.4 | n |  | TRUE
136 | bus_LV_115-3_0_2_node_281 | 0.4 | n |  | TRUE
137 | bus_MV_357_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-3_0_2_load_0 | 0 | 0.0071066 | 0.0017811 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-3_0_2_load_1 | 1 | 0.0034592 | 0.00086696 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-3_0_2_load_2 | 2 | 0.0015837 | 0.00039691 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-3_0_2_load_3 | 3 | 0.0033009 | 0.00082728 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-3_0_2_load_4 | 4 | 0.0072843 | 0.0018256 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-3_0_2_load_6 | 6 | 0.00060917 | 0.00015267 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-3_0_2_load_30 | 7 | 0.0038195 | 0.00095725 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-3_0_2_load_27 | 8 | 0.0058841 | 0.0014747 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-3_0_2_load_7 | 9 | 0.0032295 | 0.00080938 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-3_0_2_load_8 | 10 | 0.0047457 | 0.0011894 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-3_0_2_load_11 | 12 | 0.0020613 | 0.0005166 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-3_0_2_load_14 | 13 | 0.0024281 | 0.00060853 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-3_0_2_load_40 | 14 | 0.0048423 | 0.0012136 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-3_0_2_load_15 | 15 | 0.0022567 | 0.00056557 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-3_0_2_load_16 | 16 | 0.0011567 | 0.0002899 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-3_0_2_load_17 | 17 | 0.0042933 | 0.001076 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-3_0_2_load_18 | 18 | 0.003883 | 0.00097317 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-3_0_2_load_19 | 19 | 0.0011567 | 0.0002899 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-3_0_2_load_21 | 20 | 0.0099974 | 0.0025056 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-3_0_2_load_20 | 21 | 0.0014573 | 0.00036523 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-3_0_2_load_24 | 24 | 0.0021327 | 0.0005345 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-3_0_2_load_26 | 26 | 0.00062201 | 0.00015589 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-3_0_2_load_28 | 27 | 0.00085871 | 0.00021521 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-3_0_2_load_82 | 29 | 0.0008608 | 0.00021574 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-3_0_2_load_29 | 30 | 0.0095852 | 0.0024023 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-3_0_2_load_32 | 32 | 0.0037814 | 0.0009477 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-3_0_2_load_36 | 33 | 0.0013287 | 0.000333 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-3_0_2_load_33 | 34 | 0.006436 | 0.001613 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-3_0_2_load_253 | 35 | 0.0038926 | 0.00097559 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-3_0_2_load_34 | 36 | 0.0055996 | 0.0014034 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-3_0_2_load_35 | 37 | 0.0013541 | 0.00033937 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-3_0_2_load_37 | 38 | 0.0013565 | 0.00033998 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-3_0_2_load_38 | 39 | 0.00084256 | 0.00021117 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-3_0_2_load_42 | 40 | 0.0013554 | 0.0003397 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-3_0_2_load_43 | 41 | 0.0057509 | 0.0014413 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-3_0_2_load_41 | 42 | 0.0013546 | 0.0003395 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-3_0_2_load_44 | 43 | 0.0022904 | 0.00057403 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-3_0_2_load_45 | 44 | 0.0022794 | 0.00057128 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-3_0_2_load_46 | 45 | 0.0022907 | 0.0005741 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-3_0_2_load_47 | 46 | 0.0055803 | 0.0013986 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-3_0_2_load_51 | 50 | 0.0021251 | 0.00053259 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-3_0_2_load_53 | 52 | 0.0012106 | 0.0003034 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-3_0_2_load_54 | 53 | 0.001083 | 0.00027141 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-3_0_2_load_56 | 55 | 0.0024952 | 0.00062536 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-3_0_2_load_57 | 56 | 0.042766 | 0.010718 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-3_0_2_load_58 | 57 | 0.0016729 | 0.00041927 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_115-3_0_2_load_59 | 58 | 0.0030139 | 0.00075535 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_115-3_0_2_load_247 | 59 | 0.00049639 | 0.00012441 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_115-3_0_2_load_204 | 60 | 0.0078035 | 0.0019557 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_115-3_0_2_load_199 | 61 | 0.0017622 | 0.00044165 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_115-3_0_2_load_162 | 62 | 0.0012761 | 0.00031981 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_115-3_0_2_load_81 | 63 | 0.0014013 | 0.00035119 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_115-3_0_2_load_83 | 64 | 0.0013601 | 0.00034086 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_115-3_0_2_load_252 | 65 | 0.0016426 | 0.00041169 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_115-3_0_2_load_250 | 66 | 0.0010924 | 0.00027377 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_115-3_0_2_load_165 | 67 | 0.00070971 | 0.00017787 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_115-3_0_2_load_166 | 68 | 0.00076053 | 0.00019061 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_115-3_0_2_load_168 | 70 | 0.00076036 | 0.00019056 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_115-3_0_2_load_170 | 71 | 0.0013112 | 0.00032862 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_115-3_0_2_load_171 | 72 | 0.00093609 | 0.00023461 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_115-3_0_2_load_210 | 74 | 0.000718 | 0.00017995 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_115-3_0_2_load_172 | 75 | 0.0011601 | 0.00029075 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_115-3_0_2_load_268 | 76 | 0.00060861 | 0.00015253 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_115-3_0_2_load_213 | 77 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_115-3_0_2_load_214 | 78 | 0.0010965 | 0.0002748 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_115-3_0_2_load_194 | 79 | 0.0010593 | 0.00026549 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_115-3_0_2_load_196 | 80 | 0.0016122 | 0.00040405 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_115-3_0_2_load_198 | 81 | 0.00073086 | 0.00018317 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_115-3_0_2_load_212 | 82 | 0.00055788 | 0.00013982 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_115-3_0_2_load_205 | 83 | 0.0017852 | 0.00044742 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_115-3_0_2_load_206 | 84 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_115-3_0_2_load_242 | 86 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_115-3_0_2_load_211 | 87 | 0.00066438 | 0.00016651 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_115-3_0_2_load_215 | 88 | 0.00060593 | 0.00015186 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_115-3_0_2_load_260 | 90 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_115-3_0_2_load_266 | 91 | 0.00060662 | 0.00015203 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_115-3_0_2_load_265 | 92 | 0.00060593 | 0.00015186 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_115-3_0_2_load_217 | 93 | 0.0010487 | 0.00026282 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_115-3_0_2_load_218 | 94 | 0.001232 | 0.00030877 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_115-3_0_2_load_219 | 95 | 0.0017609 | 0.00044132 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_115-3_0_2_load_220 | 96 | 0.0029253 | 0.00073315 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_115-3_0_2_load_221 | 97 | 0.0013312 | 0.00033364 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_115-3_0_2_load_223 | 100 | 0.0020232 | 0.00050706 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_115-3_0_2_load_228 | 104 | 0.00020405 | 5.1139e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_115-3_0_2_load_230 | 106 | 0.00046833 | 0.00011738 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_115-3_0_2_load_241 | 109 | 0.00083915 | 0.00021031 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_115-3_0_2_load_238 | 110 | 0.00041604 | 0.00010427 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_115-3_0_2_load_236 | 111 | 0.00067982 | 0.00017038 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_115-3_0_2_load_232 | 112 | 0.0010921 | 0.00027371 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_115-3_0_2_load_233 | 113 | 0.0017323 | 0.00043416 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_115-3_0_2_load_234 | 114 | 0.00067909 | 0.0001702 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_115-3_0_2_load_237 | 115 | 0.00019938 | 4.9968e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_115-3_0_2_load_239 | 116 | 0.00041574 | 0.00010419 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_115-3_0_2_load_240 | 117 | 0.00046353 | 0.00011617 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_115-3_0_2_load_259 | 118 | 0.00060593 | 0.00015186 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_115-3_0_2_load_244 | 119 | 0.00049645 | 0.00012442 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_115-3_0_2_load_245 | 120 | 0.00049674 | 0.00012449 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_115-3_0_2_load_246 | 121 | 0.00049598 | 0.0001243 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_115-3_0_2_load_248 | 122 | 0.00049645 | 0.00012442 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_115-3_0_2_load_256 | 124 | 0.00049761 | 0.00012471 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_115-3_0_2_load_251 | 126 | 0.0016416 | 0.00041142 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_115-3_0_2_load_254 | 127 | 0.0032526 | 0.00081518 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_115-3_0_2_load_255 | 128 | 0.00049616 | 0.00012435 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_115-3_0_2_load_258 | 129 | 0.0011931 | 0.00029901 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_115-3_0_2_load_261 | 131 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_115-3_0_2_load_262 | 132 | 0.00060594 | 0.00015186 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_115-3_0_2_load_263 | 133 | 0.0012114 | 0.0003036 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_115-3_0_2_load_264 | 134 | 0.00060546 | 0.00015174 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_115-3_0_2_load_267 | 135 | 0.00060637 | 0.00015197 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_115-3_0_2_load_281 | 136 | 0.00047176 | 0.00011823 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-3_0_2_line_0 |  | 0 | 1 | 0.01748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-3_0_2_line_1 |  | 0 | 2 | 0.015738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-3_0_2_line_2 |  | 1 | 3 | 0.0019655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-3_0_2_line_3 |  | 2 | 4 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-3_0_2_line_4 |  | 3 | 5 | 0.018504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-3_0_2_line_5 |  | 4 | 6 | 0.0045243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-3_0_2_line_6 |  | 5 | 7 | 0.012945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-3_0_2_line_7 |  | 5 | 8 | 0.012033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-3_0_2_line_8 |  | 7 | 32 | 0.026283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-3_0_2_line_9 |  | 8 | 23 | 0.028651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-3_0_2_line_10 |  | 9 | 10 | 0.017137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-3_0_2_line_11 |  | 9 | 11 | 0.013934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-3_0_2_line_12 |  | 11 | 12 | 0.027547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-3_0_2_line_13 |  | 12 | 13 | 0.0025219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_115-3_0_2_line_14 |  | 13 | 14 | 0.027386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-3_0_2_line_15 |  | 14 | 42 | 0.0017813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-3_0_2_line_16 |  | 15 | 16 | 0.002053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-3_0_2_line_17 |  | 15 | 17 | 0.0033821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-3_0_2_line_18 |  | 16 | 18 | 0.01935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_115-3_0_2_line_19 |  | 18 | 19 | 0.0077887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-3_0_2_line_20 |  | 19 | 20 | 0.021807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-3_0_2_line_21 |  | 20 | 21 | 0.0039157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-3_0_2_line_22 |  | 21 | 22 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_115-3_0_2_line_23 |  | 22 | 23 | 0.033063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-3_0_2_line_24 |  | 22 | 24 | 0.029854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-3_0_2_line_25 |  | 22 | 25 | 0.036703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-3_0_2_line_26 |  | 23 | 26 | 0.0037593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-3_0_2_line_27 |  | 25 | 27 | 0.018596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-3_0_2_line_28 |  | 26 | 28 | 0.031653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-3_0_2_line_29 |  | 27 | 29 | 0.00049254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-3_0_2_line_30 |  | 28 | 33 | 0.013063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-3_0_2_line_31 |  | 28 | 34 | 0.017743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_115-3_0_2_line_32 |  | 29 | 65 | 0.021844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-3_0_2_line_33 |  | 30 | 31 | 0.0077594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_115-3_0_2_line_34 |  | 31 | 63 | 0.006955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-3_0_2_line_35 |  | 31 | 53 | 0.011285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-3_0_2_line_36 |  | 32 | 35 | 0.0099959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_115-3_0_2_line_37 |  | 33 | 39 | 0.034619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_115-3_0_2_line_38 |  | 34 | 36 | 0.0085746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_115-3_0_2_line_39 |  | 35 | 127 | 0.050717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_115-3_0_2_line_40 |  | 36 | 37 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_115-3_0_2_line_41 |  | 37 | 38 | 0.00038531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_115-3_0_2_line_42 |  | 38 | 40 | 0.0003814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_115-3_0_2_line_43 |  | 39 | 41 | 0.027571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_115-3_0_2_line_44 |  | 40 | 42 | 0.00038188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_115-3_0_2_line_45 |  | 41 | 43 | 0.0071245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_115-3_0_2_line_46 |  | 43 | 44 | 0.0021137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_115-3_0_2_line_47 |  | 44 | 45 | 0.0012537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_115-3_0_2_line_48 |  | 46 | 47 | 0.05261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_115-3_0_2_line_49 |  | 46 | 48 | 0.071498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-3_0_2_line_50 |  | 47 | 49 | 0.010556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_115-3_0_2_line_51 |  | 47 | 50 | 0.0027518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-3_0_2_line_52 |  | 48 | 51 | 0.054432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_115-3_0_2_line_53 |  | 48 | 52 | 0.060686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_115-3_0_2_line_54 |  | 49 | 53 | 0.0033642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-3_0_2_line_55 |  | 49 | 54 | 0.011248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_115-3_0_2_line_56 |  | 50 | 55 | 0.0081815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_115-3_0_2_line_57 |  | 51 | 56 | 0.028431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-3_0_2_line_58 |  | 51 | 57 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-3_0_2_line_59 |  | 52 | 58 | 0.014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-3_0_2_line_60 |  | 54 | 59 | 0.034463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_115-3_0_2_line_61 |  | 55 | 60 | 0.028147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_115-3_0_2_line_62 |  | 56 | 61 | 0.017302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_115-3_0_2_line_63 |  | 57 | 62 | 0.027229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_115-3_0_2_line_64 |  | 59 | 120 | 0.0050202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_115-3_0_2_line_65 |  | 60 | 83 | 0.033887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_115-3_0_2_line_66 |  | 61 | 82 | 0.040197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_115-3_0_2_line_67 |  | 63 | 64 | 0.00515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_115-3_0_2_line_68 |  | 64 | 66 | 0.0046807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_115-3_0_2_line_69 |  | 65 | 126 | 0.0061586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_115-3_0_2_line_70 |  | 66 | 126 | 0.005127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_115-3_0_2_line_71 |  | 67 | 68 | 0.022281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_115-3_0_2_line_72 |  | 67 | 69 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_115-3_0_2_line_73 |  | 68 | 70 | 0.010377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_115-3_0_2_line_74 |  | 69 | 71 | 0.017716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_115-3_0_2_line_75 |  | 70 | 72 | 0.023856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_115-3_0_2_line_76 |  | 71 | 73 | 0.034053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_115-3_0_2_line_77 |  | 72 | 74 | 0.030023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_115-3_0_2_line_78 |  | 73 | 77 | 0.025018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_115-3_0_2_line_79 |  | 73 | 78 | 0.014311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_115-3_0_2_line_80 |  | 74 | 87 | 0.031193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_115-3_0_2_line_81 |  | 75 | 76 | 0.0087623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_115-3_0_2_line_82 |  | 76 | 135 | 0.0059691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_115-3_0_2_line_83 |  | 77 | 88 | 0.0059673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_115-3_0_2_line_84 |  | 78 | 89 | 0.029534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_115-3_0_2_line_85 |  | 79 | 80 | 0.029365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_115-3_0_2_line_86 |  | 80 | 81 | 0.0086741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_115-3_0_2_line_87 |  | 81 | 82 | 0.013588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_115-3_0_2_line_88 |  | 83 | 84 | 0.00050051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_115-3_0_2_line_89 |  | 84 | 85 | 0.059293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_115-3_0_2_line_90 |  | 85 | 86 | 0.014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_115-3_0_2_line_91 |  | 86 | 118 | 0.0059673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_115-3_0_2_line_92 |  | 86 | 98 | 0.088631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_115-3_0_2_line_93 |  | 88 | 90 | 0.0059673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_115-3_0_2_line_94 |  | 89 | 91 | 0.017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_115-3_0_2_line_95 |  | 89 | 92 | 0.0021551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_115-3_0_2_line_96 |  | 90 | 118 | 0.0059673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_115-3_0_2_line_97 |  | 91 | 135 | 0.0059679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_115-3_0_2_line_98 |  | 92 | 134 | 0.0059681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_115-3_0_2_line_99 |  | 93 | 94 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_115-3_0_2_line_100 |  | 93 | 95 | 0.0050942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_115-3_0_2_line_101 |  | 94 | 96 | 0.0053542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_115-3_0_2_line_102 |  | 95 | 97 | 0.0051837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_115-3_0_2_line_103 |  | 96 | 98 | 0.020135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_115-3_0_2_line_104 |  | 98 | 99 | 0.032508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_115-3_0_2_line_105 |  | 99 | 111 | 0.014416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_115-3_0_2_line_106 |  | 100 | 101 | 0.0097058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_115-3_0_2_line_107 |  | 100 | 102 | 0.03878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_115-3_0_2_line_108 |  | 101 | 103 | 0.052592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_115-3_0_2_line_109 |  | 102 | 104 | 0.039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_115-3_0_2_line_110 |  | 102 | 105 | 0.079195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_115-3_0_2_line_111 |  | 103 | 106 | 0.036704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_115-3_0_2_line_112 |  | 105 | 109 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_115-3_0_2_line_113 |  | 105 | 110 | 0.01698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_115-3_0_2_line_114 |  | 106 | 107 | 0.034174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_115-3_0_2_line_115 |  | 107 | 108 | 0.085838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_115-3_0_2_line_116 |  | 108 | 113 | 0.051666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_115-3_0_2_line_117 |  | 110 | 115 | 0.0065406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_115-3_0_2_line_118 |  | 111 | 114 | 0.0058638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_115-3_0_2_line_119 |  | 112 | 113 | 0.010129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_115-3_0_2_line_120 |  | 112 | 114 | 0.011338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_115-3_0_2_line_121 |  | 115 | 116 | 0.00088551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_115-3_0_2_line_122 |  | 116 | 117 | 0.0045605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_115-3_0_2_line_123 |  | 119 | 120 | 0.0061719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_115-3_0_2_line_124 |  | 119 | 121 | 0.0050332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_115-3_0_2_line_125 |  | 121 | 122 | 0.005845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_115-3_0_2_line_126 |  | 122 | 123 | 0.025481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_115-3_0_2_line_127 |  | 123 | 124 | 0.026228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_115-3_0_2_line_128 |  | 123 | 125 | 0.097578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_115-3_0_2_line_129 |  | 124 | 128 | 0.00082467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_115-3_0_2_line_130 |  | 125 | 129 | 0.058056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_115-3_0_2_line_131 |  | 129 | 130 | 0.4291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_115-3_0_2_line_132 |  | 130 | 136 | 0.018402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_115-3_0_2_line_133 |  | 131 | 132 | 0.0059681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_115-3_0_2_line_134 |  | 131 | 133 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_115-3_0_2_line_135 |  | 132 | 134 | 0.0059681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-3_0_2_trafo_25 | 0.63 MVA 20/0.4 kV | 137 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2699877.2734 | 1241926.0936 | 2699868.753 | 1241941.3562
1 | 2699877.2734 | 1241926.0936 | 2699877.2734 | 1241926.0936 | 2699878.4633 | 1241918.2965 | 2699879.0337 | 1241910.4668
2 | 2699868.753 | 1241941.3562 | 2699867.7949 | 1241943.0724
3 | 2699879.0337 | 1241910.4668 | 2699879.0337 | 1241910.4668 | 2699876.3218 | 1241900.8805 | 2699873.3276 | 1241896.7018
4 | 2699855.6607 | 1241956.7867 | 2699864.9862 | 1241948.1036 | 2699867.7949 | 1241943.0724
5 | 2699870.6924 | 1241893.0242 | 2699873.3276 | 1241896.7018
6 | 2699855.6607 | 1241956.7867 | 2699843.096 | 1241953.6729
7 | 2699855.6607 | 1241956.7867 | 2699858.3208 | 1241968.5224
8 | 2699843.096 | 1241953.6729 | 2699826.1513 | 1241949.4736 | 2699818.3779 | 1241945.2944
9 | 2699856.2287 | 1241996.7046 | 2699858.6237 | 1241987.3822 | 2699859.5318 | 1241973.8649 | 2699858.3208 | 1241968.5224
10 | 2699728.4602 | 1241954.7849 | 2699725.8231 | 1241959.7061 | 2699720.689 | 1241967.8038 | 2699719.3733 | 1241969.2643
11 | 2699734.0895 | 1241942.0537 | 2699730.1399 | 1241951.6502 | 2699728.4602 | 1241954.7849
12 | 2699734.0895 | 1241942.0537 | 2699759.0755 | 1241953.6532
13 | 2699761.363 | 1241954.7151 | 2699759.0755 | 1241953.6532
14 | 2699761.363 | 1241954.7151 | 2699783.4719 | 1241964.9789 | 2699786.0755 | 1241966.4902
15 | 2699786.0755 | 1241966.4902 | 2699787.6161 | 1241967.3844
16 | 2699921.5181 | 1241950.9868 | 2699923.5496 | 1241951.2829
17 | 2699926.8964 | 1241951.7706 | 2699923.5496 | 1241951.2829
18 | 2699921.5181 | 1241950.9868 | 2699913.6966 | 1241949.8469 | 2699905.5687 | 1241957.9052
19 | 2699902.9056 | 1241965.2244 | 2699905.5687 | 1241957.9052 | 2699905.5687 | 1241957.9052
20 | 2699902.9056 | 1241965.2244 | 2699895.4494 | 1241985.7172
21 | 2699894.1105 | 1241989.3969 | 2699895.4494 | 1241985.7172
22 | 2699887.976 | 1242006.2572 | 2699894.1105 | 1241989.3969
23 | 2699887.976 | 1242006.2572 | 2699856.2287 | 1241996.7046
24 | 2699887.976 | 1242006.2572 | 2699882.4454 | 1242016.7832 | 2699877.71 | 1242017.8043 | 2699865.0296 | 1242014.2327
25 | 2699887.976 | 1242006.2572 | 2699923.0297 | 1242017.4669
26 | 2699856.2287 | 1241996.7046 | 2699852.6224 | 1241995.6428
27 | 2699923.0297 | 1242017.4669 | 2699940.9709 | 1242013.0656 | 2699941.0922 | 1242013.0823
28 | 2699822.2583 | 1241986.7033 | 2699852.6224 | 1241995.6428
29 | 2699941.5801 | 1242013.1494 | 2699941.0922 | 1242013.0823
30 | 2699822.2583 | 1241986.7033 | 2699817.8001 | 1241997.759 | 2699817.1975 | 1241998.7294
31 | 2699822.2583 | 1241986.7033 | 2699817.011 | 1241984.4466 | 2699806.6056 | 1241978.4069
32 | 2699963.1988 | 1242016.2515 | 2699961.3991 | 1242015.8784 | 2699941.5801 | 1242013.1494
33 | 2699982.2191 | 1242027.2933 | 2699974.6821 | 1242025.4489
34 | 2699982.2191 | 1242027.2933 | 2699983.8755 | 1242020.5383
35 | 2699982.2191 | 1242027.2933 | 2699991.2588 | 1242030.6371 | 2699992.6404 | 1242031.5338
36 | 2699818.3779 | 1241945.2944 | 2699809.5738 | 1241940.561
37 | 2699817.1975 | 1241998.7294 | 2699813.0982 | 1242005.3301 | 2699793.1818 | 1242023.3365
38 | 2699799.1898 | 1241974.1023 | 2699806.6056 | 1241978.4069
39 | 2699809.5738 | 1241940.561 | 2699800.9359 | 1241935.917 | 2699800.5009 | 1241925.3683 | 2699810.8571 | 1241905.7608 | 2699814.4931 | 1241898.4359
40 | 2699788.6095 | 1241967.961 | 2699799.1898 | 1241974.1023
41 | 2699788.6095 | 1241967.961 | 2699788.2762 | 1241967.7676
42 | 2699788.2762 | 1241967.7676 | 2699787.9464 | 1241967.5761
43 | 2699771.9721 | 1242040.9404 | 2699788.237 | 1242027.8071 | 2699793.1818 | 1242023.3365
44 | 2699787.9464 | 1241967.5761 | 2699787.6161 | 1241967.3844
45 | 2699771.9721 | 1242040.9404 | 2699766.429 | 1242045.4163
46 | 2699766.429 | 1242045.4163 | 2699764.7845 | 1242046.7441
47 | 2699764.7845 | 1242046.7441 | 2699763.8091 | 1242047.5317
48 | 2700003.5898 | 1242040.1298 | 2699997.8046 | 1242046.4594 | 2699990.4629 | 1242052.7294 | 2699965.1642 | 1242076.01
49 | 2699918.6352 | 1242130.2013 | 2699935.7375 | 1242108.7061 | 2699953.4757 | 1242087.622 | 2699965.1642 | 1242076.01
50 | 2699995.4622 | 1242033.3655 | 2700003.5898 | 1242040.1298
51 | 2700003.5898 | 1242040.1298 | 2700005.6926 | 1242041.9049
52 | 2699918.6352 | 1242130.2013 | 2699892.7336 | 1242159.6879 | 2699881.8251 | 1242170.3458
53 | 2699918.6352 | 1242130.2013 | 2699946.8423 | 1242152.8157 | 2699949.2702 | 1242156.8041 | 2699956.5164 | 1242162.4749 | 2699951.0058 | 1242171.6027
54 | 2699995.4622 | 1242033.3655 | 2699992.6404 | 1242031.5338
55 | 2699995.4622 | 1242033.3655 | 2700002.7373 | 1242024.7704
56 | 2700011.9445 | 1242047.1823 | 2700005.6926 | 1242041.9049
57 | 2699881.8251 | 1242170.3458 | 2699886.7586 | 1242174.1651 | 2699894.916 | 1242180.4961 | 2699904.0733 | 1242188.0427
58 | 2699881.8251 | 1242170.3458 | 2699866.2455 | 1242185.2931
59 | 2699943.4181 | 1242184.171 | 2699951.0058 | 1242171.6027
60 | 2700002.7373 | 1242024.7704 | 2700020.7785 | 1241995.4069
61 | 2700011.9445 | 1242047.1823 | 2700029.4512 | 1242061.9601 | 2700033.2381 | 1242065.5767
62 | 2699904.0733 | 1242188.0427 | 2699909.9577 | 1242192.8921 | 2699913.4212 | 1242195.9972 | 2699917.1525 | 1242199.3626
63 | 2699846.597 | 1242204.1443 | 2699866.2455 | 1242185.2931
64 | 2700023.4066 | 1241991.1295 | 2700020.7785 | 1241995.4069
65 | 2700057.7036 | 1242089.0232 | 2700054.4537 | 1242085.8331 | 2700042.7263 | 1242074.638 | 2700033.2381 | 1242065.5767
66 | 2699917.1525 | 1242199.3626 | 2699917.6397 | 1242239.5571
67 | 2699983.8755 | 1242020.5383 | 2699978.8327 | 1242019.4928
68 | 2699978.8327 | 1242019.4928 | 2699974.2495 | 1242018.5426
69 | 2699969.2292 | 1242017.5018 | 2699963.1988 | 1242016.2515
70 | 2699974.2495 | 1242018.5426 | 2699969.2292 | 1242017.5018
71 | 2700006.4738 | 1242250.0598 | 2700020.6064 | 1242232.8339
72 | 2700029.7513 | 1242221.6874 | 2700020.6064 | 1242232.8339
73 | 2700006.4738 | 1242250.0598 | 2699999.8919 | 1242258.0824
74 | 2700029.7513 | 1242221.6874 | 2700039.0509 | 1242209.1568 | 2700040.3264 | 1242207.474
75 | 2699999.8919 | 1242258.0824 | 2699984.7605 | 1242276.5257
76 | 2700060.8967 | 1242180.3363 | 2700040.3264 | 1242207.474
77 | 2699965.7176 | 1242299.7367 | 2699984.7605 | 1242276.5257
78 | 2700060.8967 | 1242180.3363 | 2700076.5099 | 1242160.7883
79 | 2700060.8967 | 1242180.3363 | 2700049.6921 | 1242171.4329
80 | 2699965.7176 | 1242299.7367 | 2699945.9323 | 1242323.8525
81 | 2700008.0274 | 1242175.3627 | 2700006.9509 | 1242176.6576 | 2700002.389 | 1242182.0699
82 | 2700011.8432 | 1242170.7726 | 2700008.0274 | 1242175.3627
83 | 2700080.2339 | 1242156.1257 | 2700076.5099 | 1242160.7883
84 | 2700026.5688 | 1242153.059 | 2700049.6921 | 1242171.4329
85 | 2699883.2573 | 1242278.0692 | 2699902.8139 | 1242256.1637
86 | 2699902.8139 | 1242256.1637 | 2699908.5906 | 1242249.6931
87 | 2699917.6397 | 1242239.5571 | 2699908.5906 | 1242249.6931
88 | 2700057.7036 | 1242089.0232 | 2700058.0608 | 1242089.3738
89 | 2700100.375 | 1242130.9086 | 2700058.0608 | 1242089.3738
90 | 2700100.375 | 1242130.9086 | 2700091.4061 | 1242142.1379
91 | 2700091.4061 | 1242142.1379 | 2700087.682 | 1242146.8005
92 | 2700091.4061 | 1242142.1379 | 2700161.4423 | 1242196.4556
93 | 2700083.958 | 1242151.4631 | 2700080.2339 | 1242156.1257
94 | 2700026.5688 | 1242153.059 | 2700015.6583 | 1242166.1834
95 | 2700026.5688 | 1242153.059 | 2700027.9323 | 1242151.3901
96 | 2700087.682 | 1242146.8005 | 2700083.958 | 1242151.4631
97 | 2700015.6583 | 1242166.1834 | 2700011.8432 | 1242170.7726
98 | 2700031.7082 | 1242146.7682 | 2700027.9323 | 1242151.3901
99 | 2700178.5086 | 1242177.5656 | 2700187.3656 | 1242165.6122
100 | 2700190.3983 | 1242161.5192 | 2700187.3656 | 1242165.6122
101 | 2700178.5086 | 1242177.5656 | 2700175.3211 | 1242181.8676
102 | 2700190.3983 | 1242161.5192 | 2700193.4844 | 1242157.3542
103 | 2700161.4423 | 1242196.4556 | 2700175.3211 | 1242181.8676 | 2700175.3211 | 1242181.8676
104 | 2700161.4423 | 1242196.4556 | 2700165.6769 | 1242203.1433 | 2700168.6731 | 1242209.2875 | 2700170.3953 | 1242215.6548 | 2700170.2978 | 1242220.9794 | 2700169.0219 | 1242226.6845
105 | 2700169.0219 | 1242226.6845 | 2700177.9555 | 1242237.9988
106 | 2700391.6255 | 1242293.0631 | 2700399.5976 | 1242287.527
107 | 2700423.5123 | 1242268.7839 | 2700416.8899 | 1242267.8378 | 2700404.4516 | 1242271.4524 | 2700399.1991 | 1242274.4436 | 2700399.2273 | 1242280.3708 | 2700399.5976 | 1242287.527
108 | 2700391.6255 | 1242293.0631 | 2700392.383 | 1242301.0153 | 2700391.67 | 1242308.2977 | 2700388.722 | 1242316.2985 | 2700370.1657 | 1242338.3126
109 | 2700423.5123 | 1242268.7839 | 2700426.5991 | 1242278.0432 | 2700427.8706 | 1242286.0042 | 2700426.5618 | 1242290.5188 | 2700421.5943 | 1242294.5379 | 2700419.7118 | 1242297.2081 | 2700420.2531 | 1242301.4093 | 2700421.2846 | 1242303.7796
110 | 2700423.5123 | 1242268.7839 | 2700420.3242 | 1242259.256 | 2700455.868 | 1242243.1785 | 2700469.0819 | 1242249.1289 | 2700473.4747 | 1242253.1508 | 2700474.8811 | 1242257.6114 | 2700473.9282 | 1242262.5324
111 | 2700370.1657 | 1242338.3126 | 2700353.8492 | 1242309.2922 | 2700351.9844 | 1242306.436
112 | 2700473.9282 | 1242262.5324 | 2700487.9216 | 1242257.4194
113 | 2700473.9282 | 1242262.5324 | 2700470.9963 | 1242267.7868 | 2700467.7794 | 1242275.1379 | 2700467.8025 | 1242278.0762
114 | 2700333.3021 | 1242277.8207 | 2700351.9844 | 1242306.436
115 | 2700333.3021 | 1242277.8207 | 2700247.6703 | 1242271.8692
116 | 2700247.6703 | 1242271.8692 | 2700214.1216 | 1242261.6504 | 2700203.3463 | 1242257.6876 | 2700198.8443 | 1242255.2606
117 | 2700467.8541 | 1242284.6167 | 2700467.8025 | 1242278.0762
118 | 2700177.9555 | 1242237.9988 | 2700179.2819 | 1242239.6787 | 2700181.8559 | 1242242.3691
119 | 2700190.291 | 1242249.8815 | 2700194.1903 | 1242252.7515 | 2700198.8443 | 1242255.2606
120 | 2700190.291 | 1242249.8815 | 2700186.0726 | 1242246.7766 | 2700181.8559 | 1242242.3691
121 | 2700467.8611 | 1242285.5021 | 2700467.8541 | 1242284.6167
122 | 2700467.897 | 1242290.0625 | 2700467.8611 | 1242285.5021
123 | 2700026.6025 | 1241985.8496 | 2700024.646 | 1241989.1123 | 2700023.4066 | 1241991.1295
124 | 2700026.6025 | 1241985.8496 | 2700029.1911 | 1241981.5331
125 | 2700032.1972 | 1241976.5203 | 2700029.1911 | 1241981.5331
126 | 2700045.302 | 1241954.6674 | 2700032.1972 | 1241976.5203
127 | 2700045.302 | 1241954.6674 | 2700032.72 | 1241948.395 | 2700021.4371 | 1241943.8356
128 | 2700045.302 | 1241954.6674 | 2700134.0908 | 1241995.1401
129 | 2700021.4371 | 1241943.8356 | 2700020.6725 | 1241943.5266
130 | 2700134.0908 | 1241995.1401 | 2700138.1127 | 1241988.9143 | 2700150.0722 | 1241962.6293 | 2700159.5752 | 1241943.0191
131 | 2700159.5752 | 1241943.0191 | 2700495.2943 | 1241675.778
132 | 2700495.2943 | 1241675.778 | 2700507.0589 | 1241677.1893 | 2700512.909 | 1241680.1421
133 | 2700039.2599 | 1242137.5245 | 2700035.484 | 1242142.1464
134 | 2700048.711 | 1242125.9559 | 2700039.2599 | 1242137.5245
135 | 2700035.484 | 1242142.1464 | 2700031.7082 | 1242146.7682

## bus_geodata
| x | y | coords
0 | 2699877.2734 | 1241926.0936
1 | 2699868.753 | 1241941.3562
2 | 2699879.0337 | 1241910.4668
3 | 2699867.7949 | 1241943.0724
4 | 2699873.3276 | 1241896.7018
5 | 2699855.6607 | 1241956.7867
6 | 2699870.6924 | 1241893.0242
7 | 2699843.096 | 1241953.6729
8 | 2699858.3208 | 1241968.5224
9 | 2699728.4602 | 1241954.7849
10 | 2699719.3733 | 1241969.2643
11 | 2699734.0895 | 1241942.0537
12 | 2699759.0755 | 1241953.6532
13 | 2699761.363 | 1241954.7151
14 | 2699786.0755 | 1241966.4902
15 | 2699923.5496 | 1241951.2829
16 | 2699921.5181 | 1241950.9868
17 | 2699926.8964 | 1241951.7706
18 | 2699905.5687 | 1241957.9052
19 | 2699902.9056 | 1241965.2244
20 | 2699895.4494 | 1241985.7172
21 | 2699894.1105 | 1241989.3969
22 | 2699887.976 | 1242006.2572
23 | 2699856.2287 | 1241996.7046
24 | 2699865.0296 | 1242014.2327
25 | 2699923.0297 | 1242017.4669
26 | 2699852.6224 | 1241995.6428
27 | 2699941.0922 | 1242013.0823
28 | 2699822.2583 | 1241986.7033
29 | 2699941.5801 | 1242013.1494
30 | 2699974.6821 | 1242025.4489
31 | 2699982.2191 | 1242027.2933
32 | 2699818.3779 | 1241945.2944
33 | 2699817.1975 | 1241998.7294
34 | 2699806.6056 | 1241978.4069
35 | 2699809.5738 | 1241940.561
36 | 2699799.1898 | 1241974.1023
37 | 2699788.6095 | 1241967.961
38 | 2699788.2762 | 1241967.7676
39 | 2699793.1818 | 1242023.3365
40 | 2699787.9464 | 1241967.5761
41 | 2699771.9721 | 1242040.9404
42 | 2699787.6161 | 1241967.3844
43 | 2699766.429 | 1242045.4163
44 | 2699764.7845 | 1242046.7441
45 | 2699763.8091 | 1242047.5317
46 | 2699965.1642 | 1242076.01
47 | 2700003.5898 | 1242040.1298
48 | 2699918.6352 | 1242130.2013
49 | 2699995.4622 | 1242033.3655
50 | 2700005.6926 | 1242041.9049
51 | 2699881.8251 | 1242170.3458
52 | 2699951.0058 | 1242171.6027
53 | 2699992.6404 | 1242031.5338
54 | 2700002.7373 | 1242024.7704
55 | 2700011.9445 | 1242047.1823
56 | 2699904.0733 | 1242188.0427
57 | 2699866.2455 | 1242185.2931
58 | 2699943.4181 | 1242184.171
59 | 2700020.7785 | 1241995.4069
60 | 2700033.2381 | 1242065.5767
61 | 2699917.1525 | 1242199.3626
62 | 2699846.597 | 1242204.1443
63 | 2699983.8755 | 1242020.5383
64 | 2699978.8327 | 1242019.4928
65 | 2699963.1988 | 1242016.2515
66 | 2699974.2495 | 1242018.5426
67 | 2700020.6064 | 1242232.8339
68 | 2700006.4738 | 1242250.0598
69 | 2700029.7513 | 1242221.6874
70 | 2699999.8919 | 1242258.0824
71 | 2700040.3264 | 1242207.474
72 | 2699984.7605 | 1242276.5257
73 | 2700060.8967 | 1242180.3363
74 | 2699965.7176 | 1242299.7367
75 | 2700002.389 | 1242182.0699
76 | 2700008.0274 | 1242175.3627
77 | 2700076.5099 | 1242160.7883
78 | 2700049.6921 | 1242171.4329
79 | 2699883.2573 | 1242278.0692
80 | 2699902.8139 | 1242256.1637
81 | 2699908.5906 | 1242249.6931
82 | 2699917.6397 | 1242239.5571
83 | 2700057.7036 | 1242089.0232
84 | 2700058.0608 | 1242089.3738
85 | 2700100.375 | 1242130.9086
86 | 2700091.4061 | 1242142.1379
87 | 2699945.9323 | 1242323.8525
88 | 2700080.2339 | 1242156.1257
89 | 2700026.5688 | 1242153.059
90 | 2700083.958 | 1242151.4631
91 | 2700015.6583 | 1242166.1834
92 | 2700027.9323 | 1242151.3901
93 | 2700187.3656 | 1242165.6122
94 | 2700178.5086 | 1242177.5656
95 | 2700190.3983 | 1242161.5192
96 | 2700175.3211 | 1242181.8676
97 | 2700193.4844 | 1242157.3542
98 | 2700161.4423 | 1242196.4556
99 | 2700169.0219 | 1242226.6845
100 | 2700399.5976 | 1242287.527
101 | 2700391.6255 | 1242293.0631
102 | 2700423.5123 | 1242268.7839
103 | 2700370.1657 | 1242338.3126
104 | 2700421.2846 | 1242303.7796
105 | 2700473.9282 | 1242262.5324
106 | 2700351.9844 | 1242306.436
107 | 2700333.3021 | 1242277.8207
108 | 2700247.6703 | 1242271.8692
109 | 2700487.9216 | 1242257.4194
110 | 2700467.8025 | 1242278.0762
111 | 2700177.9555 | 1242237.9988
112 | 2700190.291 | 1242249.8815
113 | 2700198.8443 | 1242255.2606
114 | 2700181.8559 | 1242242.3691
115 | 2700467.8541 | 1242284.6167
116 | 2700467.8611 | 1242285.5021
117 | 2700467.897 | 1242290.0625
118 | 2700087.682 | 1242146.8005
119 | 2700026.6025 | 1241985.8496
120 | 2700023.4066 | 1241991.1295
121 | 2700029.1911 | 1241981.5331
122 | 2700032.1972 | 1241976.5203
123 | 2700045.302 | 1241954.6674
124 | 2700021.4371 | 1241943.8356
125 | 2700134.0908 | 1241995.1401
126 | 2699969.2292 | 1242017.5018
127 | 2699814.4931 | 1241898.4359
128 | 2700020.6725 | 1241943.5266
129 | 2700159.5752 | 1241943.0191
130 | 2700495.2943 | 1241675.778
131 | 2700039.2599 | 1242137.5245
132 | 2700035.484 | 1242142.1464
133 | 2700048.711 | 1242125.9559
134 | 2700031.7082 | 1242146.7682
135 | 2700011.8432 | 1242170.7726
136 | 2700512.909 | 1241680.1421
137 | 2699887.976 | 1242006.2572

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99084 | -0.17618 | 0.0071066 | 0.0017811
1 | 0.9911 | -0.17103 | 0.0034592 | 0.00086696
2 | 0.9907 | -0.17883 | 0.0015837 | 0.00039691
3 | 0.99114 | -0.17033 | 0.0033009 | 0.00082728
4 | 0.99059 | -0.18094 | 0.0072843 | 0.0018256
5 | 0.99153 | -0.16267 | 0 | 0
6 | 0.99059 | -0.18099 | 0.00060917 | 0.00015267
7 | 0.99136 | -0.16606 | 0.0038195 | 0.00095725
8 | 0.99195 | -0.15455 | 0.0058841 | 0.0014747
9 | 0.98977 | -0.19691 | 0.0032295 | 0.00080938
10 | 0.98969 | -0.19836 | 0.0047457 | 0.0011894
11 | 0.98987 | -0.19493 | 0 | 0
12 | 0.99007 | -0.19103 | 0.0020613 | 0.0005166
13 | 0.99009 | -0.19058 | 0.0024281 | 0.00060853
14 | 0.99041 | -0.18451 | 0.0048423 | 0.0012136
15 | 0.995 | -0.095936 | 0.0022567 | 0.00056557
16 | 0.99501 | -0.0957 | 0.0011567 | 0.0002899
17 | 0.99498 | -0.096192 | 0.0042933 | 0.001076
18 | 0.99514 | -0.093075 | 0.003883 | 0.00097317
19 | 0.99523 | -0.091486 | 0.0011567 | 0.0002899
20 | 0.99548 | -0.086595 | 0.0099974 | 0.0025056
21 | 0.99556 | -0.085029 | 0.0014573 | 0.00036523
22 | 0.99596 | -0.077396 | 0 | 0
23 | 0.99311 | -0.13225 | 0 | 0
24 | 0.9959 | -0.078515 | 0.0021327 | 0.0005345
25 | 1 | 0 | -0.25997 | -0.065873
26 | 0.99293 | -0.13559 | 0.00062201 | 0.00015589
27 | 0.99768 | -0.043828 | 0.00085871 | 0.00021521
28 | 0.9915 | -0.16336 | 0 | 0
29 | 0.99762 | -0.044985 | 0.0008608 | 0.00021574
30 | 0.99154 | -0.16121 | 0.0095852 | 0.0024023
31 | 0.99161 | -0.15989 | 0 | 0
32 | 0.9911 | -0.17115 | 0.0037814 | 0.0009477
33 | 0.99132 | -0.16678 | 0.0013287 | 0.000333
34 | 0.99093 | -0.1743 | 0.006436 | 0.001613
35 | 0.99103 | -0.17242 | 0.0038926 | 0.00097559
36 | 0.99071 | -0.17861 | 0.0055996 | 0.0014034
37 | 0.99046 | -0.18355 | 0.0013541 | 0.00033937
38 | 0.99045 | -0.1837 | 0.0013565 | 0.00033998
39 | 0.99089 | -0.17505 | 0.00084256 | 0.00021117
40 | 0.99044 | -0.18383 | 0.0013554 | 0.0003397
41 | 0.99058 | -0.18122 | 0.0057509 | 0.0014413
42 | 0.99044 | -0.18396 | 0.0013546 | 0.0003395
43 | 0.99053 | -0.18209 | 0.0022904 | 0.00057403
44 | 0.99052 | -0.18226 | 0.0022794 | 0.00057128
45 | 0.99052 | -0.18231 | 0.0022907 | 0.0005741
46 | 0.98597 | -0.26843 | 0.0055803 | 0.0013986
47 | 0.98896 | -0.21083 | 0 | 0
48 | 0.98228 | -0.34007 | 0 | 0
49 | 0.99003 | -0.19012 | 0 | 0
50 | 0.98883 | -0.21323 | 0.0021251 | 0.00053259
51 | 0.97969 | -0.39078 | 0 | 0
52 | 0.98205 | -0.3447 | 0.0012106 | 0.0003034
53 | 0.99039 | -0.18322 | 0.001083 | 0.00027141
54 | 0.98998 | -0.19115 | 0 | 0
55 | 0.98848 | -0.22006 | 0.0024952 | 0.00062536
56 | 0.97841 | -0.41585 | 0.042766 | 0.010718
57 | 0.97963 | -0.39194 | 0.0016729 | 0.00041927
58 | 0.98201 | -0.3455 | 0.0030139 | 0.00075535
59 | 0.98982 | -0.19432 | 0.00049639 | 0.00012441
60 | 0.98733 | -0.24235 | 0.0078035 | 0.0019557
61 | 0.97832 | -0.41766 | 0.0017622 | 0.00044165
62 | 0.9796 | -0.39257 | 0.0012761 | 0.00031981
63 | 0.99241 | -0.14436 | 0.0014013 | 0.00035119
64 | 0.99302 | -0.13275 | 0.0013601 | 0.00034086
65 | 0.99494 | -0.096074 | 0.0016426 | 0.00041169
66 | 0.99358 | -0.1221 | 0.0010924 | 0.00027377
67 | 0.98289 | -0.32887 | 0.00070971 | 0.00017787
68 | 0.98281 | -0.33042 | 0.00076053 | 0.00019061
69 | 0.98295 | -0.32769 | 0 | 0
70 | 0.98278 | -0.33099 | 0.00076036 | 0.00019056
71 | 0.98302 | -0.32623 | 0.0013112 | 0.00032862
72 | 0.98273 | -0.33199 | 0.00093609 | 0.00023461
73 | 0.98321 | -0.32263 | 0 | 0
74 | 0.98269 | -0.33274 | 0.000718 | 0.00017995
75 | 0.98285 | -0.3297 | 0.0011601 | 0.00029075
76 | 0.98286 | -0.32951 | 0.00060861 | 0.00015253
77 | 0.98352 | -0.31651 | 0.00060546 | 0.00015174
78 | 0.98311 | -0.32462 | 0.0010965 | 0.0002748
79 | 0.97808 | -0.42239 | 0.0010593 | 0.00026549
80 | 0.97811 | -0.42182 | 0.0016122 | 0.00040405
81 | 0.97813 | -0.4214 | 0.00073086 | 0.00018317
82 | 0.97817 | -0.42056 | 0.00055788 | 0.00013982
83 | 0.98619 | -0.26452 | 0.0017852 | 0.00044742
84 | 0.98617 | -0.26483 | 0.00060546 | 0.00015174
85 | 0.98431 | -0.30118 | 0 | 0
86 | 0.98385 | -0.31002 | 0.00060546 | 0.00015174
87 | 0.98267 | -0.33312 | 0.00066438 | 0.00016651
88 | 0.9836 | -0.31498 | 0.00060593 | 0.00015186
89 | 0.98293 | -0.32815 | 0 | 0
90 | 0.98368 | -0.31339 | 0.00060546 | 0.00015174
91 | 0.98288 | -0.32907 | 0.00060662 | 0.00015203
92 | 0.98292 | -0.32829 | 0.00060593 | 0.00015186
93 | 0.98218 | -0.34269 | 0.0010487 | 0.00026282
94 | 0.98224 | -0.34157 | 0.001232 | 0.00030877
95 | 0.98217 | -0.34297 | 0.0017609 | 0.00044132
96 | 0.98227 | -0.34105 | 0.0029253 | 0.00073315
97 | 0.98216 | -0.3431 | 0.0013312 | 0.00033364
98 | 0.98242 | -0.33803 | 0 | 0
99 | 0.98214 | -0.34345 | 0 | 0
100 | 0.98061 | -0.37348 | 0.0020232 | 0.00050706
101 | 0.98066 | -0.37267 | 0 | 0
102 | 0.98052 | -0.37527 | 0 | 0
103 | 0.98088 | -0.36832 | 0 | 0
104 | 0.98052 | -0.37541 | 0.00020405 | 5.1139e-05
105 | 0.98035 | -0.37862 | 0 | 0
106 | 0.98103 | -0.36528 | 0.00046833 | 0.00011738
107 | 0.98119 | -0.36216 | 0 | 0
108 | 0.98159 | -0.35433 | 0 | 0
109 | 0.98034 | -0.37885 | 0.00083915 | 0.00021031
110 | 0.98033 | -0.37908 | 0.00041604 | 0.00010427
111 | 0.98202 | -0.34586 | 0.00067982 | 0.00017038
112 | 0.98189 | -0.34838 | 0.0010921 | 0.00027371
113 | 0.98183 | -0.34962 | 0.0017323 | 0.00043416
114 | 0.98198 | -0.34677 | 0.00067909 | 0.0001702
115 | 0.98032 | -0.37921 | 0.00019938 | 4.9968e-05
116 | 0.98032 | -0.37922 | 0.00041574 | 0.00010419
117 | 0.98032 | -0.37926 | 0.00046353 | 0.00011617
118 | 0.98377 | -0.31174 | 0.00060593 | 0.00015186
119 | 0.98977 | -0.19519 | 0.00049645 | 0.00012442
120 | 0.9898 | -0.19473 | 0.00049674 | 0.00012449
121 | 0.98976 | -0.19552 | 0.00049598 | 0.0001243
122 | 0.98974 | -0.19585 | 0.00049645 | 0.00012442
123 | 0.98968 | -0.19706 | 0 | 0
124 | 0.98965 | -0.19753 | 0.00049761 | 0.00012471
125 | 0.98953 | -0.19999 | 0 | 0
126 | 0.99419 | -0.11035 | 0.0016416 | 0.00041142
127 | 0.99088 | -0.17535 | 0.0032526 | 0.00081518
128 | 0.98965 | -0.19754 | 0.00049616 | 0.00012435
129 | 0.98944 | -0.20172 | 0.0011931 | 0.00029901
130 | 0.98926 | -0.20539 | 0 | 0
131 | 0.98288 | -0.32907 | 0.00060546 | 0.00015174
132 | 0.98289 | -0.32888 | 0.00060594 | 0.00015186
133 | 0.98286 | -0.3294 | 0.0012114 | 0.0003036
134 | 0.9829 | -0.32862 | 0.00060546 | 0.00015174
135 | 0.98287 | -0.32932 | 0.00060637 | 0.00015197
136 | 0.98925 | -0.20554 | 0.00047176 | 0.00011823
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016586 | -0.0041571 | 0.01659 | 0.0041595 | 4.0668e-06 | 2.3775e-06 | 0.024908 | 0.024908 | 0.024908 | 0.99084 | -0.17618 | 0.9911 | -0.17103 | 6.8429
1 | 0.0094791 | 0.002376 | -0.0094779 | -0.0023754 | 1.196e-06 | 5.6276e-07 | 0.014236 | 0.014236 | 0.014236 | 0.99084 | -0.17618 | 0.9907 | -0.17883 | 3.9109
2 | -0.020049 | -0.0050264 | 0.02005 | 0.0050268 | 6.6785e-07 | 4.0209e-07 | 0.030102 | 0.030102 | 0.030102 | 0.9911 | -0.17103 | 0.99114 | -0.17033 | 8.2697
3 | 0.0078942 | 0.0019785 | -0.0078934 | -0.0019782 | 7.9626e-07 | 3.1515e-07 | 0.011857 | 0.011857 | 0.011857 | 0.9907 | -0.17883 | 0.99059 | -0.18094 | 3.2574
4 | -0.02335 | -0.0058541 | 0.023359 | 0.0058593 | 8.5282e-06 | 5.2195e-06 | 0.035057 | 0.035057 | 0.035057 | 0.99114 | -0.17033 | 0.99153 | -0.16267 | 9.6311
5 | 0.00060917 | 0.00015261 | -0.00060917 | -0.00015267 | 1.4206e-09 | -5.7335e-08 | 0.00091504 | 0.00091507 | 0.00091507 | 0.99059 | -0.18094 | 0.99059 | -0.18099 | 0.25139
6 | 0.014752 | 0.0036982 | -0.01475 | -0.0036969 | 2.3793e-06 | 1.3558e-06 | 0.022139 | 0.022139 | 0.022139 | 0.99153 | -0.16267 | 0.99136 | -0.16606 | 6.0822
7 | -0.038111 | -0.0095575 | 0.038126 | 0.0095668 | 1.4762e-05 | 9.2926e-06 | 0.057196 | 0.057196 | 0.057196 | 0.99153 | -0.16267 | 0.99195 | -0.15455 | 15.7132
8 | 0.01093 | 0.0027396 | -0.010927 | -0.0027383 | 2.6529e-06 | 1.3591e-06 | 0.016406 | 0.016406 | 0.016406 | 0.99136 | -0.16606 | 0.9911 | -0.17115 | 4.5072
9 | -0.04401 | -0.011042 | 0.044057 | 0.011071 | 4.6833e-05 | 2.9603e-05 | 0.066023 | 0.066023 | 0.066023 | 0.99195 | -0.15455 | 0.99311 | -0.13225 | 18.1381
10 | 0.004746 | 0.0011894 | -0.0047457 | -0.0011894 | 3.2717e-07 | -1.0846e-08 | 0.0071351 | 0.0071351 | 0.0071351 | 0.98977 | -0.19691 | 0.98969 | -0.19836 | 1.9602
11 | -0.0079754 | -0.0019987 | 0.0079762 | 0.001999 | 7.512e-07 | 3.0167e-07 | 0.01199 | 0.01199 | 0.01199 | 0.98977 | -0.19691 | 0.98987 | -0.19493 | 3.294
12 | -0.0079762 | -0.001999 | 0.0079777 | 0.0019996 | 1.4851e-06 | 5.9628e-07 | 0.01199 | 0.01199 | 0.01199 | 0.98987 | -0.19493 | 0.99007 | -0.19103 | 3.294
13 | -0.010039 | -0.0025162 | 0.010039 | 0.0025163 | 2.1529e-07 | 1.0535e-07 | 0.015088 | 0.015088 | 0.015088 | 0.99007 | -0.19103 | 0.99009 | -0.19058 | 4.1451
14 | -0.012467 | -0.0031249 | 0.012471 | 0.0031268 | 3.6054e-06 | 1.9552e-06 | 0.018737 | 0.018737 | 0.018737 | 0.99009 | -0.19058 | 0.99041 | -0.18451 | 5.1476
15 | -0.017313 | -0.0043404 | 0.017314 | 0.0043407 | 4.5197e-07 | 2.6634e-07 | 0.026012 | 0.026012 | 0.026012 | 0.99041 | -0.18451 | 0.99044 | -0.18396 | 7.1462
16 | -0.00655 | -0.0016416 | 0.0065501 | 0.0016416 | 7.3871e-08 | 2.0612e-08 | 0.0097956 | 0.0097956 | 0.0097956 | 0.995 | -0.095936 | 0.99501 | -0.0957 | 2.6911
17 | 0.0042934 | 0.001076 | -0.0042933 | -0.001076 | 5.2287e-08 | -1.0464e-08 | 0.0064208 | 0.0064208 | 0.0064208 | 0.995 | -0.095936 | 0.99498 | -0.096192 | 1.7639
18 | -0.0077068 | -0.0019315 | 0.0077078 | 0.0019319 | 9.6386e-07 | 3.6551e-07 | 0.011525 | 0.011525 | 0.011525 | 0.99501 | -0.0957 | 0.99514 | -0.093075 | 3.1663
19 | -0.011591 | -0.002905 | 0.011592 | 0.0029055 | 8.7733e-07 | 4.6029e-07 | 0.017331 | 0.017331 | 0.017331 | 0.99514 | -0.093075 | 0.99523 | -0.091486 | 4.7614
20 | -0.012748 | -0.0031954 | 0.012751 | 0.003197 | 2.9711e-06 | 1.6181e-06 | 0.019061 | 0.019061 | 0.019061 | 0.99523 | -0.091486 | 0.99548 | -0.086595 | 5.2365
21 | -0.022749 | -0.0057026 | 0.02275 | 0.0057036 | 1.6979e-06 | 1.0358e-06 | 0.034005 | 0.034005 | 0.034005 | 0.99548 | -0.086595 | 0.99556 | -0.085029 | 9.342
22 | -0.024208 | -0.0060689 | 0.024217 | 0.0060743 | 8.8084e-06 | 5.404e-06 | 0.036183 | 0.036183 | 0.036183 | 0.99556 | -0.085029 | 0.99596 | -0.077396 | 9.9403
23 | 0.094594 | 0.023877 | -0.094346 | -0.023719 | 0.00024786 | 0.0001582 | 0.14139 | 0.14139 | 0.14139 | 0.99596 | -0.077396 | 0.99311 | -0.13225 | 38.8433
24 | 0.0021328 | 0.00053418 | -0.0021327 | -0.0005345 | 1.1367e-07 | -3.1573e-07 | 0.0031864 | 0.0031865 | 0.0031865 | 0.99596 | -0.077396 | 0.9959 | -0.078515 | 0.87542
25 | -0.12094 | -0.030486 | 0.12139 | 0.030773 | 0.00044971 | 0.00028733 | 0.18076 | 0.18076 | 0.18076 | 0.99596 | -0.077396 | 1 | 0 | 49.6589
26 | 0.05029 | 0.012648 | -0.050282 | -0.012643 | 8.0077e-06 | 5.0763e-06 | 0.075367 | 0.075367 | 0.075367 | 0.99311 | -0.13225 | 0.99293 | -0.13559 | 20.7052
27 | 0.13693 | 0.0351 | -0.13664 | -0.034914 | 0.00029027 | 0.00018553 | 0.20402 | 0.20403 | 0.20403 | 1 | 0 | 0.99768 | -0.043828 | 56.0508
28 | 0.04966 | 0.012487 | -0.049594 | -0.012445 | 6.5765e-05 | 4.1681e-05 | 0.074435 | 0.074435 | 0.074435 | 0.99293 | -0.13559 | 0.9915 | -0.16336 | 20.4492
29 | 0.13578 | 0.034699 | -0.13577 | -0.034694 | 7.5922e-06 | 4.8526e-06 | 0.20274 | 0.20274 | 0.20274 | 0.99768 | -0.043828 | 0.99762 | -0.044985 | 55.699
30 | 0.014794 | 0.0037113 | -0.014792 | -0.0037099 | 2.4152e-06 | 1.3773e-06 | 0.022204 | 0.022204 | 0.022204 | 0.9915 | -0.16336 | 0.99132 | -0.16678 | 6.1001
31 | 0.034799 | 0.0087341 | -0.034781 | -0.0087227 | 1.8152e-05 | 1.1388e-05 | 0.052231 | 0.052231 | 0.052231 | 0.9915 | -0.16336 | 0.99093 | -0.1743 | 14.3491
32 | 0.13491 | 0.034479 | -0.13458 | -0.034266 | 0.00033246 | 0.00021249 | 0.20146 | 0.20146 | 0.20146 | 0.99762 | -0.044985 | 0.99494 | -0.096074 | 55.3463
33 | -0.0095852 | -0.0024023 | 0.0095858 | 0.0024026 | 6.0209e-07 | 2.8525e-07 | 0.014385 | 0.014385 | 0.014385 | 0.99154 | -0.16121 | 0.99161 | -0.15989 | 3.9518
34 | -0.12704 | -0.032222 | 0.12713 | 0.032283 | 9.492e-05 | 6.0659e-05 | 0.19077 | 0.19077 | 0.19077 | 0.99161 | -0.15989 | 0.99241 | -0.14436 | 52.4099
35 | 0.11745 | 0.029819 | -0.11732 | -0.029735 | 0.00013167 | 8.4122e-05 | 0.17639 | 0.17639 | 0.17639 | 0.99161 | -0.15989 | 0.99039 | -0.18322 | 48.4581
36 | 0.0071461 | 0.0017906 | -0.0071457 | -0.0017904 | 4.3149e-07 | 1.4735e-07 | 0.010729 | 0.010729 | 0.010729 | 0.9911 | -0.17115 | 0.99103 | -0.17242 | 2.9475
37 | 0.013463 | 0.0033769 | -0.013458 | -0.003374 | 5.3025e-06 | 2.9475e-06 | 0.02021 | 0.02021 | 0.02021 | 0.99132 | -0.16678 | 0.99089 | -0.17505 | 5.5522
38 | 0.028345 | 0.0071097 | -0.02834 | -0.0071061 | 5.8261e-06 | 3.6183e-06 | 0.042566 | 0.042566 | 0.042566 | 0.99093 | -0.1743 | 0.99071 | -0.17861 | 11.6941
39 | 0.0032531 | 0.00081482 | -0.0032526 | -0.00081518 | 4.5373e-07 | -3.63e-07 | 0.0048842 | 0.0048845 | 0.0048845 | 0.99103 | -0.17242 | 0.99088 | -0.17535 | 1.3419
40 | 0.02274 | 0.0057027 | -0.022735 | -0.0056995 | 5.352e-06 | 3.2678e-06 | 0.034156 | 0.034156 | 0.034156 | 0.99071 | -0.17861 | 0.99046 | -0.18355 | 9.3835
41 | 0.021381 | 0.0053601 | -0.02138 | -0.00536 | 1.4909e-07 | 9.0458e-08 | 0.032122 | 0.032122 | 0.032122 | 0.99046 | -0.18355 | 0.99045 | -0.1837 | 8.8246
42 | 0.020024 | 0.00502 | -0.020024 | -0.00502 | 1.2944e-07 | 7.7933e-08 | 0.030084 | 0.030084 | 0.030084 | 0.99045 | -0.1837 | 0.99044 | -0.18383 | 8.2647
43 | 0.012615 | 0.0031628 | -0.012612 | -0.0031608 | 3.7109e-06 | 2.0199e-06 | 0.018945 | 0.018945 | 0.018945 | 0.99089 | -0.17505 | 0.99058 | -0.18122 | 5.2047
44 | 0.018668 | 0.0046802 | -0.018668 | -0.0046802 | 1.1265e-07 | 6.7183e-08 | 0.028047 | 0.028047 | 0.028047 | 0.99044 | -0.18383 | 0.99044 | -0.18396 | 7.7053
45 | 0.0068608 | 0.0017195 | -0.0068606 | -0.0017194 | 2.8378e-07 | 8.9908e-08 | 0.010306 | 0.010306 | 0.010306 | 0.99058 | -0.18122 | 0.99053 | -0.18209 | 2.8314
46 | 0.0045702 | 0.0011454 | -0.0045701 | -0.0011454 | 3.736e-08 | -3.2964e-09 | 0.0068655 | 0.0068655 | 0.0068655 | 0.99053 | -0.18209 | 0.99052 | -0.18226 | 1.8861
47 | 0.0022907 | 0.00057409 | -0.0022907 | -0.0005741 | 5.5673e-09 | -1.2574e-08 | 0.0034412 | 0.0034412 | 0.0034412 | 0.99052 | -0.18226 | 0.99052 | -0.18231 | 0.94539
48 | -0.061619 | -0.015585 | 0.06179 | 0.015694 | 0.0001708 | 0.00010864 | 0.093046 | 0.093045 | 0.093046 | 0.98597 | -0.26843 | 0.98896 | -0.21083 | 25.562
49 | 0.056039 | 0.014187 | -0.055847 | -0.014065 | 0.00019201 | 0.00012197 | 0.084624 | 0.084624 | 0.084624 | 0.98597 | -0.26843 | 0.98228 | -0.34007 | 23.2484
50 | -0.11095 | -0.028088 | 0.11106 | 0.028159 | 0.00011044 | 7.0549e-05 | 0.16703 | 0.16703 | 0.16703 | 0.98896 | -0.21083 | 0.99003 | -0.19012 | 45.8885
51 | 0.049157 | 0.012395 | -0.049151 | -0.012391 | 5.6491e-06 | 3.5801e-06 | 0.073989 | 0.073989 | 0.073989 | 0.98896 | -0.21083 | 0.98883 | -0.21323 | 20.3267
52 | 0.051621 | 0.013006 | -0.051496 | -0.012927 | 0.0001249 | 7.9248e-05 | 0.078223 | 0.078224 | 0.078224 | 0.98228 | -0.34007 | 0.97969 | -0.39078 | 21.49
53 | 0.0042255 | 0.0010585 | -0.0042246 | -0.0010586 | 9.3242e-07 | -1.7127e-07 | 0.0064008 | 0.0064011 | 0.0064011 | 0.98228 | -0.34007 | 0.98205 | -0.3447 | 1.7585
54 | -0.1162 | -0.029439 | 0.11624 | 0.029464 | 3.853e-05 | 2.4616e-05 | 0.17476 | 0.17476 | 0.17476 | 0.99003 | -0.19012 | 0.99039 | -0.18322 | 48.0111
55 | 0.0051425 | 0.0012803 | -0.0051423 | -0.0012803 | 2.5179e-07 | 1.6516e-08 | 0.0077262 | 0.0077263 | 0.0077263 | 0.99003 | -0.19012 | 0.98998 | -0.19115 | 2.1226
56 | 0.047026 | 0.011858 | -0.04701 | -0.011849 | 1.5375e-05 | 9.7353e-06 | 0.070791 | 0.070791 | 0.070791 | 0.98883 | -0.21323 | 0.98848 | -0.22006 | 19.4481
57 | 0.048547 | 0.012188 | -0.048489 | -0.012152 | 5.7981e-05 | 3.675e-05 | 0.073744 | 0.073745 | 0.073745 | 0.97969 | -0.39078 | 0.97841 | -0.41585 | 20.2595
58 | 0.0029492 | 0.00073859 | -0.002949 | -0.00073876 | 1.6244e-07 | -1.6788e-07 | 0.0044792 | 0.0044793 | 0.0044793 | 0.97969 | -0.39078 | 0.97963 | -0.39194 | 1.2306
59 | 0.003014 | 0.00075524 | -0.0030139 | -0.00075535 | 1.1482e-07 | -1.1226e-07 | 0.0045668 | 0.0045669 | 0.0045669 | 0.98205 | -0.3447 | 0.98201 | -0.3455 | 1.2546
60 | 0.0051423 | 0.0012803 | -0.0051415 | -0.0012802 | 7.7149e-07 | 5.0712e-08 | 0.0077263 | 0.0077264 | 0.0077264 | 0.98998 | -0.19115 | 0.98982 | -0.19432 | 2.1226
61 | 0.044515 | 0.011223 | -0.044468 | -0.011193 | 4.7431e-05 | 2.9995e-05 | 0.067035 | 0.067035 | 0.067035 | 0.98848 | -0.22006 | 0.98733 | -0.24235 | 18.4163
62 | 0.0057237 | 0.0014336 | -0.0057232 | -0.0014335 | 4.9161e-07 | 9.7359e-08 | 0.0087046 | 0.0087047 | 0.0087047 | 0.97841 | -0.41585 | 0.97832 | -0.41766 | 2.3914
63 | 0.0012761 | 0.00031949 | -0.0012761 | -0.00031981 | 3.8362e-08 | -3.1826e-07 | 0.0019382 | 0.0019383 | 0.0019383 | 0.97963 | -0.39194 | 0.9796 | -0.39257 | 0.53251
64 | 0.0046451 | 0.0011558 | -0.004645 | -0.0011558 | 9.1725e-08 | -5.8219e-09 | 0.0069802 | 0.0069802 | 0.0069802 | 0.98982 | -0.19432 | 0.9898 | -0.19473 | 1.9176
65 | 0.036664 | 0.0092376 | -0.036626 | -0.0092132 | 3.8825e-05 | 2.4415e-05 | 0.055275 | 0.055275 | 0.055275 | 0.98733 | -0.24235 | 0.98619 | -0.26452 | 15.1854
66 | 0.003961 | 0.00099187 | -0.0039605 | -0.00099202 | 5.4709e-07 | -1.5453e-07 | 0.0060243 | 0.0060245 | 0.0060245 | 0.97832 | -0.41766 | 0.97817 | -0.42056 | 1.6551
67 | -0.12853 | -0.032634 | 0.12861 | 0.03268 | 7.1843e-05 | 4.5913e-05 | 0.19287 | 0.19287 | 0.19287 | 0.99241 | -0.14436 | 0.99302 | -0.13275 | 52.9871
68 | -0.12997 | -0.033021 | 0.13003 | 0.033063 | 6.6683e-05 | 4.2616e-05 | 0.19491 | 0.19491 | 0.19491 | 0.99302 | -0.13275 | 0.99358 | -0.1221 | 53.547
69 | 0.13293 | 0.033854 | -0.13284 | -0.033796 | 9.1461e-05 | 5.8455e-05 | 0.199 | 0.199 | 0.199 | 0.99494 | -0.096074 | 0.99419 | -0.11035 | 54.6714
70 | -0.13113 | -0.033337 | 0.1312 | 0.033385 | 7.4273e-05 | 4.7468e-05 | 0.19655 | 0.19655 | 0.19655 | 0.99358 | -0.1221 | 0.99419 | -0.11035 | 53.9964
71 | 0.0038399 | 0.00096109 | -0.0038396 | -0.00096119 | 2.8233e-07 | -1.0168e-07 | 0.0058128 | 0.0058129 | 0.0058129 | 0.98289 | -0.32887 | 0.98281 | -0.33042 | 1.597
72 | -0.0045496 | -0.001139 | 0.0045499 | 0.0011389 | 2.5646e-07 | -1.861e-08 | 0.0068873 | 0.0068872 | 0.0068873 | 0.98289 | -0.32887 | 0.98295 | -0.32769 | 1.8921
73 | 0.0030791 | 0.00077058 | -0.003079 | -0.00077066 | 8.4558e-08 | -7.7379e-08 | 0.0046615 | 0.0046615 | 0.0046615 | 0.98281 | -0.33042 | 0.98278 | -0.33099 | 1.2806
74 | -0.0045499 | -0.0011389 | 0.0045502 | 0.0011389 | 3.1512e-07 | -2.2902e-08 | 0.0068872 | 0.0068871 | 0.0068872 | 0.98295 | -0.32769 | 0.98302 | -0.32623 | 1.8921
75 | 0.0023186 | 0.00058009 | -0.0023185 | -0.00058033 | 1.1024e-07 | -2.3172e-07 | 0.0035103 | 0.0035104 | 0.0035104 | 0.98278 | -0.33099 | 0.98273 | -0.33199 | 0.96439
76 | -0.0058614 | -0.0014675 | 0.0058624 | 0.0014678 | 1.0051e-06 | 2.1148e-07 | 0.008872 | 0.0088718 | 0.008872 | 0.98302 | -0.32623 | 0.98321 | -0.32263 | 2.4374
77 | 0.0013824 | 0.00034572 | -0.0013824 | -0.00034607 | 4.9322e-08 | -3.4881e-07 | 0.002093 | 0.0020931 | 0.0020931 | 0.98273 | -0.33199 | 0.98269 | -0.33274 | 0.57503
78 | -0.013577 | -0.0034006 | 0.013581 | 0.0034028 | 3.9607e-06 | 2.2175e-06 | 0.020547 | 0.020547 | 0.020547 | 0.98321 | -0.32263 | 0.98352 | -0.31651 | 5.6448
79 | 0.0077145 | 0.0019328 | -0.0077138 | -0.0019325 | 7.3154e-07 | 2.867e-07 | 0.011675 | 0.011675 | 0.011675 | 0.98321 | -0.32263 | 0.98311 | -0.32462 | 3.2075
80 | 0.00066439 | 0.00016612 | -0.00066438 | -0.00016651 | 1.1838e-08 | -3.8761e-07 | 0.0010059 | 0.001006 | 0.001006 | 0.98269 | -0.33274 | 0.98267 | -0.33312 | 0.27638
81 | -0.0011601 | -0.00029075 | 0.0011601 | 0.00029064 | 1.0136e-08 | -1.0456e-07 | 0.0017564 | 0.0017563 | 0.0017564 | 0.98285 | -0.3297 | 0.98286 | -0.32951 | 0.48252
82 | -0.0017687 | -0.00044318 | 0.0017687 | 0.00044311 | 1.605e-08 | -6.5377e-08 | 0.0026778 | 0.0026777 | 0.0026778 | 0.98286 | -0.32951 | 0.98287 | -0.32932 | 0.73565
83 | -0.014186 | -0.0035545 | 0.014187 | 0.0035551 | 1.0308e-06 | 5.8399e-07 | 0.021463 | 0.021463 | 0.021463 | 0.98352 | -0.31651 | 0.9836 | -0.31498 | 5.8964
84 | 0.0066173 | 0.0016577 | -0.0066162 | -0.0016574 | 1.111e-06 | 3.3663e-07 | 0.010016 | 0.010016 | 0.010016 | 0.98311 | -0.32462 | 0.98293 | -0.32815 | 2.7516
85 | -0.0010593 | -0.00026549 | 0.0010594 | 0.00026514 | 2.86e-08 | -3.5025e-07 | 0.0016116 | 0.0016115 | 0.0016116 | 0.97808 | -0.42239 | 0.97811 | -0.42182 | 0.44276
86 | -0.0026715 | -0.00066919 | 0.0026716 | 0.00066912 | 5.3726e-08 | -7.4488e-08 | 0.0040641 | 0.0040641 | 0.0040641 | 0.97811 | -0.42182 | 0.97813 | -0.4214 | 1.1165
87 | -0.0034024 | -0.00085229 | 0.0034026 | 0.0008522 | 1.365e-07 | -8.3193e-08 | 0.0051759 | 0.0051759 | 0.0051759 | 0.97813 | -0.4214 | 0.97817 | -0.42056 | 1.422
88 | 0.03484 | 0.0087657 | -0.03484 | -0.0087654 | 5.1893e-07 | 3.2573e-07 | 0.052581 | 0.052581 | 0.052581 | 0.98619 | -0.26452 | 0.98617 | -0.26483 | 14.4454
89 | 0.034234 | 0.0086137 | -0.034175 | -0.0085764 | 5.9357e-05 | 3.7233e-05 | 0.051668 | 0.051668 | 0.051668 | 0.98617 | -0.26483 | 0.98431 | -0.30118 | 14.1944
90 | 0.034175 | 0.0085764 | -0.034161 | -0.0085674 | 1.4387e-05 | 9.0251e-06 | 0.051668 | 0.051668 | 0.051668 | 0.98431 | -0.30118 | 0.98385 | -0.31002 | 14.1945
91 | 0.016008 | 0.0040127 | -0.016007 | -0.0040119 | 1.3118e-06 | 7.6377e-07 | 0.024212 | 0.024212 | 0.024212 | 0.98385 | -0.31002 | 0.98377 | -0.31174 | 6.6516
92 | 0.017547 | 0.004403 | -0.017523 | -0.0043891 | 2.3412e-05 | 1.386e-05 | 0.02654 | 0.026541 | 0.026541 | 0.98385 | -0.31002 | 0.98242 | -0.33803 | 7.2914
93 | -0.014793 | -0.003707 | 0.014794 | 0.0037076 | 1.1208e-06 | 6.4153e-07 | 0.02238 | 0.022379 | 0.02238 | 0.9836 | -0.31498 | 0.98368 | -0.31339 | 6.1482
94 | 0.0029819 | 0.00074693 | -0.0029818 | -0.00074706 | 1.3042e-07 | -1.3285e-07 | 0.004514 | 0.0045141 | 0.0045141 | 0.98293 | -0.32815 | 0.98288 | -0.32907 | 1.2401
95 | 0.0036343 | 0.00091046 | -0.0036343 | -0.00091047 | 2.4462e-08 | -1.166e-08 | 0.0055017 | 0.0055017 | 0.0055017 | 0.98293 | -0.32815 | 0.98292 | -0.32829 | 1.5115
96 | -0.0154 | -0.0038593 | 0.015401 | 0.00386 | 1.2144e-06 | 7.0143e-07 | 0.023295 | 0.023295 | 0.023295 | 0.98368 | -0.31339 | 0.98377 | -0.31174 | 6.3998
97 | 0.0023751 | 0.00059502 | -0.0023751 | -0.00059508 | 2.8935e-08 | -5.7117e-08 | 0.0035957 | 0.0035957 | 0.0035957 | 0.98288 | -0.32907 | 0.98287 | -0.32932 | 0.98784
98 | 0.0030284 | 0.00075861 | -0.0030283 | -0.00075865 | 4.7037e-08 | -4.5541e-08 | 0.0045844 | 0.0045845 | 0.0045845 | 0.98292 | -0.32829 | 0.9829 | -0.32862 | 1.2595
99 | -0.0041408 | -0.0010377 | 0.0041411 | 0.0010376 | 2.1956e-07 | -4.7779e-08 | 0.0062734 | 0.0062733 | 0.0062734 | 0.98218 | -0.34269 | 0.98224 | -0.34157 | 1.7235
100 | 0.0030922 | 0.00077486 | -0.0030921 | -0.0007749 | 4.1924e-08 | -3.764e-08 | 0.0046846 | 0.0046846 | 0.0046846 | 0.98218 | -0.34269 | 0.98217 | -0.34297 | 1.287
101 | -0.0053731 | -0.0013464 | 0.0053732 | 0.0013464 | 1.3303e-07 | 1.7365e-08 | 0.0081397 | 0.0081397 | 0.0081397 | 0.98224 | -0.34157 | 0.98227 | -0.34105 | 2.2362
102 | 0.0013312 | 0.00033358 | -0.0013312 | -0.00033364 | 7.9072e-09 | -6.0541e-08 | 0.0020169 | 0.0020169 | 0.0020169 | 0.98217 | -0.34297 | 0.98216 | -0.3431 | 0.55409
103 | -0.0082985 | -0.0020796 | 0.0082997 | 0.0020801 | 1.1933e-06 | 5.0878e-07 | 0.012571 | 0.012571 | 0.012571 | 0.98227 | -0.34105 | 0.98242 | -0.33803 | 3.4536
104 | 0.0092237 | 0.0023091 | -0.0092213 | -0.0023079 | 2.379e-06 | 1.1111e-06 | 0.01397 | 0.01397 | 0.01397 | 0.98242 | -0.33803 | 0.98214 | -0.34345 | 3.8379
105 | 0.0092213 | 0.0023079 | -0.0092202 | -0.0023074 | 1.055e-06 | 4.928e-07 | 0.01397 | 0.01397 | 0.01397 | 0.98214 | -0.34345 | 0.98202 | -0.34586 | 3.8379
106 | -0.0045617 | -0.001141 | 0.0045619 | 0.001141 | 1.7435e-07 | -1.0864e-08 | 0.0069212 | 0.0069212 | 0.0069212 | 0.98061 | -0.37348 | 0.98066 | -0.37267 | 1.9014
107 | 0.0025385 | 0.00063393 | -0.0025383 | -0.00063428 | 2.157e-07 | -3.5114e-07 | 0.0038512 | 0.0038514 | 0.0038514 | 0.98061 | -0.37348 | 0.98052 | -0.37527 | 1.0581
108 | -0.0045619 | -0.001141 | 0.0045628 | 0.0011409 | 9.4471e-07 | -5.9068e-08 | 0.0069212 | 0.006921 | 0.0069212 | 0.98066 | -0.37267 | 0.98088 | -0.36832 | 1.9014
109 | 0.00020405 | 5.0648e-05 | -0.00020405 | -5.1139e-05 | 1.4016e-09 | -4.9102e-07 | 0.00030948 | 0.00030966 | 0.00030966 | 0.98052 | -0.37527 | 0.98052 | -0.37541 | 0.08507
110 | 0.0023342 | 0.00058363 | -0.0023339 | -0.00058439 | 3.726e-07 | -7.6027e-07 | 0.0035419 | 0.0035423 | 0.0035423 | 0.98052 | -0.37527 | 0.98035 | -0.37862 | 0.97315
111 | -0.0045628 | -0.0011409 | 0.0045635 | 0.0011409 | 6.5927e-07 | -4.1426e-08 | 0.006921 | 0.0069208 | 0.006921 | 0.98088 | -0.36832 | 0.98103 | -0.36528 | 1.9014
112 | 0.00083915 | 0.00021013 | -0.00083915 | -0.00021031 | 9.0632e-09 | -1.8205e-07 | 0.0012736 | 0.0012737 | 0.0012737 | 0.98035 | -0.37862 | 0.98034 | -0.37885 | 0.34992
113 | 0.0014947 | 0.00037426 | -0.0014947 | -0.00037446 | 3.2772e-08 | -1.9311e-07 | 0.0022686 | 0.0022687 | 0.0022687 | 0.98035 | -0.37862 | 0.98033 | -0.37908 | 0.62327
114 | -0.0050318 | -0.0012582 | 0.0050326 | 0.0012583 | 7.4628e-07 | 4.6056e-08 | 0.0076312 | 0.007631 | 0.0076312 | 0.98103 | -0.36528 | 0.98119 | -0.36216 | 2.0965
115 | -0.0050326 | -0.0012583 | 0.0050344 | 0.0012584 | 1.8744e-06 | 1.1498e-07 | 0.007631 | 0.0076306 | 0.007631 | 0.98119 | -0.36216 | 0.98159 | -0.35433 | 2.0964
116 | -0.0050344 | -0.0012584 | 0.0050356 | 0.0012585 | 1.1281e-06 | 6.8723e-08 | 0.0076306 | 0.0076304 | 0.0076306 | 0.98159 | -0.35433 | 0.98183 | -0.34962 | 2.0963
117 | 0.0010786 | 0.00027019 | -0.0010786 | -0.00027026 | 6.5744e-09 | -7.8257e-08 | 0.0016372 | 0.0016372 | 0.0016372 | 0.98033 | -0.37908 | 0.98032 | -0.37921 | 0.44979
118 | 0.0085404 | 0.0021371 | -0.0085401 | -0.0021369 | 3.6818e-07 | 1.6145e-07 | 0.01294 | 0.01294 | 0.01294 | 0.98202 | -0.34586 | 0.98198 | -0.34677 | 3.5549
119 | 0.0067683 | 0.0016928 | -0.0067679 | -0.0016926 | 3.9951e-07 | 1.2758e-07 | 0.010256 | 0.010256 | 0.010256 | 0.98189 | -0.34838 | 0.98183 | -0.34962 | 2.8175
120 | -0.0078604 | -0.0019665 | 0.007861 | 0.0019667 | 6.0316e-07 | 2.426e-07 | 0.011911 | 0.011911 | 0.011911 | 0.98189 | -0.34838 | 0.98198 | -0.34677 | 3.2722
121 | 0.00087926 | 0.0002203 | -0.00087926 | -0.00022031 | 5.9146e-10 | -1.0786e-08 | 0.0013346 | 0.0013346 | 0.0013346 | 0.98032 | -0.37921 | 0.98032 | -0.37922 | 0.36665
122 | 0.00046353 | 0.00011611 | -0.00046353 | -0.00011617 | 8.4658e-10 | -5.6957e-08 | 0.00070356 | 0.00070358 | 0.00070358 | 0.98032 | -0.37922 | 0.98032 | -0.37926 | 0.19329
123 | -0.0041482 | -0.0010314 | 0.0041483 | 0.0010313 | 8.993e-08 | -2.177e-08 | 0.0062335 | 0.0062334 | 0.0062335 | 0.98977 | -0.19519 | 0.9898 | -0.19473 | 1.7125
124 | 0.0036518 | 0.00090694 | -0.0036517 | -0.00090697 | 5.6828e-08 | -2.8317e-08 | 0.0054871 | 0.0054871 | 0.0054871 | 0.98977 | -0.19519 | 0.98976 | -0.19552 | 1.5074
125 | 0.0031557 | 0.00078266 | -0.0031557 | -0.00078271 | 4.9277e-08 | -4.3581e-08 | 0.0047415 | 0.0047415 | 0.0047415 | 0.98976 | -0.19552 | 0.98974 | -0.19585 | 1.3026
126 | 0.0026592 | 0.00065829 | -0.0026591 | -0.00065852 | 1.5252e-07 | -2.2984e-07 | 0.0039951 | 0.0039952 | 0.0039952 | 0.98974 | -0.19585 | 0.98968 | -0.19706 | 1.0976
127 | 0.00099379 | 0.00024873 | -0.00099377 | -0.00024905 | 2.1957e-08 | -3.2297e-07 | 0.0014941 | 0.0014942 | 0.0014942 | 0.98968 | -0.19706 | 0.98965 | -0.19753 | 0.41049
128 | 0.0016653 | 0.00040979 | -0.001665 | -0.00041089 | 2.2895e-07 | -1.1071e-06 | 0.0025011 | 0.0025016 | 0.0025016 | 0.98968 | -0.19706 | 0.98953 | -0.19999 | 0.68725
129 | 0.00049616 | 0.00012434 | -0.00049616 | -0.00012435 | 1.7203e-10 | -1.0486e-08 | 0.00074601 | 0.00074601 | 0.00074601 | 0.98965 | -0.19753 | 0.98965 | -0.19754 | 0.20495
130 | 0.001665 | 0.00041089 | -0.0016649 | -0.00041155 | 1.3625e-07 | -6.5852e-07 | 0.0025016 | 0.0025018 | 0.0025018 | 0.98953 | -0.19999 | 0.98944 | -0.20172 | 0.68732
131 | 0.00047185 | 0.00011254 | -0.00047177 | -0.000118 | 8.0789e-08 | -5.4585e-06 | 0.00070763 | 0.00070954 | 0.00070954 | 0.98944 | -0.20172 | 0.98926 | -0.20539 | 0.19493
132 | 0.00047177 | 0.000118 | -0.00047176 | -0.00011823 | 3.4745e-09 | -2.3404e-07 | 0.00070954 | 0.00070962 | 0.00070962 | 0.98926 | -0.20539 | 0.98925 | -0.20554 | 0.19495
133 | -0.0018169 | -0.00045517 | 0.0018169 | 0.0004551 | 1.6932e-08 | -6.4804e-08 | 0.0027506 | 0.0027505 | 0.0027506 | 0.98288 | -0.32907 | 0.98289 | -0.32888 | 0.75565
134 | 0.0012114 | 0.00030343 | -0.0012114 | -0.0003036 | 1.8842e-08 | -1.7727e-07 | 0.0018339 | 0.001834 | 0.001834 | 0.98288 | -0.32907 | 0.98286 | -0.3294 | 0.50385
135 | -0.0024228 | -0.00060697 | 0.0024229 | 0.00060691 | 3.0109e-08 | -5.6372e-08 | 0.0036679 | 0.0036679 | 0.0036679 | 0.98289 | -0.32888 | 0.9829 | -0.32862 | 1.0077

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25997 | 0.065873

## res_load
| p_mw | q_mvar
0 | 0.0071066 | 0.0017811
1 | 0.0034592 | 0.00086696
2 | 0.0015837 | 0.00039691
3 | 0.0033009 | 0.00082728
4 | 0.0072843 | 0.0018256
5 | 0.00060917 | 0.00015267
6 | 0.0038195 | 0.00095725
7 | 0.0058841 | 0.0014747
8 | 0.0032295 | 0.00080938
9 | 0.0047457 | 0.0011894
10 | 0.0020613 | 0.0005166
11 | 0.0024281 | 0.00060853
12 | 0.0048423 | 0.0012136
13 | 0.0022567 | 0.00056557
14 | 0.0011567 | 0.0002899
15 | 0.0042933 | 0.001076
16 | 0.003883 | 0.00097317
17 | 0.0011567 | 0.0002899
18 | 0.0099974 | 0.0025056
19 | 0.0014573 | 0.00036523
20 | 0.0021327 | 0.0005345
21 | 0.00062201 | 0.00015589
22 | 0.00085871 | 0.00021521
23 | 0.0008608 | 0.00021574
24 | 0.0095852 | 0.0024023
25 | 0.0037814 | 0.0009477
26 | 0.0013287 | 0.000333
27 | 0.006436 | 0.001613
28 | 0.0038926 | 0.00097559
29 | 0.0055996 | 0.0014034
30 | 0.0013541 | 0.00033937
31 | 0.0013565 | 0.00033998
32 | 0.00084256 | 0.00021117
33 | 0.0013554 | 0.0003397
34 | 0.0057509 | 0.0014413
35 | 0.0013546 | 0.0003395
36 | 0.0022904 | 0.00057403
37 | 0.0022794 | 0.00057128
38 | 0.0022907 | 0.0005741
39 | 0.0055803 | 0.0013986
40 | 0.0021251 | 0.00053259
41 | 0.0012106 | 0.0003034
42 | 0.001083 | 0.00027141
43 | 0.0024952 | 0.00062536
44 | 0.042766 | 0.010718
45 | 0.0016729 | 0.00041927
46 | 0.0030139 | 0.00075535
47 | 0.00049639 | 0.00012441
48 | 0.0078035 | 0.0019557
49 | 0.0017622 | 0.00044165
50 | 0.0012761 | 0.00031981
51 | 0.0014013 | 0.00035119
52 | 0.0013601 | 0.00034086
53 | 0.0016426 | 0.00041169
54 | 0.0010924 | 0.00027377
55 | 0.00070971 | 0.00017787
56 | 0.00076053 | 0.00019061
57 | 0.00076036 | 0.00019056
58 | 0.0013112 | 0.00032862
59 | 0.00093609 | 0.00023461
60 | 0.000718 | 0.00017995
61 | 0.0011601 | 0.00029075
62 | 0.00060861 | 0.00015253
63 | 0.00060546 | 0.00015174
64 | 0.0010965 | 0.0002748
65 | 0.0010593 | 0.00026549
66 | 0.0016122 | 0.00040405
67 | 0.00073086 | 0.00018317
68 | 0.00055788 | 0.00013982
69 | 0.0017852 | 0.00044742
70 | 0.00060546 | 0.00015174
71 | 0.00060546 | 0.00015174
72 | 0.00066438 | 0.00016651
73 | 0.00060593 | 0.00015186
74 | 0.00060546 | 0.00015174
75 | 0.00060662 | 0.00015203
76 | 0.00060593 | 0.00015186
77 | 0.0010487 | 0.00026282
78 | 0.001232 | 0.00030877
79 | 0.0017609 | 0.00044132
80 | 0.0029253 | 0.00073315
81 | 0.0013312 | 0.00033364
82 | 0.0020232 | 0.00050706
83 | 0.00020405 | 5.1139e-05
84 | 0.00046833 | 0.00011738
85 | 0.00083915 | 0.00021031
86 | 0.00041604 | 0.00010427
87 | 0.00067982 | 0.00017038
88 | 0.0010921 | 0.00027371
89 | 0.0017323 | 0.00043416
90 | 0.00067909 | 0.0001702
91 | 0.00019938 | 4.9968e-05
92 | 0.00041574 | 0.00010419
93 | 0.00046353 | 0.00011617
94 | 0.00060593 | 0.00015186
95 | 0.00049645 | 0.00012442
96 | 0.00049674 | 0.00012449
97 | 0.00049598 | 0.0001243
98 | 0.00049645 | 0.00012442
99 | 0.00049761 | 0.00012471
100 | 0.0016416 | 0.00041142
101 | 0.0032526 | 0.00081518
102 | 0.00049616 | 0.00012435
103 | 0.0011931 | 0.00029901
104 | 0.00060546 | 0.00015174
105 | 0.00060594 | 0.00015186
106 | 0.0012114 | 0.0003036
107 | 0.00060546 | 0.00015174
108 | 0.00060637 | 0.00015197
109 | 0.00047176 | 0.00011823

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1