## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_115-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_115-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_115-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_115-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_115-6_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_115-6_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_115-6_0_3_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_115-6_0_3_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_115-6_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_115-6_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_115-6_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_115-6_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_115-6_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_115-6_0_3_node_261 | 0.4 | n |  | TRUE
14 | bus_LV_115-6_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_115-6_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_115-6_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_115-6_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_115-6_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_115-6_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_115-6_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_115-6_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_115-6_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_115-6_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_115-6_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_115-6_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_115-6_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_115-6_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_115-6_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_115-6_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_115-6_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_115-6_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_115-6_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_115-6_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_115-6_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_115-6_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_115-6_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_115-6_0_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_115-6_0_3_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_115-6_0_3_node_60 | 0.4 | n |  | TRUE
40 | bus_LV_115-6_0_3_node_99 | 0.4 | n |  | TRUE
41 | bus_LV_115-6_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_115-6_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_115-6_0_3_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_115-6_0_3_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_115-6_0_3_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_115-6_0_3_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_115-6_0_3_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_115-6_0_3_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_115-6_0_3_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_115-6_0_3_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_115-6_0_3_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_115-6_0_3_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_115-6_0_3_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_115-6_0_3_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_115-6_0_3_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_115-6_0_3_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_115-6_0_3_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_115-6_0_3_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_115-6_0_3_node_86 | 0.4 | n |  | TRUE
60 | bus_LV_115-6_0_3_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_115-6_0_3_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_115-6_0_3_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_115-6_0_3_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_115-6_0_3_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_115-6_0_3_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_115-6_0_3_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_115-6_0_3_node_89 | 0.4 | n |  | TRUE
68 | bus_LV_115-6_0_3_node_104 | 0.4 | n |  | TRUE
69 | bus_LV_115-6_0_3_node_96 | 0.4 | n |  | TRUE
70 | bus_LV_115-6_0_3_node_126 | 0.4 | n |  | TRUE
71 | bus_LV_115-6_0_3_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_115-6_0_3_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_115-6_0_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_115-6_0_3_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_115-6_0_3_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_115-6_0_3_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_115-6_0_3_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_115-6_0_3_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_115-6_0_3_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_115-6_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_115-6_0_3_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_115-6_0_3_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_115-6_0_3_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_115-6_0_3_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_115-6_0_3_node_265 | 0.4 | n |  | TRUE
86 | bus_LV_115-6_0_3_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_115-6_0_3_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_115-6_0_3_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_115-6_0_3_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_115-6_0_3_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_115-6_0_3_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_115-6_0_3_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_115-6_0_3_node_116 | 0.4 | n |  | TRUE
94 | bus_LV_115-6_0_3_node_262 | 0.4 | n |  | TRUE
95 | bus_LV_115-6_0_3_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_115-6_0_3_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_115-6_0_3_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_115-6_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_115-6_0_3_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_115-6_0_3_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_115-6_0_3_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_115-6_0_3_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_115-6_0_3_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_115-6_0_3_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_115-6_0_3_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_115-6_0_3_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_115-6_0_3_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_115-6_0_3_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_115-6_0_3_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_115-6_0_3_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_115-6_0_3_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_115-6_0_3_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_115-6_0_3_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_115-6_0_3_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_115-6_0_3_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_115-6_0_3_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_115-6_0_3_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_115-6_0_3_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_115-6_0_3_node_120 | 0.4 | n |  | TRUE
120 | bus_LV_115-6_0_3_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_115-6_0_3_node_122 | 0.4 | n |  | TRUE
122 | bus_LV_115-6_0_3_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_115-6_0_3_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_115-6_0_3_node_125 | 0.4 | n |  | TRUE
125 | bus_LV_115-6_0_3_node_263 | 0.4 | n |  | TRUE
126 | bus_LV_115-6_0_3_node_264 | 0.4 | n |  | TRUE
127 | bus_MV_356_0_node_22 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_115-6_0_3_load_0 | 0 | 0.016671 | 0.004178 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_115-6_0_3_load_2 | 2 | 0.0026946 | 0.00067533 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_115-6_0_3_load_3 | 3 | 0.012801 | 0.0032083 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_115-6_0_3_load_5 | 5 | 0.00213 | 0.00053384 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_115-6_0_3_load_6 | 8 | 0.0085667 | 0.002147 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_115-6_0_3_load_7 | 9 | 0.00038291 | 9.5967e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_115-6_0_3_load_9 | 11 | 0.0018866 | 0.00047283 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_115-6_0_3_load_261 | 13 | 0.00055458 | 0.00013899 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_115-6_0_3_load_11 | 14 | 0.0055151 | 0.0013822 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_115-6_0_3_load_12 | 15 | 0.0061124 | 0.0015319 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_115-6_0_3_load_14 | 17 | 0.0014714 | 0.00036878 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_115-6_0_3_load_15 | 18 | 0.0013605 | 0.00034098 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_115-6_0_3_load_25 | 21 | 0.0070748 | 0.0017731 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_115-6_0_3_load_26 | 22 | 0.0062901 | 0.0015764 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_115-6_0_3_load_18 | 23 | 0.0025686 | 0.00064374 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_115-6_0_3_load_21 | 26 | 0.0017492 | 0.00043838 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_115-6_0_3_load_23 | 27 | 0.0034728 | 0.00087038 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_115-6_0_3_load_30 | 31 | 0.0017368 | 0.00043528 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_115-6_0_3_load_28 | 32 | 0.0022094 | 0.00055374 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_115-6_0_3_load_31 | 33 | 0.004346 | 0.0010892 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_115-6_0_3_load_32 | 34 | 0.006096 | 0.0015278 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_115-6_0_3_load_33 | 35 | 0.0052128 | 0.0013065 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_115-6_0_3_load_35 | 37 | 0.0031559 | 0.00079094 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_115-6_0_3_load_36 | 38 | 0.0036502 | 0.00091483 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_115-6_0_3_load_60 | 39 | 0.0020244 | 0.00050736 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_115-6_0_3_load_99 | 40 | 0.0031484 | 0.00078906 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_115-6_0_3_load_39 | 42 | 0.0034479 | 0.00086414 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_115-6_0_3_load_59 | 43 | 0.0022486 | 0.00056356 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_115-6_0_3_load_55 | 44 | 0.002713 | 0.00067993 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_115-6_0_3_load_40 | 45 | 0.00092003 | 0.00023058 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_115-6_0_3_load_41 | 46 | 0.0010536 | 0.00026406 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_115-6_0_3_load_42 | 47 | 0.00083869 | 0.00021019 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_115-6_0_3_load_43 | 48 | 0.0012471 | 0.00031256 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_115-6_0_3_load_44 | 49 | 0.00067686 | 0.00016964 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_115-6_0_3_load_45 | 50 | 0.0012472 | 0.00031257 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_115-6_0_3_load_46 | 51 | 0.0006764 | 0.00016952 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_115-6_0_3_load_61 | 52 | 0.0020942 | 0.00052487 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_115-6_0_3_load_77 | 53 | 0.00063036 | 0.00015798 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_115-6_0_3_load_47 | 54 | 0.0013655 | 0.00034223 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_115-6_0_3_load_48 | 55 | 0.0013392 | 0.00033563 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_115-6_0_3_load_49 | 56 | 0.0012905 | 0.00032343 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_115-6_0_3_load_50 | 57 | 0.0019014 | 0.00047655 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_115-6_0_3_load_51 | 58 | 0.0020571 | 0.00051555 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_115-6_0_3_load_86 | 59 | 0.0013908 | 0.00034856 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_115-6_0_3_load_52 | 60 | 0.0021622 | 0.00054189 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_115-6_0_3_load_53 | 61 | 0.0012832 | 0.00032159 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_115-6_0_3_load_54 | 62 | 0.0015228 | 0.00038166 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_115-6_0_3_load_58 | 64 | 0.00089884 | 0.00022527 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_115-6_0_3_load_57 | 65 | 0.00066218 | 0.00016596 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_115-6_0_3_load_72 | 66 | 0.00089911 | 0.00022534 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_115-6_0_3_load_89 | 67 | 0.00089889 | 0.00022528 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_115-6_0_3_load_104 | 68 | 0.0058478 | 0.0014656 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_115-6_0_3_load_96 | 69 | 0.0018003 | 0.0004512 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_115-6_0_3_load_62 | 71 | 0.0029661 | 0.00074338 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_115-6_0_3_load_63 | 72 | 0.00066298 | 0.00016616 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_115-6_0_3_load_64 | 73 | 0.0015103 | 0.00037851 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_115-6_0_3_load_65 | 74 | 0.00066255 | 0.00016605 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_115-6_0_3_load_66 | 75 | 0.00089805 | 0.00022507 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_115-6_0_3_load_68 | 76 | 0.00089889 | 0.00022528 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_115-6_0_3_load_69 | 77 | 0.0019381 | 0.00048573 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_115-6_0_3_load_70 | 78 | 0.0012623 | 0.00031636 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_115-6_0_3_load_75 | 82 | 0.0025623 | 0.00064216 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_115-6_0_3_load_76 | 83 | 0.0006182 | 0.00015493 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_115-6_0_3_load_83 | 84 | 0.0023066 | 0.00057809 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_115-6_0_3_load_265 | 85 | 0.0006301 | 0.00015792 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_115-6_0_3_load_78 | 86 | 0.0017643 | 0.00044218 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_115-6_0_3_load_79 | 87 | 0.0010037 | 0.00025154 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_115-6_0_3_load_81 | 89 | 0.0010025 | 0.00025124 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_115-6_0_3_load_82 | 90 | 0.00061844 | 0.000155 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_115-6_0_3_load_84 | 91 | 0.0010036 | 0.00025153 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_115-6_0_3_load_85 | 92 | 0.00055458 | 0.00013899 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_115-6_0_3_load_116 | 93 | 0.0010036 | 0.00025153 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_115-6_0_3_load_87 | 95 | 0.001648 | 0.00041304 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_115-6_0_3_load_88 | 96 | 0.0040993 | 0.0010274 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_115-6_0_3_load_95 | 97 | 0.0017464 | 0.0004377 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_115-6_0_3_load_90 | 98 | 0.0026992 | 0.00067649 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_115-6_0_3_load_92 | 100 | 0.0029003 | 0.00072689 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_115-6_0_3_load_93 | 101 | 0.0027816 | 0.00069715 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_115-6_0_3_load_94 | 102 | 0.0027252 | 0.000683 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_115-6_0_3_load_101 | 104 | 0.0025681 | 0.00064362 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_115-6_0_3_load_115 | 105 | 0.0016189 | 0.00040574 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_115-6_0_3_load_97 | 106 | 0.0019617 | 0.00049164 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_115-6_0_3_load_105 | 107 | 0.0021285 | 0.00053346 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_115-6_0_3_load_102 | 108 | 0.0038267 | 0.00095906 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_115-6_0_3_load_103 | 109 | 0.0023215 | 0.00058181 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_115-6_0_3_load_112 | 110 | 0.0019237 | 0.00048213 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_115-6_0_3_load_106 | 111 | 0.0014644 | 0.00036701 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_115-6_0_3_load_107 | 112 | 0.0026753 | 0.00067049 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_115-6_0_3_load_108 | 113 | 0.0041063 | 0.0010291 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_115-6_0_3_load_113 | 114 | 0.0027137 | 0.00068013 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_115-6_0_3_load_109 | 115 | 0.0018337 | 0.00045957 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_115-6_0_3_load_111 | 116 | 0.0003798 | 9.5187e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_115-6_0_3_load_117 | 117 | 0.007027 | 0.0017611 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_115-6_0_3_load_120 | 119 | 0.0022186 | 0.00055603 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_115-6_0_3_load_121 | 120 | 0.0046192 | 0.0011577 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_115-6_0_3_load_123 | 122 | 0.0024314 | 0.00060937 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_115-6_0_3_load_125 | 124 | 0.0014155 | 0.00035476 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_115-6_0_3_load_263 | 125 | 0.00063036 | 0.00015798 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_115-6_0_3_load_264 | 126 | 0.00063024 | 0.00015795 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_115-6_0_3_line_0 |  | 0 | 1 | 0.027894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_115-6_0_3_line_1 |  | 1 | 2 | 0.0029916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_115-6_0_3_line_2 |  | 1 | 3 | 0.027139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_115-6_0_3_line_3 |  | 2 | 4 | 0.025755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_115-6_0_3_line_4 |  | 3 | 5 | 0.021403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_115-6_0_3_line_5 |  | 4 | 6 | 0.009104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_115-6_0_3_line_6 |  | 5 | 7 | 0.004094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_115-6_0_3_line_7 |  | 6 | 21 | 0.026134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_115-6_0_3_line_8 |  | 6 | 22 | 0.011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_115-6_0_3_line_9 |  | 7 | 41 | 0.034841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_115-6_0_3_line_10 |  | 7 | 42 | 0.0273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_115-6_0_3_line_11 |  | 8 | 9 | 0.001405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_115-6_0_3_line_12 |  | 8 | 10 | 0.021011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_115-6_0_3_line_13 |  | 10 | 11 | 0.13409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_115-6_0_3_line_14 |  | 11 | 12 | 0.036858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_115-6_0_3_line_15 |  | 12 | 13 | 0.038132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_115-6_0_3_line_16 |  | 13 | 94 | 0.0040647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_115-6_0_3_line_17 |  | 14 | 15 | 0.032675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_115-6_0_3_line_18 |  | 14 | 16 | 0.032522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_115-6_0_3_line_19 |  | 15 | 17 | 0.02512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_115-6_0_3_line_20 |  | 16 | 18 | 0.0025172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_115-6_0_3_line_21 |  | 18 | 19 | 0.021394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_115-6_0_3_line_22 |  | 19 | 20 | 0.038741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_115-6_0_3_line_23 |  | 20 | 32 | 0.016086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_115-6_0_3_line_24 |  | 22 | 28 | 0.02955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_115-6_0_3_line_25 |  | 23 | 24 | 0.05027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_115-6_0_3_line_26 |  | 23 | 25 | 0.033313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_115-6_0_3_line_27 |  | 24 | 26 | 0.0090003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_115-6_0_3_line_28 |  | 25 | 27 | 0.008144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_115-6_0_3_line_29 |  | 25 | 28 | 0.037212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_115-6_0_3_line_30 |  | 26 | 29 | 0.012005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_115-6_0_3_line_31 |  | 28 | 31 | 0.0061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_115-6_0_3_line_32 |  | 29 | 30 | 0.028009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_115-6_0_3_line_33 |  | 30 | 32 | 0.037289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_115-6_0_3_line_34 |  | 33 | 34 | 0.0012278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_115-6_0_3_line_35 |  | 34 | 35 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_115-6_0_3_line_36 |  | 35 | 36 | 0.016147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_115-6_0_3_line_37 |  | 36 | 37 | 0.0017073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_115-6_0_3_line_38 |  | 36 | 38 | 0.025612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_115-6_0_3_line_39 |  | 37 | 39 | 0.028644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_115-6_0_3_line_40 |  | 38 | 40 | 0.026887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_115-6_0_3_line_41 |  | 39 | 41 | 0.034698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_115-6_0_3_line_42 |  | 41 | 43 | 0.023533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_115-6_0_3_line_43 |  | 42 | 44 | 0.010711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_115-6_0_3_line_44 |  | 43 | 68 | 0.002455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_115-6_0_3_line_45 |  | 44 | 61 | 0.022364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_115-6_0_3_line_46 |  | 45 | 46 | 0.023601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_115-6_0_3_line_47 |  | 45 | 47 | 0.026946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_115-6_0_3_line_48 |  | 46 | 48 | 0.021991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_115-6_0_3_line_49 |  | 47 | 49 | 0.031163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_115-6_0_3_line_50 |  | 48 | 50 | 0.0084458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_115-6_0_3_line_51 |  | 49 | 51 | 0.0085359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_115-6_0_3_line_52 |  | 50 | 52 | 0.024215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_115-6_0_3_line_53 |  | 51 | 53 | 0.019287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_115-6_0_3_line_54 |  | 52 | 69 | 0.025195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_115-6_0_3_line_55 |  | 52 | 70 | 0.11447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_115-6_0_3_line_56 |  | 53 | 85 | 0.0048202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_115-6_0_3_line_57 |  | 54 | 55 | 0.026708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_115-6_0_3_line_58 |  | 55 | 56 | 0.010814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_115-6_0_3_line_59 |  | 56 | 57 | 0.004059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_115-6_0_3_line_60 |  | 57 | 58 | 0.032728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_115-6_0_3_line_61 |  | 58 | 59 | 0.0097311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_115-6_0_3_line_62 |  | 59 | 95 | 0.021115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_115-6_0_3_line_63 |  | 59 | 96 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_115-6_0_3_line_64 |  | 60 | 61 | 0.025577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_115-6_0_3_line_65 |  | 60 | 62 | 0.0053401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_115-6_0_3_line_66 |  | 62 | 63 | 0.022408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_115-6_0_3_line_67 |  | 63 | 64 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_115-6_0_3_line_68 |  | 64 | 67 | 0.0062147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_115-6_0_3_line_69 |  | 65 | 66 | 0.0071032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_115-6_0_3_line_70 |  | 66 | 78 | 0.014716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_115-6_0_3_line_71 |  | 67 | 76 | 0.0062191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_115-6_0_3_line_72 |  | 68 | 100 | 0.030433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_115-6_0_3_line_73 |  | 69 | 106 | 0.024762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_115-6_0_3_line_74 |  | 70 | 124 | 0.051081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_115-6_0_3_line_75 |  | 71 | 72 | 0.027771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_115-6_0_3_line_76 |  | 71 | 73 | 0.014204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_115-6_0_3_line_77 |  | 72 | 74 | 0.00060037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_115-6_0_3_line_78 |  | 73 | 75 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_115-6_0_3_line_79 |  | 75 | 76 | 0.0064516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_115-6_0_3_line_80 |  | 77 | 78 | 0.019325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_115-6_0_3_line_81 |  | 77 | 79 | 0.014596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_115-6_0_3_line_82 |  | 79 | 80 | 0.048428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_115-6_0_3_line_83 |  | 79 | 81 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_115-6_0_3_line_84 |  | 80 | 82 | 0.013282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_115-6_0_3_line_85 |  | 81 | 83 | 0.011068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_115-6_0_3_line_86 |  | 83 | 84 | 0.041012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_115-6_0_3_line_87 |  | 84 | 88 | 0.0073111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_115-6_0_3_line_88 |  | 85 | 126 | 0.0055881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_115-6_0_3_line_89 |  | 86 | 87 | 0.032473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_115-6_0_3_line_90 |  | 86 | 88 | 0.037472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_115-6_0_3_line_91 |  | 87 | 89 | 0.0057058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_115-6_0_3_line_92 |  | 88 | 90 | 0.046395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_115-6_0_3_line_93 |  | 89 | 91 | 0.0057057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_115-6_0_3_line_94 |  | 90 | 92 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_115-6_0_3_line_95 |  | 91 | 93 | 0.0057091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_115-6_0_3_line_96 |  | 92 | 94 | 0.010952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_115-6_0_3_line_97 |  | 94 | 125 | 0.035652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_115-6_0_3_line_98 |  | 95 | 97 | 0.0033047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_115-6_0_3_line_99 |  | 96 | 98 | 0.01404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_115-6_0_3_line_100 |  | 97 | 105 | 0.00021349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_115-6_0_3_line_101 |  | 98 | 99 | 0.024317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_115-6_0_3_line_102 |  | 99 | 100 | 0.015011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_115-6_0_3_line_103 |  | 99 | 101 | 0.034905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_115-6_0_3_line_104 |  | 99 | 102 | 0.049068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_115-6_0_3_line_105 |  | 101 | 103 | 0.024241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_115-6_0_3_line_106 |  | 102 | 104 | 0.03394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_115-6_0_3_line_107 |  | 103 | 107 | 0.039604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_115-6_0_3_line_108 |  | 103 | 106 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_115-6_0_3_line_109 |  | 104 | 108 | 0.032796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_115-6_0_3_line_110 |  | 107 | 110 | 0.013857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_115-6_0_3_line_111 |  | 108 | 109 | 0.033448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_115-6_0_3_line_112 |  | 110 | 115 | 0.024137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_115-6_0_3_line_113 |  | 111 | 112 | 0.035151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_115-6_0_3_line_114 |  | 111 | 113 | 0.027771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_115-6_0_3_line_115 |  | 112 | 114 | 0.067359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_115-6_0_3_line_116 |  | 113 | 115 | 0.032895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_115-6_0_3_line_117 |  | 114 | 116 | 0.019553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_115-6_0_3_line_118 |  | 117 | 118 | 0.10755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_115-6_0_3_line_119 |  | 118 | 119 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_115-6_0_3_line_120 |  | 119 | 120 | 0.010822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_115-6_0_3_line_121 |  | 120 | 121 | 0.019187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_115-6_0_3_line_122 |  | 121 | 122 | 0.0014681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_115-6_0_3_line_123 |  | 122 | 123 | 0.012757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_115-6_0_3_line_124 |  | 123 | 124 | 0.019239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_115-6_0_3_line_125 |  | 125 | 126 | 0.0059643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_115-6_0_3_trafo_88 | 0.63 MVA 20/0.4 kV | 127 | 96 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2699948.9896 | 1240567.2979 | 2699953.7897 | 1240566.5448 | 2699959.6146 | 1240568.2553 | 2699975.5644 | 1240562.4767
1 | 2699948.9896 | 1240567.2979 | 2699948.5515 | 1240564.3385
2 | 2699948.9896 | 1240567.2979 | 2699949.5917 | 1240571.5112 | 2699952.5827 | 1240594.1977
3 | 2699944.7796 | 1240538.8609 | 2699948.5515 | 1240564.3385
4 | 2699952.5827 | 1240594.1977 | 2699955.3803 | 1240615.4175
5 | 2699943.8507 | 1240529.8051 | 2699944.7796 | 1240538.8609
6 | 2699955.9154 | 1240619.4764 | 2699955.3803 | 1240615.4175
7 | 2699943.8507 | 1240529.8051 | 2699967.7723 | 1240519.2823
8 | 2699943.8507 | 1240529.8051 | 2699942.5827 | 1240518.8754
9 | 2699955.9154 | 1240619.4764 | 2699968.7124 | 1240619.0026 | 2699990.8224 | 1240617.8964
10 | 2699955.9154 | 1240619.4764 | 2699956.043 | 1240630.309 | 2699955.0506 | 1240646.7455
11 | 2699716.0949 | 1241069.8254 | 2699715.2108 | 1241070.9174
12 | 2699729.3161 | 1241053.4958 | 2699716.0949 | 1241069.8254
13 | 2699729.3161 | 1241053.4958 | 2699746.2654 | 1241039.4366 | 2699782.924 | 1241011.3423 | 2699797.0943 | 1240995.7131 | 2699806.9469 | 1240976.9088 | 2699814.0915 | 1240954.4569
14 | 2699820.5645 | 1240918.182 | 2699817.9122 | 1240935.1281 | 2699814.2289 | 1240954.025 | 2699814.0915 | 1240954.4569
15 | 2699820.5645 | 1240918.182 | 2699829.235 | 1240921.0967 | 2699843.0045 | 1240923.9081 | 2699850.9732 | 1240920.8954 | 2699854.8315 | 1240915.7748
16 | 2699857.2775 | 1240912.5284 | 2699854.8315 | 1240915.7748
17 | 2699838.3046 | 1240522.6488 | 2699854.8708 | 1240520.4007 | 2699865.763 | 1240518.9717 | 2699870.6976 | 1240519.5717
18 | 2699805.9959 | 1240522.7918 | 2699824.2537 | 1240524.5556 | 2699838.3046 | 1240522.6488
19 | 2699870.6976 | 1240519.5717 | 2699881.0469 | 1240520.8302 | 2699895.0101 | 1240525.4092
20 | 2699805.9959 | 1240522.7918 | 2699803.6639 | 1240521.8441
21 | 2699783.8439 | 1240513.7903 | 2699803.6639 | 1240521.8441
22 | 2699785.8408 | 1240475.1056 | 2699783.8439 | 1240513.7903
23 | 2699785.8408 | 1240475.1056 | 2699801.88 | 1240473.8854
24 | 2699942.3469 | 1240489.3267 | 2699942.5827 | 1240518.8754
25 | 2699845.2476 | 1240436.9976 | 2699852.9495 | 1240439.985 | 2699854.8656 | 1240440.7289 | 2699858.0308 | 1240441.8497 | 2699891.321 | 1240453.2517 | 2699892.649 | 1240453.7175
26 | 2699924.3028 | 1240464.0927 | 2699899.4788 | 1240456.1133 | 2699892.649 | 1240453.7175
27 | 2699845.2476 | 1240436.9976 | 2699843.4226 | 1240439.3799 | 2699840.8994 | 1240441.0053 | 2699837.9834 | 1240441.7013
28 | 2699924.3028 | 1240464.0927 | 2699924.0478 | 1240465.3116 | 2699922.2398 | 1240471.1745 | 2699922.0157 | 1240471.9046
29 | 2699924.3028 | 1240464.0927 | 2699934.7051 | 1240467.0589 | 2699934.4643 | 1240468.7784 | 2699934.5819 | 1240470.7819 | 2699935.2118 | 1240472.8941 | 2699936.7588 | 1240475.3443 | 2699939.3034 | 1240477.3887 | 2699942.5451 | 1240478.4551 | 2699942.3469 | 1240489.3267
30 | 2699828.903 | 1240435.2326 | 2699830.1734 | 1240437.9449 | 2699832.2855 | 1240440.0709 | 2699834.9939 | 1240441.373 | 2699837.9834 | 1240441.7013
31 | 2699942.3469 | 1240489.3267 | 2699936.2317 | 1240489.1236
32 | 2699800.9415 | 1240436.608 | 2699818.6252 | 1240436.5496 | 2699821.0935 | 1240436.391 | 2699825.2266 | 1240436.1715 | 2699828.903 | 1240435.2326
33 | 2699800.9415 | 1240436.608 | 2699801.88 | 1240473.8854
34 | 2700025.7719 | 1240547.396 | 2700025.2414 | 1240546.2888
35 | 2700025.7719 | 1240547.396 | 2700034.4521 | 1240565.514
36 | 2700041.4285 | 1240580.0757 | 2700034.4521 | 1240565.514
37 | 2700041.4285 | 1240580.0757 | 2700040.3277 | 1240581.3806
38 | 2700041.4285 | 1240580.0757 | 2700057.33 | 1240559.9975
39 | 2700040.3277 | 1240581.3806 | 2700021.8576 | 1240603.2747
40 | 2700074.0231 | 1240538.9198 | 2700057.33 | 1240559.9975
41 | 2699990.8224 | 1240617.8964 | 2700004.6567 | 1240614.2043 | 2700021.8576 | 1240603.2747 | 2700021.8576 | 1240603.2747
42 | 2699990.8224 | 1240617.8964 | 2699992.8974 | 1240631.6418 | 2699997.8863 | 1240639.8808
43 | 2699955.0506 | 1240646.7455 | 2699954.8995 | 1240649.2486 | 2699953.3167 | 1240657.2979
44 | 2699999.1579 | 1240641.9808 | 2699997.8863 | 1240639.8808
45 | 2699947.4515 | 1240678.8252 | 2699951.26 | 1240667.757 | 2699953.3167 | 1240657.2979
46 | 2699969.618 | 1240836.5402 | 2699985.2945 | 1240818.8981
47 | 2699969.618 | 1240836.5402 | 2699951.7194 | 1240856.683
48 | 2699999.8033 | 1240802.3732 | 2699991.7465 | 1240811.6372 | 2699985.2945 | 1240818.8981
49 | 2699927.7358 | 1240876.1776 | 2699932.7255 | 1240873.6906 | 2699945.6321 | 1240863.5335 | 2699951.7194 | 1240856.683
50 | 2699999.8033 | 1240802.3732 | 2700005.3457 | 1240796.0003
51 | 2699920.0962 | 1240879.9853 | 2699927.7358 | 1240876.1776
52 | 2700005.3457 | 1240796.0003 | 2700019.1095 | 1240780.1742 | 2700021.0541 | 1240777.5814
53 | 2699902.8342 | 1240888.5889 | 2699920.0962 | 1240879.9853
54 | 2700021.0541 | 1240777.5814 | 2700036.1714 | 1240757.4254
55 | 2700021.0541 | 1240777.5814 | 2700105.5706 | 1240854.7883
56 | 2699898.5201 | 1240890.739 | 2699898.5201 | 1240890.739 | 2699902.8342 | 1240888.5889
57 | 2699920.9265 | 1240781.3102 | 2699937.453 | 1240760.329
58 | 2699937.453 | 1240760.329 | 2699944.1442 | 1240751.8341
59 | 2699944.1442 | 1240751.8341 | 2699946.6558 | 1240748.6455
60 | 2699946.6558 | 1240748.6455 | 2699966.9068 | 1240722.9358
61 | 2699972.9282 | 1240715.2914 | 2699966.9068 | 1240722.9358
62 | 2699972.9282 | 1240715.2914 | 2699982.6663 | 1240726.2303 | 2699986.9712 | 1240731.0595
63 | 2699972.9282 | 1240715.2914 | 2699990.9449 | 1240699.0157
64 | 2699936.8926 | 1240702.0661 | 2699944.93 | 1240686.1533 | 2699947.4515 | 1240678.8252
65 | 2699936.8926 | 1240702.0661 | 2699936.2925 | 1240703.2543 | 2699934.0229 | 1240706.5589
66 | 2699921.337 | 1240725.0302 | 2699934.0229 | 1240706.5589
67 | 2699921.337 | 1240725.0302 | 2699911.8612 | 1240722.3131 | 2699907.6469 | 1240724.6552
68 | 2699907.6469 | 1240724.6552 | 2699902.2147 | 1240727.6741
69 | 2699865.6545 | 1240799.7 | 2699869.708 | 1240793.8669
70 | 2699865.6545 | 1240799.7 | 2699857.2567 | 1240811.7847 | 2699857.2567 | 1240811.7847
71 | 2699902.2147 | 1240727.6741 | 2699896.7787 | 1240730.6951
72 | 2699999.1579 | 1240641.9808 | 2700013.625 | 1240665.8725 | 2700015.1248 | 1240667.8761
73 | 2700036.1714 | 1240757.4254 | 2700051.0289 | 1240737.6158
74 | 2700105.5706 | 1240854.7883 | 2700120.0642 | 1240867.1199 | 2700123.8621 | 1240873.7557 | 2700124.6667 | 1240879.8517 | 2700122.39 | 1240888.3864 | 2700116.9107 | 1240896.0526
75 | 2699840.1722 | 1240761.1117 | 2699864.6378 | 1240747.9727
76 | 2699877.1518 | 1240741.2521 | 2699864.6378 | 1240747.9727
77 | 2699840.1722 | 1240761.1117 | 2699839.9266 | 1240761.2437 | 2699839.6238 | 1240761.3519
78 | 2699891.1018 | 1240733.7603 | 2699877.1518 | 1240741.2521
79 | 2699896.7787 | 1240730.6951 | 2699895.898 | 1240731.1846 | 2699891.1018 | 1240733.7603
80 | 2699848.3509 | 1240828.9355 | 2699857.2567 | 1240811.7847
81 | 2699841.6246 | 1240841.8892 | 2699848.3509 | 1240828.9355
82 | 2699841.6246 | 1240841.8892 | 2699835.2669 | 1240836.8006 | 2699801.9167 | 1240849.316 | 2699797.8733 | 1240851.8611
83 | 2699833.6932 | 1240865.1513 | 2699841.6246 | 1240841.8892
84 | 2699797.8733 | 1240851.8611 | 2699784.6831 | 1240853.7186
85 | 2699833.6932 | 1240865.1513 | 2699843.6596 | 1240860.3369
86 | 2699843.6596 | 1240860.3369 | 2699846.35 | 1240859.0372 | 2699864.9761 | 1240857.7273 | 2699881.2532 | 1240847.2598
87 | 2699888.5514 | 1240847.6941 | 2699881.2532 | 1240847.2598
88 | 2699893.7752 | 1240893.6907 | 2699898.5201 | 1240890.739
89 | 2699941.4449 | 1240803.4848 | 2699920.394 | 1240828.2103
90 | 2699888.5514 | 1240847.6941 | 2699918.6726 | 1240830.2321 | 2699920.394 | 1240828.2103
91 | 2699941.4449 | 1240803.4848 | 2699945.1437 | 1240799.1403
92 | 2699888.5514 | 1240847.6941 | 2699872.8308 | 1240862.8411 | 2699863.9734 | 1240880.0052 | 2699862.9148 | 1240885.1468
93 | 2699945.1437 | 1240799.1403 | 2699948.8425 | 1240794.7958
94 | 2699859.486 | 1240901.8016 | 2699862.9148 | 1240885.1468
95 | 2699948.8425 | 1240794.7958 | 2699952.5435 | 1240790.4488
96 | 2699857.2775 | 1240912.5284 | 2699859.486 | 1240901.8016
97 | 2699857.2775 | 1240912.5284 | 2699865.504 | 1240911.277 | 2699888.7108 | 1240896.841
98 | 2699989.1703 | 1240733.5263 | 2699986.9712 | 1240731.0595
99 | 2699990.9449 | 1240699.0157 | 2700002.6789 | 1240691.3065
100 | 2699989.3123 | 1240733.6857 | 2699989.1703 | 1240733.5263
101 | 2700024.1203 | 1240679.8933 | 2700006.9513 | 1240688.4995 | 2700002.6789 | 1240691.3065
102 | 2700024.1203 | 1240679.8933 | 2700015.1248 | 1240667.8761
103 | 2700024.1203 | 1240679.8933 | 2700037.1068 | 1240697.7702 | 2700043.6267 | 1240704.0071 | 2700045.7967 | 1240707.1103
104 | 2700024.1203 | 1240679.8933 | 2700040.3734 | 1240671.7944 | 2700053.8668 | 1240662.3034 | 2700064.2651 | 1240652.325
105 | 2700063.294 | 1240721.2628 | 2700058.4257 | 1240721.1362 | 2700054.3198 | 1240719.2989 | 2700045.7967 | 1240707.1103
106 | 2700064.2651 | 1240652.325 | 2700065.4362 | 1240651.2011 | 2700074.7094 | 1240639.4818 | 2700084.9226 | 1240625.4291
107 | 2700063.294 | 1240721.2628 | 2700086.5831 | 1240689.2301
108 | 2700063.294 | 1240721.2628 | 2700051.0289 | 1240737.6158
109 | 2700084.9226 | 1240625.4291 | 2700100.3764 | 1240604.1654 | 2700104.9947 | 1240599.5775
110 | 2700094.7314 | 1240678.0226 | 2700086.5831 | 1240689.2301
111 | 2700128.7236 | 1240576.0044 | 2700104.9947 | 1240599.5775
112 | 2700094.7314 | 1240678.0226 | 2700108.4174 | 1240659.1984 | 2700108.9199 | 1240658.4957
113 | 2700144.516 | 1240609.3992 | 2700154.2387 | 1240598.8587 | 2700166.7753 | 1240589.1739 | 2700171.235 | 1240586.9821
114 | 2700144.516 | 1240609.3992 | 2700142.3515 | 1240611.7457 | 2700128.0546 | 1240631.7382
115 | 2700171.235 | 1240586.9821 | 2700237.5038 | 1240599.0529
116 | 2700128.0546 | 1240631.7382 | 2700108.9199 | 1240658.4957
117 | 2700237.5038 | 1240599.0529 | 2700254.6899 | 1240589.7276
118 | 2700074.0381 | 1240956.3229 | 2700087.8655 | 1240974.5144 | 2700094.8432 | 1240986.7636 | 2700114.3494 | 1241020.218 | 2700112.0265 | 1241031.9433 | 2700097.236 | 1241045.293
119 | 2700074.0381 | 1240956.3229 | 2700085.1921 | 1240946.3712
120 | 2700093.2669 | 1240939.1667 | 2700085.1921 | 1240946.3712
121 | 2700106.6539 | 1240925.4827 | 2700100.3971 | 1240932.805 | 2700093.2669 | 1240939.1667
122 | 2700106.6539 | 1240925.4827 | 2700107.607 | 1240924.3661
123 | 2700115.8889 | 1240914.6635 | 2700107.607 | 1240924.3661
124 | 2700115.8889 | 1240914.6635 | 2700115.024 | 1240898.6923 | 2700116.9107 | 1240896.0526
125 | 2699888.7108 | 1240896.841 | 2699893.7752 | 1240893.6907

## bus_geodata
| x | y | coords
0 | 2699975.5644 | 1240562.4767
1 | 2699948.9896 | 1240567.2979
2 | 2699948.5515 | 1240564.3385
3 | 2699952.5827 | 1240594.1977
4 | 2699944.7796 | 1240538.8609
5 | 2699955.3803 | 1240615.4175
6 | 2699943.8507 | 1240529.8051
7 | 2699955.9154 | 1240619.4764
8 | 2699716.0949 | 1241069.8254
9 | 2699715.2108 | 1241070.9174
10 | 2699729.3161 | 1241053.4958
11 | 2699814.0915 | 1240954.4569
12 | 2699820.5645 | 1240918.182
13 | 2699854.8315 | 1240915.7748
14 | 2699838.3046 | 1240522.6488
15 | 2699870.6976 | 1240519.5717
16 | 2699805.9959 | 1240522.7918
17 | 2699895.0101 | 1240525.4092
18 | 2699803.6639 | 1240521.8441
19 | 2699783.8439 | 1240513.7903
20 | 2699785.8408 | 1240475.1056
21 | 2699967.7723 | 1240519.2823
22 | 2699942.5827 | 1240518.8754
23 | 2699892.649 | 1240453.7175
24 | 2699845.2476 | 1240436.9976
25 | 2699924.3028 | 1240464.0927
26 | 2699837.9834 | 1240441.7013
27 | 2699922.0157 | 1240471.9046
28 | 2699942.3469 | 1240489.3267
29 | 2699828.903 | 1240435.2326
30 | 2699800.9415 | 1240436.608
31 | 2699936.2317 | 1240489.1236
32 | 2699801.88 | 1240473.8854
33 | 2700025.2414 | 1240546.2888
34 | 2700025.7719 | 1240547.396
35 | 2700034.4521 | 1240565.514
36 | 2700041.4285 | 1240580.0757
37 | 2700040.3277 | 1240581.3806
38 | 2700057.33 | 1240559.9975
39 | 2700021.8576 | 1240603.2747
40 | 2700074.0231 | 1240538.9198
41 | 2699990.8224 | 1240617.8964
42 | 2699955.0506 | 1240646.7455
43 | 2699997.8863 | 1240639.8808
44 | 2699953.3167 | 1240657.2979
45 | 2699969.618 | 1240836.5402
46 | 2699985.2945 | 1240818.8981
47 | 2699951.7194 | 1240856.683
48 | 2699999.8033 | 1240802.3732
49 | 2699927.7358 | 1240876.1776
50 | 2700005.3457 | 1240796.0003
51 | 2699920.0962 | 1240879.9853
52 | 2700021.0541 | 1240777.5814
53 | 2699902.8342 | 1240888.5889
54 | 2699920.9265 | 1240781.3102
55 | 2699937.453 | 1240760.329
56 | 2699944.1442 | 1240751.8341
57 | 2699946.6558 | 1240748.6455
58 | 2699966.9068 | 1240722.9358
59 | 2699972.9282 | 1240715.2914
60 | 2699936.8926 | 1240702.0661
61 | 2699947.4515 | 1240678.8252
62 | 2699934.0229 | 1240706.5589
63 | 2699921.337 | 1240725.0302
64 | 2699907.6469 | 1240724.6552
65 | 2699869.708 | 1240793.8669
66 | 2699865.6545 | 1240799.7
67 | 2699902.2147 | 1240727.6741
68 | 2699999.1579 | 1240641.9808
69 | 2700036.1714 | 1240757.4254
70 | 2700105.5706 | 1240854.7883
71 | 2699864.6378 | 1240747.9727
72 | 2699840.1722 | 1240761.1117
73 | 2699877.1518 | 1240741.2521
74 | 2699839.6238 | 1240761.3519
75 | 2699891.1018 | 1240733.7603
76 | 2699896.7787 | 1240730.6951
77 | 2699848.3509 | 1240828.9355
78 | 2699857.2567 | 1240811.7847
79 | 2699841.6246 | 1240841.8892
80 | 2699797.8733 | 1240851.8611
81 | 2699833.6932 | 1240865.1513
82 | 2699784.6831 | 1240853.7186
83 | 2699843.6596 | 1240860.3369
84 | 2699881.2532 | 1240847.2598
85 | 2699898.5201 | 1240890.739
86 | 2699920.394 | 1240828.2103
87 | 2699941.4449 | 1240803.4848
88 | 2699888.5514 | 1240847.6941
89 | 2699945.1437 | 1240799.1403
90 | 2699862.9148 | 1240885.1468
91 | 2699948.8425 | 1240794.7958
92 | 2699859.486 | 1240901.8016
93 | 2699952.5435 | 1240790.4488
94 | 2699857.2775 | 1240912.5284
95 | 2699986.9712 | 1240731.0595
96 | 2699990.9449 | 1240699.0157
97 | 2699989.1703 | 1240733.5263
98 | 2700002.6789 | 1240691.3065
99 | 2700024.1203 | 1240679.8933
100 | 2700015.1248 | 1240667.8761
101 | 2700045.7967 | 1240707.1103
102 | 2700064.2651 | 1240652.325
103 | 2700063.294 | 1240721.2628
104 | 2700084.9226 | 1240625.4291
105 | 2699989.3123 | 1240733.6857
106 | 2700051.0289 | 1240737.6158
107 | 2700086.5831 | 1240689.2301
108 | 2700104.9947 | 1240599.5775
109 | 2700128.7236 | 1240576.0044
110 | 2700094.7314 | 1240678.0226
111 | 2700144.516 | 1240609.3992
112 | 2700171.235 | 1240586.9821
113 | 2700128.0546 | 1240631.7382
114 | 2700237.5038 | 1240599.0529
115 | 2700108.9199 | 1240658.4957
116 | 2700254.6899 | 1240589.7276
117 | 2700097.236 | 1241045.293
118 | 2700074.0381 | 1240956.3229
119 | 2700085.1921 | 1240946.3712
120 | 2700093.2669 | 1240939.1666
121 | 2700106.6539 | 1240925.4827
122 | 2700107.607 | 1240924.3661
123 | 2700115.8889 | 1240914.6635
124 | 2700116.9107 | 1240896.0526
125 | 2699888.7108 | 1240896.841
126 | 2699893.7752 | 1240893.6907
127 | 2699972.9282 | 1240715.2914

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98088 | -0.36743 | 0.016671 | 0.004178
1 | 0.98131 | -0.35901 | 0 | 0
2 | 0.9812 | -0.3613 | 0.0026946 | 0.00067533
3 | 0.9828 | -0.3301 | 0.012801 | 0.0032083
4 | 0.98025 | -0.37977 | 0 | 0
5 | 0.98422 | -0.30243 | 0.00213 | 0.00053384
6 | 0.97992 | -0.38631 | 0 | 0
7 | 0.9845 | -0.29699 | 0 | 0
8 | 0.97911 | -0.40271 | 0.0085667 | 0.002147
9 | 0.97911 | -0.40272 | 0.00038291 | 9.5967e-05
10 | 0.97929 | -0.39929 | 0 | 0
11 | 0.9804 | -0.3775 | 0.0018866 | 0.00047283
12 | 0.98077 | -0.37025 | 0 | 0
13 | 0.98115 | -0.36277 | 0.00055458 | 0.00013899
14 | 0.9737 | -0.50843 | 0.0055151 | 0.0013822
15 | 0.97347 | -0.51298 | 0.0061124 | 0.0015319
16 | 0.97409 | -0.5006 | 0 | 0
17 | 0.97343 | -0.51366 | 0.0014714 | 0.00036878
18 | 0.97412 | -0.49999 | 0.0013605 | 0.00034098
19 | 0.97441 | -0.49431 | 0 | 0
20 | 0.97493 | -0.48403 | 0 | 0
21 | 0.97974 | -0.38967 | 0.0070748 | 0.0017731
22 | 0.97958 | -0.3928 | 0.0062901 | 0.0015764
23 | 0.97737 | -0.43622 | 0.0025686 | 0.00064374
24 | 0.9765 | -0.45313 | 0 | 0
25 | 0.97802 | -0.42346 | 0 | 0
26 | 0.97635 | -0.45616 | 0.0017492 | 0.00043838
27 | 0.97799 | -0.42398 | 0.0034728 | 0.00087038
28 | 0.97886 | -0.40688 | 0 | 0
29 | 0.97616 | -0.45982 | 0 | 0
30 | 0.97573 | -0.46837 | 0 | 0
31 | 0.97885 | -0.40708 | 0.0017368 | 0.00043528
32 | 0.97515 | -0.47976 | 0.0022094 | 0.00055374
33 | 0.98552 | -0.27741 | 0.004346 | 0.0010892
34 | 0.98553 | -0.27731 | 0.006096 | 0.0015278
35 | 0.98572 | -0.27355 | 0.0052128 | 0.0013065
36 | 0.98595 | -0.26901 | 0 | 0
37 | 0.98599 | -0.26833 | 0.0031559 | 0.00079094
38 | 0.98579 | -0.27214 | 0.0036502 | 0.00091483
39 | 0.98666 | -0.25518 | 0.0020244 | 0.00050736
40 | 0.98571 | -0.27365 | 0.0031484 | 0.00078906
41 | 0.98754 | -0.23803 | 0 | 0
42 | 0.98398 | -0.30708 | 0.0034479 | 0.00086414
43 | 0.9902 | -0.18683 | 0.0022486 | 0.00056356
44 | 0.98381 | -0.31037 | 0.002713 | 0.00067993
45 | 0.98516 | -0.28456 | 0.00092003 | 0.00023058
46 | 0.98591 | -0.27006 | 0.0010536 | 0.00026406
47 | 0.98433 | -0.3007 | 0.00083869 | 0.00021019
48 | 0.98663 | -0.25614 | 0.0012471 | 0.00031256
49 | 0.98339 | -0.31893 | 0.00067686 | 0.00016964
50 | 0.98691 | -0.25062 | 0.0012472 | 0.00031257
51 | 0.98314 | -0.32382 | 0.0006764 | 0.00016952
52 | 0.98776 | -0.23426 | 0.0020942 | 0.00052487
53 | 0.98259 | -0.33466 | 0.00063036 | 0.00015798
54 | 0.99936 | -0.012228 | 0.0013655 | 0.00034223
55 | 0.9994 | -0.011592 | 0.0013392 | 0.00033563
56 | 0.99942 | -0.011081 | 0.0012905 | 0.00032343
57 | 0.99944 | -0.010798 | 0.0019014 | 0.00047655
58 | 0.99961 | -0.00743 | 0.0020571 | 0.00051555
59 | 0.99968 | -0.0060796 | 0.0013908 | 0.00034856
60 | 0.98321 | -0.3222 | 0.0021622 | 0.00054189
61 | 0.98352 | -0.31616 | 0.0012832 | 0.00032159
62 | 0.98315 | -0.32325 | 0.0015228 | 0.00038166
63 | 0.98296 | -0.32705 | 0 | 0
64 | 0.98283 | -0.32954 | 0.00089884 | 0.00022527
65 | 0.97931 | -0.39874 | 0.00066218 | 0.00016596
66 | 0.97932 | -0.39866 | 0.00089911 | 0.00022534
67 | 0.98278 | -0.33049 | 0.00089889 | 0.00022528
68 | 0.99048 | -0.18141 | 0.0058478 | 0.0014656
69 | 0.9891 | -0.20836 | 0.0018003 | 0.0004512
70 | 0.98589 | -0.27056 | 0 | 0
71 | 0.98256 | -0.33488 | 0.0029661 | 0.00074338
72 | 0.98253 | -0.33555 | 0.00066298 | 0.00016616
73 | 0.98262 | -0.33378 | 0.0015103 | 0.00037851
74 | 0.98253 | -0.33555 | 0.00066255 | 0.00016605
75 | 0.9827 | -0.33212 | 0.00089805 | 0.00022507
76 | 0.98274 | -0.33134 | 0.00089889 | 0.00022528
77 | 0.97939 | -0.39725 | 0.0019381 | 0.00048573
78 | 0.97934 | -0.39824 | 0.0012623 | 0.00031636
79 | 0.97946 | -0.39598 | 0 | 0
80 | 0.97934 | -0.39824 | 0 | 0
81 | 0.97962 | -0.39271 | 0 | 0
82 | 0.97931 | -0.39886 | 0.0025623 | 0.00064216
83 | 0.9797 | -0.39124 | 0.0006182 | 0.00015493
84 | 0.98 | -0.38532 | 0.0023066 | 0.00057809
85 | 0.98245 | -0.33731 | 0.0006301 | 0.00015792
86 | 0.97987 | -0.38789 | 0.0017643 | 0.00044218
87 | 0.97975 | -0.39026 | 0.0010037 | 0.00025154
88 | 0.98007 | -0.38396 | 0 | 0
89 | 0.97973 | -0.39057 | 0.0010025 | 0.00025124
90 | 0.98076 | -0.37047 | 0.00061844 | 0.000155
91 | 0.97972 | -0.39078 | 0.0010036 | 0.00025153
92 | 0.98102 | -0.36534 | 0.00055458 | 0.00013899
93 | 0.97972 | -0.39088 | 0.0010036 | 0.00025153
94 | 0.98119 | -0.36193 | 0 | 0
95 | 0.99959 | -0.0079262 | 0.001648 | 0.00041304
96 | 1 | 0 | -0.24796 | -0.063037
97 | 0.99958 | -0.0081202 | 0.0017464 | 0.0004377
98 | 0.99852 | -0.028011 | 0.0026992 | 0.00067649
99 | 0.99599 | -0.076145 | 0 | 0
100 | 0.99414 | -0.1113 | 0.0029003 | 0.00072689
101 | 0.99337 | -0.1262 | 0.0027816 | 0.00069715
102 | 0.99547 | -0.086018 | 0.0027252 | 0.000683
103 | 0.99161 | -0.15992 | 0 | 0
104 | 0.9952 | -0.091224 | 0.0025681 | 0.00064362
105 | 0.99958 | -0.0081262 | 0.0016189 | 0.00040574
106 | 0.99045 | -0.18218 | 0.0019617 | 0.00049164
107 | 0.99099 | -0.17202 | 0.0021285 | 0.00053346
108 | 0.99502 | -0.094774 | 0.0038267 | 0.00095906
109 | 0.99495 | -0.096141 | 0.0023215 | 0.00058181
110 | 0.9908 | -0.17574 | 0.0019237 | 0.00048213
111 | 0.98998 | -0.19159 | 0.0014644 | 0.00036701
112 | 0.98979 | -0.1952 | 0.0026753 | 0.00067049
113 | 0.99016 | -0.18802 | 0.0041063 | 0.0010291
114 | 0.9896 | -0.19891 | 0.0027137 | 0.00068013
115 | 0.99051 | -0.18139 | 0.0018337 | 0.00045957
116 | 0.9896 | -0.19904 | 0.0003798 | 9.5187e-05
117 | 0.98342 | -0.31864 | 0.007027 | 0.0017611
118 | 0.98412 | -0.30502 | 0 | 0
119 | 0.98422 | -0.30313 | 0.0022186 | 0.00055603
120 | 0.98431 | -0.30133 | 0.0046192 | 0.0011577
121 | 0.98456 | -0.29655 | 0 | 0
122 | 0.98457 | -0.29618 | 0.0024314 | 0.00060937
123 | 0.98477 | -0.29244 | 0 | 0
124 | 0.98505 | -0.28681 | 0.0014155 | 0.00035476
125 | 0.98214 | -0.34348 | 0.00063036 | 0.00015798
126 | 0.9823 | -0.34033 | 0.00063024 | 0.00015795
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016671 | -0.004178 | 0.016677 | 0.004182 | 6.6899e-06 | 3.9293e-06 | 0.02529 | 0.025289 | 0.02529 | 0.98088 | -0.36743 | 0.98131 | -0.35901 | 6.9477
1 | 0.042427 | 0.010693 | -0.042422 | -0.01069 | 4.6462e-06 | 2.9358e-06 | 0.064355 | 0.064355 | 0.064355 | 0.98131 | -0.35901 | 0.9812 | -0.3613 | 17.68
2 | -0.059104 | -0.014875 | 0.059186 | 0.014927 | 8.1785e-05 | 5.1999e-05 | 0.089645 | 0.089644 | 0.089645 | 0.98131 | -0.35901 | 0.9828 | -0.3301 | 24.6276
3 | 0.039727 | 0.010015 | -0.039692 | -0.009993 | 3.5082e-05 | 2.2127e-05 | 0.060269 | 0.060269 | 0.060269 | 0.9812 | -0.3613 | 0.98025 | -0.37977 | 16.5574
4 | -0.071987 | -0.018136 | 0.072082 | 0.018196 | 9.5407e-05 | 6.0789e-05 | 0.10903 | 0.10903 | 0.10903 | 0.9828 | -0.3301 | 0.98422 | -0.30243 | 29.9523
5 | 0.039692 | 0.009993 | -0.03968 | -0.0099852 | 1.2401e-05 | 7.8218e-06 | 0.060269 | 0.060269 | 0.060269 | 0.98025 | -0.37977 | 0.97992 | -0.38631 | 16.5574
6 | -0.074212 | -0.01873 | 0.074232 | 0.018743 | 1.9343e-05 | 1.2328e-05 | 0.11225 | 0.11225 | 0.11225 | 0.98422 | -0.30243 | 0.9845 | -0.29699 | 30.837
7 | 0.0070759 | 0.0017735 | -0.0070748 | -0.0017731 | 1.1315e-06 | 3.9498e-07 | 0.010745 | 0.010745 | 0.010745 | 0.97992 | -0.38631 | 0.97974 | -0.38967 | 2.9519
8 | 0.032604 | 0.0082117 | -0.032594 | -0.0082053 | 1.012e-05 | 6.3381e-06 | 0.049524 | 0.049524 | 0.049524 | 0.97992 | -0.38631 | 0.97958 | -0.3928 | 13.6055
9 | -0.094783 | -0.0239 | 0.095051 | 0.024072 | 0.00026834 | 0.00017129 | 0.14331 | 0.14331 | 0.14331 | 0.9845 | -0.29699 | 0.98754 | -0.23803 | 39.3711
10 | 0.020551 | 0.0051578 | -0.020541 | -0.0051518 | 9.8791e-06 | 5.9757e-06 | 0.031064 | 0.031064 | 0.031064 | 0.9845 | -0.29699 | 0.98398 | -0.30708 | 8.5342
11 | 0.00038291 | 9.5949e-05 | -0.00038291 | -9.5967e-05 | 1.7845e-10 | -1.7556e-08 | 0.00058193 | 0.00058193 | 0.00058193 | 0.97911 | -0.40271 | 0.97911 | -0.40272 | 0.15987
12 | -0.0089497 | -0.002243 | 0.0089511 | 0.0022436 | 1.4576e-06 | 6.6856e-07 | 0.013601 | 0.013601 | 0.013601 | 0.97911 | -0.40271 | 0.97929 | -0.39929 | 3.7366
13 | -0.0089511 | -0.0022436 | 0.0089604 | 0.0022479 | 9.3021e-06 | 4.2643e-06 | 0.013601 | 0.013601 | 0.013601 | 0.97929 | -0.39929 | 0.9804 | -0.3775 | 3.7366
14 | -0.010847 | -0.0027207 | 0.010851 | 0.0027227 | 3.7466e-06 | 1.9329e-06 | 0.016464 | 0.016464 | 0.016464 | 0.9804 | -0.3775 | 0.98077 | -0.37025 | 4.5231
15 | -0.010851 | -0.0027227 | 0.010855 | 0.0027247 | 3.8759e-06 | 1.9992e-06 | 0.016464 | 0.016464 | 0.016464 | 0.98077 | -0.37025 | 0.98115 | -0.36277 | 4.523
16 | -0.011409 | -0.0028637 | 0.01141 | 0.0028639 | 4.5645e-07 | 2.4079e-07 | 0.017305 | 0.017305 | 0.017305 | 0.98115 | -0.36277 | 0.98119 | -0.36193 | 4.7541
17 | 0.0075855 | 0.001901 | -0.0075839 | -0.0019004 | 1.6466e-06 | 6.4749e-07 | 0.011592 | 0.011592 | 0.011592 | 0.9737 | -0.50843 | 0.97347 | -0.51298 | 3.1847
18 | -0.013101 | -0.0032833 | 0.013106 | 0.003286 | 4.8884e-06 | 2.7239e-06 | 0.020021 | 0.02002 | 0.020021 | 0.9737 | -0.50843 | 0.97409 | -0.5006 | 5.5002
19 | 0.0014715 | 0.0003685 | -0.0014714 | -0.00036878 | 4.7657e-08 | -2.8179e-07 | 0.0022492 | 0.0022493 | 0.0022493 | 0.97347 | -0.51298 | 0.97343 | -0.51366 | 0.61794
20 | -0.013106 | -0.003286 | 0.013106 | 0.0032862 | 3.7835e-07 | 2.1081e-07 | 0.02002 | 0.02002 | 0.02002 | 0.97409 | -0.5006 | 0.97412 | -0.49999 | 5.5001
21 | -0.014466 | -0.0036272 | 0.01447 | 0.0036294 | 3.9179e-06 | 2.241e-06 | 0.022099 | 0.022099 | 0.022099 | 0.97412 | -0.49999 | 0.97441 | -0.49431 | 6.0711
22 | -0.01447 | -0.0036294 | 0.014477 | 0.0036335 | 7.0946e-06 | 4.0577e-06 | 0.022099 | 0.022098 | 0.022099 | 0.97441 | -0.49431 | 0.97493 | -0.48403 | 6.071
23 | -0.014477 | -0.0036335 | 0.01448 | 0.0036352 | 2.9457e-06 | 1.6846e-06 | 0.022098 | 0.022098 | 0.022098 | 0.97493 | -0.48403 | 0.97515 | -0.47976 | 6.071
24 | 0.026304 | 0.0066289 | -0.026286 | -0.0066179 | 1.7703e-05 | 1.0958e-05 | 0.039969 | 0.039969 | 0.039969 | 0.97958 | -0.3928 | 0.97886 | -0.40688 | 10.9806
25 | 0.018475 | 0.0046489 | -0.01846 | -0.00464 | 1.4922e-05 | 8.9209e-06 | 0.028135 | 0.028135 | 0.028135 | 0.97737 | -0.43622 | 0.9765 | -0.45313 | 7.7295
26 | -0.021044 | -0.0052926 | 0.021057 | 0.0053004 | 1.2829e-05 | 7.7925e-06 | 0.032046 | 0.032045 | 0.032046 | 0.97737 | -0.43622 | 0.97802 | -0.42346 | 8.8037
27 | 0.01846 | 0.00464 | -0.018458 | -0.0046384 | 2.6717e-06 | 1.5973e-06 | 0.028135 | 0.028135 | 0.028135 | 0.9765 | -0.45313 | 0.97635 | -0.45616 | 7.7295
28 | 0.0034729 | 0.00087033 | -0.0034728 | -0.00087038 | 8.5267e-08 | -4.7624e-08 | 0.0052839 | 0.005284 | 0.005284 | 0.97802 | -0.42346 | 0.97799 | -0.42398 | 1.4516
29 | -0.02453 | -0.0061707 | 0.024549 | 0.0061827 | 1.9445e-05 | 1.1978e-05 | 0.037329 | 0.037329 | 0.037329 | 0.97802 | -0.42346 | 0.97886 | -0.40688 | 10.2553
30 | 0.016709 | 0.0042 | -0.016706 | -0.0041983 | 2.9202e-06 | 1.7188e-06 | 0.025469 | 0.025469 | 0.025469 | 0.97635 | -0.45616 | 0.97616 | -0.45982 | 6.9971
31 | 0.0017368 | 0.00043522 | -0.0017368 | -0.00043528 | 1.5945e-08 | -6.6475e-08 | 0.0026402 | 0.0026402 | 0.0026402 | 0.97886 | -0.40688 | 0.97885 | -0.40708 | 0.72533
32 | 0.016706 | 0.0041983 | -0.016699 | -0.0041942 | 6.8135e-06 | 4.0107e-06 | 0.025469 | 0.02547 | 0.02547 | 0.97616 | -0.45982 | 0.97573 | -0.46837 | 6.9971
33 | 0.016699 | 0.0041942 | -0.01669 | -0.0041889 | 9.0712e-06 | 5.3401e-06 | 0.02547 | 0.02547 | 0.02547 | 0.97573 | -0.46837 | 0.97515 | -0.47976 | 6.9972
34 | -0.004346 | -0.0010892 | 0.0043461 | 0.0010892 | 1.9825e-08 | -2.9562e-09 | 0.006562 | 0.006562 | 0.006562 | 0.98552 | -0.27741 | 0.98553 | -0.27731 | 1.8027
35 | -0.010442 | -0.002617 | 0.010444 | 0.002618 | 1.8727e-06 | 9.4247e-07 | 0.015766 | 0.015766 | 0.015766 | 0.98553 | -0.27731 | 0.98572 | -0.27355 | 4.3314
36 | -0.015657 | -0.0039244 | 0.01566 | 0.0039264 | 3.3825e-06 | 1.9589e-06 | 0.023635 | 0.023635 | 0.023635 | 0.98572 | -0.27355 | 0.98595 | -0.26901 | 6.4932
37 | -0.02246 | -0.0056304 | 0.022461 | 0.0056309 | 7.3565e-07 | 4.4904e-07 | 0.033898 | 0.033898 | 0.033898 | 0.98595 | -0.26901 | 0.98599 | -0.26833 | 9.3125
38 | 0.0067999 | 0.001704 | -0.0067988 | -0.0017037 | 1.0115e-06 | 3.208e-07 | 0.010262 | 0.010263 | 0.010263 | 0.98595 | -0.26901 | 0.98579 | -0.27214 | 2.8194
39 | -0.025617 | -0.0064218 | 0.025633 | 0.0064317 | 1.6055e-05 | 9.9094e-06 | 0.03866 | 0.03866 | 0.03866 | 0.98599 | -0.26833 | 0.98666 | -0.25518 | 10.621
40 | 0.0031486 | 0.00078887 | -0.0031484 | -0.00078906 | 2.2775e-07 | -1.97e-07 | 0.0047527 | 0.0047528 | 0.0047528 | 0.98579 | -0.27214 | 0.98571 | -0.27365 | 1.3057
41 | -0.027657 | -0.0069391 | 0.02768 | 0.0069531 | 2.264e-05 | 1.4046e-05 | 0.041713 | 0.041713 | 0.041713 | 0.98666 | -0.25518 | 0.98754 | -0.23803 | 11.4597
42 | -0.12273 | -0.031025 | 0.12303 | 0.031218 | 0.00030211 | 0.00019305 | 0.18502 | 0.18502 | 0.18502 | 0.98754 | -0.23803 | 0.9902 | -0.18683 | 50.8308
43 | 0.017093 | 0.0042877 | -0.017091 | -0.0042861 | 2.6841e-06 | 1.5818e-06 | 0.02585 | 0.02585 | 0.02585 | 0.98398 | -0.30708 | 0.98381 | -0.31037 | 7.1018
44 | -0.12528 | -0.031781 | 0.12531 | 0.031802 | 3.2678e-05 | 2.0883e-05 | 0.1884 | 0.1884 | 0.1884 | 0.9902 | -0.18683 | 0.99048 | -0.18141 | 51.7591
45 | 0.014378 | 0.0036062 | -0.014374 | -0.0036039 | 3.9664e-06 | 2.2546e-06 | 0.021747 | 0.021747 | 0.021747 | 0.98381 | -0.31037 | 0.98352 | -0.31616 | 5.9745
46 | -0.034382 | -0.0086694 | 0.034406 | 0.0086844 | 2.3885e-05 | 1.4986e-05 | 0.05195 | 0.05195 | 0.05195 | 0.98516 | -0.28456 | 0.98591 | -0.27006 | 14.272
47 | 0.033462 | 0.0084388 | -0.033436 | -0.0084226 | 2.5832e-05 | 1.6189e-05 | 0.050561 | 0.050561 | 0.050561 | 0.98516 | -0.28456 | 0.98433 | -0.3007 | 13.8903
48 | -0.035459 | -0.0089484 | 0.035483 | 0.0089633 | 2.3639e-05 | 1.4848e-05 | 0.05354 | 0.05354 | 0.05354 | 0.98591 | -0.27006 | 0.98663 | -0.25614 | 14.7089
49 | 0.032597 | 0.0082124 | -0.032569 | -0.0081947 | 2.8395e-05 | 1.7777e-05 | 0.049293 | 0.049293 | 0.049293 | 0.98433 | -0.3007 | 0.98339 | -0.31893 | 13.542
50 | -0.03673 | -0.0092758 | 0.03674 | 0.009282 | 9.7279e-06 | 6.118e-06 | 0.055421 | 0.055421 | 0.055421 | 0.98663 | -0.25614 | 0.98691 | -0.25062 | 15.2256
51 | 0.031892 | 0.008025 | -0.031885 | -0.0080204 | 7.4578e-06 | 4.6647e-06 | 0.048269 | 0.048269 | 0.048269 | 0.98339 | -0.31893 | 0.98314 | -0.32382 | 13.2607
52 | -0.037987 | -0.0095945 | 0.038017 | 0.0096133 | 2.9816e-05 | 1.8772e-05 | 0.057302 | 0.057301 | 0.057302 | 0.98691 | -0.25062 | 0.98776 | -0.23426 | 15.7422
53 | 0.031208 | 0.0078508 | -0.031192 | -0.0078407 | 1.6144e-05 | 1.0088e-05 | 0.047245 | 0.047245 | 0.047245 | 0.98314 | -0.32382 | 0.98259 | -0.33466 | 12.9795
54 | -0.057884 | -0.014612 | 0.057956 | 0.014658 | 7.1904e-05 | 4.5696e-05 | 0.087237 | 0.087237 | 0.087237 | 0.98776 | -0.23426 | 0.9891 | -0.20836 | 23.9663
55 | 0.017773 | 0.0044737 | -0.017742 | -0.0044554 | 3.0789e-05 | 1.8243e-05 | 0.026781 | 0.026782 | 0.026782 | 0.98776 | -0.23426 | 0.98589 | -0.27056 | 7.3576
56 | 0.030562 | 0.0076828 | -0.030558 | -0.0076803 | 3.8733e-06 | 2.4179e-06 | 0.046291 | 0.046291 | 0.046291 | 0.98259 | -0.33466 | 0.98245 | -0.33731 | 12.7172
57 | -0.0013655 | -0.00034223 | 0.0013656 | 0.00034191 | 4.1401e-08 | -3.2346e-07 | 0.0020332 | 0.0020331 | 0.0020332 | 0.99936 | -0.012228 | 0.9994 | -0.011592 | 0.55857
58 | -0.0027047 | -0.00067754 | 0.0027048 | 0.00067744 | 6.5761e-08 | -9.9614e-08 | 0.004027 | 0.004027 | 0.004027 | 0.9994 | -0.011592 | 0.99942 | -0.011081 | 1.1063
59 | -0.0039953 | -0.0010009 | 0.0039954 | 0.0010009 | 5.3857e-08 | -1.8722e-08 | 0.0059484 | 0.0059483 | 0.0059484 | 0.99942 | -0.011081 | 0.99944 | -0.010798 | 1.6342
60 | -0.0058968 | -0.0014774 | 0.0058978 | 0.0014776 | 9.4593e-07 | 1.7644e-07 | 0.0087793 | 0.0087792 | 0.0087793 | 0.99944 | -0.010798 | 0.99961 | -0.00743 | 2.4119
61 | -0.0079548 | -0.0019931 | 0.0079553 | 0.0019933 | 5.1167e-07 | 1.999e-07 | 0.011841 | 0.011841 | 0.011841 | 0.99961 | -0.00743 | 0.99968 | -0.0060796 | 3.2531
62 | 0.0050139 | 0.0012565 | -0.0050135 | -0.0012565 | 4.4102e-07 | 5.4446e-09 | 0.0074631 | 0.0074632 | 0.0074632 | 0.99968 | -0.0060796 | 0.99959 | -0.0079262 | 2.0503
63 | -0.01436 | -0.0035984 | 0.014364 | 0.0036007 | 4.1597e-06 | 2.3438e-06 | 0.021375 | 0.021374 | 0.021375 | 0.99968 | -0.0060796 | 1 | 0 | 5.8721
64 | -0.013087 | -0.0032803 | 0.01309 | 0.0032823 | 3.7624e-06 | 2.0835e-06 | 0.019806 | 0.019806 | 0.019806 | 0.98321 | -0.3222 | 0.98352 | -0.31616 | 5.4412
65 | 0.010924 | 0.0027384 | -0.010924 | -0.0027381 | 5.4741e-07 | 2.8262e-07 | 0.016534 | 0.016534 | 0.016534 | 0.98321 | -0.3222 | 0.98315 | -0.32325 | 4.5422
66 | 0.0094011 | 0.0023564 | -0.0093994 | -0.0023556 | 1.7013e-06 | 8.0471e-07 | 0.014229 | 0.014229 | 0.014229 | 0.98315 | -0.32325 | 0.98296 | -0.32705 | 3.909
67 | 0.0093994 | 0.0023556 | -0.0093983 | -0.0023551 | 1.1145e-06 | 5.2722e-07 | 0.014229 | 0.014229 | 0.014229 | 0.98296 | -0.32705 | 0.98283 | -0.32954 | 3.909
68 | 0.0084994 | 0.0021298 | -0.008499 | -0.0021297 | 3.859e-07 | 1.6823e-07 | 0.012868 | 0.012868 | 0.012868 | 0.98283 | -0.32954 | 0.98278 | -0.33049 | 3.5352
69 | -0.00066218 | -0.00016596 | 0.00066218 | 0.00016587 | 2.6965e-09 | -8.7649e-08 | 0.0010061 | 0.0010061 | 0.0010061 | 0.97931 | -0.39874 | 0.97932 | -0.39866 | 0.27641
70 | -0.0015613 | -0.00039121 | 0.0015613 | 0.00039104 | 3.1055e-08 | -1.6529e-07 | 0.0023722 | 0.0023722 | 0.0023722 | 0.97932 | -0.39866 | 0.97934 | -0.39824 | 0.65172
71 | 0.0076002 | 0.0019044 | -0.0075998 | -0.0019043 | 3.0881e-07 | 1.1884e-07 | 0.011507 | 0.011507 | 0.011507 | 0.98278 | -0.33049 | 0.98274 | -0.33134 | 3.1613
72 | -0.13116 | -0.033268 | 0.13161 | 0.033552 | 0.00044375 | 0.00028361 | 0.19719 | 0.19719 | 0.19719 | 0.99048 | -0.18141 | 0.99414 | -0.1113 | 54.1726
73 | -0.059756 | -0.015109 | 0.059831 | 0.015157 | 7.5124e-05 | 4.7761e-05 | 0.089946 | 0.089946 | 0.089946 | 0.9891 | -0.20836 | 0.99045 | -0.18218 | 24.7104
74 | 0.017742 | 0.0044554 | -0.017728 | -0.0044473 | 1.3739e-05 | 8.1424e-06 | 0.026782 | 0.026782 | 0.026782 | 0.98589 | -0.27056 | 0.98505 | -0.28681 | 7.3577
75 | 0.0013256 | 0.00033188 | -0.0013255 | -0.0003322 | 4.1966e-08 | -3.2486e-07 | 0.0020074 | 0.0020075 | 0.0020075 | 0.98256 | -0.33488 | 0.98253 | -0.33555 | 0.55151
76 | -0.0042917 | -0.0010753 | 0.0042919 | 0.0010752 | 2.25e-07 | -3.5917e-08 | 0.0064993 | 0.0064993 | 0.0064993 | 0.98256 | -0.33488 | 0.98262 | -0.33378 | 1.7855
77 | 0.00066255 | 0.00016604 | -0.00066255 | -0.00016605 | 2.2661e-10 | -7.4585e-09 | 0.0010034 | 0.0010034 | 0.0010034 | 0.98253 | -0.33555 | 0.98253 | -0.33555 | 0.27566
78 | -0.0058022 | -0.0014537 | 0.0058026 | 0.0014538 | 4.584e-07 | 9.2784e-08 | 0.0087863 | 0.0087863 | 0.0087863 | 0.98262 | -0.33378 | 0.9827 | -0.33212 | 2.4138
79 | -0.0067007 | -0.0016789 | 0.006701 | 0.001679 | 2.4906e-07 | 7.7656e-08 | 0.010146 | 0.010146 | 0.010146 | 0.9827 | -0.33212 | 0.98274 | -0.33134 | 2.7874
80 | 0.0028237 | 0.00070725 | -0.0028236 | -0.0007074 | 1.3338e-07 | -1.5782e-07 | 0.00429 | 0.0042901 | 0.0042901 | 0.97939 | -0.39725 | 0.97934 | -0.39824 | 1.1786
81 | -0.0047619 | -0.001193 | 0.0047621 | 0.001193 | 2.8648e-07 | -3.4173e-10 | 0.0072347 | 0.0072346 | 0.0072347 | 0.97939 | -0.39725 | 0.97946 | -0.39598 | 1.9875
82 | 0.0025626 | 0.00064161 | -0.0025623 | -0.00064204 | 2.7524e-07 | -4.3328e-07 | 0.0038929 | 0.0038932 | 0.0038932 | 0.97946 | -0.39598 | 0.97934 | -0.39824 | 1.0696
83 | -0.0073247 | -0.0018346 | 0.0073259 | 0.001835 | 1.141e-06 | 4.2091e-07 | 0.011128 | 0.011127 | 0.011128 | 0.97946 | -0.39598 | 0.97962 | -0.39271 | 3.057
84 | 0.0025623 | 0.00064204 | -0.0025623 | -0.00064216 | 7.5493e-08 | -1.188e-07 | 0.0038932 | 0.0038932 | 0.0038932 | 0.97934 | -0.39824 | 0.97931 | -0.39886 | 1.0696
85 | -0.0073259 | -0.001835 | 0.0073264 | 0.0018352 | 5.1393e-07 | 1.8955e-07 | 0.011127 | 0.011127 | 0.011127 | 0.97962 | -0.39271 | 0.9797 | -0.39124 | 3.057
86 | -0.0079446 | -0.0019901 | 0.0079468 | 0.0019911 | 2.2392e-06 | 9.1649e-07 | 0.012066 | 0.012066 | 0.012066 | 0.9797 | -0.39124 | 0.98 | -0.38532 | 3.3149
87 | -0.010253 | -0.0025691 | 0.010254 | 0.0025695 | 6.6452e-07 | 3.3317e-07 | 0.015568 | 0.015568 | 0.015568 | 0.98 | -0.38532 | 0.98007 | -0.38396 | 4.2771
88 | 0.029928 | 0.0075224 | -0.029923 | -0.0075197 | 4.3071e-06 | 2.6858e-06 | 0.045336 | 0.045336 | 0.045336 | 0.98245 | -0.33731 | 0.9823 | -0.34033 | 12.455
89 | 0.0040139 | 0.0010055 | -0.0040134 | -0.0010057 | 4.5242e-07 | -1.1944e-07 | 0.0060953 | 0.0060954 | 0.0060954 | 0.97987 | -0.38789 | 0.97975 | -0.39026 | 1.6746
90 | -0.0057782 | -0.0014477 | 0.0057793 | 0.0014479 | 1.0819e-06 | 2.203e-07 | 0.0087745 | 0.0087744 | 0.0087745 | 0.97987 | -0.38789 | 0.98007 | -0.38396 | 2.4106
91 | 0.0030097 | 0.00075413 | -0.0030097 | -0.00075417 | 4.4708e-08 | -4.3241e-08 | 0.0045711 | 0.0045711 | 0.0045711 | 0.97975 | -0.39026 | 0.97973 | -0.39057 | 1.2558
92 | -0.016033 | -0.0040174 | 0.016044 | 0.0040234 | 1.0309e-05 | 6.013e-06 | 0.024343 | 0.024343 | 0.024343 | 0.98007 | -0.38396 | 0.98076 | -0.37047 | 6.6876
93 | 0.0020072 | 0.00050293 | -0.0020072 | -0.00050299 | 1.9885e-08 | -5.9123e-08 | 0.0030486 | 0.0030486 | 0.0030486 | 0.97973 | -0.39057 | 0.97972 | -0.39078 | 0.83752
94 | -0.016662 | -0.0041784 | 0.016666 | 0.0041808 | 4.0754e-06 | 2.3936e-06 | 0.025281 | 0.025281 | 0.025281 | 0.98076 | -0.37047 | 0.98102 | -0.36534 | 6.9453
95 | 0.0010036 | 0.00025146 | -0.0010036 | -0.00025153 | 4.9744e-09 | -6.8709e-08 | 0.0015243 | 0.0015243 | 0.0015243 | 0.97972 | -0.39078 | 0.97972 | -0.39088 | 0.41877
96 | -0.017221 | -0.0043198 | 0.017224 | 0.0043215 | 2.8024e-06 | 1.6552e-06 | 0.026122 | 0.026122 | 0.026122 | 0.98102 | -0.36534 | 0.98119 | -0.36193 | 7.1764
97 | -0.028633 | -0.0071854 | 0.028658 | 0.0072011 | 2.5213e-05 | 1.5686e-05 | 0.043427 | 0.043427 | 0.043427 | 0.98119 | -0.36193 | 0.98214 | -0.34348 | 11.9304
98 | 0.0033654 | 0.00084342 | -0.0033654 | -0.00084344 | 3.1104e-08 | -2.3413e-08 | 0.0050098 | 0.0050099 | 0.0050099 | 0.99959 | -0.0079262 | 0.99958 | -0.0081202 | 1.3763
99 | 0.23195 | 0.059436 | -0.23163 | -0.059236 | 0.00031442 | 0.00020086 | 0.3456 | 0.3456 | 0.3456 | 1 | 0 | 0.99852 | -0.028011 | 47.4728
100 | 0.0016189 | 0.00040574 | -0.0016189 | -0.00040574 | 4.6461e-10 | -2.5006e-09 | 0.00241 | 0.00241 | 0.00241 | 0.99958 | -0.0081202 | 0.99958 | -0.0081262 | 0.6621
101 | 0.22893 | 0.058559 | -0.2284 | -0.058219 | 0.00053198 | 0.00033984 | 0.34158 | 0.34158 | 0.34158 | 0.99852 | -0.028011 | 0.99599 | -0.076145 | 46.9203
102 | 0.13473 | 0.034425 | -0.13451 | -0.034278 | 0.00022862 | 0.00014612 | 0.20153 | 0.20153 | 0.20153 | 0.99599 | -0.076145 | 0.99414 | -0.1113 | 55.3652
103 | 0.082215 | 0.020923 | -0.082017 | -0.020797 | 0.00019785 | 0.00012617 | 0.12294 | 0.12294 | 0.12294 | 0.99599 | -0.076145 | 0.99337 | -0.1262 | 33.7757
104 | 0.01145 | 0.0028711 | -0.011445 | -0.0028683 | 5.3851e-06 | 2.8082e-06 | 0.017107 | 0.017107 | 0.017107 | 0.99599 | -0.076145 | 0.99547 | -0.086018 | 4.6999
105 | 0.079235 | 0.0201 | -0.079107 | -0.020018 | 0.00012825 | 8.1765e-05 | 0.11878 | 0.11878 | 0.11878 | 0.99337 | -0.1262 | 0.99161 | -0.15992 | 32.631
106 | 0.0087196 | 0.0021853 | -0.0087174 | -0.0021844 | 2.1622e-06 | 9.4267e-07 | 0.013034 | 0.013034 | 0.013034 | 0.99547 | -0.086018 | 0.9952 | -0.091224 | 3.5808
107 | 0.017248 | 0.0043282 | -0.017238 | -0.0043223 | 9.9505e-06 | 5.8577e-06 | 0.025884 | 0.025884 | 0.025884 | 0.99161 | -0.15992 | 0.99099 | -0.17202 | 7.1111
108 | 0.061859 | 0.01569 | -0.061793 | -0.015648 | 6.6146e-05 | 4.207e-05 | 0.092893 | 0.092893 | 0.092893 | 0.99161 | -0.15992 | 0.99045 | -0.18218 | 25.52
109 | 0.0061494 | 0.0015408 | -0.0061483 | -0.0015405 | 1.0397e-06 | 2.3933e-07 | 0.0091943 | 0.0091945 | 0.0091945 | 0.9952 | -0.091224 | 0.99502 | -0.094774 | 2.5259
110 | 0.015109 | 0.0037889 | -0.015107 | -0.0037873 | 2.6748e-06 | 1.5334e-06 | 0.022688 | 0.022688 | 0.022688 | 0.99099 | -0.17202 | 0.9908 | -0.17574 | 6.2331
111 | 0.0023216 | 0.00058148 | -0.0023215 | -0.00058181 | 1.5119e-07 | -3.3766e-07 | 0.0034718 | 0.0034719 | 0.0034719 | 0.99502 | -0.094774 | 0.99495 | -0.096141 | 0.95382
112 | 0.013183 | 0.0033052 | -0.01318 | -0.0033032 | 3.5483e-06 | 1.9602e-06 | 0.019799 | 0.019799 | 0.019799 | 0.9908 | -0.17574 | 0.99051 | -0.18139 | 5.4394
113 | 0.0057704 | 0.0014452 | -0.0057694 | -0.001445 | 9.9155e-07 | 1.8272e-07 | 0.008673 | 0.0086732 | 0.0086732 | 0.98998 | -0.19159 | 0.98979 | -0.1952 | 2.3827
114 | -0.0072348 | -0.0018122 | 0.007236 | 0.0018127 | 1.2314e-06 | 4.3096e-07 | 0.010874 | 0.010874 | 0.010874 | 0.98998 | -0.19159 | 0.99016 | -0.18802 | 2.9874
115 | 0.0030941 | 0.00077455 | -0.0030935 | -0.00077506 | 5.465e-07 | -5.1583e-07 | 0.0046512 | 0.0046515 | 0.0046515 | 0.98979 | -0.1952 | 0.9896 | -0.19891 | 1.2779
116 | -0.011342 | -0.0028418 | 0.011346 | 0.0028437 | 3.5838e-06 | 1.8704e-06 | 0.017045 | 0.017045 | 0.017045 | 0.99016 | -0.18802 | 0.99051 | -0.18139 | 4.6826
117 | 0.0003798 | 9.4938e-05 | -0.0003798 | -9.5187e-05 | 2.3911e-09 | -2.4968e-07 | 0.000571 | 0.00057109 | 0.00057109 | 0.9896 | -0.19891 | 0.9896 | -0.19904 | 0.15689
118 | -0.007027 | -0.0017611 | 0.0070316 | 0.0017627 | 4.5593e-06 | 1.5524e-06 | 0.010633 | 0.010632 | 0.010633 | 0.98342 | -0.31864 | 0.98412 | -0.30502 | 2.921
119 | -0.0070316 | -0.0017627 | 0.0070322 | 0.0017629 | 6.3366e-07 | 2.1559e-07 | 0.010632 | 0.010632 | 0.010632 | 0.98412 | -0.30502 | 0.98422 | -0.30313 | 2.9209
120 | -0.0092508 | -0.0023189 | 0.0092516 | 0.0023193 | 7.9382e-07 | 3.7051e-07 | 0.013986 | 0.013986 | 0.013986 | 0.98422 | -0.30313 | 0.98431 | -0.30133 | 3.8424
121 | -0.013871 | -0.003477 | 0.013874 | 0.0034788 | 3.1637e-06 | 1.7808e-06 | 0.020969 | 0.020969 | 0.020969 | 0.98431 | -0.30133 | 0.98456 | -0.29655 | 5.7608
122 | -0.013874 | -0.0034788 | 0.013874 | 0.0034789 | 2.4207e-07 | 1.3626e-07 | 0.020969 | 0.020969 | 0.020969 | 0.98456 | -0.29655 | 0.98457 | -0.29618 | 5.7607
123 | -0.016306 | -0.0040883 | 0.016309 | 0.00409 | 2.9052e-06 | 1.6971e-06 | 0.024644 | 0.024644 | 0.024644 | 0.98457 | -0.29618 | 0.98477 | -0.29244 | 6.7703
124 | -0.016309 | -0.00409 | 0.016313 | 0.0040925 | 4.3816e-06 | 2.5594e-06 | 0.024644 | 0.024644 | 0.024644 | 0.98477 | -0.29244 | 0.98505 | -0.28681 | 6.7702
125 | -0.029289 | -0.007359 | 0.029293 | 0.0073618 | 4.4055e-06 | 2.744e-06 | 0.044382 | 0.044382 | 0.044382 | 0.98214 | -0.34348 | 0.9823 | -0.34033 | 12.1928

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25206 | 0.064065

## res_load
| p_mw | q_mvar
0 | 0.016671 | 0.004178
1 | 0.0026946 | 0.00067533
2 | 0.012801 | 0.0032083
3 | 0.00213 | 0.00053384
4 | 0.0085667 | 0.002147
5 | 0.00038291 | 9.5967e-05
6 | 0.0018866 | 0.00047283
7 | 0.00055458 | 0.00013899
8 | 0.0055151 | 0.0013822
9 | 0.0061124 | 0.0015319
10 | 0.0014714 | 0.00036878
11 | 0.0013605 | 0.00034098
12 | 0.0070748 | 0.0017731
13 | 0.0062901 | 0.0015764
14 | 0.0025686 | 0.00064374
15 | 0.0017492 | 0.00043838
16 | 0.0034728 | 0.00087038
17 | 0.0017368 | 0.00043528
18 | 0.0022094 | 0.00055374
19 | 0.004346 | 0.0010892
20 | 0.006096 | 0.0015278
21 | 0.0052128 | 0.0013065
22 | 0.0031559 | 0.00079094
23 | 0.0036502 | 0.00091483
24 | 0.0020244 | 0.00050736
25 | 0.0031484 | 0.00078906
26 | 0.0034479 | 0.00086414
27 | 0.0022486 | 0.00056356
28 | 0.002713 | 0.00067993
29 | 0.00092003 | 0.00023058
30 | 0.0010536 | 0.00026406
31 | 0.00083869 | 0.00021019
32 | 0.0012471 | 0.00031256
33 | 0.00067686 | 0.00016964
34 | 0.0012472 | 0.00031257
35 | 0.0006764 | 0.00016952
36 | 0.0020942 | 0.00052487
37 | 0.00063036 | 0.00015798
38 | 0.0013655 | 0.00034223
39 | 0.0013392 | 0.00033563
40 | 0.0012905 | 0.00032343
41 | 0.0019014 | 0.00047655
42 | 0.0020571 | 0.00051555
43 | 0.0013908 | 0.00034856
44 | 0.0021622 | 0.00054189
45 | 0.0012832 | 0.00032159
46 | 0.0015228 | 0.00038166
47 | 0.00089884 | 0.00022527
48 | 0.00066218 | 0.00016596
49 | 0.00089911 | 0.00022534
50 | 0.00089889 | 0.00022528
51 | 0.0058478 | 0.0014656
52 | 0.0018003 | 0.0004512
53 | 0.0029661 | 0.00074338
54 | 0.00066298 | 0.00016616
55 | 0.0015103 | 0.00037851
56 | 0.00066255 | 0.00016605
57 | 0.00089805 | 0.00022507
58 | 0.00089889 | 0.00022528
59 | 0.0019381 | 0.00048573
60 | 0.0012623 | 0.00031636
61 | 0.0025623 | 0.00064216
62 | 0.0006182 | 0.00015493
63 | 0.0023066 | 0.00057809
64 | 0.0006301 | 0.00015792
65 | 0.0017643 | 0.00044218
66 | 0.0010037 | 0.00025154
67 | 0.0010025 | 0.00025124
68 | 0.00061844 | 0.000155
69 | 0.0010036 | 0.00025153
70 | 0.00055458 | 0.00013899
71 | 0.0010036 | 0.00025153
72 | 0.001648 | 0.00041304
73 | 0.0040993 | 0.0010274
74 | 0.0017464 | 0.0004377
75 | 0.0026992 | 0.00067649
76 | 0.0029003 | 0.00072689
77 | 0.0027816 | 0.00069715
78 | 0.0027252 | 0.000683
79 | 0.0025681 | 0.00064362
80 | 0.0016189 | 0.00040574
81 | 0.0019617 | 0.00049164
82 | 0.0021285 | 0.00053346
83 | 0.0038267 | 0.00095906
84 | 0.0023215 | 0.00058181
85 | 0.0019237 | 0.00048213
86 | 0.0014644 | 0.00036701
87 | 0.0026753 | 0.00067049
88 | 0.0041063 | 0.0010291
89 | 0.0027137 | 0.00068013
90 | 0.0018337 | 0.00045957
91 | 0.0003798 | 9.5187e-05
92 | 0.007027 | 0.0017611
93 | 0.0022186 | 0.00055603
94 | 0.0046192 | 0.0011577
95 | 0.0024314 | 0.00060937
96 | 0.0014155 | 0.00035476
97 | 0.00063036 | 0.00015798
98 | 0.00063024 | 0.00015795

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1