## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_119-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_119-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_119-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_119-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_119-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_119-2_0_4_node_122 | 0.4 | n |  | TRUE
6 | bus_LV_119-2_0_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_119-2_0_4_node_99 | 0.4 | n |  | TRUE
8 | bus_LV_119-2_0_4_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_119-2_0_4_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_119-2_0_4_node_100 | 0.4 | n |  | TRUE
11 | bus_LV_119-2_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_119-2_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_119-2_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_119-2_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_119-2_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_119-2_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_119-2_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_119-2_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_119-2_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_119-2_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_119-2_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_119-2_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_119-2_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_119-2_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_119-2_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_119-2_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_119-2_0_4_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_119-2_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_119-2_0_4_node_40 | 0.4 | n |  | TRUE
30 | bus_LV_119-2_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_119-2_0_4_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_119-2_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_119-2_0_4_node_58 | 0.4 | n |  | TRUE
34 | bus_LV_119-2_0_4_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_119-2_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_119-2_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_119-2_0_4_node_81 | 0.4 | n |  | TRUE
38 | bus_LV_119-2_0_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_119-2_0_4_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_119-2_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_119-2_0_4_node_61 | 0.4 | n |  | TRUE
42 | bus_LV_119-2_0_4_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_119-2_0_4_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_119-2_0_4_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_119-2_0_4_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_119-2_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_119-2_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_119-2_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_119-2_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_119-2_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_119-2_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_119-2_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_119-2_0_4_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_119-2_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_119-2_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_119-2_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_119-2_0_4_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_119-2_0_4_node_111 | 0.4 | n |  | TRUE
59 | bus_LV_119-2_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_119-2_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_119-2_0_4_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_119-2_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_119-2_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_119-2_0_4_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_119-2_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_119-2_0_4_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_119-2_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_119-2_0_4_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_119-2_0_4_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_119-2_0_4_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_119-2_0_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_119-2_0_4_node_85 | 0.4 | n |  | TRUE
73 | bus_LV_119-2_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_119-2_0_4_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_119-2_0_4_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_119-2_0_4_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_119-2_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_119-2_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_119-2_0_4_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_119-2_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_119-2_0_4_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_119-2_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_119-2_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_119-2_0_4_node_82 | 0.4 | n |  | TRUE
85 | bus_LV_119-2_0_4_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_119-2_0_4_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_119-2_0_4_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_119-2_0_4_node_112 | 0.4 | n |  | TRUE
89 | bus_LV_119-2_0_4_node_107 | 0.4 | n |  | TRUE
90 | bus_LV_119-2_0_4_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_119-2_0_4_node_106 | 0.4 | n |  | TRUE
92 | bus_LV_119-2_0_4_node_87 | 0.4 | n |  | TRUE
93 | bus_LV_119-2_0_4_node_88 | 0.4 | n |  | TRUE
94 | bus_LV_119-2_0_4_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_119-2_0_4_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_119-2_0_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_119-2_0_4_node_103 | 0.4 | n |  | TRUE
98 | bus_LV_119-2_0_4_node_102 | 0.4 | n |  | TRUE
99 | bus_LV_119-2_0_4_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_119-2_0_4_node_110 | 0.4 | n |  | TRUE
101 | bus_LV_119-2_0_4_node_113 | 0.4 | n |  | TRUE
102 | bus_LV_119-2_0_4_node_101 | 0.4 | n |  | TRUE
103 | bus_LV_119-2_0_4_node_109 | 0.4 | n |  | TRUE
104 | bus_LV_119-2_0_4_node_120 | 0.4 | n |  | TRUE
105 | bus_LV_119-2_0_4_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_119-2_0_4_node_119 | 0.4 | n |  | TRUE
107 | bus_LV_119-2_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_119-2_0_4_node_114 | 0.4 | n |  | TRUE
109 | bus_LV_119-2_0_4_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_119-2_0_4_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_119-2_0_4_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_119-2_0_4_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_119-2_0_4_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_119-2_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_119-2_0_4_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_119-2_0_4_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_119-2_0_4_node_121 | 0.4 | n |  | TRUE
118 | bus_LV_119-2_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_119-2_0_4_node_118 | 0.4 | n |  | TRUE
120 | bus_MV_357_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_119-2_0_4_load_0 | 0 | 0.0022798 | 0.00057138 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_119-2_0_4_load_122 | 5 | 0.0025853 | 0.00064793 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_119-2_0_4_load_99 | 7 | 0.00051622 | 0.00012938 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_119-2_0_4_load_60 | 9 | 0.0003998 | 0.0001002 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_119-2_0_4_load_100 | 10 | 0.000903 | 0.00022631 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_119-2_0_4_load_5 | 11 | 0.0034489 | 0.00086439 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_119-2_0_4_load_8 | 14 | 0.002654 | 0.00066516 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_119-2_0_4_load_29 | 16 | 0.0018951 | 0.00047495 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_119-2_0_4_load_11 | 19 | 0.00091199 | 0.00022857 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_119-2_0_4_load_12 | 20 | 0.00091597 | 0.00022956 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_119-2_0_4_load_14 | 22 | 0.00034389 | 8.6187e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_119-2_0_4_load_51 | 27 | 0.0014298 | 0.00035834 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_119-2_0_4_load_40 | 29 | 0.0040566 | 0.0010167 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_119-2_0_4_load_54 | 31 | 0.0019353 | 0.00048503 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_119-2_0_4_load_58 | 33 | 0.00049997 | 0.00012531 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_119-2_0_4_load_57 | 34 | 0.020672 | 0.0051809 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_119-2_0_4_load_50 | 35 | 0.010486 | 0.002628 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_119-2_0_4_load_27 | 36 | 0.00055595 | 0.00013933 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_119-2_0_4_load_38 | 38 | 0.019524 | 0.0048932 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_119-2_0_4_load_48 | 39 | 0.061472 | 0.015406 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_119-2_0_4_load_61 | 41 | 0.0012023 | 0.00030133 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_119-2_0_4_load_72 | 42 | 0.0044143 | 0.0011063 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_119-2_0_4_load_80 | 44 | 0.00021484 | 5.3844e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_119-2_0_4_load_33 | 46 | 0.0022965 | 0.00057556 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_119-2_0_4_load_30 | 47 | 0.0036246 | 0.00090842 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_119-2_0_4_load_31 | 48 | 0.0022934 | 0.00057478 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_119-2_0_4_load_32 | 49 | 0.0022965 | 0.00057556 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_119-2_0_4_load_34 | 50 | 0.0027057 | 0.0006781 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_119-2_0_4_load_35 | 51 | 0.0027071 | 0.00067847 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_119-2_0_4_load_55 | 53 | 0.002707 | 0.00067843 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_119-2_0_4_load_59 | 55 | 0.0027042 | 0.00067773 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_119-2_0_4_load_111 | 58 | 0.011522 | 0.0028877 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_119-2_0_4_load_52 | 61 | 0.0026133 | 0.00065495 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_119-2_0_4_load_37 | 62 | 0.068774 | 0.017236 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_119-2_0_4_load_44 | 65 | 0.0098498 | 0.0024686 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_119-2_0_4_load_43 | 66 | 0.00603 | 0.0015113 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_119-2_0_4_load_53 | 67 | 0.017021 | 0.004266 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_119-2_0_4_load_70 | 69 | 0.00017331 | 4.3437e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_119-2_0_4_load_71 | 70 | 0.0018491 | 0.00046342 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_119-2_0_4_load_66 | 71 | 0.00056633 | 0.00014194 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_119-2_0_4_load_62 | 73 | 0.001564 | 0.00039198 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_119-2_0_4_load_75 | 75 | 0.00021484 | 5.3844e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_119-2_0_4_load_63 | 76 | 0.0013456 | 0.00033724 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_119-2_0_4_load_64 | 77 | 0.00066758 | 0.00016731 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_119-2_0_4_load_65 | 78 | 0.00071448 | 0.00017907 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_119-2_0_4_load_67 | 79 | 0.00071481 | 0.00017915 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_119-2_0_4_load_79 | 80 | 0.0058791 | 0.0014735 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_119-2_0_4_load_73 | 81 | 0.00043026 | 0.00010783 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_119-2_0_4_load_74 | 82 | 0.00029138 | 7.3027e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_119-2_0_4_load_76 | 83 | 0.00027087 | 6.7886e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_119-2_0_4_load_82 | 84 | 0.0018926 | 0.00047433 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_119-2_0_4_load_84 | 86 | 0.00066262 | 0.00016607 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_119-2_0_4_load_86 | 87 | 0.0041987 | 0.0010523 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_119-2_0_4_load_112 | 88 | 0.0028482 | 0.00071382 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_119-2_0_4_load_108 | 90 | 0.0015266 | 0.0003826 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_119-2_0_4_load_106 | 91 | 0.0058943 | 0.0014773 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_119-2_0_4_load_87 | 92 | 0.00073215 | 0.00018349 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_119-2_0_4_load_88 | 93 | 0.00092743 | 0.00023243 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_119-2_0_4_load_103 | 97 | 0.00096516 | 0.00024189 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_119-2_0_4_load_102 | 98 | 0.00074683 | 0.00018717 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_119-2_0_4_load_110 | 100 | 0.00063779 | 0.00015984 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_119-2_0_4_load_113 | 101 | 0.00093857 | 0.00023523 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_119-2_0_4_load_109 | 103 | 0.0013131 | 0.0003291 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_119-2_0_4_load_120 | 104 | 0.0013871 | 0.00034765 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_119-2_0_4_load_119 | 106 | 0.00028748 | 7.205e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_119-2_0_4_load_114 | 108 | 0.0017273 | 0.00043289 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_119-2_0_4_load_93 | 109 | 0.0014296 | 0.00035829 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_119-2_0_4_load_94 | 110 | 0.0020311 | 0.00050904 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_119-2_0_4_load_96 | 111 | 0.0046656 | 0.0011693 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_119-2_0_4_load_104 | 114 | 0.0013133 | 0.00032915 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_119-2_0_4_load_116 | 115 | 0.0037815 | 0.00094773 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_119-2_0_4_load_121 | 117 | 0.00081473 | 0.00020419 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_119-2_0_4_load_115 | 118 | 0.001678 | 0.00042054 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_119-2_0_4_load_118 | 119 | 0.0010751 | 0.00026945 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_119-2_0_4_line_0 |  | 0 | 1 | 0.12425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_119-2_0_4_line_1 |  | 0 | 2 | 0.22401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_119-2_0_4_line_2 |  | 1 | 3 | 0.051848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_119-2_0_4_line_3 |  | 2 | 4 | 0.29613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_119-2_0_4_line_4 |  | 3 | 5 | 0.14719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_119-2_0_4_line_5 |  | 3 | 6 | 0.32777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_119-2_0_4_line_6 |  | 4 | 7 | 0.078855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_119-2_0_4_line_7 |  | 6 | 8 | 0.019128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_119-2_0_4_line_8 |  | 6 | 9 | 0.014484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_119-2_0_4_line_9 |  | 7 | 10 | 0.029438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_119-2_0_4_line_10 |  | 8 | 31 | 0.053388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_119-2_0_4_line_11 |  | 9 | 41 | 0.0053663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_119-2_0_4_line_12 |  | 10 | 95 | 0.070815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_119-2_0_4_line_13 |  | 11 | 12 | 0.015935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_119-2_0_4_line_14 |  | 12 | 13 | 0.009703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_119-2_0_4_line_15 |  | 13 | 14 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_119-2_0_4_line_16 |  | 14 | 17 | 0.032122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_119-2_0_4_line_17 |  | 15 | 16 | 0.030029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_119-2_0_4_line_18 |  | 15 | 17 | 0.030273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_119-2_0_4_line_19 |  | 16 | 18 | 0.016382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_119-2_0_4_line_20 |  | 18 | 21 | 0.063941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_119-2_0_4_line_21 |  | 19 | 20 | 0.011964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_119-2_0_4_line_22 |  | 19 | 21 | 0.013707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_119-2_0_4_line_23 |  | 20 | 22 | 0.099513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_119-2_0_4_line_24 |  | 21 | 23 | 0.032823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_119-2_0_4_line_25 |  | 21 | 24 | 0.11229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_119-2_0_4_line_26 |  | 22 | 25 | 0.10304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_119-2_0_4_line_27 |  | 23 | 30 | 0.066386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_119-2_0_4_line_28 |  | 23 | 31 | 0.0058821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_119-2_0_4_line_29 |  | 24 | 36 | 0.0099056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_119-2_0_4_line_30 |  | 25 | 37 | 0.032477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_119-2_0_4_line_31 |  | 26 | 27 | 0.016876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_119-2_0_4_line_32 |  | 26 | 28 | 0.036051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_119-2_0_4_line_33 |  | 26 | 29 | 0.026689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_119-2_0_4_line_34 |  | 27 | 35 | 0.0024614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_119-2_0_4_line_35 |  | 28 | 32 | 0.015604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_119-2_0_4_line_36 |  | 28 | 33 | 0.021473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_119-2_0_4_line_37 |  | 29 | 38 | 0.021832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_119-2_0_4_line_38 |  | 30 | 35 | 0.023191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_119-2_0_4_line_39 |  | 32 | 34 | 0.0075386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_119-2_0_4_line_40 |  | 37 | 46 | 0.0047791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_119-2_0_4_line_41 |  | 39 | 40 | 0.041378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_119-2_0_4_line_42 |  | 40 | 43 | 0.005777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_119-2_0_4_line_43 |  | 40 | 63 | 0.006049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_119-2_0_4_line_44 |  | 41 | 73 | 0.0094011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_119-2_0_4_line_45 |  | 42 | 43 | 0.014942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_119-2_0_4_line_46 |  | 44 | 45 | 0.046219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_119-2_0_4_line_47 |  | 45 | 80 | 0.0030439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_119-2_0_4_line_48 |  | 45 | 83 | 0.01013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_119-2_0_4_line_49 |  | 46 | 48 | 0.0062537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_119-2_0_4_line_50 |  | 47 | 48 | 0.004449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_119-2_0_4_line_51 |  | 47 | 49 | 0.0018047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_119-2_0_4_line_52 |  | 50 | 51 | 0.009527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_119-2_0_4_line_53 |  | 51 | 52 | 0.0073237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_119-2_0_4_line_54 |  | 52 | 53 | 0.0090575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_119-2_0_4_line_55 |  | 52 | 54 | 0.14019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_119-2_0_4_line_56 |  | 53 | 55 | 0.009527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_119-2_0_4_line_57 |  | 54 | 59 | 0.006175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_119-2_0_4_line_58 |  | 54 | 60 | 0.021291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_119-2_0_4_line_59 |  | 56 | 57 | 0.19762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_119-2_0_4_line_60 |  | 56 | 58 | 0.009441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_119-2_0_4_line_61 |  | 57 | 71 | 0.12443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_119-2_0_4_line_62 |  | 58 | 72 | 0.0061326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_119-2_0_4_line_63 |  | 59 | 61 | 0.072262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_119-2_0_4_line_64 |  | 60 | 62 | 0.075309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_119-2_0_4_line_65 |  | 61 | 64 | 0.052607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_119-2_0_4_line_66 |  | 63 | 64 | 0.005526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_119-2_0_4_line_67 |  | 63 | 65 | 0.01663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_119-2_0_4_line_68 |  | 64 | 67 | 0.035938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_119-2_0_4_line_69 |  | 65 | 66 | 0.030059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_119-2_0_4_line_70 |  | 67 | 68 | 0.024032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_119-2_0_4_line_71 |  | 68 | 69 | 0.018317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_119-2_0_4_line_72 |  | 68 | 70 | 0.010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_119-2_0_4_line_73 |  | 69 | 80 | 0.0065778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_119-2_0_4_line_74 |  | 70 | 79 | 0.00038931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_119-2_0_4_line_75 |  | 71 | 77 | 0.014939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_119-2_0_4_line_76 |  | 72 | 88 | 0.13321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_119-2_0_4_line_77 |  | 72 | 85 | 0.011491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_119-2_0_4_line_78 |  | 73 | 74 | 0.0087926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_119-2_0_4_line_79 |  | 74 | 75 | 0.012446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_119-2_0_4_line_80 |  | 75 | 81 | 0.0092907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_119-2_0_4_line_81 |  | 76 | 77 | 0.011346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_119-2_0_4_line_82 |  | 76 | 78 | 0.011568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_119-2_0_4_line_83 |  | 78 | 79 | 0.000391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_119-2_0_4_line_84 |  | 81 | 82 | 0.016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_119-2_0_4_line_85 |  | 82 | 83 | 0.018377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_119-2_0_4_line_86 |  | 84 | 85 | 0.027714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_119-2_0_4_line_87 |  | 84 | 86 | 0.0083197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_119-2_0_4_line_88 |  | 85 | 87 | 0.022561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_119-2_0_4_line_89 |  | 87 | 89 | 0.028106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_119-2_0_4_line_90 |  | 89 | 90 | 0.044986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_119-2_0_4_line_91 |  | 89 | 91 | 0.003187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_119-2_0_4_line_92 |  | 90 | 103 | 0.0083375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_119-2_0_4_line_93 |  | 91 | 113 | 0.02851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_119-2_0_4_line_94 |  | 92 | 93 | 0.010355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_119-2_0_4_line_95 |  | 92 | 94 | 0.071426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_119-2_0_4_line_96 |  | 94 | 95 | 0.007124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_119-2_0_4_line_97 |  | 96 | 97 | 0.027604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_119-2_0_4_line_98 |  | 96 | 98 | 0.0038395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_119-2_0_4_line_99 |  | 97 | 100 | 0.023986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_119-2_0_4_line_100 |  | 99 | 100 | 0.038543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_119-2_0_4_line_101 |  | 99 | 101 | 0.026679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_119-2_0_4_line_102 |  | 101 | 108 | 0.020465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_119-2_0_4_line_103 |  | 102 | 103 | 0.014553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_119-2_0_4_line_104 |  | 102 | 104 | 0.017712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_119-2_0_4_line_105 |  | 104 | 117 | 0.0026807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_119-2_0_4_line_106 |  | 105 | 106 | 0.013182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_119-2_0_4_line_107 |  | 105 | 107 | 0.007968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_119-2_0_4_line_108 |  | 106 | 116 | 0.0040129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_119-2_0_4_line_109 |  | 107 | 112 | 0.020887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_119-2_0_4_line_110 |  | 107 | 109 | 0.030105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_119-2_0_4_line_111 |  | 108 | 118 | 0.023146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_119-2_0_4_line_112 |  | 109 | 110 | 0.018804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_119-2_0_4_line_113 |  | 110 | 111 | 0.012054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_119-2_0_4_line_114 |  | 112 | 113 | 0.026774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_119-2_0_4_line_115 |  | 113 | 114 | 0.013716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_119-2_0_4_line_116 |  | 115 | 116 | 0.016357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_119-2_0_4_line_117 |  | 116 | 119 | 0.02283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_119-2_0_4_line_118 |  | 118 | 119 | 0.0087518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_119-2_0_4_trafo_44 | 0.63 MVA 20/0.4 kV | 120 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25
0 | 2700583.544 | 1243994.0879 | 2700590.5577 | 1243965.6182 | 2700612.2273 | 1243873.1911
1 | 2700715.7821 | 1243686.6494 | 2700685.5831 | 1243698.2569 | 2700654.4058 | 1243743.007 | 2700636.6189 | 1243787.573 | 2700622.9644 | 1243827.3943 | 2700612.2273 | 1243873.1911
2 | 2700559.1877 | 1243948.3175 | 2700569.0211 | 1243967.0653 | 2700583.544 | 1243994.0879
3 | 2700715.7821 | 1243686.6494 | 2700730.1403 | 1243745.6164 | 2700768.0271 | 1243746.4381 | 2700769.2691 | 1243753.8649 | 2700835.6478 | 1243847.0089 | 2700842.4485 | 1243854.697 | 2700846.9871 | 1243858.4993 | 2700854.5059 | 1243863.9647 | 2700899.1055 | 1243886.9184
4 | 2700598.3995 | 1243821.9625 | 2700589.3485 | 1243823.4769 | 2700584.7214 | 1243830.2259 | 2700582.9876 | 1243839.7483 | 2700582.6237 | 1243849.1716 | 2700583.7425 | 1243851.8371 | 2700587.9506 | 1243855.9783 | 2700588.5365 | 1243859.7578 | 2700577.3297 | 1243906.8152 | 2700576.5783 | 1243914.5751 | 2700577.2745 | 1243929.6764 | 2700574.6314 | 1243936.2144 | 2700571.9444 | 1243939.5492 | 2700565.7187 | 1243944.7366 | 2700559.1877 | 1243948.3175
5 | 2700559.1877 | 1243948.3175 | 2700543.8946 | 1243922.1271 | 2700541.4583 | 1243914.6912 | 2700540.8736 | 1243906.3748 | 2700542.2075 | 1243899.0362 | 2700540.5892 | 1243891.9478 | 2700547.2079 | 1243876.9595 | 2700550.0906 | 1243868.7687 | 2700551.6306 | 1243862.6456 | 2700552.7029 | 1243856.0253 | 2700553.1905 | 1243828.6125 | 2700553.6996 | 1243811.0742 | 2700555.1269 | 1243796.8875 | 2700557.4332 | 1243781.2367 | 2700560.494 | 1243765.6766 | 2700564.9839 | 1243746.9605 | 2700573.2545 | 1243717.0443 | 2700575.6011 | 1243707.043 | 2700576.2137 | 1243697.2236 | 2700575.8128 | 1243687.8762 | 2700573.1535 | 1243662.3893 | 2700571.3593 | 1243650.9612 | 2700569.1041 | 1243637.7461 | 2700568.0946 | 1243634.8712 | 2700566.9908 | 1243633.0956 | 2700565.4958 | 1243631.658
6 | 2700899.1055 | 1243886.9184 | 2700931.1407 | 1243830.0304 | 2700938.0758 | 1243818.37
7 | 2700565.4958 | 1243631.658 | 2700564.118 | 1243630.8897 | 2700562.5389 | 1243630.3959 | 2700560.7145 | 1243630.1092 | 2700556.9022 | 1243626.6864 | 2700550.1064 | 1243620.9001
8 | 2700565.4958 | 1243631.658 | 2700579.2269 | 1243627.0478
9 | 2700938.0758 | 1243818.37 | 2700941.4591 | 1243812.6815 | 2700953.3023 | 1243793.1759
10 | 2700550.1064 | 1243620.9001 | 2700529.5294 | 1243629.4358 | 2700523.9294 | 1243632.0318 | 2700505.8024 | 1243620.4492 | 2700502.7713 | 1243618.8505
11 | 2700579.2269 | 1243627.0478 | 2700584.3142 | 1243625.3398
12 | 2700990.058 | 1243732.6466 | 2700988.9769 | 1243734.4296 | 2700976.2692 | 1243755.3517 | 2700960.8784 | 1243780.6982 | 2700953.3023 | 1243793.1759
13 | 2700324.7584 | 1243601.4041 | 2700313.2496 | 1243612.4249
14 | 2700324.7584 | 1243601.4041 | 2700331.6344 | 1243608.2701
15 | 2700331.6344 | 1243608.2701 | 2700343.471 | 1243597.0283
16 | 2700366.1167 | 1243594.1312 | 2700363.4892 | 1243590.8176 | 2700356.9641 | 1243584.2133 | 2700343.471 | 1243597.0283
17 | 2700387.5321 | 1243615.0985 | 2700392.6238 | 1243612.1602 | 2700396.3109 | 1243610.0321 | 2700413.2959 | 1243599.6765
18 | 2700387.5321 | 1243615.0985 | 2700369.3755 | 1243595.4207 | 2700367.7658 | 1243594.5039 | 2700366.1167 | 1243594.1312
19 | 2700426.3589 | 1243589.925 | 2700423.2441 | 1243593.0747 | 2700419.3089 | 1243596.0104 | 2700413.2959 | 1243599.6765
20 | 2700426.3589 | 1243589.925 | 2700430.0273 | 1243592.0221 | 2700432.7468 | 1243589.8998 | 2700437.0012 | 1243589.0934 | 2700441.3501 | 1243590.2902 | 2700446.0845 | 1243593.2726 | 2700456.9044 | 1243600.6948 | 2700468.5511 | 1243609.2875 | 2700477.0507 | 1243620.7069
21 | 2700464.1225 | 1243625.2615 | 2700457.4462 | 1243627.6136 | 2700453.4089 | 1243630.365
22 | 2700477.0507 | 1243620.7069 | 2700464.1225 | 1243625.2615
23 | 2700453.4089 | 1243630.365 | 2700452.0012 | 1243631.3243 | 2700427.6088 | 1243658.9438 | 2700418.4722 | 1243670.4091 | 2700413.3223 | 1243675.4481 | 2700394.8819 | 1243685.9441 | 2700379.7637 | 1243695.4855
24 | 2700477.0507 | 1243620.7069 | 2700478.9651 | 1243623.2635 | 2700480.1952 | 1243627.3986 | 2700486.9082 | 1243622.9088 | 2700492.0691 | 1243619.4602 | 2700494.7389 | 1243622.4967 | 2700497.5685 | 1243616.1063
25 | 2700426.297 | 1243673.9109 | 2700446.3377 | 1243663.1085 | 2700481.9545 | 1243643.5742 | 2700497.1232 | 1243635.2469 | 2700486.9082 | 1243622.9088 | 2700480.1952 | 1243627.3986 | 2700478.9651 | 1243623.2635 | 2700477.0507 | 1243620.7069
26 | 2700294.6135 | 1243753.2781 | 2700297.5507 | 1243751.2373 | 2700299.2536 | 1243750.2209 | 2700302.8947 | 1243748.5701 | 2700305.1966 | 1243747.4414 | 2700307.0587 | 1243746.3943 | 2700323.5473 | 1243734.1859 | 2700338.065 | 1243723.6455 | 2700354.0819 | 1243712.5189 | 2700375.9559 | 1243697.8887 | 2700379.7637 | 1243695.4855
27 | 2700497.5685 | 1243616.1063 | 2700494.7389 | 1243622.4967 | 2700497.4722 | 1243624.0219 | 2700501.7906 | 1243623.895 | 2700504.253 | 1243623.5586 | 2700506.4337 | 1243622.8951 | 2700547.518 | 1243599.6954
28 | 2700497.5685 | 1243616.1063 | 2700502.7713 | 1243618.8505
29 | 2700426.297 | 1243673.9109 | 2700417.5756 | 1243678.6074
30 | 2700275.7241 | 1243726.883 | 2700279.4627 | 1243731.5387 | 2700282.6344 | 1243735.74 | 2700285.1891 | 1243739.3303 | 2700287.7657 | 1243742.9656 | 2700292.6151 | 1243750.3199 | 2700294.6135 | 1243753.2781
31 | 2700526.2556 | 1243563.4851 | 2700527.813 | 1243567.9371 | 2700532.4983 | 1243571.586 | 2700535.4517 | 1243577.061
32 | 2700493.0139 | 1243553.4587 | 2700506.376 | 1243561.191 | 2700511.0998 | 1243563.9064 | 2700523.8752 | 1243563.4447 | 2700526.2556 | 1243563.4851
33 | 2700526.2556 | 1243563.4851 | 2700527.2606 | 1243559.499 | 2700539.4653 | 1243543.2043 | 2700541.3859 | 1243542.092
34 | 2700536.6203 | 1243579.2272 | 2700535.4517 | 1243577.061
35 | 2700479.4796 | 1243545.6235 | 2700493.0139 | 1243553.4587
36 | 2700493.0139 | 1243553.4587 | 2700511.4089 | 1243542.3803
37 | 2700560.2778 | 1243531.1502 | 2700541.3859 | 1243542.092
38 | 2700547.518 | 1243599.6954 | 2700546.3131 | 1243597.1953 | 2700536.6203 | 1243579.2272
39 | 2700479.4796 | 1243545.6235 | 2700485.9916 | 1243541.8255
40 | 2700275.7241 | 1243726.883 | 2700272.5952 | 1243723.2706
41 | 2700655.9728 | 1243539.3765 | 2700620.1677 | 1243560.1152
42 | 2700658.5992 | 1243544.5251 | 2700655.9728 | 1243539.3765
43 | 2700661.3203 | 1243536.5206 | 2700655.9728 | 1243539.3765
44 | 2700584.3142 | 1243625.3398 | 2700593.2264 | 1243622.3475
45 | 2700658.5992 | 1243544.5251 | 2700645.5921 | 1243551.8794
46 | 2700661.3675 | 1243602.7614 | 2700657.0502 | 1243603.2663 | 2700652.4922 | 1243603.2556 | 2700647.619 | 1243602.6614 | 2700617.1585 | 1243595.8062 | 2700616.0179 | 1243595.4929
47 | 2700661.3675 | 1243602.7614 | 2700664.2468 | 1243601.7739
48 | 2700661.3675 | 1243602.7614 | 2700661.987 | 1243605.8965 | 2700661.3655 | 1243607.7763 | 2700660.0744 | 1243609.022 | 2700658.2467 | 1243609.8139 | 2700657.1258 | 1243610.143
49 | 2700272.5952 | 1243723.2706 | 2700268.5008 | 1243718.5436
50 | 2700268.5008 | 1243718.5436 | 2700265.588 | 1243715.1807
51 | 2700264.4064 | 1243713.8166 | 2700265.588 | 1243715.1807
52 | 2700819.3235 | 1243330.5914 | 2700824.8129 | 1243322.8049
53 | 2700815.1036 | 1243336.5772 | 2700819.3235 | 1243330.5914
54 | 2700815.1036 | 1243336.5772 | 2700809.8847 | 1243343.9801
55 | 2700739.0732 | 1243443.624 | 2700758.2023 | 1243416.2611 | 2700765.0996 | 1243406.7375 | 2700770.3951 | 1243399.8332 | 2700774.9952 | 1243394.2626 | 2700807.3058 | 1243359.4846 | 2700814.8757 | 1243350.4284 | 2700821.8782 | 1243340.9512 | 2700815.1036 | 1243336.5772
56 | 2700809.8847 | 1243343.9801 | 2700804.3954 | 1243351.7667
57 | 2700739.0732 | 1243443.624 | 2700744.3476 | 1243446.8605
58 | 2700739.0732 | 1243443.624 | 2700731.7049 | 1243439.051 | 2700721.1873 | 1243432.0782
59 | 2700986.7761 | 1243395.4083 | 2700984.6816 | 1243395.8841 | 2700979.1402 | 1243398.5696 | 2700974.3289 | 1243403.2136 | 2700952.0988 | 1243428.8329 | 2700929.8692 | 1243454.4412 | 2700907.6537 | 1243474.3454 | 2700896.4538 | 1243482.6057 | 2700882.8115 | 1243490.9135 | 2700868.2342 | 1243497.304 | 2700855.7982 | 1243501.3624 | 2700830.1111 | 1243507.6196
60 | 2700986.7761 | 1243395.4083 | 2700994.7568 | 1243394.6435 | 2700996.1712 | 1243394.8059
61 | 2700830.1111 | 1243507.6196 | 2700827.1702 | 1243504.5228 | 2700822.9131 | 1243503.2606 | 2700818.311 | 1243503.616 | 2700812.895 | 1243506.0481 | 2700807.1476 | 1243511.5213 | 2700791.496 | 1243530.4256 | 2700786.3642 | 1243536.154 | 2700781.525 | 1243541.5648 | 2700767.4298 | 1243550.7436 | 2700750.0495 | 1243560.178 | 2700731.1528 | 1243569.6564
62 | 2701002.2638 | 1243395.5053 | 2700996.1712 | 1243394.8059
63 | 2700744.3476 | 1243446.8605 | 2700716.2634 | 1243486.0918 | 2700702.4674 | 1243505.7476
64 | 2700721.1873 | 1243432.0782 | 2700714.7961 | 1243427.8331 | 2700660.1749 | 1243467.7233
65 | 2700664.2569 | 1243541.2074 | 2700671.9643 | 1243536.0453 | 2700679.0586 | 1243530.9283 | 2700687.7191 | 1243523.9477 | 2700693.7027 | 1243517.4664 | 2700698.7324 | 1243511.0691 | 2700702.4674 | 1243505.7476
66 | 2700661.3203 | 1243536.5206 | 2700664.2569 | 1243541.2074
67 | 2700661.3203 | 1243536.5206 | 2700667.5201 | 1243532.4449 | 2700674.9576 | 1243527.0112
68 | 2700664.2569 | 1243541.2074 | 2700667.1973 | 1243546.1166 | 2700667.4546 | 1243546.5435 | 2700662.4273 | 1243549.6829 | 2700674.4696 | 1243570.1996
69 | 2700696.0741 | 1243505.9713 | 2700691.7505 | 1243512.2404 | 2700687.3183 | 1243517.2802 | 2700682.3992 | 1243521.1664 | 2700675.136 | 1243526.8809 | 2700674.9576 | 1243527.0112
70 | 2700686.6346 | 1243590.9254 | 2700674.4696 | 1243570.1996
71 | 2700686.6346 | 1243590.9254 | 2700670.2416 | 1243599.097
72 | 2700686.6346 | 1243590.9254 | 2700696.3059 | 1243586.3337
73 | 2700670.2416 | 1243599.097 | 2700666.2489 | 1243601.0873 | 2700664.2468 | 1243601.7739
74 | 2700696.3059 | 1243586.3337 | 2700696.6576 | 1243586.1667
75 | 2700717.7102 | 1243576.1714 | 2700718.3365 | 1243575.874 | 2700725.9266 | 1243572.2778 | 2700731.1528 | 1243569.6564
76 | 2700936.15 | 1243509.5683 | 2700956.6232 | 1243488.1 | 2700970.7514 | 1243467.6913 | 2700977.7411 | 1243454.0887 | 2700985.4499 | 1243436.8844 | 2701002.2638 | 1243395.5053
77 | 2701002.2638 | 1243395.5053 | 2701013.3853 | 1243398.5191
78 | 2700601.5618 | 1243619.5489 | 2700593.2264 | 1243622.3475
79 | 2700601.5618 | 1243619.5489 | 2700605.7953 | 1243618.6311 | 2700609.7654 | 1243618.098 | 2700613.8709 | 1243617.9559
80 | 2700623.1609 | 1243618.0113 | 2700614.5077 | 1243617.9339 | 2700613.8709 | 1243617.9559
81 | 2700707.461 | 1243581.0374 | 2700717.7102 | 1243576.1714
82 | 2700707.461 | 1243581.0374 | 2700697.0108 | 1243585.999
83 | 2700696.6576 | 1243586.1667 | 2700697.0108 | 1243585.999
84 | 2700623.1609 | 1243618.0113 | 2700625.5953 | 1243618.0331 | 2700629.1053 | 1243617.8814 | 2700632.6524 | 1243617.33 | 2700639.4935 | 1243615.321
85 | 2700639.4935 | 1243615.321 | 2700657.1258 | 1243610.143
86 | 2701013.3853 | 1243398.5191 | 2701000.0296 | 1243422.8025
87 | 2700996.0202 | 1243430.0923 | 2701000.0296 | 1243422.8025
88 | 2701013.3853 | 1243398.5191 | 2701029.368 | 1243402.839 | 2701035.1971 | 1243404.2791
89 | 2701062.4825 | 1243411.0203 | 2701035.1971 | 1243404.2791
90 | 2701062.4825 | 1243411.0203 | 2701051.3614 | 1243440.3646 | 2701047.5598 | 1243453.428
91 | 2701062.4825 | 1243411.0203 | 2701065.5764 | 1243411.785
92 | 2701047.5598 | 1243453.428 | 2701045.2302 | 1243461.4334
93 | 2701093.2559 | 1243418.617 | 2701073.5482 | 1243413.7553 | 2701065.5764 | 1243411.785
94 | 2700956.6994 | 1243795.6459 | 2700951.3156 | 1243804.4914
95 | 2700996.0776 | 1243736.4853 | 2700989.0304 | 1243748.597 | 2700985.2298 | 1243752.502 | 2700980.1082 | 1243757.1851 | 2700956.6994 | 1243795.6459
96 | 2700996.0776 | 1243736.4853 | 2700990.058 | 1243732.6466
97 | 2701271.4987 | 1243474.8775 | 2701262.3518 | 1243474.4433 | 2701252.7651 | 1243472.7561 | 2701244.2643 | 1243470.8484
98 | 2701271.4987 | 1243474.8775 | 2701275.2625 | 1243474.119
99 | 2701244.2643 | 1243470.8484 | 2701220.8608 | 1243465.5964
100 | 2701183.3245 | 1243457.7156 | 2701193.1644 | 1243461.3974 | 2701201.3618 | 1243462.9939 | 2701217.9591 | 1243464.9452 | 2701220.8608 | 1243465.5964
101 | 2701183.3245 | 1243457.7156 | 2701198.1219 | 1243435.5169
102 | 2701198.1219 | 1243435.5169 | 2701204.9228 | 1243425.3145 | 2701207.1756 | 1243420.438 | 2701204.4826 | 1243419.5628
103 | 2701041.1638 | 1243475.4069 | 2701045.2302 | 1243461.4334
104 | 2701041.1638 | 1243475.4069 | 2701024.3661 | 1243469.7895
105 | 2701021.8238 | 1243468.9393 | 2701024.3661 | 1243469.7895
106 | 2701145.7655 | 1243436.6813 | 2701153.1724 | 1243425.7767
107 | 2701138.677 | 1243433.0021 | 2701145.7655 | 1243436.6813
108 | 2701155.4271 | 1243422.4572 | 2701153.1724 | 1243425.7767
109 | 2701138.677 | 1243433.0021 | 2701131.6143 | 1243429.5902 | 2701124.337 | 1243426.7862 | 2701119.2762 | 1243425.221
110 | 2701138.677 | 1243433.0021 | 2701119.0061 | 1243443.7196 | 2701113.0233 | 1243448.5736
111 | 2701204.4826 | 1243419.5628 | 2701191.9371 | 1243415.4854 | 2701184.2635 | 1243418.6348 | 2701182.6706 | 1243418.1699
112 | 2701113.0233 | 1243448.5736 | 2701110.2675 | 1243450.8095 | 2701095.5522 | 1243446.7881
113 | 2701083.9248 | 1243443.6107 | 2701095.5522 | 1243446.7881
114 | 2701119.2762 | 1243425.221 | 2701116.1328 | 1243424.2556 | 2701093.2559 | 1243418.617
115 | 2701093.2559 | 1243418.617 | 2701095.2963 | 1243405.054
116 | 2701155.4271 | 1243422.4572 | 2701139.8011 | 1243417.6237
117 | 2701155.4271 | 1243422.4572 | 2701165.5263 | 1243413.1667 | 2701174.2692 | 1243415.7181
118 | 2701174.2692 | 1243415.7181 | 2701182.6706 | 1243418.1699

## bus_geodata
| x | y | coords
0 | 2700612.2273 | 1243873.1911
1 | 2700583.544 | 1243994.0879
2 | 2700715.7821 | 1243686.6494
3 | 2700559.1877 | 1243948.3175
4 | 2700899.1055 | 1243886.9184
5 | 2700598.3995 | 1243821.9625
6 | 2700565.4958 | 1243631.658
7 | 2700938.0758 | 1243818.37
8 | 2700550.1064 | 1243620.9001
9 | 2700579.2269 | 1243627.0478
10 | 2700953.3023 | 1243793.1759
11 | 2700313.2496 | 1243612.4249
12 | 2700324.7584 | 1243601.4041
13 | 2700331.6344 | 1243608.2701
14 | 2700343.471 | 1243597.0283
15 | 2700387.5321 | 1243615.0985
16 | 2700413.2959 | 1243599.6765
17 | 2700366.1167 | 1243594.1312
18 | 2700426.3589 | 1243589.925
19 | 2700464.1225 | 1243625.2615
20 | 2700453.4089 | 1243630.365
21 | 2700477.0507 | 1243620.7069
22 | 2700379.7637 | 1243695.4855
23 | 2700497.5685 | 1243616.1063
24 | 2700426.297 | 1243673.9109
25 | 2700294.6135 | 1243753.2781
26 | 2700526.2556 | 1243563.4851
27 | 2700535.4517 | 1243577.061
28 | 2700493.0139 | 1243553.4587
29 | 2700541.3859 | 1243542.092
30 | 2700547.518 | 1243599.6954
31 | 2700502.7713 | 1243618.8505
32 | 2700479.4796 | 1243545.6235
33 | 2700511.4089 | 1243542.3803
34 | 2700485.9916 | 1243541.8255
35 | 2700536.6203 | 1243579.2272
36 | 2700417.5756 | 1243678.6074
37 | 2700275.7241 | 1243726.883
38 | 2700560.2778 | 1243531.1502
39 | 2700620.1677 | 1243560.1152
40 | 2700655.9728 | 1243539.3765
41 | 2700584.3142 | 1243625.3398
42 | 2700645.5921 | 1243551.8794
43 | 2700658.5992 | 1243544.5251
44 | 2700616.0179 | 1243595.4929
45 | 2700661.3675 | 1243602.7614
46 | 2700272.5952 | 1243723.2706
47 | 2700265.588 | 1243715.1807
48 | 2700268.5008 | 1243718.5436
49 | 2700264.4064 | 1243713.8166
50 | 2700824.8129 | 1243322.8049
51 | 2700819.3235 | 1243330.5914
52 | 2700815.1036 | 1243336.5772
53 | 2700809.8847 | 1243343.9801
54 | 2700739.0732 | 1243443.624
55 | 2700804.3954 | 1243351.7667
56 | 2700986.7761 | 1243395.4083
57 | 2700830.1111 | 1243507.6196
58 | 2700996.1712 | 1243394.8059
59 | 2700744.3476 | 1243446.8605
60 | 2700721.1873 | 1243432.0782
61 | 2700702.4674 | 1243505.7476
62 | 2700660.1749 | 1243467.7233
63 | 2700661.3203 | 1243536.5206
64 | 2700664.2569 | 1243541.2074
65 | 2700674.9576 | 1243527.0112
66 | 2700696.0741 | 1243505.9713
67 | 2700674.4696 | 1243570.1996
68 | 2700686.6346 | 1243590.9254
69 | 2700670.2416 | 1243599.097
70 | 2700696.3059 | 1243586.3337
71 | 2700731.1528 | 1243569.6564
72 | 2701002.2638 | 1243395.5053
73 | 2700593.2264 | 1243622.3475
74 | 2700601.5618 | 1243619.549
75 | 2700613.8709 | 1243617.9559
76 | 2700707.461 | 1243581.0374
77 | 2700717.7102 | 1243576.1714
78 | 2700697.0108 | 1243585.999
79 | 2700696.6576 | 1243586.1667
80 | 2700664.2468 | 1243601.7739
81 | 2700623.1609 | 1243618.0113
82 | 2700639.4935 | 1243615.321
83 | 2700657.1258 | 1243610.143
84 | 2701000.0296 | 1243422.8025
85 | 2701013.3853 | 1243398.5191
86 | 2700996.0202 | 1243430.0923
87 | 2701035.1971 | 1243404.2791
88 | 2700936.15 | 1243509.5683
89 | 2701062.4825 | 1243411.0203
90 | 2701047.5598 | 1243453.428
91 | 2701065.5764 | 1243411.785
92 | 2700956.6994 | 1243795.6459
93 | 2700951.3156 | 1243804.4914
94 | 2700996.0776 | 1243736.4853
95 | 2700990.058 | 1243732.6466
96 | 2701271.4987 | 1243474.8775
97 | 2701244.2643 | 1243470.8484
98 | 2701275.2625 | 1243474.119
99 | 2701183.3245 | 1243457.7156
100 | 2701220.8608 | 1243465.5964
101 | 2701198.1219 | 1243435.5169
102 | 2701041.1638 | 1243475.4069
103 | 2701045.2302 | 1243461.4334
104 | 2701024.3661 | 1243469.7895
105 | 2701145.7655 | 1243436.6813
106 | 2701153.1724 | 1243425.7767
107 | 2701138.677 | 1243433.0021
108 | 2701204.4826 | 1243419.5628
109 | 2701113.0233 | 1243448.5736
110 | 2701095.5522 | 1243446.7881
111 | 2701083.9248 | 1243443.6107
112 | 2701119.2762 | 1243425.221
113 | 2701093.2559 | 1243418.617
114 | 2701095.2963 | 1243405.054
115 | 2701139.8011 | 1243417.6237
116 | 2701155.4271 | 1243422.4572
117 | 2701021.8238 | 1243468.9393
118 | 2701182.6706 | 1243418.1699
119 | 2701174.2692 | 1243415.7181
120 | 2700661.3203 | 1243536.5206

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97949 | -0.39275 | 0.0022798 | 0.00057138
1 | 0.98011 | -0.3806 | 0 | 0
2 | 0.97885 | -0.40538 | 0 | 0
3 | 0.98036 | -0.37554 | 0 | 0
4 | 0.97801 | -0.42205 | 0 | 0
5 | 0.98001 | -0.38244 | 0.0025853 | 0.00064793
6 | 0.98277 | -0.32819 | 0 | 0
7 | 0.97778 | -0.42649 | 0.00051622 | 0.00012938
8 | 0.98135 | -0.3558 | 0 | 0
9 | 0.98396 | -0.30525 | 0.0003998 | 0.0001002
10 | 0.97771 | -0.42787 | 0.000903 | 0.00022631
11 | 0.97503 | -0.47916 | 0.0034489 | 0.00086439
12 | 0.97509 | -0.47815 | 0 | 0
13 | 0.97512 | -0.47754 | 0 | 0
14 | 0.97517 | -0.4765 | 0.002654 | 0.00066516
15 | 0.97552 | -0.46952 | 0 | 0
16 | 0.97569 | -0.46617 | 0.0018951 | 0.00047495
17 | 0.97535 | -0.47291 | 0 | 0
18 | 0.97582 | -0.46377 | 0 | 0
19 | 0.97613 | -0.45758 | 0.00091199 | 0.00022857
20 | 0.976 | -0.46016 | 0.00091597 | 0.00022956
21 | 0.97629 | -0.4544 | 0 | 0
22 | 0.97499 | -0.47996 | 0.00034389 | 8.6187e-05
23 | 0.97694 | -0.44165 | 0 | 0
24 | 0.97623 | -0.45555 | 0 | 0
25 | 0.97398 | -0.49984 | 0 | 0
26 | 0.97139 | -0.55085 | 0 | 0
27 | 0.97209 | -0.53691 | 0.0014298 | 0.00035834
28 | 0.97067 | -0.56496 | 0 | 0
29 | 0.9708 | -0.56249 | 0.0040566 | 0.0010167
30 | 0.97342 | -0.51061 | 0 | 0
31 | 0.97737 | -0.43328 | 0.0019353 | 0.00048503
32 | 0.97037 | -0.57093 | 0 | 0
33 | 0.97066 | -0.56516 | 0.00049997 | 0.00012531
34 | 0.97022 | -0.57382 | 0.020672 | 0.0051809
35 | 0.9722 | -0.53482 | 0.010486 | 0.002628
36 | 0.97623 | -0.45565 | 0.00055595 | 0.00013933
37 | 0.97367 | -0.50612 | 0 | 0
38 | 0.9704 | -0.57037 | 0.019524 | 0.0048932
39 | 0.99567 | -0.082837 | 0.061472 | 0.015406
40 | 0.99798 | -0.03822 | 0 | 0
41 | 0.9844 | -0.29673 | 0.0012023 | 0.00030133
42 | 0.9979 | -0.039821 | 0.0044143 | 0.0011063
43 | 0.99796 | -0.038667 | 0 | 0
44 | 0.99164 | -0.15809 | 0.00021484 | 5.3844e-05
45 | 0.99165 | -0.15792 | 0 | 0
46 | 0.97362 | -0.50704 | 0.0022965 | 0.00057556
47 | 0.97355 | -0.50847 | 0.0036246 | 0.00090842
48 | 0.97357 | -0.50799 | 0.0022934 | 0.00057478
49 | 0.97354 | -0.50855 | 0.0022965 | 0.00057556
50 | 0.98669 | -0.25466 | 0.0027057 | 0.0006781
51 | 0.98672 | -0.2542 | 0.0027071 | 0.00067847
52 | 0.98675 | -0.25349 | 0 | 0
53 | 0.98671 | -0.25437 | 0.002707 | 0.00067843
54 | 0.98815 | -0.22636 | 0 | 0
55 | 0.98668 | -0.25483 | 0.0027042 | 0.00067773
56 | 0.9756 | -0.46788 | 0 | 0
57 | 0.98543 | -0.27669 | 0 | 0
58 | 0.97513 | -0.47711 | 0.011522 | 0.0028877
59 | 0.9886 | -0.21758 | 0 | 0
60 | 0.98679 | -0.25253 | 0 | 0
61 | 0.99391 | -0.11554 | 0.0026133 | 0.00065495
62 | 0.98201 | -0.34569 | 0.068774 | 0.017236
63 | 0.99835 | -0.031248 | 0 | 0
64 | 0.99791 | -0.03953 | 0 | 0
65 | 1 | 0 | -0.33581 | -0.085793
66 | 0.99984 | -0.0031599 | 0.00603 | 0.0015113
67 | 0.99596 | -0.076244 | 0.017021 | 0.004266
68 | 0.99419 | -0.10961 | 0 | 0
69 | 0.99251 | -0.14148 | 0.00017331 | 4.3437e-05
70 | 0.9936 | -0.1208 | 0.0018491 | 0.00046342
71 | 0.99163 | -0.15825 | 0.00056633 | 0.00014194
72 | 0.97489 | -0.48181 | 0 | 0
73 | 0.98518 | -0.28161 | 0.001564 | 0.00039198
74 | 0.98593 | -0.26725 | 0 | 0
75 | 0.98699 | -0.24696 | 0.00021484 | 5.3844e-05
76 | 0.99296 | -0.13302 | 0.0013456 | 0.00033724
77 | 0.99238 | -0.14397 | 0.00066758 | 0.00016731
78 | 0.99356 | -0.12158 | 0.00071448 | 0.00017907
79 | 0.99358 | -0.12119 | 0.00071481 | 0.00017915
80 | 0.99191 | -0.15293 | 0.0058791 | 0.0014735
81 | 0.98778 | -0.2318 | 0.00043026 | 0.00010783
82 | 0.9892 | -0.20455 | 0.00029138 | 7.3027e-05
83 | 0.99078 | -0.17449 | 0.00027087 | 6.7886e-05
84 | 0.97441 | -0.49133 | 0.0018926 | 0.00047433
85 | 0.97448 | -0.49003 | 0 | 0
86 | 0.97441 | -0.49143 | 0.00066262 | 0.00016607
87 | 0.97371 | -0.50513 | 0.0041987 | 0.0010523
88 | 0.97454 | -0.48878 | 0.0028482 | 0.00071382
89 | 0.97287 | -0.52179 | 0 | 0
90 | 0.97265 | -0.52597 | 0.0015266 | 0.0003826
91 | 0.97278 | -0.52339 | 0.0058943 | 0.0014773
92 | 0.97748 | -0.43239 | 0.00073215 | 0.00018349
93 | 0.97747 | -0.43257 | 0.00092743 | 0.00023243
94 | 0.97759 | -0.43023 | 0 | 0
95 | 0.9776 | -0.43001 | 0 | 0
96 | 0.97046 | -0.56937 | 0 | 0
97 | 0.97048 | -0.56899 | 0.00096516 | 0.00024189
98 | 0.97046 | -0.56943 | 0.00074683 | 0.00018717
99 | 0.9706 | -0.56655 | 0 | 0
100 | 0.97052 | -0.56823 | 0.00063779 | 0.00015984
101 | 0.97066 | -0.56539 | 0.00093857 | 0.00023523
102 | 0.9726 | -0.5271 | 0 | 0
103 | 0.97263 | -0.52651 | 0.0013131 | 0.0003291
104 | 0.97256 | -0.52782 | 0.0013871 | 0.00034765
105 | 0.97124 | -0.55389 | 0 | 0
106 | 0.9711 | -0.55677 | 0.00028748 | 7.205e-05
107 | 0.97133 | -0.55214 | 0 | 0
108 | 0.97072 | -0.56414 | 0.0017273 | 0.00043289
109 | 0.9711 | -0.55667 | 0.0014296 | 0.00035829
110 | 0.97098 | -0.55899 | 0.0020311 | 0.00050904
111 | 0.97093 | -0.56003 | 0.0046656 | 0.0011693
112 | 0.97172 | -0.54444 | 0 | 0
113 | 0.97222 | -0.53457 | 0 | 0
114 | 0.9722 | -0.53491 | 0.0013133 | 0.00032915
115 | 0.971 | -0.55877 | 0.0037815 | 0.00094773
116 | 0.97105 | -0.55763 | 0 | 0
117 | 0.97256 | -0.52786 | 0.00081473 | 0.00020419
118 | 0.97083 | -0.562 | 0.001678 | 0.00042054
119 | 0.97089 | -0.56091 | 0.0010751 | 0.00026945
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0053641 | -0.0013366 | 0.0053672 | 0.001337 | 3.0919e-06 | 4.1387e-07 | 0.0081462 | 0.0081456 | 0.0081462 | 0.97949 | -0.39275 | 0.98011 | -0.3806 | 2.238
1 | 0.0030843 | 0.00076522 | -0.0030824 | -0.00076686 | 1.8425e-06 | -1.6385e-06 | 0.0046828 | 0.0046838 | 0.0046838 | 0.97949 | -0.39275 | 0.97885 | -0.40538 | 1.2867
2 | -0.0053672 | -0.001337 | 0.0053685 | 0.0013372 | 1.29e-06 | 1.7204e-07 | 0.0081456 | 0.0081454 | 0.0081456 | 0.98011 | -0.3806 | 0.98036 | -0.37554 | 2.2378
3 | 0.0030824 | 0.00076686 | -0.00308 | -0.00076902 | 2.4369e-06 | -2.1596e-06 | 0.0046838 | 0.0046851 | 0.0046851 | 0.97885 | -0.40538 | 0.97801 | -0.42205 | 1.2871
4 | 0.0025861 | 0.00064662 | -0.0025853 | -0.00064793 | 8.5033e-07 | -1.311e-06 | 0.0039247 | 0.0039254 | 0.0039254 | 0.98036 | -0.37554 | 0.98001 | -0.38244 | 1.0784
5 | -0.0079546 | -0.0019838 | 0.0079725 | 0.0019911 | 1.7905e-05 | 7.3161e-06 | 0.01207 | 0.012069 | 0.01207 | 0.98036 | -0.37554 | 0.98277 | -0.32819 | 3.316
6 | 0.00308 | 0.00076902 | -0.0030793 | -0.00076959 | 6.4912e-07 | -5.7384e-07 | 0.0046851 | 0.0046854 | 0.0046854 | 0.97801 | -0.42205 | 0.97778 | -0.42649 | 1.2872
7 | 0.080658 | 0.020521 | -0.080551 | -0.020453 | 0.00010717 | 6.8348e-05 | 0.12223 | 0.12223 | 0.12223 | 0.98277 | -0.32819 | 0.98135 | -0.3558 | 33.5809
8 | -0.08863 | -0.022512 | 0.088728 | 0.022575 | 9.7972e-05 | 6.2518e-05 | 0.1343 | 0.1343 | 0.1343 | 0.98277 | -0.32819 | 0.98396 | -0.30525 | 36.8964
9 | 0.0025631 | 0.00064021 | -0.0025629 | -0.00064047 | 1.679e-07 | -2.6175e-07 | 0.0038998 | 0.0039 | 0.0039 | 0.97778 | -0.42649 | 0.97771 | -0.42787 | 1.0714
10 | 0.080551 | 0.020453 | -0.080252 | -0.020262 | 0.00029913 | 0.00019077 | 0.12223 | 0.12223 | 0.12223 | 0.98135 | -0.3558 | 0.97737 | -0.43328 | 33.5809
11 | -0.089128 | -0.022675 | 0.089165 | 0.022698 | 3.6625e-05 | 2.3372e-05 | 0.13491 | 0.13491 | 0.13491 | 0.98396 | -0.30525 | 0.9844 | -0.29673 | 37.0625
12 | 0.0016599 | 0.00041416 | -0.0016598 | -0.00041494 | 1.6942e-07 | -7.7956e-07 | 0.0025257 | 0.002526 | 0.002526 | 0.97771 | -0.42787 | 0.9776 | -0.43001 | 0.69395
13 | -0.0034489 | -0.00086439 | 0.0034491 | 0.00086429 | 1.6554e-07 | -9.2805e-08 | 0.0052635 | 0.0052634 | 0.0052635 | 0.97503 | -0.47916 | 0.97509 | -0.47815 | 1.446
14 | -0.0034491 | -0.00086429 | 0.0034492 | 0.00086424 | 1.008e-07 | -5.6523e-08 | 0.0052634 | 0.0052634 | 0.0052634 | 0.97509 | -0.47815 | 0.97512 | -0.47754 | 1.446
15 | -0.0034492 | -0.00086424 | 0.0034494 | 0.00086414 | 1.6958e-07 | -9.5114e-08 | 0.0052634 | 0.0052633 | 0.0052634 | 0.97512 | -0.47754 | 0.97517 | -0.4765 | 1.446
16 | -0.0061034 | -0.0015293 | 0.0061044 | 0.0015296 | 1.0448e-06 | 2.6782e-07 | 0.0093131 | 0.0093129 | 0.0093131 | 0.97517 | -0.4765 | 0.97535 | -0.47291 | 2.5585
17 | -0.0061054 | -0.0015298 | 0.0061064 | 0.0015301 | 9.7662e-07 | 2.5006e-07 | 0.0093128 | 0.0093127 | 0.0093128 | 0.97552 | -0.46952 | 0.97569 | -0.46617 | 2.5585
18 | 0.0061054 | 0.0015298 | -0.0061044 | -0.0015296 | 9.8459e-07 | 2.5225e-07 | 0.0093128 | 0.0093129 | 0.0093129 | 0.97552 | -0.46952 | 0.97535 | -0.47291 | 2.5585
19 | -0.0080015 | -0.002005 | 0.0080024 | 0.0020054 | 9.1476e-07 | 3.8083e-07 | 0.012203 | 0.012203 | 0.012203 | 0.97569 | -0.46617 | 0.97582 | -0.46377 | 3.3524
20 | -0.0080024 | -0.0020054 | 0.008006 | 0.0020069 | 3.5704e-06 | 1.4859e-06 | 0.012203 | 0.012202 | 0.012203 | 0.97582 | -0.46377 | 0.97629 | -0.4544 | 3.3524
21 | 0.011797 | 0.0029633 | -0.011795 | -0.0029625 | 1.4513e-06 | 7.7929e-07 | 0.017985 | 0.017985 | 0.017985 | 0.97613 | -0.45758 | 0.976 | -0.46016 | 4.9411
22 | -0.012709 | -0.0031919 | 0.012711 | 0.0031929 | 1.9297e-06 | 1.0636e-06 | 0.019376 | 0.019376 | 0.019376 | 0.97613 | -0.45758 | 0.97629 | -0.4544 | 5.323
23 | 0.010879 | 0.0027329 | -0.010869 | -0.0027276 | 1.027e-05 | 5.3303e-06 | 0.016589 | 0.016589 | 0.016589 | 0.976 | -0.46016 | 0.97499 | -0.47996 | 4.5575
24 | -0.021273 | -0.0053376 | 0.021285 | 0.0053455 | 1.2941e-05 | 7.8715e-06 | 0.032425 | 0.032425 | 0.032425 | 0.97629 | -0.4544 | 0.97694 | -0.44165 | 8.9079
25 | 0.00055598 | 0.00013783 | -0.00055595 | -0.00013921 | 3.0219e-08 | -1.3848e-06 | 0.00084686 | 0.00084736 | 0.00084736 | 0.97629 | -0.4544 | 0.97623 | -0.45555 | 0.23279
26 | 0.010525 | 0.0026414 | -0.010515 | -0.0026363 | 9.9716e-06 | 5.0982e-06 | 0.016065 | 0.016065 | 0.016065 | 0.97499 | -0.47996 | 0.97398 | -0.49984 | 4.4135
27 | 0.056999 | 0.014411 | -0.056812 | -0.014292 | 0.00018784 | 0.00011939 | 0.086864 | 0.086864 | 0.086864 | 0.97694 | -0.44165 | 0.97342 | -0.51061 | 23.8637
28 | -0.078285 | -0.019757 | 0.078316 | 0.019777 | 3.1388e-05 | 2.0014e-05 | 0.11929 | 0.11929 | 0.11929 | 0.97694 | -0.44165 | 0.97737 | -0.43328 | 32.7715
29 | 0.00055595 | 0.00013921 | -0.00055595 | -0.00013933 | 2.6673e-09 | -1.2214e-07 | 0.00084736 | 0.00084741 | 0.00084741 | 0.97623 | -0.45555 | 0.97623 | -0.45565 | 0.2328
30 | 0.010515 | 0.0026363 | -0.010512 | -0.0026347 | 3.1432e-06 | 1.6076e-06 | 0.016065 | 0.016065 | 0.016065 | 0.97398 | -0.49984 | 0.97367 | -0.50612 | 4.4135
31 | -0.044796 | -0.011242 | 0.044826 | 0.011261 | 2.9804e-05 | 1.8866e-05 | 0.068626 | 0.068626 | 0.068626 | 0.97139 | -0.55085 | 0.97209 | -0.53691 | 18.8533
32 | 0.021195 | 0.0053199 | -0.021181 | -0.0053112 | 1.4254e-05 | 8.6764e-06 | 0.03247 | 0.03247 | 0.03247 | 0.97139 | -0.55085 | 0.97067 | -0.56496 | 8.9205
33 | 0.023601 | 0.0059223 | -0.023588 | -0.0059143 | 1.3083e-05 | 8.0432e-06 | 0.036156 | 0.036156 | 0.036156 | 0.97139 | -0.55085 | 0.9708 | -0.56249 | 9.933
34 | -0.046256 | -0.011619 | 0.04626 | 0.011622 | 4.6287e-06 | 2.9318e-06 | 0.070815 | 0.070815 | 0.070815 | 0.97209 | -0.53691 | 0.9722 | -0.53482 | 19.4546
35 | 0.020681 | 0.0051862 | -0.020675 | -0.0051826 | 5.8816e-06 | 3.5714e-06 | 0.031704 | 0.031704 | 0.031704 | 0.97067 | -0.56496 | 0.97037 | -0.57093 | 8.7099
36 | 0.00049998 | 0.00012504 | -0.00049997 | -0.00012531 | 4.7299e-09 | -2.624e-07 | 0.00076636 | 0.00076645 | 0.00076645 | 0.97067 | -0.56496 | 0.97066 | -0.56516 | 0.21056
37 | 0.019531 | 0.0048976 | -0.019524 | -0.0048932 | 7.3379e-06 | 4.4264e-06 | 0.029938 | 0.029938 | 0.029938 | 0.9708 | -0.56249 | 0.9704 | -0.57037 | 8.2248
38 | 0.056812 | 0.014292 | -0.056746 | -0.01425 | 6.5619e-05 | 4.1708e-05 | 0.086864 | 0.086864 | 0.086864 | 0.97342 | -0.51061 | 0.9722 | -0.53482 | 23.8637
39 | 0.020675 | 0.0051826 | -0.020672 | -0.0051809 | 2.8416e-06 | 1.7255e-06 | 0.031704 | 0.031704 | 0.031704 | 0.97037 | -0.57093 | 0.97022 | -0.57382 | 8.7099
40 | 0.010512 | 0.0026347 | -0.010512 | -0.0026345 | 4.6254e-07 | 2.3659e-07 | 0.016065 | 0.016065 | 0.016065 | 0.97367 | -0.50612 | 0.97362 | -0.50704 | 4.4135
41 | -0.061472 | -0.015406 | 0.061603 | 0.01549 | 0.00013096 | 8.3275e-05 | 0.09187 | 0.09187 | 0.09187 | 0.99567 | -0.082837 | 0.99798 | -0.03822 | 25.2389
42 | 0.0044146 | 0.0011063 | -0.0044145 | -0.0011063 | 9.3861e-08 | -1.5412e-08 | 0.0065823 | 0.0065823 | 0.0065823 | 0.99798 | -0.03822 | 0.99796 | -0.038667 | 1.8083
43 | -0.066018 | -0.016596 | 0.06604 | 0.01661 | 2.1987e-05 | 1.3992e-05 | 0.098452 | 0.098452 | 0.098452 | 0.99798 | -0.03822 | 0.99835 | -0.031248 | 27.0472
44 | -0.090367 | -0.023 | 0.090433 | 0.023042 | 6.5903e-05 | 4.2058e-05 | 0.13672 | 0.13672 | 0.13672 | 0.9844 | -0.29673 | 0.98518 | -0.28161 | 37.5617
45 | -0.0044143 | -0.0011063 | 0.0044145 | 0.0011063 | 2.4278e-07 | -3.9844e-08 | 0.0065824 | 0.0065823 | 0.0065824 | 0.9979 | -0.039821 | 0.99796 | -0.038667 | 1.8083
46 | -0.00021484 | -5.3844e-05 | 0.00021484 | 5.3249e-05 | 1.8002e-09 | -5.9512e-07 | 0.00032238 | 0.00032217 | 0.00032238 | 0.99164 | -0.15809 | 0.99165 | -0.15792 | 0.088567
47 | -0.093975 | -0.024144 | 0.093998 | 0.024159 | 2.2766e-05 | 1.4531e-05 | 0.14123 | 0.14123 | 0.14123 | 0.99165 | -0.15792 | 0.99191 | -0.15293 | 38.7983
48 | 0.09376 | 0.024091 | -0.093685 | -0.024043 | 7.5418e-05 | 4.8137e-05 | 0.1409 | 0.1409 | 0.1409 | 0.99165 | -0.15792 | 0.99078 | -0.17449 | 38.7098
49 | 0.008215 | 0.0020589 | -0.0082147 | -0.0020588 | 3.6968e-07 | 1.5883e-07 | 0.012555 | 0.012555 | 0.012555 | 0.97362 | -0.50704 | 0.97357 | -0.50799 | 3.4493
50 | -0.0059211 | -0.001484 | 0.0059213 | 0.001484 | 1.3665e-07 | 3.2133e-08 | 0.0090501 | 0.0090501 | 0.0090501 | 0.97355 | -0.50847 | 0.97357 | -0.50799 | 2.4863
51 | 0.0022965 | 0.00057554 | -0.0022965 | -0.00057556 | 8.338e-09 | -1.7103e-08 | 0.0035101 | 0.0035101 | 0.0035101 | 0.97355 | -0.50847 | 0.97354 | -0.50855 | 0.96431
52 | -0.0027057 | -0.0006781 | 0.0027057 | 0.00067802 | 5.9482e-08 | -8.3618e-08 | 0.0040804 | 0.0040803 | 0.0040804 | 0.98669 | -0.25466 | 0.98672 | -0.2542 | 1.121
53 | -0.0054129 | -0.0013565 | 0.005413 | 0.0013565 | 1.83e-07 | 2.3567e-08 | 0.0081628 | 0.0081628 | 0.0081628 | 0.98672 | -0.2542 | 0.98675 | -0.25349 | 2.2425
54 | 0.0054114 | 0.0013561 | -0.0054112 | -0.0013561 | 2.2619e-07 | 2.9063e-08 | 0.0081604 | 0.0081604 | 0.0081604 | 0.98675 | -0.25349 | 0.98671 | -0.25437 | 2.2419
55 | -0.010824 | -0.0027126 | 0.010838 | 0.0027198 | 1.4007e-05 | 7.1712e-06 | 0.016323 | 0.016323 | 0.016323 | 0.98675 | -0.25349 | 0.98815 | -0.22636 | 4.4844
56 | 0.0027042 | 0.00067765 | -0.0027042 | -0.00067773 | 5.9418e-08 | -8.3657e-08 | 0.0040781 | 0.0040782 | 0.0040782 | 0.98671 | -0.25437 | 0.98668 | -0.25483 | 1.1204
57 | -0.080006 | -0.020207 | 0.08004 | 0.020228 | 3.3642e-05 | 2.1452e-05 | 0.12053 | 0.12053 | 0.12053 | 0.98815 | -0.22636 | 0.9886 | -0.21758 | 33.1136
58 | 0.069167 | 0.017487 | -0.069081 | -0.017432 | 8.6708e-05 | 5.5221e-05 | 0.10421 | 0.10421 | 0.10421 | 0.98815 | -0.22636 | 0.98679 | -0.25253 | 28.6294
59 | -0.053479 | -0.013449 | 0.053972 | 0.013762 | 0.00049325 | 0.00031318 | 0.081584 | 0.081583 | 0.081584 | 0.9756 | -0.46788 | 0.98543 | -0.27669 | 22.4131
60 | 0.053479 | 0.013449 | -0.053455 | -0.013434 | 2.3564e-05 | 1.4963e-05 | 0.081584 | 0.081584 | 0.081584 | 0.9756 | -0.46788 | 0.97513 | -0.47711 | 22.4131
61 | -0.053972 | -0.013762 | 0.054283 | 0.013959 | 0.00031056 | 0.00019717 | 0.081583 | 0.081582 | 0.081583 | 0.98543 | -0.27669 | 0.99163 | -0.15825 | 22.4129
62 | 0.041933 | 0.010546 | -0.041924 | -0.010541 | 9.4202e-06 | 5.9524e-06 | 0.064002 | 0.064002 | 0.064002 | 0.97513 | -0.47711 | 0.97489 | -0.48181 | 17.5829
63 | -0.08004 | -0.020228 | 0.080433 | 0.020479 | 0.00039369 | 0.00025103 | 0.12053 | 0.12053 | 0.12053 | 0.9886 | -0.21758 | 0.99391 | -0.11554 | 33.1136
64 | 0.069081 | 0.017432 | -0.068774 | -0.017236 | 0.0003067 | 0.00019533 | 0.10421 | 0.10421 | 0.10421 | 0.98679 | -0.25253 | 0.98201 | -0.34569 | 28.6295
65 | -0.083047 | -0.021134 | 0.083352 | 0.021329 | 0.00030552 | 0.00019485 | 0.12445 | 0.12445 | 0.12445 | 0.99391 | -0.11554 | 0.99791 | -0.03953 | 34.1884
66 | 0.26159 | 0.067354 | -0.26149 | -0.067287 | 0.00010535 | 6.721e-05 | 0.39054 | 0.39054 | 0.39054 | 0.99835 | -0.031248 | 0.99791 | -0.03953 | 35.7636
67 | -0.32763 | -0.083964 | 0.32813 | 0.084281 | 0.00049706 | 0.00031747 | 0.48899 | 0.48899 | 0.48899 | 0.99835 | -0.031248 | 1 | 0 | 44.7792
68 | 0.17814 | 0.045958 | -0.17782 | -0.045756 | 0.00031807 | 0.00020216 | 0.26609 | 0.26609 | 0.26609 | 0.99791 | -0.03953 | 0.99596 | -0.076244 | 24.3676
69 | 0.0060309 | 0.0015115 | -0.00603 | -0.0015113 | 9.078e-07 | 1.8671e-07 | 0.0089741 | 0.0089743 | 0.0089743 | 1 | 0 | 0.99984 | -0.0031599 | 2.4655
70 | 0.1608 | 0.04149 | -0.16054 | -0.041323 | 0.00026099 | 0.00016641 | 0.24066 | 0.24066 | 0.24066 | 0.99596 | -0.076244 | 0.99419 | -0.10961 | 33.0582
71 | 0.10026 | 0.02581 | -0.10011 | -0.025711 | 0.00015518 | 9.9077e-05 | 0.15031 | 0.15031 | 0.15031 | 0.99419 | -0.10961 | 0.99251 | -0.14148 | 41.2926
72 | 0.060275 | 0.015513 | -0.060242 | -0.015492 | 3.2779e-05 | 2.084e-05 | 0.090359 | 0.090359 | 0.090359 | 0.99419 | -0.10961 | 0.9936 | -0.1208 | 24.8239
73 | 0.099932 | 0.025668 | -0.099877 | -0.025632 | 5.5534e-05 | 3.5457e-05 | 0.15005 | 0.15005 | 0.15005 | 0.99251 | -0.14148 | 0.99191 | -0.15293 | 41.2213
74 | 0.058393 | 0.015029 | -0.058392 | -0.015028 | 1.12e-06 | 7.1179e-07 | 0.08759 | 0.08759 | 0.08759 | 0.9936 | -0.1208 | 0.99358 | -0.12119 | 24.0632
75 | -0.054849 | -0.014101 | 0.054887 | 0.014126 | 3.8067e-05 | 2.417e-05 | 0.082432 | 0.082432 | 0.082432 | 0.99163 | -0.15825 | 0.99238 | -0.14397 | 22.6462
76 | 0.0028491 | 0.00071277 | -0.0028482 | -0.00071382 | 9.4465e-07 | -1.0558e-06 | 0.0043483 | 0.0043489 | 0.0043489 | 0.97489 | -0.48181 | 0.97454 | -0.48878 | 1.1947
77 | 0.039075 | 0.0098278 | -0.039059 | -0.0098181 | 1.5334e-05 | 9.6707e-06 | 0.059654 | 0.059654 | 0.059654 | 0.97489 | -0.48181 | 0.97448 | -0.49003 | 16.3884
78 | -0.091997 | -0.023434 | 0.092061 | 0.023474 | 6.3785e-05 | 4.0711e-05 | 0.13909 | 0.13909 | 0.13909 | 0.98518 | -0.28161 | 0.98593 | -0.26725 | 38.2107
79 | -0.092061 | -0.023474 | 0.092151 | 0.023532 | 9.0286e-05 | 5.7624e-05 | 0.13909 | 0.13909 | 0.13909 | 0.98593 | -0.26725 | 0.98699 | -0.24696 | 38.2107
80 | -0.092366 | -0.023586 | 0.092434 | 0.023629 | 6.7713e-05 | 4.3218e-05 | 0.13941 | 0.13941 | 0.13941 | 0.98699 | -0.24696 | 0.98778 | -0.2318 | 38.2997
81 | 0.055584 | 0.014312 | -0.055555 | -0.014293 | 2.9617e-05 | 1.8808e-05 | 0.083433 | 0.083433 | 0.083433 | 0.99296 | -0.13302 | 0.99238 | -0.14397 | 22.9212
82 | -0.05693 | -0.014649 | 0.056961 | 0.014669 | 3.1675e-05 | 2.0122e-05 | 0.085449 | 0.085449 | 0.085449 | 0.99296 | -0.13302 | 0.99356 | -0.12158 | 23.4751
83 | -0.057676 | -0.014848 | 0.057677 | 0.014849 | 1.0976e-06 | 6.9738e-07 | 0.086519 | 0.086519 | 0.086519 | 0.99356 | -0.12158 | 0.99358 | -0.12119 | 23.7691
84 | -0.092864 | -0.023737 | 0.092986 | 0.023815 | 0.00012261 | 7.8256e-05 | 0.14006 | 0.14006 | 0.14006 | 0.98778 | -0.2318 | 0.9892 | -0.20455 | 38.4777
85 | -0.093278 | -0.023888 | 0.093414 | 0.023975 | 0.00013603 | 8.6823e-05 | 0.1405 | 0.1405 | 0.1405 | 0.9892 | -0.20455 | 0.99078 | -0.17449 | 38.5981
86 | -0.0025552 | -0.0006403 | 0.0025554 | 0.00064005 | 1.5823e-07 | -2.4397e-07 | 0.003902 | 0.0039019 | 0.003902 | 0.97441 | -0.49133 | 0.97448 | -0.49003 | 1.072
87 | 0.00066262 | 0.00016597 | -0.00066262 | -0.00016607 | 3.1944e-09 | -1.0159e-07 | 0.0010118 | 0.0010119 | 0.0010119 | 0.97441 | -0.49133 | 0.97441 | -0.49143 | 0.27799
88 | 0.036504 | 0.009178 | -0.036478 | -0.0091615 | 2.6297e-05 | 1.6549e-05 | 0.055752 | 0.055752 | 0.055752 | 0.97448 | -0.49003 | 0.97371 | -0.50513 | 15.3164
89 | 0.032279 | 0.0081092 | -0.032253 | -0.0080931 | 2.5653e-05 | 1.6069e-05 | 0.049335 | 0.049335 | 0.049335 | 0.97371 | -0.50513 | 0.97287 | -0.52179 | 13.5537
90 | 0.0050428 | 0.0012632 | -0.0050418 | -0.0012631 | 1.0036e-06 | 8.382e-08 | 0.0077129 | 0.0077131 | 0.0077131 | 0.97287 | -0.52179 | 0.97265 | -0.52597 | 2.119
91 | 0.02721 | 0.0068299 | -0.027208 | -0.0068286 | 2.0705e-06 | 1.2855e-06 | 0.041623 | 0.041623 | 0.041623 | 0.97287 | -0.52179 | 0.97278 | -0.52339 | 11.4348
92 | 0.0035152 | 0.00088055 | -0.0035151 | -0.0008806 | 9.0416e-08 | -4.5612e-08 | 0.0053776 | 0.0053776 | 0.0053776 | 0.97265 | -0.52597 | 0.97263 | -0.52651 | 1.4774
93 | 0.021314 | 0.0053513 | -0.021303 | -0.0053444 | 1.1367e-05 | 6.921e-06 | 0.032606 | 0.032607 | 0.032607 | 0.97278 | -0.52339 | 0.97222 | -0.53457 | 8.9578
94 | 0.00092743 | 0.00023231 | -0.00092743 | -0.00023243 | 7.7399e-09 | -1.2485e-07 | 0.0014118 | 0.0014118 | 0.0014118 | 0.97748 | -0.43239 | 0.97747 | -0.43257 | 0.38787
95 | -0.0016596 | -0.0004158 | 0.0016598 | 0.00041502 | 1.7093e-07 | -7.8604e-07 | 0.0025263 | 0.002526 | 0.0025263 | 0.97748 | -0.43239 | 0.97759 | -0.43023 | 0.69405
96 | -0.0016598 | -0.00041502 | 0.0016598 | 0.00041494 | 1.7046e-08 | -7.8412e-08 | 0.002526 | 0.002526 | 0.002526 | 0.97759 | -0.43023 | 0.9776 | -0.43001 | 0.69396
97 | -0.00074683 | -0.00018713 | 0.00074685 | 0.0001868 | 1.3572e-08 | -3.3238e-07 | 0.0011451 | 0.001145 | 0.0011451 | 0.97046 | -0.56937 | 0.97048 | -0.56899 | 0.31459
98 | 0.00074683 | 0.00018713 | -0.00074683 | -0.00018717 | 1.888e-09 | -4.6231e-08 | 0.0011451 | 0.0011451 | 0.0011451 | 0.97046 | -0.56937 | 0.97046 | -0.56943 | 0.3146
99 | -0.001712 | -0.00042869 | 0.0017121 | 0.00042843 | 6.1969e-08 | -2.5672e-07 | 0.0026249 | 0.0026247 | 0.0026249 | 0.97048 | -0.56899 | 0.97052 | -0.56823 | 0.72111
100 | 0.00235 | 0.00058792 | -0.0023499 | -0.00058828 | 1.8758e-07 | -3.5627e-07 | 0.0036024 | 0.0036026 | 0.0036026 | 0.9706 | -0.56655 | 0.97052 | -0.56823 | 0.98973
101 | -0.00235 | -0.00058792 | 0.0023502 | 0.00058767 | 1.2983e-07 | -2.4666e-07 | 0.0036024 | 0.0036023 | 0.0036024 | 0.9706 | -0.56655 | 0.97066 | -0.56539 | 0.98968
102 | -0.0032887 | -0.0008229 | 0.0032889 | 0.00082277 | 1.9502e-07 | -1.2816e-07 | 0.0050411 | 0.0050411 | 0.0050411 | 0.97066 | -0.56539 | 0.97072 | -0.56414 | 1.3849
103 | -0.0022019 | -0.00055164 | 0.002202 | 0.00055149 | 6.1933e-08 | -1.4098e-07 | 0.0033688 | 0.0033687 | 0.0033688 | 0.9726 | -0.5271 | 0.97263 | -0.52651 | 0.92548
104 | 0.0022019 | 0.00055164 | -0.0022019 | -0.00055181 | 7.5379e-08 | -1.7156e-07 | 0.0033688 | 0.0033688 | 0.0033688 | 0.9726 | -0.5271 | 0.97256 | -0.52782 | 0.92551
105 | 0.00081473 | 0.00020416 | -0.00081473 | -0.00020419 | 1.562e-09 | -3.2265e-08 | 0.0012465 | 0.0012465 | 0.0012465 | 0.97256 | -0.52782 | 0.97256 | -0.52786 | 0.34245
106 | 0.011843 | 0.0029671 | -0.011841 | -0.0029663 | 1.6273e-06 | 8.7835e-07 | 0.018143 | 0.018144 | 0.018144 | 0.97124 | -0.55389 | 0.9711 | -0.55677 | 4.9845
107 | -0.011843 | -0.0029671 | 0.011844 | 0.0029677 | 9.8361e-07 | 5.3089e-07 | 0.018143 | 0.018143 | 0.018143 | 0.97124 | -0.55389 | 0.97133 | -0.55214 | 4.9845
108 | 0.011554 | 0.0028942 | -0.011553 | -0.002894 | 4.7161e-07 | 2.5219e-07 | 0.017703 | 0.017703 | 0.017703 | 0.9711 | -0.55677 | 0.97105 | -0.55763 | 4.8635
109 | -0.019973 | -0.0050053 | 0.01998 | 0.0050097 | 7.3326e-06 | 4.4342e-06 | 0.030597 | 0.030597 | 0.030597 | 0.97133 | -0.55214 | 0.97172 | -0.54444 | 8.4057
110 | 0.008129 | 0.0020376 | -0.0081273 | -0.0020369 | 1.7508e-06 | 7.4798e-07 | 0.012453 | 0.012453 | 0.012453 | 0.97133 | -0.55214 | 0.9711 | -0.55667 | 3.4213
111 | -0.0050162 | -0.0012557 | 0.0050167 | 0.0012557 | 5.1311e-07 | 4.2222e-08 | 0.0076888 | 0.0076887 | 0.0076888 | 0.97072 | -0.56414 | 0.97083 | -0.562 | 2.1123
112 | 0.0066977 | 0.0016786 | -0.0066969 | -0.0016783 | 7.4269e-07 | 2.4271e-07 | 0.010263 | 0.010263 | 0.010263 | 0.9711 | -0.55667 | 0.97098 | -0.55899 | 2.8195
113 | 0.0046658 | 0.0011693 | -0.0046656 | -0.0011693 | 2.311e-07 | -1.1806e-09 | 0.0071503 | 0.0071503 | 0.0071503 | 0.97098 | -0.55899 | 0.97093 | -0.56003 | 1.9644
114 | -0.01998 | -0.0050097 | 0.019989 | 0.0050154 | 9.3992e-06 | 5.6836e-06 | 0.030597 | 0.030596 | 0.030597 | 0.97172 | -0.54444 | 0.97222 | -0.53457 | 8.4057
115 | 0.0013133 | 0.00032899 | -0.0013133 | -0.00032915 | 2.0782e-08 | -1.5678e-07 | 0.0020101 | 0.0020101 | 0.0020101 | 0.97222 | -0.53457 | 0.9722 | -0.53491 | 0.55223
116 | -0.0037815 | -0.00094773 | 0.0037817 | 0.00094766 | 2.0598e-07 | -7.0503e-08 | 0.005795 | 0.0057949 | 0.005795 | 0.971 | -0.55877 | 0.97105 | -0.55763 | 1.592
117 | 0.0077714 | 0.0019463 | -0.0077701 | -0.0019458 | 1.214e-06 | 4.946e-07 | 0.011908 | 0.011908 | 0.011908 | 0.97105 | -0.55763 | 0.97089 | -0.56091 | 3.2715
118 | -0.0066947 | -0.0016762 | 0.006695 | 0.0016764 | 3.4552e-07 | 1.1291e-07 | 0.010261 | 0.01026 | 0.010261 | 0.97083 | -0.562 | 0.97089 | -0.56091 | 2.8188

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34566 | 0.088262

## res_load
| p_mw | q_mvar
0 | 0.0022798 | 0.00057138
1 | 0.0025853 | 0.00064793
2 | 0.00051622 | 0.00012938
3 | 0.0003998 | 0.0001002
4 | 0.000903 | 0.00022631
5 | 0.0034489 | 0.00086439
6 | 0.002654 | 0.00066516
7 | 0.0018951 | 0.00047495
8 | 0.00091199 | 0.00022857
9 | 0.00091597 | 0.00022956
10 | 0.00034389 | 8.6187e-05
11 | 0.0014298 | 0.00035834
12 | 0.0040566 | 0.0010167
13 | 0.0019353 | 0.00048503
14 | 0.00049997 | 0.00012531
15 | 0.020672 | 0.0051809
16 | 0.010486 | 0.002628
17 | 0.00055595 | 0.00013933
18 | 0.019524 | 0.0048932
19 | 0.061472 | 0.015406
20 | 0.0012023 | 0.00030133
21 | 0.0044143 | 0.0011063
22 | 0.00021484 | 5.3844e-05
23 | 0.0022965 | 0.00057556
24 | 0.0036246 | 0.00090842
25 | 0.0022934 | 0.00057478
26 | 0.0022965 | 0.00057556
27 | 0.0027057 | 0.0006781
28 | 0.0027071 | 0.00067847
29 | 0.002707 | 0.00067843
30 | 0.0027042 | 0.00067773
31 | 0.011522 | 0.0028877
32 | 0.0026133 | 0.00065495
33 | 0.068774 | 0.017236
34 | 0.0098498 | 0.0024686
35 | 0.00603 | 0.0015113
36 | 0.017021 | 0.004266
37 | 0.00017331 | 4.3437e-05
38 | 0.0018491 | 0.00046342
39 | 0.00056633 | 0.00014194
40 | 0.001564 | 0.00039198
41 | 0.00021484 | 5.3844e-05
42 | 0.0013456 | 0.00033724
43 | 0.00066758 | 0.00016731
44 | 0.00071448 | 0.00017907
45 | 0.00071481 | 0.00017915
46 | 0.0058791 | 0.0014735
47 | 0.00043026 | 0.00010783
48 | 0.00029138 | 7.3027e-05
49 | 0.00027087 | 6.7886e-05
50 | 0.0018926 | 0.00047433
51 | 0.00066262 | 0.00016607
52 | 0.0041987 | 0.0010523
53 | 0.0028482 | 0.00071382
54 | 0.0015266 | 0.0003826
55 | 0.0058943 | 0.0014773
56 | 0.00073215 | 0.00018349
57 | 0.00092743 | 0.00023243
58 | 0.00096516 | 0.00024189
59 | 0.00074683 | 0.00018717
60 | 0.00063779 | 0.00015984
61 | 0.00093857 | 0.00023523
62 | 0.0013131 | 0.0003291
63 | 0.0013871 | 0.00034765
64 | 0.00028748 | 7.205e-05
65 | 0.0017273 | 0.00043289
66 | 0.0014296 | 0.00035829
67 | 0.0020311 | 0.00050904
68 | 0.0046656 | 0.0011693
69 | 0.0013133 | 0.00032915
70 | 0.0037815 | 0.00094773
71 | 0.00081473 | 0.00020419
72 | 0.001678 | 0.00042054
73 | 0.0010751 | 0.00026945

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1