## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_119-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_119-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_119-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_119-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_119-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_119-3_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_119-3_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_119-3_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_119-3_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_119-3_0_3_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_119-3_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_119-3_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_119-3_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_119-3_0_3_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_119-3_0_3_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_119-3_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_119-3_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_119-3_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_119-3_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_119-3_0_3_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_119-3_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_119-3_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_119-3_0_3_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_119-3_0_3_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_119-3_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_119-3_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_119-3_0_3_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_119-3_0_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_119-3_0_3_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_119-3_0_3_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_119-3_0_3_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_119-3_0_3_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_119-3_0_3_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_119-3_0_3_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_119-3_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_119-3_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_119-3_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_119-3_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_119-3_0_3_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_119-3_0_3_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_119-3_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_119-3_0_3_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_119-3_0_3_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_119-3_0_3_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_119-3_0_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_119-3_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_119-3_0_3_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_119-3_0_3_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_119-3_0_3_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_119-3_0_3_node_46 | 0.4 | n |  | TRUE
50 | bus_MV_357_0_node_21 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_119-3_0_3_load_0 | 0 | 0.0022878 | 0.00057338 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_119-3_0_3_load_1 | 1 | 0.0038313 | 0.00096022 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_119-3_0_3_load_2 | 2 | 0.0012196 | 0.00030566 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_119-3_0_3_load_4 | 4 | 0.0012195 | 0.00030564 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_119-3_0_3_load_10 | 5 | 0.0014457 | 0.00036233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_119-3_0_3_load_11 | 6 | 0.0012568 | 0.00031498 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_119-3_0_3_load_17 | 8 | 0.003084 | 0.00077293 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_119-3_0_3_load_5 | 11 | 0.052315 | 0.013111 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_119-3_0_3_load_9 | 12 | 0.048302 | 0.012106 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_119-3_0_3_load_52 | 13 | 0.0079887 | 0.0020022 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_119-3_0_3_load_12 | 16 | 0.00099006 | 0.00024813 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_119-3_0_3_load_13 | 17 | 0.0016242 | 0.00040706 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_119-3_0_3_load_15 | 18 | 0.0059737 | 0.0014972 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_119-3_0_3_load_33 | 19 | 0.0023862 | 0.00059804 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_119-3_0_3_load_22 | 20 | 0.0020784 | 0.00052089 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_119-3_0_3_load_19 | 21 | 0.0056567 | 0.0014177 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_119-3_0_3_load_34 | 22 | 0.0030806 | 0.00077208 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_119-3_0_3_load_20 | 24 | 0.005117 | 0.0012824 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_119-3_0_3_load_43 | 27 | 0.0010335 | 0.00025903 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_119-3_0_3_load_53 | 28 | 0.0051772 | 0.0012975 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_119-3_0_3_load_37 | 29 | 0.00076323 | 0.00019128 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_119-3_0_3_load_42 | 30 | 0.0012927 | 0.00032397 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_119-3_0_3_load_38 | 31 | 0.0053683 | 0.0013454 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_119-3_0_3_load_23 | 32 | 0.0013404 | 0.00033594 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_119-3_0_3_load_24 | 33 | 0.00079049 | 0.00019812 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_119-3_0_3_load_25 | 34 | 0.0017005 | 0.00042617 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_119-3_0_3_load_26 | 35 | 0.00073224 | 0.00018352 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_119-3_0_3_load_29 | 36 | 0.0013523 | 0.00033893 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_119-3_0_3_load_27 | 37 | 0.00082736 | 0.00020736 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_119-3_0_3_load_35 | 38 | 0.00081988 | 0.00020548 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_119-3_0_3_load_28 | 39 | 0.0015801 | 0.000396 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_119-3_0_3_load_30 | 40 | 0.0014172 | 0.00035517 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_119-3_0_3_load_32 | 41 | 0.0020676 | 0.00051819 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_119-3_0_3_load_36 | 42 | 0.001287 | 0.00032256 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_119-3_0_3_load_47 | 43 | 0.0010986 | 0.00027532 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_119-3_0_3_load_40 | 44 | 0.059732 | 0.01497 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_119-3_0_3_load_41 | 45 | 0.0049834 | 0.001249 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_119-3_0_3_load_50 | 46 | 0.0012584 | 0.0003154 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_119-3_0_3_load_48 | 47 | 0.0027483 | 0.00068879 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_119-3_0_3_load_45 | 48 | 0.0018921 | 0.00047421 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_119-3_0_3_load_46 | 49 | 0.001781 | 0.00044637 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_119-3_0_3_line_0 |  | 0 | 1 | 0.0033049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_119-3_0_3_line_1 |  | 0 | 2 | 0.0002356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_119-3_0_3_line_2 |  | 1 | 3 | 0.026665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_119-3_0_3_line_3 |  | 2 | 4 | 0.0049932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_119-3_0_3_line_4 |  | 3 | 5 | 0.011758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_119-3_0_3_line_5 |  | 3 | 6 | 0.006549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_119-3_0_3_line_6 |  | 4 | 7 | 0.050235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_119-3_0_3_line_7 |  | 5 | 8 | 0.042102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_119-3_0_3_line_8 |  | 6 | 9 | 0.016029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_119-3_0_3_line_9 |  | 7 | 10 | 0.026709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_119-3_0_3_line_10 |  | 8 | 14 | 0.041517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_119-3_0_3_line_11 |  | 9 | 15 | 0.006492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_119-3_0_3_line_12 |  | 9 | 16 | 0.025889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_119-3_0_3_line_13 |  | 10 | 12 | 0.014883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_119-3_0_3_line_14 |  | 10 | 11 | 0.031092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_119-3_0_3_line_15 |  | 13 | 14 | 0.022871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_119-3_0_3_line_16 |  | 15 | 20 | 0.014069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_119-3_0_3_line_17 |  | 15 | 21 | 0.016511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_119-3_0_3_line_18 |  | 16 | 17 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_119-3_0_3_line_19 |  | 17 | 18 | 0.0010057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_119-3_0_3_line_20 |  | 18 | 19 | 0.021419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_119-3_0_3_line_21 |  | 19 | 22 | 0.0011949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_119-3_0_3_line_22 |  | 20 | 23 | 0.019578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_119-3_0_3_line_23 |  | 21 | 24 | 0.034045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_119-3_0_3_line_24 |  | 22 | 42 | 0.030743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_119-3_0_3_line_25 |  | 23 | 30 | 0.0074084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_119-3_0_3_line_26 |  | 23 | 31 | 0.022337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_119-3_0_3_line_27 |  | 24 | 25 | 0.0056591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_119-3_0_3_line_28 |  | 25 | 26 | 0.014491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_119-3_0_3_line_29 |  | 25 | 27 | 0.011924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_119-3_0_3_line_30 |  | 26 | 28 | 0.041853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_119-3_0_3_line_31 |  | 27 | 29 | 0.00084593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_119-3_0_3_line_32 |  | 29 | 37 | 0.0071809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_119-3_0_3_line_33 |  | 30 | 43 | 0.0019702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_119-3_0_3_line_34 |  | 32 | 33 | 0.024204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_119-3_0_3_line_35 |  | 32 | 34 | 0.029912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_119-3_0_3_line_36 |  | 33 | 35 | 0.011141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_119-3_0_3_line_37 |  | 33 | 36 | 0.064675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_119-3_0_3_line_38 |  | 34 | 37 | 0.012739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_119-3_0_3_line_39 |  | 35 | 38 | 0.0089706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_119-3_0_3_line_40 |  | 36 | 39 | 0.033212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_119-3_0_3_line_41 |  | 39 | 40 | 0.015786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_119-3_0_3_line_42 |  | 40 | 41 | 0.0092515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_119-3_0_3_line_43 |  | 43 | 48 | 0.005229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_119-3_0_3_line_44 |  | 44 | 45 | 0.022869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_119-3_0_3_line_45 |  | 44 | 46 | 0.17698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_119-3_0_3_line_46 |  | 46 | 47 | 0.018914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_119-3_0_3_line_47 |  | 47 | 49 | 0.039845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_119-3_0_3_line_48 |  | 48 | 49 | 0.007157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_119-3_0_3_trafo_4 | 0.63 MVA 20/0.4 kV | 50 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2699911.0208 | 1243092.1523 | 2699914.1811 | 1243093.1193
1 | 2699911.0208 | 1243092.1523 | 2699910.7956 | 1243092.0834
2 | 2699939.6793 | 1243100.9216 | 2699914.1811 | 1243093.1193
3 | 2699906.0209 | 1243090.6223 | 2699910.7956 | 1243092.0834
4 | 2699939.6793 | 1243100.9216 | 2699935.5436 | 1243093.7798 | 2699934.028 | 1243090.6195
5 | 2699939.6793 | 1243100.9216 | 2699939.9437 | 1243101.382 | 2699942.9554 | 1243106.5922
6 | 2699861.7478 | 1243067.1282 | 2699877.9995 | 1243075.7639 | 2699900.9913 | 1243089.0833 | 2699906.0209 | 1243090.6223
7 | 2699920.1838 | 1243051.0779 | 2699922.2705 | 1243061.8095 | 2699927.4955 | 1243076.9981 | 2699934.028 | 1243090.6195
8 | 2699952.7813 | 1243119.2563 | 2699942.9554 | 1243106.5922
9 | 2699836.2732 | 1243074.6387 | 2699848.7485 | 1243072.7471 | 2699861.7478 | 1243067.1282
10 | 2699912.2594 | 1243010.3237 | 2699920.1838 | 1243051.0779
11 | 2699957.0301 | 1243124.1761 | 2699952.7813 | 1243119.2563
12 | 2699952.7813 | 1243119.2563 | 2699959.0824 | 1243111.8568 | 2699966.3074 | 1243103.0161 | 2699968.6424 | 1243098.8765
13 | 2699836.2732 | 1243074.6387 | 2699821.5166 | 1243076.881
14 | 2699836.2732 | 1243074.6387 | 2699831.2742 | 1243043.9507
15 | 2699912.2594 | 1243010.3237 | 2699898.3918 | 1243014.082 | 2699892.8849 | 1243020.561
16 | 2699957.0301 | 1243124.1761 | 2699951.8421 | 1243133.7183 | 2699950.8283 | 1243136.7611
17 | 2699957.0301 | 1243124.1761 | 2699964.2602 | 1243130.2804 | 2699970.1118 | 1243134.2104
18 | 2699968.6424 | 1243098.8765 | 2699973.2351 | 1243090.7345 | 2699975.6843 | 1243082.1473
19 | 2699975.6843 | 1243082.1473 | 2699975.9601 | 1243081.1802
20 | 2699981.835 | 1243060.5828 | 2699975.9601 | 1243081.1802
21 | 2699981.835 | 1243060.5828 | 2699982.1627 | 1243059.4337
22 | 2699944.8242 | 1243155.3945 | 2699948.2908 | 1243144.3778 | 2699950.8283 | 1243136.7611
23 | 2699998.7931 | 1243152.542 | 2699981.3109 | 1243141.732 | 2699970.1118 | 1243134.2104
24 | 2699990.519 | 1243029.848 | 2699985.3997 | 1243048.0845 | 2699982.1627 | 1243059.4337
25 | 2699944.8242 | 1243155.3945 | 2699946.5556 | 1243160.7611 | 2699946.7188 | 1243162.523
26 | 2699944.8242 | 1243155.3945 | 2699936.0956 | 1243159.7064 | 2699929.0249 | 1243164.3353 | 2699925.8341 | 1243166.9894
27 | 2700003.6064 | 1243155.5182 | 2699998.7931 | 1243152.542
28 | 2700015.9586 | 1243163.1545 | 2700003.6064 | 1243155.5182
29 | 2700003.6064 | 1243155.5182 | 2700007.5071 | 1243144.2508
30 | 2700015.9586 | 1243163.1545 | 2700006.1275 | 1243181.2916 | 2699998.3183 | 1243199.6741 | 2699997.8073 | 1243200.8148
31 | 2700007.5071 | 1243144.2508 | 2700007.7839 | 1243143.4515
32 | 2700007.7839 | 1243143.4515 | 2700010.1331 | 1243136.6657
33 | 2699946.7188 | 1243162.523 | 2699946.9006 | 1243164.4848
34 | 2700024.0284 | 1243072.0824 | 2700016.5214 | 1243095.0923
35 | 2700011.2473 | 1243124.1085 | 2700010.8752 | 1243116.2884 | 2700010.9444 | 1243112.1864 | 2700016.5214 | 1243095.0923
36 | 2700024.0284 | 1243072.0824 | 2700027.484 | 1243061.4906
37 | 2700024.0284 | 1243072.0824 | 2700082.3985 | 1243099.936
38 | 2700011.2473 | 1243124.1085 | 2700011.5673 | 1243130.8334 | 2700010.1625 | 1243136.5808 | 2700010.1331 | 1243136.6657
39 | 2700030.2664 | 1243052.9624 | 2700027.484 | 1243061.4906
40 | 2700082.3985 | 1243099.936 | 2700092.907 | 1243072.3488 | 2700095.415 | 1243069.6413
41 | 2700108.3616 | 1243061.6829 | 2700100.8073 | 1243063.8199 | 2700095.415 | 1243069.6413
42 | 2700117.4695 | 1243060.4806 | 2700111.9356 | 1243060.6719 | 2700108.3616 | 1243061.6829
43 | 2699947.383 | 1243169.6915 | 2699946.9006 | 1243164.4848
44 | 2699777.612 | 1243275.9803 | 2699756.1578 | 1243283.9004
45 | 2699949.8832 | 1243235.4077 | 2699777.612 | 1243275.9803
46 | 2699949.8832 | 1243235.4077 | 2699950.7878 | 1243228.1063 | 2699950.6364 | 1243216.5505
47 | 2699948.0434 | 1243176.818 | 2699950.4572 | 1243202.8703 | 2699950.6364 | 1243216.5505
48 | 2699947.383 | 1243169.6915 | 2699948.0434 | 1243176.818

## bus_geodata
| x | y | coords
0 | 2699911.0208 | 1243092.1523
1 | 2699914.1811 | 1243093.1193
2 | 2699910.7956 | 1243092.0834
3 | 2699939.6793 | 1243100.9216
4 | 2699906.0209 | 1243090.6223
5 | 2699934.028 | 1243090.6195
6 | 2699942.9554 | 1243106.5922
7 | 2699861.7478 | 1243067.1282
8 | 2699920.1838 | 1243051.0779
9 | 2699952.7813 | 1243119.2563
10 | 2699836.2732 | 1243074.6387
11 | 2699831.2742 | 1243043.9507
12 | 2699821.5166 | 1243076.881
13 | 2699892.8849 | 1243020.561
14 | 2699912.2594 | 1243010.3237
15 | 2699957.0301 | 1243124.1761
16 | 2699968.6424 | 1243098.8765
17 | 2699975.6843 | 1243082.1473
18 | 2699975.9601 | 1243081.1802
19 | 2699981.835 | 1243060.5828
20 | 2699950.8283 | 1243136.7611
21 | 2699970.1118 | 1243134.2104
22 | 2699982.1627 | 1243059.4337
23 | 2699944.8242 | 1243155.3945
24 | 2699998.7931 | 1243152.542
25 | 2700003.6064 | 1243155.5182
26 | 2700015.9586 | 1243163.1545
27 | 2700007.5071 | 1243144.2508
28 | 2699997.8073 | 1243200.8148
29 | 2700007.7839 | 1243143.4515
30 | 2699946.7188 | 1243162.523
31 | 2699925.8341 | 1243166.9894
32 | 2700016.5214 | 1243095.0923
33 | 2700024.0284 | 1243072.0824
34 | 2700011.2473 | 1243124.1085
35 | 2700027.484 | 1243061.4906
36 | 2700082.3985 | 1243099.936
37 | 2700010.1331 | 1243136.6657
38 | 2700030.2664 | 1243052.9624
39 | 2700095.415 | 1243069.6413
40 | 2700108.3616 | 1243061.6829
41 | 2700117.4695 | 1243060.4806
42 | 2699990.519 | 1243029.848
43 | 2699946.9006 | 1243164.4848
44 | 2699777.612 | 1243275.9803
45 | 2699756.1578 | 1243283.9004
46 | 2699949.8832 | 1243235.4077
47 | 2699950.6364 | 1243216.5505
48 | 2699947.383 | 1243169.6915
49 | 2699948.0434 | 1243176.818
50 | 2699939.6793 | 1243100.9216

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99964 | -0.0067939 | 0.0022878 | 0.00057338
1 | 0.99942 | -0.010991 | 0.0038313 | 0.00096022
2 | 0.99966 | -0.0064901 | 0.0012196 | 0.00030566
3 | 0.99768 | -0.044028 | 0 | 0
4 | 1 | 0 | -0.25403 | -0.064286
5 | 0.99754 | -0.046607 | 0.0014457 | 0.00036233
6 | 0.9969 | -0.05886 | 0.0012568 | 0.00031498
7 | 0.99538 | -0.088508 | 0 | 0
8 | 0.99712 | -0.054778 | 0.003084 | 0.00077293
9 | 0.99501 | -0.094905 | 0 | 0
10 | 0.99292 | -0.1359 | 0 | 0
11 | 0.99143 | -0.1647 | 0.052315 | 0.013111
12 | 0.99226 | -0.14862 | 0.048302 | 0.012106
13 | 0.99665 | -0.0638 | 0.0079887 | 0.0020022
14 | 0.99682 | -0.060595 | 0 | 0
15 | 0.99433 | -0.10779 | 0 | 0
16 | 0.99464 | -0.1019 | 0.00099006 | 0.00024813
17 | 0.99441 | -0.10652 | 0.0016242 | 0.00040706
18 | 0.99439 | -0.10675 | 0.0059737 | 0.0014972
19 | 0.99426 | -0.1093 | 0.0023862 | 0.00059804
20 | 0.99326 | -0.12821 | 0.0020784 | 0.00052089
21 | 0.99387 | -0.11663 | 0.0056567 | 0.0014177
22 | 0.99426 | -0.10939 | 0.0030806 | 0.00077208
23 | 0.9918 | -0.15597 | 0 | 0
24 | 0.9931 | -0.1315 | 0.005117 | 0.0012824
25 | 0.993 | -0.13346 | 0 | 0
26 | 0.99293 | -0.13479 | 0 | 0
27 | 0.99285 | -0.13651 | 0.0010335 | 0.00025903
28 | 0.99274 | -0.13862 | 0.0051772 | 0.0012975
29 | 0.99284 | -0.13671 | 0.00076323 | 0.00019128
30 | 0.99129 | -0.1658 | 0.0012927 | 0.00032397
31 | 0.99169 | -0.1581 | 0.0053683 | 0.0013454
32 | 0.99234 | -0.14632 | 0.0013404 | 0.00033594
33 | 0.99215 | -0.15008 | 0.00079049 | 0.00019812
34 | 0.99262 | -0.14097 | 0.0017005 | 0.00042617
35 | 0.99213 | -0.15038 | 0.00073224 | 0.00018352
36 | 0.99177 | -0.15743 | 0.0013523 | 0.00033893
37 | 0.99275 | -0.13831 | 0.00082736 | 0.00020736
38 | 0.99212 | -0.15051 | 0.00081988 | 0.00020548
39 | 0.99161 | -0.16041 | 0.0015801 | 0.000396
40 | 0.99156 | -0.16139 | 0.0014172 | 0.00035517
41 | 0.99154 | -0.16173 | 0.0020676 | 0.00051819
42 | 0.99422 | -0.11009 | 0.001287 | 0.00032256
43 | 0.99115 | -0.16836 | 0.0010986 | 0.00027532
44 | 0.97598 | -0.46249 | 0.059732 | 0.01497
45 | 0.97588 | -0.46457 | 0.0049834 | 0.001249
46 | 0.98663 | -0.25516 | 0.0012584 | 0.0003154
47 | 0.98779 | -0.23284 | 0.0027483 | 0.00068879
48 | 0.9908 | -0.17508 | 0.0018921 | 0.00047421
49 | 0.99033 | -0.18405 | 0.001781 | 0.00044637
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14744 | 0.037675 | -0.14741 | -0.037656 | 2.992e-05 | 1.9062e-05 | 0.21973 | 0.21973 | 0.21973 | 0.99964 | -0.0067939 | 0.99942 | -0.010991 | 30.1831
1 | -0.14973 | -0.038248 | 0.14973 | 0.03825 | 2.1995e-06 | 1.4015e-06 | 0.22314 | 0.22314 | 0.22314 | 0.99964 | -0.0067939 | 0.99966 | -0.0064901 | 30.6509
2 | 0.14358 | 0.036695 | -0.14335 | -0.03655 | 0.00022903 | 0.00014588 | 0.21403 | 0.21403 | 0.21403 | 0.99942 | -0.010991 | 0.99768 | -0.044028 | 29.3996
3 | -0.15095 | -0.038555 | 0.151 | 0.038585 | 4.7377e-05 | 3.019e-05 | 0.22495 | 0.22495 | 0.22495 | 0.99966 | -0.0064901 | 1 | 0 | 30.9002
4 | 0.012528 | 0.0031418 | -0.012526 | -0.003141 | 1.5395e-06 | 8.3174e-07 | 0.018686 | 0.018686 | 0.018686 | 0.99768 | -0.044028 | 0.99754 | -0.046607 | 5.1334
5 | 0.13083 | 0.033408 | -0.13073 | -0.033348 | 9.3713e-05 | 5.9891e-05 | 0.19534 | 0.19534 | 0.19534 | 0.99768 | -0.044028 | 0.9969 | -0.05886 | 53.6658
6 | 0.10138 | 0.025701 | -0.10095 | -0.025427 | 0.00042925 | 0.00027406 | 0.15095 | 0.15095 | 0.15095 | 1 | 0 | 0.99538 | -0.088508 | 41.4702
7 | 0.011081 | 0.0027787 | -0.011076 | -0.0027765 | 4.3136e-06 | 2.2113e-06 | 0.016529 | 0.016529 | 0.016529 | 0.99754 | -0.046607 | 0.99712 | -0.054778 | 4.541
8 | 0.12948 | 0.033033 | -0.12925 | -0.032889 | 0.00022498 | 0.00014378 | 0.19347 | 0.19347 | 0.19347 | 0.9969 | -0.05886 | 0.99501 | -0.094905 | 53.1504
9 | 0.10095 | 0.025427 | -0.10072 | -0.025281 | 0.00022823 | 0.00014572 | 0.15095 | 0.15095 | 0.15095 | 0.99538 | -0.088508 | 0.99292 | -0.1359 | 41.4703
10 | 0.0079922 | 0.0020035 | -0.00799 | -0.0020026 | 2.2148e-06 | 8.7608e-07 | 0.011927 | 0.011927 | 0.011927 | 0.99712 | -0.054778 | 0.99682 | -0.060595 | 3.2767
11 | 0.1139 | 0.029039 | -0.11383 | -0.028994 | 7.0779e-05 | 4.5215e-05 | 0.17051 | 0.17051 | 0.17051 | 0.99501 | -0.094905 | 0.99433 | -0.10779 | 46.8432
12 | 0.015351 | 0.0038497 | -0.015346 | -0.0038468 | 5.1172e-06 | 2.9388e-06 | 0.022958 | 0.022958 | 0.022958 | 0.99501 | -0.094905 | 0.99464 | -0.1019 | 6.3073
13 | 0.048331 | 0.012124 | -0.048302 | -0.012106 | 2.9283e-05 | 1.8549e-05 | 0.072434 | 0.072434 | 0.072434 | 0.99292 | -0.1359 | 0.99226 | -0.14862 | 19.8995
14 | 0.052386 | 0.013157 | -0.052315 | -0.013111 | 7.1882e-05 | 4.5603e-05 | 0.078517 | 0.078518 | 0.078518 | 0.99292 | -0.1359 | 0.99143 | -0.1647 | 21.5708
15 | -0.0079887 | -0.0020022 | 0.00799 | 0.0020026 | 1.2201e-06 | 4.8277e-07 | 0.011927 | 0.011927 | 0.011927 | 0.99665 | -0.0638 | 0.99682 | -0.060595 | 3.2767
16 | 0.083407 | 0.021357 | -0.083325 | -0.021304 | 8.2407e-05 | 5.2558e-05 | 0.12498 | 0.12498 | 0.12498 | 0.99433 | -0.10779 | 0.99326 | -0.12821 | 34.3352
17 | 0.030421 | 0.0076375 | -0.030408 | -0.0076295 | 1.2835e-05 | 8.0005e-06 | 0.04553 | 0.04553 | 0.04553 | 0.99433 | -0.10779 | 0.99387 | -0.11663 | 12.5082
18 | 0.014356 | 0.0035986 | -0.014353 | -0.0035969 | 3.1616e-06 | 1.7863e-06 | 0.021477 | 0.021477 | 0.021477 | 0.99464 | -0.1019 | 0.99441 | -0.10652 | 5.9004
19 | 0.012729 | 0.0031898 | -0.012729 | -0.0031897 | 1.3681e-07 | 7.4515e-08 | 0.019047 | 0.019047 | 0.019047 | 0.99441 | -0.10652 | 0.99439 | -0.10675 | 5.2327
20 | 0.0067548 | 0.0016926 | -0.006754 | -0.0016923 | 8.2062e-07 | 2.4738e-07 | 0.010108 | 0.010108 | 0.010108 | 0.99439 | -0.10675 | 0.99426 | -0.1093 | 2.7769
21 | 0.0043677 | 0.0010943 | -0.0043677 | -0.0010943 | 1.9145e-08 | -3.2434e-09 | 0.0065367 | 0.0065367 | 0.0065367 | 0.99426 | -0.1093 | 0.99426 | -0.10939 | 1.7958
22 | 0.081246 | 0.020783 | -0.081137 | -0.020714 | 0.00010903 | 6.9528e-05 | 0.12187 | 0.12187 | 0.12187 | 0.99326 | -0.12821 | 0.9918 | -0.15597 | 33.4798
23 | 0.024752 | 0.0062119 | -0.024734 | -0.0062011 | 1.7535e-05 | 1.0782e-05 | 0.037061 | 0.037061 | 0.037061 | 0.99387 | -0.11663 | 0.9931 | -0.1315 | 10.1816
24 | 0.0012871 | 0.00032219 | -0.001287 | -0.00032256 | 4.2775e-08 | -3.7132e-07 | 0.0019261 | 0.0019263 | 0.0019263 | 0.99426 | -0.10939 | 0.99422 | -0.11009 | 0.5292
25 | 0.075768 | 0.019368 | -0.075732 | -0.019345 | 3.5986e-05 | 2.2935e-05 | 0.11381 | 0.11381 | 0.11381 | 0.9918 | -0.15597 | 0.99129 | -0.1658 | 31.2669
26 | 0.0053688 | 0.0013455 | -0.0053683 | -0.0013454 | 5.4348e-07 | 5.9599e-08 | 0.0080549 | 0.008055 | 0.008055 | 0.9918 | -0.15597 | 0.99169 | -0.1581 | 2.2129
27 | 0.019617 | 0.0049186 | -0.019615 | -0.0049175 | 1.8336e-06 | 1.1003e-06 | 0.029394 | 0.029394 | 0.029394 | 0.9931 | -0.1315 | 0.993 | -0.13346 | 8.0753
28 | 0.0051785 | 0.0012976 | -0.0051782 | -0.0012976 | 3.2722e-07 | 2.1976e-08 | 0.0077599 | 0.00776 | 0.00776 | 0.993 | -0.13346 | 0.99293 | -0.13479 | 2.1319
29 | 0.014437 | 0.0036199 | -0.014435 | -0.0036187 | 2.0927e-06 | 1.1851e-06 | 0.021634 | 0.021634 | 0.021634 | 0.993 | -0.13346 | 0.99285 | -0.13651 | 5.9435
30 | 0.0051782 | 0.0012976 | -0.0051772 | -0.0012975 | 9.4512e-07 | 6.3636e-08 | 0.00776 | 0.0077602 | 0.0077602 | 0.99293 | -0.13479 | 0.99274 | -0.13862 | 2.1319
31 | 0.013401 | 0.0033597 | -0.013401 | -0.0033596 | 1.2797e-07 | 7.0963e-08 | 0.020085 | 0.020085 | 0.020085 | 0.99285 | -0.13651 | 0.99284 | -0.13671 | 5.5179
32 | 0.012638 | 0.0031683 | -0.012637 | -0.0031678 | 9.6612e-07 | 5.2546e-07 | 0.018941 | 0.018941 | 0.018941 | 0.99284 | -0.13671 | 0.99275 | -0.13831 | 5.2037
33 | 0.07444 | 0.019021 | -0.07443 | -0.019015 | 9.2467e-06 | 5.8925e-06 | 0.11187 | 0.11187 | 0.11187 | 0.99129 | -0.1658 | 0.99115 | -0.16836 | 30.7339
34 | 0.0087645 | 0.0021963 | -0.008763 | -0.0021956 | 1.5677e-06 | 6.9069e-07 | 0.013142 | 0.013142 | 0.013142 | 0.99234 | -0.14632 | 0.99215 | -0.15008 | 3.6106
35 | -0.010105 | -0.0025322 | 0.010108 | 0.0025335 | 2.5754e-06 | 1.2617e-06 | 0.015152 | 0.015152 | 0.015152 | 0.99234 | -0.14632 | 0.99262 | -0.14097 | 4.1627
36 | 0.0015521 | 0.00038875 | -0.0015521 | -0.00038888 | 2.264e-08 | -1.2939e-07 | 0.0023278 | 0.0023279 | 0.0023279 | 0.99215 | -0.15008 | 0.99213 | -0.15038 | 0.63952
37 | 0.0064203 | 0.0016087 | -0.0064181 | -0.0016081 | 2.2488e-06 | 6.0433e-07 | 0.0096291 | 0.0096294 | 0.0096294 | 0.99215 | -0.15008 | 0.99177 | -0.15743 | 2.6454
38 | -0.011808 | -0.0029597 | 0.011809 | 0.0029605 | 1.4968e-06 | 7.9328e-07 | 0.017701 | 0.017701 | 0.017701 | 0.99262 | -0.14097 | 0.99275 | -0.13831 | 4.863
39 | 0.00081988 | 0.00020537 | -0.00081988 | -0.00020548 | 5.0865e-09 | -1.1259e-07 | 0.0012296 | 0.0012297 | 0.0012297 | 0.99213 | -0.15038 | 0.99212 | -0.15051 | 0.33782
40 | 0.0050657 | 0.0012692 | -0.005065 | -0.0012692 | 7.1944e-07 | 3.1944e-08 | 0.0076004 | 0.0076005 | 0.0076005 | 0.99177 | -0.15743 | 0.99161 | -0.16041 | 2.0881
41 | 0.003485 | 0.00087316 | -0.0034848 | -0.00087326 | 1.6189e-07 | -1.0002e-07 | 0.0052294 | 0.0052295 | 0.0052295 | 0.99161 | -0.16041 | 0.99156 | -0.16139 | 1.4367
42 | 0.0020676 | 0.00051809 | -0.0020676 | -0.00051819 | 3.3401e-08 | -9.7954e-08 | 0.0031028 | 0.0031029 | 0.0031029 | 0.99156 | -0.16139 | 0.99154 | -0.16173 | 0.85244
43 | 0.073332 | 0.01874 | -0.073308 | -0.018725 | 2.3823e-05 | 1.5179e-05 | 0.11022 | 0.11022 | 0.11022 | 0.99115 | -0.16836 | 0.9908 | -0.17508 | 30.2808
44 | 0.0049839 | 0.001249 | -0.0049834 | -0.001249 | 4.9518e-07 | 3.1153e-08 | 0.0075986 | 0.0075987 | 0.0075987 | 0.97598 | -0.46249 | 0.97588 | -0.46457 | 2.0876
45 | -0.064715 | -0.016219 | 0.065362 | 0.01663 | 0.00064612 | 0.00041128 | 0.098667 | 0.098667 | 0.098667 | 0.97598 | -0.46249 | 0.98663 | -0.25516 | 27.1064
46 | -0.06662 | -0.016946 | 0.066692 | 0.016991 | 7.1731e-05 | 4.5666e-05 | 0.10056 | 0.10056 | 0.10056 | 0.98663 | -0.25516 | 0.98779 | -0.23284 | 27.6276
47 | -0.06944 | -0.01768 | 0.069604 | 0.017785 | 0.00016381 | 0.00010433 | 0.1047 | 0.1047 | 0.1047 | 0.98779 | -0.23284 | 0.99033 | -0.18405 | 28.765
48 | 0.071416 | 0.018251 | -0.071385 | -0.018231 | 3.0947e-05 | 1.9714e-05 | 0.10738 | 0.10738 | 0.10738 | 0.9908 | -0.17508 | 0.99033 | -0.18405 | 29.5001

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25525 | 0.064592

## res_load
| p_mw | q_mvar
0 | 0.0022878 | 0.00057338
1 | 0.0038313 | 0.00096022
2 | 0.0012196 | 0.00030566
3 | 0.0012195 | 0.00030564
4 | 0.0014457 | 0.00036233
5 | 0.0012568 | 0.00031498
6 | 0.003084 | 0.00077293
7 | 0.052315 | 0.013111
8 | 0.048302 | 0.012106
9 | 0.0079887 | 0.0020022
10 | 0.00099006 | 0.00024813
11 | 0.0016242 | 0.00040706
12 | 0.0059737 | 0.0014972
13 | 0.0023862 | 0.00059804
14 | 0.0020784 | 0.00052089
15 | 0.0056567 | 0.0014177
16 | 0.0030806 | 0.00077208
17 | 0.005117 | 0.0012824
18 | 0.0010335 | 0.00025903
19 | 0.0051772 | 0.0012975
20 | 0.00076323 | 0.00019128
21 | 0.0012927 | 0.00032397
22 | 0.0053683 | 0.0013454
23 | 0.0013404 | 0.00033594
24 | 0.00079049 | 0.00019812
25 | 0.0017005 | 0.00042617
26 | 0.00073224 | 0.00018352
27 | 0.0013523 | 0.00033893
28 | 0.00082736 | 0.00020736
29 | 0.00081988 | 0.00020548
30 | 0.0015801 | 0.000396
31 | 0.0014172 | 0.00035517
32 | 0.0020676 | 0.00051819
33 | 0.001287 | 0.00032256
34 | 0.0010986 | 0.00027532
35 | 0.059732 | 0.01497
36 | 0.0049834 | 0.001249
37 | 0.0012584 | 0.0003154
38 | 0.0027483 | 0.00068879
39 | 0.0018921 | 0.00047421
40 | 0.001781 | 0.00044637

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1