## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_12-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_12-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_12-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_12-2_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_12-2_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_12-2_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_12-2_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_12-2_0_3_node_59 | 0.4 | n |  | TRUE
8 | bus_LV_12-2_0_3_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_12-2_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_12-2_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_12-2_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_12-2_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_12-2_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_12-2_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_12-2_0_3_node_136 | 0.4 | n |  | TRUE
16 | bus_LV_12-2_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_12-2_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_12-2_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_12-2_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_12-2_0_3_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_12-2_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_12-2_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_12-2_0_3_node_69 | 0.4 | n |  | TRUE
24 | bus_LV_12-2_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_12-2_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_12-2_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_12-2_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_12-2_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_12-2_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_12-2_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_12-2_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_12-2_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_12-2_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_12-2_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_12-2_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_12-2_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_12-2_0_3_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_12-2_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_12-2_0_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_12-2_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_12-2_0_3_node_270 | 0.4 | n |  | TRUE
42 | bus_LV_12-2_0_3_node_203 | 0.4 | n |  | TRUE
43 | bus_LV_12-2_0_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_12-2_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_12-2_0_3_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_12-2_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_12-2_0_3_node_70 | 0.4 | n |  | TRUE
48 | bus_LV_12-2_0_3_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_12-2_0_3_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_12-2_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_12-2_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_12-2_0_3_node_197 | 0.4 | n |  | TRUE
53 | bus_LV_12-2_0_3_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_12-2_0_3_node_193 | 0.4 | n |  | TRUE
55 | bus_LV_12-2_0_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_12-2_0_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_12-2_0_3_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_12-2_0_3_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_12-2_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_12-2_0_3_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_12-2_0_3_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_12-2_0_3_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_12-2_0_3_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_12-2_0_3_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_12-2_0_3_node_78 | 0.4 | n |  | TRUE
66 | bus_LV_12-2_0_3_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_12-2_0_3_node_110 | 0.4 | n |  | TRUE
68 | bus_LV_12-2_0_3_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_12-2_0_3_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_12-2_0_3_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_12-2_0_3_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_12-2_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_12-2_0_3_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_12-2_0_3_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_12-2_0_3_node_264 | 0.4 | n |  | TRUE
76 | bus_LV_12-2_0_3_node_123 | 0.4 | n |  | TRUE
77 | bus_LV_12-2_0_3_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_12-2_0_3_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_12-2_0_3_node_96 | 0.4 | n |  | TRUE
80 | bus_LV_12-2_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_12-2_0_3_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_12-2_0_3_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_12-2_0_3_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_12-2_0_3_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_12-2_0_3_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_12-2_0_3_node_126 | 0.4 | n |  | TRUE
87 | bus_LV_12-2_0_3_node_92 | 0.4 | n |  | TRUE
88 | bus_LV_12-2_0_3_node_93 | 0.4 | n |  | TRUE
89 | bus_LV_12-2_0_3_node_94 | 0.4 | n |  | TRUE
90 | bus_LV_12-2_0_3_node_95 | 0.4 | n |  | TRUE
91 | bus_LV_12-2_0_3_node_135 | 0.4 | n |  | TRUE
92 | bus_LV_12-2_0_3_node_268 | 0.4 | n |  | TRUE
93 | bus_LV_12-2_0_3_node_125 | 0.4 | n |  | TRUE
94 | bus_LV_12-2_0_3_node_98 | 0.4 | n |  | TRUE
95 | bus_LV_12-2_0_3_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_12-2_0_3_node_100 | 0.4 | n |  | TRUE
97 | bus_LV_12-2_0_3_node_101 | 0.4 | n |  | TRUE
98 | bus_LV_12-2_0_3_node_102 | 0.4 | n |  | TRUE
99 | bus_LV_12-2_0_3_node_103 | 0.4 | n |  | TRUE
100 | bus_LV_12-2_0_3_node_104 | 0.4 | n |  | TRUE
101 | bus_LV_12-2_0_3_node_105 | 0.4 | n |  | TRUE
102 | bus_LV_12-2_0_3_node_106 | 0.4 | n |  | TRUE
103 | bus_LV_12-2_0_3_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_12-2_0_3_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_12-2_0_3_node_269 | 0.4 | n |  | TRUE
106 | bus_LV_12-2_0_3_node_111 | 0.4 | n |  | TRUE
107 | bus_LV_12-2_0_3_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_12-2_0_3_node_113 | 0.4 | n |  | TRUE
109 | bus_LV_12-2_0_3_node_124 | 0.4 | n |  | TRUE
110 | bus_LV_12-2_0_3_node_134 | 0.4 | n |  | TRUE
111 | bus_LV_12-2_0_3_node_137 | 0.4 | n |  | TRUE
112 | bus_LV_12-2_0_3_node_263 | 0.4 | n |  | TRUE
113 | bus_LV_12-2_0_3_node_191 | 0.4 | n |  | TRUE
114 | bus_LV_12-2_0_3_node_192 | 0.4 | n |  | TRUE
115 | bus_LV_12-2_0_3_node_194 | 0.4 | n |  | TRUE
116 | bus_LV_12-2_0_3_node_195 | 0.4 | n |  | TRUE
117 | bus_LV_12-2_0_3_node_201 | 0.4 | n |  | TRUE
118 | bus_LV_12-2_0_3_node_196 | 0.4 | n |  | TRUE
119 | bus_LV_12-2_0_3_node_198 | 0.4 | n |  | TRUE
120 | bus_LV_12-2_0_3_node_199 | 0.4 | n |  | TRUE
121 | bus_LV_12-2_0_3_node_200 | 0.4 | n |  | TRUE
122 | bus_LV_12-2_0_3_node_210 | 0.4 | n |  | TRUE
123 | bus_LV_12-2_0_3_node_209 | 0.4 | n |  | TRUE
124 | bus_LV_12-2_0_3_node_211 | 0.4 | n |  | TRUE
125 | bus_LV_12-2_0_3_node_271 | 0.4 | n |  | TRUE
126 | bus_MV_349_1_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_12-2_0_3_load_0 | 0 | 0.0010085 | 0.00025275 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_12-2_0_3_load_1 | 1 | 0.0027357 | 0.00068563 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_12-2_0_3_load_3 | 3 | 0.0042337 | 0.0010611 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_12-2_0_3_load_5 | 5 | 0.0016258 | 0.00040746 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_12-2_0_3_load_15 | 6 | 0.001539 | 0.00038572 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_12-2_0_3_load_59 | 7 | 0.0011643 | 0.00029181 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_12-2_0_3_load_55 | 8 | 0.0020594 | 0.00051613 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_12-2_0_3_load_11 | 9 | 0.0017423 | 0.00043666 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_12-2_0_3_load_6 | 10 | 0.0011145 | 0.00027933 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_12-2_0_3_load_9 | 13 | 0.00086691 | 0.00021727 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_12-2_0_3_load_10 | 14 | 0.001254 | 0.00031429 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_12-2_0_3_load_13 | 16 | 0.0005701 | 0.00014288 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_12-2_0_3_load_12 | 17 | 0.0025092 | 0.00062888 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_12-2_0_3_load_16 | 18 | 0.0013108 | 0.00032851 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_12-2_0_3_load_17 | 19 | 0.0040341 | 0.001011 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_12-2_0_3_load_18 | 20 | 0.0012498 | 0.00031323 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_12-2_0_3_load_19 | 21 | 0.0010156 | 0.00025453 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_12-2_0_3_load_69 | 23 | 0.0010169 | 0.00025485 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_12-2_0_3_load_27 | 24 | 0.00081899 | 0.00020526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_12-2_0_3_load_25 | 25 | 0.0044277 | 0.0011097 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_12-2_0_3_load_31 | 26 | 0.010154 | 0.0025447 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_12-2_0_3_load_21 | 27 | 0.0072422 | 0.0018151 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_12-2_0_3_load_22 | 28 | 0.0037143 | 0.00093089 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_12-2_0_3_load_23 | 29 | 0.0023473 | 0.0005883 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_12-2_0_3_load_24 | 30 | 0.008179 | 0.0020499 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_12-2_0_3_load_26 | 31 | 0.0027902 | 0.00069928 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_12-2_0_3_load_37 | 32 | 0.0010482 | 0.0002627 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_12-2_0_3_load_28 | 33 | 0.00077218 | 0.00019353 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_12-2_0_3_load_29 | 34 | 0.00084989 | 0.000213 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_12-2_0_3_load_30 | 35 | 0.0014264 | 0.0003575 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_12-2_0_3_load_32 | 37 | 0.0084276 | 0.0021122 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_12-2_0_3_load_34 | 38 | 0.00085403 | 0.00021404 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_12-2_0_3_load_203 | 42 | 0.00060567 | 0.0001518 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_12-2_0_3_load_36 | 43 | 0.0026645 | 0.00066779 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_12-2_0_3_load_39 | 44 | 0.00083148 | 0.00020839 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_12-2_0_3_load_40 | 45 | 0.0048659 | 0.0012195 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_12-2_0_3_load_46 | 46 | 0.0028212 | 0.00070705 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_12-2_0_3_load_70 | 47 | 0.0019753 | 0.00049505 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_12-2_0_3_load_45 | 48 | 0.0018775 | 0.00047056 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_12-2_0_3_load_60 | 49 | 0.000727 | 0.0001822 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_12-2_0_3_load_48 | 51 | 0.0036216 | 0.00090766 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_12-2_0_3_load_197 | 52 | 0.0025876 | 0.00064851 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_12-2_0_3_load_49 | 53 | 0.0027104 | 0.00067929 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_12-2_0_3_load_50 | 55 | 0.012095 | 0.0030313 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_12-2_0_3_load_51 | 56 | 0.0021223 | 0.0005319 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_12-2_0_3_load_52 | 57 | 0.0056117 | 0.0014064 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_12-2_0_3_load_53 | 58 | 0.005517 | 0.0013827 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_12-2_0_3_load_62 | 60 | 0.0036463 | 0.00091384 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_12-2_0_3_load_57 | 63 | 0.00040723 | 0.00010206 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_12-2_0_3_load_78 | 65 | 0.0020023 | 0.00050183 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_12-2_0_3_load_115 | 66 | 0.0016646 | 0.0004172 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_12-2_0_3_load_110 | 67 | 0.0012201 | 0.0003058 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_12-2_0_3_load_63 | 69 | 0.0024789 | 0.00062128 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_12-2_0_3_load_64 | 70 | 0.0029396 | 0.00073673 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_12-2_0_3_load_65 | 71 | 0.0023986 | 0.00060116 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_12-2_0_3_load_66 | 72 | 0.0010882 | 0.00027273 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_12-2_0_3_load_67 | 73 | 0.00092745 | 0.00023244 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_12-2_0_3_load_68 | 74 | 0.0040788 | 0.0010222 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_12-2_0_3_load_264 | 75 | 0.0013054 | 0.00032717 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_12-2_0_3_load_123 | 76 | 0.0058243 | 0.0014597 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_12-2_0_3_load_71 | 77 | 0.0011549 | 0.00028945 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_12-2_0_3_load_72 | 78 | 0.0012969 | 0.00032504 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_12-2_0_3_load_73 | 80 | 0.004409 | 0.001105 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_12-2_0_3_load_74 | 81 | 0.00048309 | 0.00012107 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_12-2_0_3_load_75 | 82 | 0.0012337 | 0.00030919 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_12-2_0_3_load_76 | 83 | 0.0024926 | 0.00062471 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_12-2_0_3_load_77 | 84 | 0.00037851 | 9.4865e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_12-2_0_3_load_79 | 85 | 0.0014725 | 0.00036903 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_12-2_0_3_load_126 | 86 | 0.0004829 | 0.00012103 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_12-2_0_3_load_92 | 87 | 0.0017456 | 0.00043748 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_12-2_0_3_load_93 | 88 | 0.001912 | 0.0004792 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_12-2_0_3_load_94 | 89 | 0.0036357 | 0.0009112 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_12-2_0_3_load_95 | 90 | 0.0017363 | 0.00043515 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_12-2_0_3_load_135 | 91 | 0.0013101 | 0.00032834 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_12-2_0_3_load_268 | 92 | 0.0061351 | 0.0015376 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_12-2_0_3_load_125 | 93 | 0.0037422 | 0.00093789 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_12-2_0_3_load_98 | 94 | 0.0039692 | 0.00099477 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_12-2_0_3_load_99 | 95 | 0.0033085 | 0.00082918 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_12-2_0_3_load_100 | 96 | 0.0016971 | 0.00042534 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_12-2_0_3_load_101 | 97 | 0.0014462 | 0.00036244 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_12-2_0_3_load_102 | 98 | 0.00097758 | 0.000245 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_12-2_0_3_load_103 | 99 | 0.0020215 | 0.00050663 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_12-2_0_3_load_104 | 100 | 0.0021425 | 0.00053696 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_12-2_0_3_load_105 | 101 | 0.0011989 | 0.00030048 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_12-2_0_3_load_106 | 102 | 0.0021254 | 0.00053268 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_12-2_0_3_load_107 | 103 | 0.0014199 | 0.00035585 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_12-2_0_3_load_114 | 104 | 0.0010449 | 0.00026187 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_12-2_0_3_load_269 | 105 | 0.0033967 | 0.00085129 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_12-2_0_3_load_111 | 106 | 0.001377 | 0.0003451 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_12-2_0_3_load_112 | 107 | 0.0016925 | 0.00042419 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_12-2_0_3_load_113 | 108 | 0.001698 | 0.00042555 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_12-2_0_3_load_124 | 109 | 0.0022152 | 0.00055517 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_12-2_0_3_load_134 | 110 | 0.0011117 | 0.00027863 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_12-2_0_3_load_137 | 111 | 0.00085641 | 0.00021464 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_12-2_0_3_load_263 | 112 | 0.0016062 | 0.00040256 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_12-2_0_3_load_191 | 113 | 0.0013927 | 0.00034904 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_12-2_0_3_load_192 | 114 | 0.001043 | 0.0002614 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_12-2_0_3_load_194 | 115 | 0.0010322 | 0.00025868 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_12-2_0_3_load_195 | 116 | 0.0018246 | 0.00045728 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_12-2_0_3_load_196 | 118 | 0.0014131 | 0.00035416 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_12-2_0_3_load_198 | 119 | 0.0014048 | 0.00035207 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_12-2_0_3_load_199 | 120 | 0.0016416 | 0.00041144 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_12-2_0_3_load_200 | 121 | 0.0093199 | 0.0023358 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_12-2_0_3_load_210 | 122 | 0.0014142 | 0.00035442 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_12-2_0_3_load_209 | 123 | 0.0014297 | 0.00035833 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_12-2_0_3_load_211 | 124 | 0.001365 | 0.0003421 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_12-2_0_3_load_271 | 125 | 0.0026758 | 0.00067061 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_12-2_0_3_line_0 |  | 0 | 1 | 0.022854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_12-2_0_3_line_1 |  | 0 | 2 | 0.019375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_12-2_0_3_line_2 |  | 1 | 3 | 0.025431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_12-2_0_3_line_3 |  | 2 | 4 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_12-2_0_3_line_4 |  | 2 | 5 | 0.039351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_12-2_0_3_line_5 |  | 3 | 6 | 0.024178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_12-2_0_3_line_6 |  | 4 | 7 | 0.025184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_12-2_0_3_line_7 |  | 4 | 8 | 0.0043621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_12-2_0_3_line_8 |  | 5 | 9 | 0.0060944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_12-2_0_3_line_9 |  | 7 | 67 | 0.023136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_12-2_0_3_line_10 |  | 8 | 62 | 0.0062972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_12-2_0_3_line_11 |  | 9 | 17 | 0.014951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_12-2_0_3_line_12 |  | 10 | 11 | 0.047027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_12-2_0_3_line_13 |  | 10 | 12 | 0.032692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_12-2_0_3_line_14 |  | 11 | 13 | 0.043201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_12-2_0_3_line_15 |  | 12 | 14 | 0.017594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_12-2_0_3_line_16 |  | 13 | 15 | 0.01474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_12-2_0_3_line_17 |  | 14 | 16 | 0.016525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_12-2_0_3_line_18 |  | 15 | 111 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_12-2_0_3_line_19 |  | 15 | 110 | 0.017694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_12-2_0_3_line_20 |  | 18 | 19 | 0.023422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_12-2_0_3_line_21 |  | 18 | 20 | 0.00011645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_12-2_0_3_line_22 |  | 19 | 21 | 0.0091247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_12-2_0_3_line_23 |  | 20 | 22 | 0.057535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_12-2_0_3_line_24 |  | 21 | 23 | 0.00016103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_12-2_0_3_line_25 |  | 22 | 24 | 0.026496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_12-2_0_3_line_26 |  | 22 | 25 | 0.0095201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_12-2_0_3_line_27 |  | 22 | 26 | 0.056507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_12-2_0_3_line_28 |  | 23 | 77 | 0.017239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_12-2_0_3_line_29 |  | 24 | 32 | 0.0069261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_12-2_0_3_line_30 |  | 25 | 31 | 0.033522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_12-2_0_3_line_31 |  | 26 | 37 | 0.0072628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_12-2_0_3_line_32 |  | 27 | 28 | 0.00083396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_12-2_0_3_line_33 |  | 27 | 29 | 0.0212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_12-2_0_3_line_34 |  | 28 | 30 | 0.0010512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_12-2_0_3_line_35 |  | 30 | 31 | 0.023412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_12-2_0_3_line_36 |  | 32 | 43 | 0.028165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_12-2_0_3_line_37 |  | 33 | 34 | 0.0010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_12-2_0_3_line_38 |  | 34 | 35 | 0.01621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_12-2_0_3_line_39 |  | 35 | 36 | 0.024087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_12-2_0_3_line_40 |  | 36 | 38 | 0.0047777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_12-2_0_3_line_41 |  | 36 | 39 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_12-2_0_3_line_42 |  | 38 | 40 | 0.016975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_12-2_0_3_line_43 |  | 39 | 41 | 0.007979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_12-2_0_3_line_44 |  | 39 | 42 | 0.0016332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_12-2_0_3_line_45 |  | 40 | 44 | 0.010794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_12-2_0_3_line_46 |  | 40 | 45 | 0.014146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_12-2_0_3_line_47 |  | 41 | 125 | 0.01229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_12-2_0_3_line_48 |  | 42 | 116 | 0.022924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_12-2_0_3_line_49 |  | 44 | 46 | 0.0065147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_12-2_0_3_line_50 |  | 45 | 47 | 0.014791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_12-2_0_3_line_51 |  | 46 | 50 | 0.0061541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_12-2_0_3_line_52 |  | 47 | 59 | 0.017928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_12-2_0_3_line_53 |  | 48 | 49 | 0.008591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_12-2_0_3_line_54 |  | 49 | 68 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_12-2_0_3_line_55 |  | 50 | 51 | 0.0065091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_12-2_0_3_line_56 |  | 51 | 52 | 0.053725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_12-2_0_3_line_57 |  | 52 | 118 | 0.013364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_12-2_0_3_line_58 |  | 53 | 54 | 0.0059103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_12-2_0_3_line_59 |  | 54 | 116 | 0.027418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_12-2_0_3_line_60 |  | 54 | 113 | 0.021066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_12-2_0_3_line_61 |  | 55 | 56 | 0.010052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_12-2_0_3_line_62 |  | 55 | 57 | 0.0063648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_12-2_0_3_line_63 |  | 56 | 58 | 0.013177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_12-2_0_3_line_64 |  | 57 | 59 | 0.021793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_12-2_0_3_line_65 |  | 58 | 60 | 0.013443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_12-2_0_3_line_66 |  | 59 | 61 | 0.010414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_12-2_0_3_line_67 |  | 60 | 68 | 0.032952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_12-2_0_3_line_68 |  | 61 | 92 | 0.015142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_12-2_0_3_line_69 |  | 61 | 93 | 0.010131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_12-2_0_3_line_70 |  | 62 | 63 | 0.023465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_12-2_0_3_line_71 |  | 62 | 64 | 0.012183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_12-2_0_3_line_72 |  | 63 | 65 | 0.011609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_12-2_0_3_line_73 |  | 64 | 66 | 0.01128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_12-2_0_3_line_74 |  | 65 | 85 | 0.00031342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_12-2_0_3_line_75 |  | 66 | 108 | 0.0096328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_12-2_0_3_line_76 |  | 68 | 69 | 0.030518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_12-2_0_3_line_77 |  | 70 | 71 | 0.018072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_12-2_0_3_line_78 |  | 70 | 72 | 0.0002943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_12-2_0_3_line_79 |  | 71 | 73 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_12-2_0_3_line_80 |  | 72 | 74 | 0.01966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_12-2_0_3_line_81 |  | 73 | 75 | 0.013977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_12-2_0_3_line_82 |  | 74 | 76 | 0.0093721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_12-2_0_3_line_83 |  | 75 | 79 | 0.0039518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_12-2_0_3_line_84 |  | 76 | 109 | 0.01099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_12-2_0_3_line_85 |  | 77 | 78 | 0.005516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_12-2_0_3_line_86 |  | 78 | 79 | 0.0083305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_12-2_0_3_line_87 |  | 79 | 89 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_12-2_0_3_line_88 |  | 80 | 81 | 0.003347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_12-2_0_3_line_89 |  | 80 | 82 | 0.00013927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_12-2_0_3_line_90 |  | 81 | 83 | 0.032895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_12-2_0_3_line_91 |  | 82 | 84 | 0.0033896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_12-2_0_3_line_92 |  | 83 | 85 | 0.013584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_12-2_0_3_line_93 |  | 84 | 86 | 0.0070309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_12-2_0_3_line_94 |  | 86 | 97 | 0.005568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_12-2_0_3_line_95 |  | 87 | 88 | 0.00051695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_12-2_0_3_line_96 |  | 87 | 89 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_12-2_0_3_line_97 |  | 88 | 90 | 0.0081906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_12-2_0_3_line_98 |  | 90 | 91 | 0.012152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_12-2_0_3_line_99 |  | 91 | 110 | 0.0014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_12-2_0_3_line_100 |  | 92 | 105 | 0.00012435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_12-2_0_3_line_101 |  | 93 | 109 | 0.0013636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_12-2_0_3_line_102 |  | 94 | 95 | 0.0088087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_12-2_0_3_line_103 |  | 94 | 96 | 0.00043374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_12-2_0_3_line_104 |  | 95 | 97 | 0.025782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_12-2_0_3_line_105 |  | 96 | 98 | 0.011866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_12-2_0_3_line_106 |  | 99 | 100 | 0.013008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_12-2_0_3_line_107 |  | 99 | 101 | 0.00063978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_12-2_0_3_line_108 |  | 100 | 102 | 0.0010749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_12-2_0_3_line_109 |  | 101 | 103 | 0.0092588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_12-2_0_3_line_110 |  | 102 | 104 | 3.5171e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_12-2_0_3_line_111 |  | 103 | 105 | 0.010912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_12-2_0_3_line_112 |  | 104 | 107 | 0.0097563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_12-2_0_3_line_113 |  | 106 | 107 | 0.0072621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_12-2_0_3_line_114 |  | 106 | 108 | 0.024418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_12-2_0_3_line_115 |  | 111 | 112 | 0.011304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_12-2_0_3_line_116 |  | 113 | 114 | 0.006365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_12-2_0_3_line_117 |  | 114 | 115 | 0.0017083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_12-2_0_3_line_118 |  | 115 | 117 | 0.016981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_12-2_0_3_line_119 |  | 117 | 122 | 0.023424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_12-2_0_3_line_120 |  | 117 | 121 | 0.015351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_12-2_0_3_line_121 |  | 118 | 119 | 0.0052231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_12-2_0_3_line_122 |  | 120 | 121 | 0.0097016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_12-2_0_3_line_123 |  | 122 | 123 | 0.0063101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_12-2_0_3_line_124 |  | 123 | 124 | 0.00094657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_12-2_0_3_trafo_68 | 0.63 MVA 20/0.4 kV | 126 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2679871.5714 | 1232898.256 | 2679849.6046 | 1232904.5611
1 | 2679890.3389 | 1232893.4428 | 2679872.111 | 1232898.1011 | 2679871.5714 | 1232898.256
2 | 2679826.0137 | 1232914.0136 | 2679829.3203 | 1232912.8477 | 2679847.6879 | 1232905.1112 | 2679849.6046 | 1232904.5611
3 | 2679890.3389 | 1232893.4428 | 2679914.8972 | 1232888.2026
4 | 2679890.3389 | 1232893.4428 | 2679891.3781 | 1232903.4415 | 2679889.882 | 1232908.8362 | 2679885.0816 | 1232915.5764 | 2679875.1287 | 1232927.3608
5 | 2679803.4516 | 1232922.6303 | 2679808.5428 | 1232920.1738 | 2679826.0137 | 1232914.0136
6 | 2679914.8972 | 1232888.2026 | 2679893.8775 | 1232874.3318
7 | 2679914.8972 | 1232888.2026 | 2679919.1611 | 1232887.2817
8 | 2679871.1963 | 1232932.0169 | 2679875.1287 | 1232927.3608
9 | 2679874.5667 | 1232861.5886 | 2679893.8775 | 1232874.3318
10 | 2679925.3163 | 1232885.9522 | 2679919.1611 | 1232887.2817
11 | 2679871.1963 | 1232932.0169 | 2679868.2846 | 1232935.4644 | 2679862.129 | 1232943.8943
12 | 2679818.0248 | 1233053.0373 | 2679810.63 | 1233074.8087 | 2679802.8843 | 1233092.8282 | 2679800.5895 | 1233096.6058
13 | 2679781.917 | 1233123.3568 | 2679791.9435 | 1233110.8383 | 2679800.5895 | 1233096.6058
14 | 2679818.0248 | 1233053.0373 | 2679829.0499 | 1233052.9965 | 2679859.6107 | 1233042.9297
15 | 2679781.917 | 1233123.3568 | 2679776.0532 | 1233121.9105 | 2679764.6807 | 1233119.8694
16 | 2679873.6105 | 1233038.3182 | 2679859.6107 | 1233042.9297
17 | 2679764.6807 | 1233119.8694 | 2679748.4159 | 1233116.9502
18 | 2679873.6105 | 1233038.3182 | 2679878.7659 | 1233056.6984
19 | 2679873.6105 | 1233038.3182 | 2679883.9411 | 1233035.3104 | 2679890.7961 | 1233034.2666
20 | 2679933.3485 | 1233065.6066 | 2679954.1785 | 1233076.3167
21 | 2679954.2821 | 1233076.37 | 2679954.1785 | 1233076.3167
22 | 2679938.1538 | 1233057.8502 | 2679937.6976 | 1233058.638 | 2679933.3485 | 1233065.6066 | 2679933.3485 | 1233065.6066
23 | 2679985.2148 | 1233114.5714 | 2679982.4839 | 1233111.577 | 2679982.9473 | 1233106.4019 | 2679985.3033 | 1233104.0653 | 2679986.334 | 1233101.7442 | 2679986.1617 | 1233099.9184 | 2679983.3098 | 1233095.7883 | 2679979.7865 | 1233090.9042 | 2679977.3165 | 1233088.2136 | 2679954.2821 | 1233076.37
24 | 2679938.1538 | 1233057.8502 | 2679938.2344 | 1233057.7108
25 | 2679985.2148 | 1233114.5714 | 2679997.5766 | 1233091.1359
26 | 2679985.2148 | 1233114.5714 | 2679980.3444 | 1233122.7513
27 | 2679985.2148 | 1233114.5714 | 2680032.3317 | 1233145.7655
28 | 2679946.872 | 1233042.7914 | 2679938.2344 | 1233057.7108
29 | 2680000.808 | 1233085.0098 | 2679997.5766 | 1233091.1359
30 | 2679980.3444 | 1233122.7513 | 2679968.9929 | 1233141.8164 | 2679960.7989 | 1233149.646
31 | 2680031.196 | 1233152.939 | 2680032.3317 | 1233145.7655
32 | 2679943.0251 | 1233166.4547 | 2679942.417 | 1233167.0254
33 | 2679927.1281 | 1233181.7089 | 2679934.5729 | 1233174.3872 | 2679942.417 | 1233167.0254
34 | 2679943.0251 | 1233166.4547 | 2679943.7916 | 1233165.7353
35 | 2679943.7916 | 1233165.7353 | 2679953.284 | 1233156.8266 | 2679960.7989 | 1233149.646
36 | 2680013.9484 | 1233060.0979 | 2680000.808 | 1233085.0098
37 | 2680048.3353 | 1233052.5125 | 2680048.544 | 1233051.5316
38 | 2680054.4783 | 1233036.7186 | 2680050.2844 | 1233043.3535 | 2680048.544 | 1233051.5316
39 | 2680068.3045 | 1233017.0113 | 2680058.6401 | 1233030.1346 | 2680054.4783 | 1233036.7186
40 | 2680068.3045 | 1233017.0113 | 2680065.4692 | 1233013.1658
41 | 2680083.6858 | 1233019.0421 | 2680074.9009 | 1233020.8472 | 2680068.3045 | 1233017.0113
42 | 2680055.3956 | 1232999.5031 | 2680065.4692 | 1233013.1658
43 | 2680079.7608 | 1233025.994 | 2680083.6858 | 1233019.0421
44 | 2680083.6858 | 1233019.0421 | 2680085.1614 | 1233018.342
45 | 2680055.3956 | 1232999.5031 | 2680064.6432 | 1232993.9356
46 | 2680055.3956 | 1232999.5031 | 2680052.4629 | 1232995.1828 | 2680047.7064 | 1232989.1035 | 2680047.0563 | 1232988.0885
47 | 2680088.3189 | 1233034.8376 | 2680079.7608 | 1233025.994
48 | 2680085.1614 | 1233018.342 | 2680090.8644 | 1233015.6364 | 2680102.5024 | 1233007.2096 | 2680104.2783 | 1233005.8389
49 | 2680064.6432 | 1232993.9356 | 2680065.2585 | 1232993.5651 | 2680069.5855 | 1232989.7081
50 | 2680039.0784 | 1232975.633 | 2680047.0563 | 1232988.0885
51 | 2680074.1794 | 1232985.6131 | 2680069.5855 | 1232989.7081
52 | 2680032.6008 | 1232959.2906 | 2680032.8251 | 1232962.8739 | 2680033.5989 | 1232966.1421 | 2680035.3144 | 1232969.7566 | 2680039.0784 | 1232975.633
53 | 2680056.9967 | 1232855.2415 | 2680057.2005 | 1232846.6528
54 | 2680057.7347 | 1232866.3759 | 2680057.1157 | 1232862.8651 | 2680056.8966 | 1232859.4598 | 2680056.9967 | 1232855.2415
55 | 2680074.1794 | 1232985.6131 | 2680078.5571 | 1232980.796
56 | 2680078.5571 | 1232980.796 | 2680096.0305 | 1232961.5686 | 2680114.9014 | 1232941.2311 | 2680114.9014 | 1232941.2311
57 | 2680124.4331 | 1232931.8644 | 2680114.9014 | 1232941.2311
58 | 2680120.7079 | 1232984.5504 | 2680114.8129 | 1232984.9748
59 | 2680120.7079 | 1232984.5504 | 2680112.3423 | 1232999.6147 | 2680104.2783 | 1233005.8389
60 | 2680120.7079 | 1232984.5504 | 2680139.8085 | 1232982.5509 | 2680141.6594 | 1232982.356
61 | 2680043.3811 | 1232933.3003 | 2680047.1954 | 1232924.0004
62 | 2680043.3811 | 1232933.3003 | 2680040.9659 | 1232939.189
63 | 2680047.1954 | 1232924.0004 | 2680048.8343 | 1232920.0042 | 2680051.6964 | 1232911.6211
64 | 2680032.6008 | 1232959.2906 | 2680034.4543 | 1232953.7895 | 2680039.9091 | 1232941.7658 | 2680040.9659 | 1232939.189
65 | 2680051.6964 | 1232911.6211 | 2680056.0399 | 1232898.8986
66 | 2680032.6008 | 1232959.2906 | 2680022.2287 | 1232958.0613
67 | 2680057.7347 | 1232866.3759 | 2680058.2115 | 1232869.2065 | 2680058.4928 | 1232871.3673 | 2680058.622 | 1232889.3148 | 2680057.8842 | 1232893.4967 | 2680056.0399 | 1232898.8986
68 | 2680022.2287 | 1232958.0613 | 2680010.9481 | 1232947.9596
69 | 2680022.2287 | 1232958.0613 | 2680015.0489 | 1232965.2087
70 | 2679925.3163 | 1232885.9522 | 2679925.4779 | 1232869.443 | 2679927.8438 | 1232862.9031
71 | 2679937.4095 | 1232884.2136 | 2679925.3163 | 1232885.9522
72 | 2679927.8438 | 1232862.9031 | 2679931.2583 | 1232853.4652 | 2679932.0133 | 1232852.0854
73 | 2679937.4095 | 1232884.2136 | 2679946.6481 | 1232890.6859
74 | 2679932.1637 | 1232851.8104 | 2679932.0133 | 1232852.0854
75 | 2679953.9663 | 1232896.9331 | 2679948.2189 | 1232891.7864 | 2679946.6481 | 1232890.6859
76 | 2680057.7347 | 1232866.3759 | 2680070.416 | 1232864.8345 | 2680084.5165 | 1232862.4895 | 2680087.8857 | 1232861.7518
77 | 2679972.702 | 1233007.3651 | 2679985.5098 | 1232994.6149
78 | 2679985.7184 | 1232994.4073 | 2679985.5098 | 1232994.6149
79 | 2679972.702 | 1233007.3651 | 2679966.3793 | 1233013.6593 | 2679959.733 | 1233020.2117
80 | 2679985.7184 | 1232994.4073 | 2679999.6517 | 1232980.5366
81 | 2679948.6103 | 1233028.6142 | 2679957.3781 | 1233022.5333 | 2679959.733 | 1233020.2117
82 | 2680006.2937 | 1232973.9245 | 2679999.6517 | 1232980.5366
83 | 2679945.363 | 1233030.8663 | 2679948.6103 | 1233028.6142
84 | 2680014.0825 | 1232966.1707 | 2680006.2937 | 1232973.9245
85 | 2679949.6357 | 1233038.0176 | 2679946.872 | 1233042.7914
86 | 2679945.363 | 1233030.8663 | 2679949.6357 | 1233038.0176 | 2679949.6357 | 1233038.0176
87 | 2679945.363 | 1233030.8663 | 2679933.8152 | 1233033.7353 | 2679927.8204 | 1233033.9553
88 | 2679958.8889 | 1232809.8044 | 2679957.0249 | 1232812.5844
89 | 2679958.9664 | 1232809.6887 | 2679958.8889 | 1232809.8044
90 | 2679938.706 | 1232839.9067 | 2679957.0249 | 1232812.5844
91 | 2679958.9664 | 1232809.6887 | 2679960.8541 | 1232806.8733
92 | 2679938.706 | 1232839.9067 | 2679938.5477 | 1232840.1429 | 2679932.1637 | 1232851.8104
93 | 2679964.7695 | 1232801.0336 | 2679960.8541 | 1232806.8733
94 | 2679967.8702 | 1232796.4089 | 2679964.7695 | 1232801.0336
95 | 2679913.0314 | 1233034.0544 | 2679912.5145 | 1233034.046
96 | 2679927.8204 | 1233033.9553 | 2679921.3988 | 1233034.1909 | 2679913.0314 | 1233034.0544
97 | 2679912.5145 | 1233034.046 | 2679904.325 | 1233033.9124
98 | 2679892.1978 | 1233034.0532 | 2679894.2068 | 1233033.7473 | 2679904.325 | 1233033.9124
99 | 2679892.1978 | 1233034.0532 | 2679890.7961 | 1233034.2666
100 | 2680010.8555 | 1232947.8767 | 2680010.9481 | 1232947.9596
101 | 2680015.0489 | 1232965.2087 | 2680014.0825 | 1232966.1707
102 | 2679987.5358 | 1232767.9539 | 2679982.4866 | 1232775.1718
103 | 2679987.7845 | 1232767.5985 | 2679987.5358 | 1232767.9539
104 | 2679967.8702 | 1232796.4089 | 2679973.4052 | 1232788.1535 | 2679982.4866 | 1232775.1718
105 | 2679987.7845 | 1232767.5985 | 2679994.5864 | 1232757.8751
106 | 2679995.3522 | 1232933.9937 | 2679985.6617 | 1232925.3159
107 | 2679995.3522 | 1232933.9937 | 2679995.8288 | 1232934.4205
108 | 2679984.8609 | 1232924.5988 | 2679985.6617 | 1232925.3159
109 | 2680002.7263 | 1232940.5971 | 2679995.8288 | 1232934.4205
110 | 2679984.8347 | 1232924.5754 | 2679984.8609 | 1232924.5988
111 | 2680010.8555 | 1232947.8767 | 2680002.7263 | 1232940.5971
112 | 2679984.8347 | 1232924.5754 | 2679977.5666 | 1232918.0669
113 | 2679972.1566 | 1232913.2223 | 2679977.5666 | 1232918.0669
114 | 2679953.9663 | 1232896.9331 | 2679972.1566 | 1232913.2223
115 | 2679881.8186 | 1233067.582 | 2679878.7659 | 1233056.6984
116 | 2680147.9894 | 1232981.6894 | 2680141.6594 | 1232982.356
117 | 2680149.6883 | 1232981.5104 | 2680147.9894 | 1232981.6894
118 | 2680166.5754 | 1232979.732 | 2680149.6883 | 1232981.5104
119 | 2680166.5754 | 1232979.732 | 2680166.2696 | 1232984.9982 | 2680164.0747 | 1232989.4161 | 2680160.3355 | 1232993.8132 | 2680154.382 | 1232998.2822
120 | 2680166.5754 | 1232979.732 | 2680181.8419 | 1232978.1205
121 | 2680128.1585 | 1232928.2035 | 2680124.4331 | 1232931.8644
122 | 2680191.3797 | 1232976.5334 | 2680188.1482 | 1232977.4547 | 2680181.8419 | 1232978.1205
123 | 2680154.382 | 1232998.2822 | 2680149.3354 | 1233002.0703
124 | 2680148.5784 | 1233002.6386 | 2680149.3354 | 1233002.0703

## bus_geodata
| x | y | coords
0 | 2679871.5714 | 1232898.256
1 | 2679849.6046 | 1232904.5611
2 | 2679890.3389 | 1232893.4428
3 | 2679826.0137 | 1232914.0136
4 | 2679914.8972 | 1232888.2026
5 | 2679875.1287 | 1232927.3608
6 | 2679803.4516 | 1232922.6303
7 | 2679893.8775 | 1232874.3318
8 | 2679919.1611 | 1232887.2817
9 | 2679871.1963 | 1232932.0169
10 | 2679800.5895 | 1233096.6058
11 | 2679818.0248 | 1233053.0373
12 | 2679781.917 | 1233123.3568
13 | 2679859.6107 | 1233042.9297
14 | 2679764.6807 | 1233119.8694
15 | 2679873.6105 | 1233038.3182
16 | 2679748.4159 | 1233116.9502
17 | 2679862.129 | 1232943.8943
18 | 2679954.1785 | 1233076.3167
19 | 2679933.3485 | 1233065.6066
20 | 2679954.2821 | 1233076.37
21 | 2679938.1538 | 1233057.8502
22 | 2679985.2148 | 1233114.5714
23 | 2679938.2344 | 1233057.7108
24 | 2679997.5766 | 1233091.1359
25 | 2679980.3444 | 1233122.7513
26 | 2680032.3317 | 1233145.7655
27 | 2679942.417 | 1233167.0254
28 | 2679943.0251 | 1233166.4547
29 | 2679927.1281 | 1233181.7089
30 | 2679943.7916 | 1233165.7353
31 | 2679960.7989 | 1233149.646
32 | 2680000.808 | 1233085.0098
33 | 2680048.3353 | 1233052.5125
34 | 2680048.544 | 1233051.5316
35 | 2680054.4783 | 1233036.7186
36 | 2680068.3045 | 1233017.0113
37 | 2680031.196 | 1233152.939
38 | 2680065.4692 | 1233013.1658
39 | 2680083.6858 | 1233019.0421
40 | 2680055.3956 | 1232999.5031
41 | 2680079.7608 | 1233025.994
42 | 2680085.1614 | 1233018.342
43 | 2680013.9484 | 1233060.0979
44 | 2680064.6432 | 1232993.9356
45 | 2680047.0563 | 1232988.0885
46 | 2680069.5855 | 1232989.7081
47 | 2680039.0784 | 1232975.633
48 | 2680057.2005 | 1232846.6528
49 | 2680056.9967 | 1232855.2415
50 | 2680074.1794 | 1232985.6131
51 | 2680078.5571 | 1232980.796
52 | 2680114.9014 | 1232941.2311
53 | 2680114.8129 | 1232984.9748
54 | 2680120.7079 | 1232984.5504
55 | 2680043.3811 | 1232933.3003
56 | 2680047.1954 | 1232924.0004
57 | 2680040.9659 | 1232939.189
58 | 2680051.6964 | 1232911.6211
59 | 2680032.6008 | 1232959.2906
60 | 2680056.0399 | 1232898.8986
61 | 2680022.2287 | 1232958.0613
62 | 2679925.3163 | 1232885.9522
63 | 2679927.8438 | 1232862.9031
64 | 2679937.4095 | 1232884.2136
65 | 2679932.0133 | 1232852.0854
66 | 2679946.6481 | 1232890.6859
67 | 2679874.5667 | 1232861.5886
68 | 2680057.7347 | 1232866.3759
69 | 2680087.8857 | 1232861.7518
70 | 2679985.5098 | 1232994.6149
71 | 2679972.702 | 1233007.3651
72 | 2679985.7184 | 1232994.4073
73 | 2679959.733 | 1233020.2117
74 | 2679999.6517 | 1232980.5366
75 | 2679948.6103 | 1233028.6142
76 | 2680006.2937 | 1232973.9245
77 | 2679946.872 | 1233042.7914
78 | 2679949.6357 | 1233038.0176
79 | 2679945.363 | 1233030.8663
80 | 2679958.8889 | 1232809.8044
81 | 2679957.0249 | 1232812.5844
82 | 2679958.9664 | 1232809.6887
83 | 2679938.706 | 1232839.9067
84 | 2679960.8541 | 1232806.8733
85 | 2679932.1637 | 1232851.8104
86 | 2679964.7695 | 1232801.0336
87 | 2679913.0314 | 1233034.0544
88 | 2679912.5145 | 1233034.046
89 | 2679927.8204 | 1233033.9553
90 | 2679904.325 | 1233033.9124
91 | 2679892.1978 | 1233034.0532
92 | 2680010.9481 | 1232947.9596
93 | 2680015.0489 | 1232965.2087
94 | 2679987.5358 | 1232767.9539
95 | 2679982.4866 | 1232775.1718
96 | 2679987.7845 | 1232767.5985
97 | 2679967.8702 | 1232796.4089
98 | 2679994.5864 | 1232757.8751
99 | 2679995.3522 | 1232933.9937
100 | 2679985.6617 | 1232925.3159
101 | 2679995.8288 | 1232934.4205
102 | 2679984.8609 | 1232924.5988
103 | 2680002.7263 | 1232940.5971
104 | 2679984.8347 | 1232924.5754
105 | 2680010.8555 | 1232947.8767
106 | 2679972.1566 | 1232913.2223
107 | 2679977.5666 | 1232918.0669
108 | 2679953.9663 | 1232896.9331
109 | 2680014.0825 | 1232966.1707
110 | 2679890.7961 | 1233034.2666
111 | 2679878.7659 | 1233056.6984
112 | 2679881.8186 | 1233067.582
113 | 2680141.6594 | 1232982.356
114 | 2680147.9894 | 1232981.6894
115 | 2680149.6883 | 1232981.5104
116 | 2680104.2783 | 1233005.8389
117 | 2680166.5754 | 1232979.732
118 | 2680124.4331 | 1232931.8644
119 | 2680128.1585 | 1232928.2035
120 | 2680191.3797 | 1232976.5334
121 | 2680181.8419 | 1232978.1205
122 | 2680154.382 | 1232998.2822
123 | 2680149.3354 | 1233002.0703
124 | 2680148.5784 | 1233002.6386
125 | 2680088.3189 | 1233034.8376
126 | 2680022.2287 | 1232958.0613

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99089 | -0.17534 | 0.0010085 | 0.00025275
1 | 0.99071 | -0.17879 | 0.0027357 | 0.00068563
2 | 0.99105 | -0.17207 | 0 | 0
3 | 0.99057 | -0.1814 | 0.0042337 | 0.0010611
4 | 0.99141 | -0.16523 | 0 | 0
5 | 0.99084 | -0.17617 | 0.0016258 | 0.00040746
6 | 0.99054 | -0.18206 | 0.001539 | 0.00038572
7 | 0.99135 | -0.16629 | 0.0011643 | 0.00029181
8 | 0.99148 | -0.16385 | 0.0020594 | 0.00051613
9 | 0.99082 | -0.17663 | 0.0017423 | 0.00043666
10 | 0.99316 | -0.13102 | 0.0011145 | 0.00027933
11 | 0.99329 | -0.12857 | 0 | 0
12 | 0.99311 | -0.13207 | 0 | 0
13 | 0.9934 | -0.12633 | 0.00086691 | 0.00021727
14 | 0.99308 | -0.13264 | 0.001254 | 0.00031429
15 | 0.99346 | -0.12533 | 0 | 0
16 | 0.99307 | -0.1328 | 0.0005701 | 0.00014288
17 | 0.99079 | -0.1773 | 0.0025092 | 0.00062888
18 | 0.99081 | -0.17629 | 0.0013108 | 0.00032851
19 | 0.99198 | -0.1537 | 0.0040341 | 0.001011
20 | 0.9908 | -0.1764 | 0.0012498 | 0.00031323
21 | 0.99247 | -0.14426 | 0.0010156 | 0.00025453
22 | 0.98806 | -0.22948 | 0 | 0
23 | 0.99248 | -0.14409 | 0.0010169 | 0.00025485
24 | 0.98795 | -0.23162 | 0.00081899 | 0.00020526
25 | 0.98781 | -0.23436 | 0.0044277 | 0.0011097
26 | 0.9871 | -0.24824 | 0.010154 | 0.0025447
27 | 0.98658 | -0.2583 | 0.0072422 | 0.0018151
28 | 0.98659 | -0.25816 | 0.0037143 | 0.00093089
29 | 0.98654 | -0.25919 | 0.0023473 | 0.0005883
30 | 0.9866 | -0.25791 | 0.008179 | 0.0020499
31 | 0.98706 | -0.24891 | 0.0027902 | 0.00069928
32 | 0.98793 | -0.23208 | 0.0010482 | 0.0002627
33 | 0.99416 | -0.11212 | 0.00077218 | 0.00019353
34 | 0.99416 | -0.1121 | 0.00084989 | 0.000213
35 | 0.99419 | -0.11164 | 0.0014264 | 0.0003575
36 | 0.99426 | -0.11035 | 0 | 0
37 | 0.98704 | -0.24934 | 0.0084276 | 0.0021122
38 | 0.99438 | -0.10786 | 0.00085403 | 0.00021404
39 | 0.99386 | -0.11807 | 0 | 0
40 | 0.99486 | -0.098779 | 0 | 0
41 | 0.99384 | -0.11845 | 0 | 0
42 | 0.99382 | -0.11876 | 0.00060567 | 0.0001518
43 | 0.98786 | -0.23342 | 0.0026645 | 0.00066779
44 | 0.99473 | -0.10119 | 0.00083148 | 0.00020839
45 | 0.99541 | -0.088061 | 0.0048659 | 0.0012195
46 | 0.99466 | -0.10255 | 0.0028212 | 0.00070705
47 | 0.99606 | -0.075602 | 0.0019753 | 0.00049505
48 | 0.99541 | -0.08812 | 0.0018775 | 0.00047056
49 | 0.99543 | -0.087836 | 0.000727 | 0.0001822
50 | 0.99461 | -0.10353 | 0 | 0
51 | 0.99456 | -0.10456 | 0.0036216 | 0.00090766
52 | 0.99429 | -0.10968 | 0.0025876 | 0.00064851
53 | 0.99279 | -0.13877 | 0.0027104 | 0.00067929
54 | 0.9928 | -0.13849 | 0 | 0
55 | 0.99603 | -0.076119 | 0.012095 | 0.0030313
56 | 0.99588 | -0.079011 | 0.0021223 | 0.0005319
57 | 0.9962 | -0.072936 | 0.0056117 | 0.0014064
58 | 0.99571 | -0.082311 | 0.005517 | 0.0013827
59 | 0.99687 | -0.059901 | 0 | 0
60 | 0.99561 | -0.084376 | 0.0036463 | 0.00091384
61 | 0.99767 | -0.044576 | 0 | 0
62 | 0.99159 | -0.16164 | 0 | 0
63 | 0.99106 | -0.17194 | 0.00040723 | 0.00010206
64 | 0.99209 | -0.15201 | 0 | 0
65 | 0.9908 | -0.17696 | 0.0020023 | 0.00050183
66 | 0.99255 | -0.1431 | 0.0016646 | 0.0004172
67 | 0.99133 | -0.16679 | 0.0012201 | 0.0003058
68 | 0.99545 | -0.087323 | 0 | 0
69 | 0.99538 | -0.088654 | 0.0024789 | 0.00062128
70 | 0.99837 | -0.031102 | 0.0029396 | 0.00073673
71 | 0.99695 | -0.058085 | 0.0023986 | 0.00060116
72 | 0.99839 | -0.030648 | 0.0010882 | 0.00027273
73 | 0.99557 | -0.084649 | 0.00092745 | 0.00023244
74 | 1 | 0 | -0.25895 | -0.065157
75 | 0.99452 | -0.10481 | 0.0013054 | 0.00032717
76 | 0.99929 | -0.013591 | 0.0058243 | 0.0014597
77 | 0.99343 | -0.12567 | 0.0011549 | 0.00028945
78 | 0.99374 | -0.11967 | 0.0012969 | 0.00032504
79 | 0.99423 | -0.11043 | 0 | 0
80 | 0.98993 | -0.19394 | 0.004409 | 0.001105
81 | 0.98998 | -0.19287 | 0.00048309 | 0.00012107
82 | 0.98992 | -0.19397 | 0.0012337 | 0.00030919
83 | 0.99054 | -0.18212 | 0.0024926 | 0.00062471
84 | 0.98989 | -0.19471 | 0.00037851 | 9.4865e-05
85 | 0.9908 | -0.17709 | 0.0014725 | 0.00036903
86 | 0.98981 | -0.1962 | 0.0004829 | 0.00012103
87 | 0.99375 | -0.1197 | 0.0017456 | 0.00043748
88 | 0.99374 | -0.11981 | 0.001912 | 0.0004792
89 | 0.99394 | -0.11602 | 0.0036357 | 0.0009112
90 | 0.99366 | -0.12132 | 0.0017363 | 0.00043515
91 | 0.99357 | -0.12319 | 0.0013101 | 0.00032834
92 | 0.9967 | -0.063296 | 0.0061351 | 0.0015376
93 | 0.99839 | -0.030881 | 0.0037422 | 0.00093789
94 | 0.98946 | -0.20294 | 0.0039692 | 0.00099477
95 | 0.98952 | -0.2019 | 0.0033085 | 0.00082918
96 | 0.98946 | -0.20296 | 0.0016971 | 0.00042534
97 | 0.98975 | -0.19733 | 0.0014462 | 0.00036244
98 | 0.98945 | -0.20316 | 0.00097758 | 0.000245
99 | 0.99554 | -0.085475 | 0.0020215 | 0.00050663
100 | 0.99487 | -0.098376 | 0.0021425 | 0.00053696
101 | 0.99557 | -0.084818 | 0.0011989 | 0.00030048
102 | 0.99482 | -0.099402 | 0.0021254 | 0.00053268
103 | 0.99608 | -0.075123 | 0.0014199 | 0.00035585
104 | 0.99481 | -0.099435 | 0.0010449 | 0.00026187
105 | 0.99669 | -0.063436 | 0.0033967 | 0.00085129
106 | 0.99403 | -0.11453 | 0.001377 | 0.0003451
107 | 0.99436 | -0.10821 | 0.0016925 | 0.00042419
108 | 0.99296 | -0.13522 | 0.001698 | 0.00042555
109 | 0.99848 | -0.028994 | 0.0022152 | 0.00055517
110 | 0.99356 | -0.12337 | 0.0011117 | 0.00027863
111 | 0.99341 | -0.12616 | 0.00085641 | 0.00021464
112 | 0.9934 | -0.12649 | 0.0016062 | 0.00040256
113 | 0.99244 | -0.14543 | 0.0013927 | 0.00034904
114 | 0.99234 | -0.14738 | 0.001043 | 0.0002614
115 | 0.99232 | -0.14787 | 0.0010322 | 0.00025868
116 | 0.99333 | -0.12814 | 0.0018246 | 0.00045728
117 | 0.99208 | -0.15243 | 0 | 0
118 | 0.99426 | -0.11035 | 0.0014131 | 0.00035416
119 | 0.99425 | -0.11048 | 0.0014048 | 0.00035207
120 | 0.99191 | -0.15569 | 0.0016416 | 0.00041144
121 | 0.99193 | -0.15541 | 0.0093199 | 0.0023358
122 | 0.99199 | -0.15417 | 0.0014142 | 0.00035442
123 | 0.99197 | -0.15449 | 0.0014297 | 0.00035833
124 | 0.99197 | -0.15451 | 0.001365 | 0.0003421
125 | 0.99381 | -0.11903 | 0.0026758 | 0.00067061
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0085106 | 0.0021329 | -0.0085092 | -0.0021323 | 1.3999e-06 | 6.0157e-07 | 0.01278 | 0.012781 | 0.012781 | 0.99089 | -0.17534 | 0.99071 | -0.17879 | 3.5111
1 | -0.0095191 | -0.0023856 | 0.0095206 | 0.0023863 | 1.4847e-06 | 7.0057e-07 | 0.014295 | 0.014295 | 0.014295 | 0.99089 | -0.17534 | 0.99105 | -0.17207 | 3.9272
2 | 0.0057735 | 0.0014466 | -0.0057728 | -0.0014465 | 7.1712e-07 | 1.3154e-07 | 0.0086716 | 0.0086717 | 0.0086717 | 0.99071 | -0.17879 | 0.99057 | -0.1814 | 2.3823
3 | -0.015399 | -0.0038594 | 0.015404 | 0.0038623 | 5.0199e-06 | 2.89e-06 | 0.023121 | 0.023121 | 0.023121 | 0.99105 | -0.17207 | 0.99141 | -0.16523 | 6.352
4 | 0.0058786 | 0.0014731 | -0.0058775 | -0.0014728 | 1.1496e-06 | 2.2881e-07 | 0.0088264 | 0.0088265 | 0.0088265 | 0.99105 | -0.17207 | 0.99084 | -0.17617 | 2.4249
5 | 0.0015391 | 0.00038544 | -0.001539 | -0.00038572 | 4.8462e-08 | -2.8022e-07 | 0.0023119 | 0.002312 | 0.002312 | 0.99057 | -0.1814 | 0.99054 | -0.18206 | 0.63516
6 | 0.0023846 | 0.00059708 | -0.0023845 | -0.00059733 | 1.2097e-07 | -2.473e-07 | 0.0035789 | 0.0035791 | 0.0035791 | 0.99141 | -0.16523 | 0.99135 | -0.16629 | 0.98326
7 | -0.017789 | -0.0044594 | 0.01779 | 0.00446 | 1.1661e-06 | 6.9008e-07 | 0.0267 | 0.0267 | 0.0267 | 0.99141 | -0.16523 | 0.99148 | -0.16385 | 7.3351
8 | 0.0042517 | 0.0010654 | -0.0042516 | -0.0010654 | 9.3173e-08 | -1.8864e-08 | 0.006385 | 0.0063851 | 0.0063851 | 0.99084 | -0.17617 | 0.99082 | -0.17663 | 1.7541
9 | 0.0012202 | 0.00030552 | -0.0012201 | -0.0003058 | 2.9101e-08 | -2.7967e-07 | 0.0018314 | 0.0018315 | 0.0018315 | 0.99135 | -0.16629 | 0.99133 | -0.16679 | 0.50315
10 | -0.019849 | -0.0049762 | 0.019852 | 0.0049774 | 2.0957e-06 | 1.2601e-06 | 0.029791 | 0.029791 | 0.029791 | 0.99148 | -0.16385 | 0.99159 | -0.16164 | 8.1842
11 | 0.0025093 | 0.00062874 | -0.0025092 | -0.00062888 | 7.9621e-08 | -1.4159e-07 | 0.0037685 | 0.0037685 | 0.0037685 | 0.99082 | -0.17663 | 0.99079 | -0.1773 | 1.0353
12 | -0.0029388 | -0.00073572 | 0.0029391 | 0.00073533 | 3.4183e-07 | -3.8985e-07 | 0.0044028 | 0.0044026 | 0.0044028 | 0.99316 | -0.13102 | 0.99329 | -0.12857 | 1.2096
13 | 0.0018243 | 0.0004564 | -0.0018242 | -0.00045676 | 9.157e-08 | -3.6442e-07 | 0.0027329 | 0.0027331 | 0.0027331 | 0.99316 | -0.13102 | 0.99311 | -0.13207 | 0.75085
14 | -0.0029391 | -0.00073533 | 0.0029394 | 0.00073497 | 3.1399e-07 | -3.583e-07 | 0.0044026 | 0.0044024 | 0.0044026 | 0.99329 | -0.12857 | 0.9934 | -0.12633 | 1.2095
15 | 0.0018242 | 0.00045676 | -0.0018241 | -0.00045696 | 4.9284e-08 | -1.961e-07 | 0.0027331 | 0.0027332 | 0.0027332 | 0.99311 | -0.13207 | 0.99308 | -0.13264 | 0.75087
16 | -0.0038064 | -0.00095224 | 0.0038065 | 0.00095217 | 1.7964e-07 | -7.5872e-08 | 0.0057009 | 0.0057008 | 0.0057009 | 0.9934 | -0.12633 | 0.99346 | -0.12533 | 1.5662
17 | 0.00057011 | 0.00014267 | -0.0005701 | -0.00014288 | 4.5215e-09 | -2.1091e-07 | 0.00085416 | 0.00085424 | 0.00085424 | 0.99308 | -0.13264 | 0.99307 | -0.1328 | 0.23468
18 | 0.0024628 | 0.00061688 | -0.0024627 | -0.00061707 | 9.7404e-08 | -1.8483e-07 | 0.0036887 | 0.0036887 | 0.0036887 | 0.99346 | -0.12533 | 0.99341 | -0.12616 | 1.0134
19 | -0.0062693 | -0.001569 | 0.0062699 | 0.0015692 | 5.8496e-07 | 1.4525e-07 | 0.0093895 | 0.0093894 | 0.0093895 | 0.99346 | -0.12533 | 0.99356 | -0.12337 | 2.5795
20 | -0.054557 | -0.013741 | 0.054616 | 0.013778 | 5.9e-05 | 3.7458e-05 | 0.081959 | 0.081959 | 0.081959 | 0.99081 | -0.17629 | 0.99198 | -0.1537 | 22.5162
21 | 0.053246 | 0.013412 | -0.053246 | -0.013412 | 2.7941e-07 | 1.7732e-07 | 0.07999 | 0.07999 | 0.07999 | 0.99081 | -0.17629 | 0.9908 | -0.1764 | 21.9754
22 | -0.05865 | -0.014789 | 0.058677 | 0.014806 | 2.6504e-05 | 1.6845e-05 | 0.08801 | 0.08801 | 0.08801 | 0.99198 | -0.1537 | 0.99247 | -0.14426 | 24.1786
23 | 0.051996 | 0.013099 | -0.051865 | -0.013016 | 0.00013165 | 8.3516e-05 | 0.078113 | 0.078114 | 0.078114 | 0.9908 | -0.1764 | 0.98806 | -0.22948 | 21.4598
24 | -0.059692 | -0.015061 | 0.059693 | 0.015061 | 4.8407e-07 | 3.0772e-07 | 0.089533 | 0.089533 | 0.089533 | 0.99247 | -0.14426 | 0.99248 | -0.14409 | 24.5969
25 | 0.0045324 | 0.0011354 | -0.0045319 | -0.0011355 | 4.629e-07 | -4.3061e-08 | 0.0068255 | 0.0068257 | 0.0068257 | 0.98806 | -0.22948 | 0.98795 | -0.23162 | 1.8752
26 | 0.028734 | 0.0072131 | -0.028727 | -0.007209 | 6.6864e-06 | 4.1574e-06 | 0.043277 | 0.043277 | 0.043277 | 0.98806 | -0.22948 | 0.98781 | -0.23436 | 11.8893
27 | 0.018598 | 0.004667 | -0.018582 | -0.0046571 | 1.6626e-05 | 9.9178e-06 | 0.028011 | 0.028011 | 0.028011 | 0.98806 | -0.22948 | 0.9871 | -0.24824 | 7.6954
28 | -0.06071 | -0.015316 | 0.060763 | 0.01535 | 5.3602e-05 | 3.4083e-05 | 0.091057 | 0.091057 | 0.091057 | 0.99248 | -0.14409 | 0.99343 | -0.12567 | 25.0158
29 | 0.0037129 | 0.00093019 | -0.0037128 | -0.00093023 | 8.1223e-08 | -3.6705e-08 | 0.0055921 | 0.0055922 | 0.0055922 | 0.98795 | -0.23162 | 0.98793 | -0.23208 | 1.5363
30 | 0.024299 | 0.0060993 | -0.024283 | -0.0060889 | 1.6846e-05 | 1.0353e-05 | 0.036607 | 0.036608 | 0.036608 | 0.98781 | -0.23436 | 0.98706 | -0.24891 | 10.057
31 | 0.0084281 | 0.0021124 | -0.0084276 | -0.0021122 | 4.3963e-07 | 1.8853e-07 | 0.012705 | 0.012705 | 0.012705 | 0.9871 | -0.24824 | 0.98704 | -0.24934 | 3.4904
32 | -0.0095897 | -0.0024032 | 0.0095897 | 0.0024032 | 6.5422e-08 | 3.1221e-08 | 0.014464 | 0.014464 | 0.014464 | 0.98658 | -0.2583 | 0.98659 | -0.25816 | 3.9735
33 | 0.0023474 | 0.00058809 | -0.0023473 | -0.0005883 | 9.9653e-08 | -2.0692e-07 | 0.0035405 | 0.0035406 | 0.0035406 | 0.98658 | -0.2583 | 0.98654 | -0.25919 | 0.97268
34 | -0.013304 | -0.0033341 | 0.013304 | 0.0033342 | 1.5871e-07 | 8.8154e-08 | 0.020066 | 0.020066 | 0.020066 | 0.98659 | -0.25816 | 0.9866 | -0.25791 | 5.5125
35 | -0.021483 | -0.005384 | 0.021492 | 0.0053896 | 9.2172e-06 | 5.5999e-06 | 0.032401 | 0.032401 | 0.032401 | 0.9866 | -0.25791 | 0.98706 | -0.24891 | 8.9015
36 | 0.0026647 | 0.00066753 | -0.0026645 | -0.00066779 | 1.7013e-07 | -2.5173e-07 | 0.0040134 | 0.0040135 | 0.0040135 | 0.98793 | -0.23208 | 0.98786 | -0.23342 | 1.1026
37 | -0.00077218 | -0.00019353 | 0.00077219 | 0.00019352 | 5.0235e-10 | -1.2683e-08 | 0.0011558 | 0.0011558 | 0.0011558 | 0.99416 | -0.11212 | 0.99416 | -0.1121 | 0.31752
38 | -0.0016221 | -0.00040652 | 0.0016221 | 0.00040633 | 3.583e-08 | -1.8727e-07 | 0.0024278 | 0.0024278 | 0.0024278 | 0.99416 | -0.1121 | 0.99419 | -0.11164 | 0.66699
39 | -0.0030485 | -0.00076383 | 0.0030487 | 0.00076364 | 1.8804e-07 | -1.9202e-07 | 0.0045627 | 0.0045626 | 0.0045627 | 0.99419 | -0.11164 | 0.99426 | -0.11035 | 1.2535
40 | -0.029548 | -0.0074201 | 0.029552 | 0.0074223 | 3.5046e-06 | 2.181e-06 | 0.044228 | 0.044228 | 0.044228 | 0.99426 | -0.11035 | 0.99438 | -0.10786 | 12.1505
41 | 0.0265 | 0.0066564 | -0.02649 | -0.0066504 | 9.7686e-06 | 6.0372e-06 | 0.039665 | 0.039665 | 0.039665 | 0.99426 | -0.11035 | 0.99386 | -0.11807 | 10.897
42 | -0.030406 | -0.0076363 | 0.030419 | 0.0076445 | 1.3182e-05 | 8.2159e-06 | 0.045506 | 0.045506 | 0.045506 | 0.99438 | -0.10786 | 0.99486 | -0.098779 | 12.5016
43 | 0.0026759 | 0.00067042 | -0.0026758 | -0.00067049 | 4.8025e-08 | -7.2658e-08 | 0.0040063 | 0.0040063 | 0.0040063 | 0.99386 | -0.11807 | 0.99384 | -0.11845 | 1.1006
44 | 0.023814 | 0.00598 | -0.023813 | -0.0059795 | 7.7876e-07 | 4.7725e-07 | 0.035659 | 0.035659 | 0.035659 | 0.99386 | -0.11807 | 0.99382 | -0.11876 | 9.7964
45 | 0.012684 | 0.0031794 | -0.012683 | -0.0031786 | 1.457e-06 | 7.9233e-07 | 0.018972 | 0.018972 | 0.018972 | 0.99486 | -0.098779 | 0.99473 | -0.10119 | 5.2121
46 | -0.043103 | -0.010824 | 0.043125 | 0.010838 | 2.2054e-05 | 1.3931e-05 | 0.064478 | 0.064478 | 0.064478 | 0.99486 | -0.098779 | 0.99541 | -0.088061 | 17.7137
47 | 0.0026758 | 0.00067049 | -0.0026758 | -0.00067061 | 7.3974e-08 | -1.1191e-07 | 0.0040063 | 0.0040064 | 0.0040064 | 0.99384 | -0.11845 | 0.99381 | -0.11903 | 1.1007
48 | 0.023208 | 0.0058277 | -0.023197 | -0.0058214 | 1.0382e-05 | 6.3476e-06 | 0.034752 | 0.034752 | 0.034752 | 0.99382 | -0.11876 | 0.99333 | -0.12814 | 9.5473
49 | 0.011851 | 0.0029702 | -0.011851 | -0.0029698 | 7.6783e-07 | 4.0685e-07 | 0.017728 | 0.017728 | 0.017728 | 0.99473 | -0.10119 | 0.99466 | -0.10255 | 4.8704
50 | -0.047991 | -0.012057 | 0.04802 | 0.012075 | 2.8556e-05 | 1.8084e-05 | 0.071751 | 0.071751 | 0.071751 | 0.99541 | -0.088061 | 0.99606 | -0.075602 | 19.7119
51 | 0.0090294 | 0.0022628 | -0.009029 | -0.0022626 | 4.2109e-07 | 1.8962e-07 | 0.013508 | 0.013508 | 0.013508 | 0.99466 | -0.10255 | 0.99461 | -0.10353 | 3.711
52 | -0.049995 | -0.01257 | 0.050033 | 0.012594 | 3.7518e-05 | 2.3778e-05 | 0.074702 | 0.074702 | 0.074702 | 0.99606 | -0.075602 | 0.99687 | -0.059901 | 20.5226
53 | -0.0018775 | -0.00047056 | 0.0018776 | 0.00047046 | 2.5378e-08 | -9.5436e-08 | 0.0028067 | 0.0028067 | 0.0028067 | 0.99541 | -0.08812 | 0.99543 | -0.087836 | 0.77107
54 | -0.0026046 | -0.00065266 | 0.0026046 | 0.00065256 | 6.3647e-08 | -1.0482e-07 | 0.0038934 | 0.0038934 | 0.0038934 | 0.99543 | -0.087836 | 0.99545 | -0.087323 | 1.0696
55 | 0.009029 | 0.0022626 | -0.0090285 | -0.0022624 | 4.4538e-07 | 2.0057e-07 | 0.013508 | 0.013508 | 0.013508 | 0.99461 | -0.10353 | 0.99456 | -0.10456 | 3.711
56 | 0.0054069 | 0.0013547 | -0.0054056 | -0.0013546 | 1.3184e-06 | 1.4681e-07 | 0.0080895 | 0.0080897 | 0.0080897 | 0.99456 | -0.10456 | 0.99429 | -0.10968 | 2.2224
57 | 0.002818 | 0.00070605 | -0.0028179 | -0.00070617 | 8.9128e-08 | -1.1628e-07 | 0.0042172 | 0.0042173 | 0.0042173 | 0.99429 | -0.10968 | 0.99426 | -0.11035 | 1.1586
58 | -0.0027104 | -0.00067929 | 0.0027104 | 0.00067923 | 3.6577e-08 | -5.3017e-08 | 0.0040624 | 0.0040624 | 0.0040624 | 0.99279 | -0.13877 | 0.9928 | -0.13849 | 1.116
59 | -0.021362 | -0.0053577 | 0.021373 | 0.0053641 | 1.0541e-05 | 6.3915e-06 | 0.032019 | 0.032019 | 0.032019 | 0.9928 | -0.13849 | 0.99333 | -0.12814 | 8.7964
60 | 0.018652 | 0.0046785 | -0.018646 | -0.0046748 | 6.1743e-06 | 3.6792e-06 | 0.027957 | 0.027957 | 0.027957 | 0.9928 | -0.13849 | 0.99244 | -0.14543 | 7.6804
61 | 0.016375 | 0.004105 | -0.016373 | -0.0041036 | 2.256e-06 | 1.313e-06 | 0.024464 | 0.024464 | 0.024464 | 0.99603 | -0.076119 | 0.99588 | -0.079011 | 6.7209
62 | -0.028471 | -0.0071363 | 0.028475 | 0.007139 | 4.318e-06 | 2.6806e-06 | 0.042534 | 0.042534 | 0.042534 | 0.99603 | -0.076119 | 0.9962 | -0.072936 | 11.6851
63 | 0.014251 | 0.0035717 | -0.014249 | -0.0035705 | 2.2405e-06 | 1.2625e-06 | 0.021293 | 0.021293 | 0.021293 | 0.99588 | -0.079011 | 0.99571 | -0.082311 | 5.8498
64 | -0.034087 | -0.0085454 | 0.034108 | 0.0085587 | 2.1186e-05 | 1.3275e-05 | 0.050916 | 0.050916 | 0.050916 | 0.9962 | -0.072936 | 0.99687 | -0.059901 | 13.9879
65 | 0.0087316 | 0.0021878 | -0.0087307 | -0.0021874 | 8.5835e-07 | 3.745e-07 | 0.013048 | 0.013049 | 0.013049 | 0.99571 | -0.082311 | 0.99561 | -0.084376 | 3.5848
66 | -0.08414 | -0.021153 | 0.084202 | 0.021192 | 6.1624e-05 | 3.9304e-05 | 0.12562 | 0.12562 | 0.12562 | 0.99687 | -0.059901 | 0.99767 | -0.044576 | 34.5104
67 | 0.0050844 | 0.0012736 | -0.0050837 | -0.0012735 | 7.1354e-07 | 2.8215e-08 | 0.0075989 | 0.007599 | 0.007599 | 0.99561 | -0.084376 | 0.99545 | -0.087323 | 2.0876
68 | 0.070873 | 0.017895 | -0.07081 | -0.017855 | 6.3506e-05 | 4.0446e-05 | 0.10575 | 0.10575 | 0.10575 | 0.99767 | -0.044576 | 0.9967 | -0.063296 | 29.0532
69 | -0.15508 | -0.039087 | 0.15518 | 0.039152 | 0.00010169 | 6.4815e-05 | 0.23137 | 0.23137 | 0.23137 | 0.99767 | -0.044576 | 0.99839 | -0.030881 | 31.7818
70 | 0.024798 | 0.0062279 | -0.024786 | -0.0062204 | 1.2188e-05 | 7.498e-06 | 0.037218 | 0.037218 | 0.037218 | 0.99159 | -0.16164 | 0.99106 | -0.17194 | 10.2247
71 | -0.04465 | -0.011205 | 0.04467 | 0.011218 | 2.0514e-05 | 1.2971e-05 | 0.067008 | 0.067008 | 0.067008 | 0.99159 | -0.16164 | 0.99209 | -0.15201 | 18.4089
72 | 0.024379 | 0.0061183 | -0.024373 | -0.0061148 | 5.8339e-06 | 3.5841e-06 | 0.036606 | 0.036606 | 0.036606 | 0.99106 | -0.17194 | 0.9908 | -0.17696 | 10.0567
73 | -0.04467 | -0.011218 | 0.044689 | 0.01123 | 1.8993e-05 | 1.201e-05 | 0.067008 | 0.067008 | 0.067008 | 0.99209 | -0.15201 | 0.99255 | -0.1431 | 18.4088
74 | 0.022371 | 0.0056129 | -0.022371 | -0.0056128 | 1.3268e-07 | 8.088e-08 | 0.033599 | 0.033599 | 0.033599 | 0.9908 | -0.17696 | 0.9908 | -0.17709 | 9.2306
75 | -0.046354 | -0.011648 | 0.046371 | 0.011659 | 1.745e-05 | 1.1044e-05 | 0.069504 | 0.069504 | 0.069504 | 0.99255 | -0.1431 | 0.99296 | -0.13522 | 19.0944
76 | 0.0024791 | 0.00062098 | -0.0024789 | -0.00062128 | 1.5715e-07 | -2.9613e-07 | 0.0037056 | 0.0037058 | 0.0037058 | 0.99545 | -0.087323 | 0.99538 | -0.088654 | 1.0181
77 | 0.085941 | 0.021802 | -0.08583 | -0.021731 | 0.00011136 | 7.1032e-05 | 0.12818 | 0.12818 | 0.12818 | 0.99837 | -0.031102 | 0.99695 | -0.058085 | 35.2155
78 | -0.088881 | -0.022539 | 0.088883 | 0.02254 | 1.9394e-06 | 1.2374e-06 | 0.13257 | 0.13257 | 0.13257 | 0.99837 | -0.031102 | 0.99839 | -0.030648 | 36.4192
79 | 0.083431 | 0.02113 | -0.083325 | -0.021062 | 0.00010628 | 6.7785e-05 | 0.1246 | 0.1246 | 0.1246 | 0.99695 | -0.058085 | 0.99557 | -0.084649 | 34.232
80 | -0.089971 | -0.022813 | 0.090104 | 0.022897 | 0.00013275 | 8.4706e-05 | 0.13419 | 0.13419 | 0.13419 | 0.99839 | -0.030648 | 1 | 0 | 36.8647
81 | 0.082398 | 0.02083 | -0.082318 | -0.020779 | 7.9578e-05 | 5.0749e-05 | 0.12322 | 0.12322 | 0.12322 | 0.99557 | -0.084649 | 0.99452 | -0.10481 | 33.8512
82 | 0.1672 | 0.042259 | -0.16709 | -0.04219 | 0.00010888 | 6.944e-05 | 0.24892 | 0.24892 | 0.24892 | 1 | 0 | 0.99929 | -0.013591 | 34.1927
83 | 0.081013 | 0.020452 | -0.080991 | -0.020438 | 2.1792e-05 | 1.3896e-05 | 0.12127 | 0.12127 | 0.12127 | 0.99452 | -0.10481 | 0.99423 | -0.11043 | 33.3146
84 | 0.16127 | 0.04073 | -0.16115 | -0.040654 | 0.00011894 | 7.5835e-05 | 0.24025 | 0.24025 | 0.24025 | 0.99929 | -0.013591 | 0.99848 | -0.028994 | 33.0014
85 | -0.061918 | -0.01564 | 0.061936 | 0.015651 | 1.7809e-05 | 1.1326e-05 | 0.092787 | 0.092787 | 0.092787 | 0.99343 | -0.12567 | 0.99374 | -0.11967 | 25.491
86 | -0.063233 | -0.015976 | 0.063261 | 0.015994 | 2.8033e-05 | 1.7833e-05 | 0.094729 | 0.094729 | 0.094729 | 0.99374 | -0.11967 | 0.99423 | -0.11043 | 26.0245
87 | 0.01773 | 0.0044441 | -0.017725 | -0.0044413 | 4.7261e-06 | 2.7927e-06 | 0.026536 | 0.026536 | 0.026536 | 0.99423 | -0.11043 | 0.99394 | -0.11602 | 7.2902
88 | -0.017907 | -0.0044888 | 0.017908 | 0.0044894 | 9.0941e-07 | 5.3899e-07 | 0.026917 | 0.026917 | 0.026917 | 0.98993 | -0.19394 | 0.98998 | -0.19287 | 7.3949
89 | 0.013498 | 0.0033838 | -0.013498 | -0.0033838 | 2.15e-08 | 1.197e-08 | 0.02029 | 0.02029 | 0.02029 | 0.98993 | -0.19394 | 0.98992 | -0.19397 | 5.5742
90 | -0.018391 | -0.0046105 | 0.0184 | 0.0046161 | 9.4265e-06 | 5.6097e-06 | 0.027644 | 0.027643 | 0.027644 | 0.98998 | -0.19287 | 0.99054 | -0.18212 | 7.5944
91 | 0.012264 | 0.0030746 | -0.012264 | -0.0030744 | 4.3201e-07 | 2.3291e-07 | 0.018436 | 0.018436 | 0.018436 | 0.98992 | -0.19397 | 0.98989 | -0.19471 | 5.0647
92 | -0.020893 | -0.0052408 | 0.020898 | 0.0052438 | 5.0187e-06 | 3.037e-06 | 0.031388 | 0.031388 | 0.031388 | 0.99054 | -0.18212 | 0.9908 | -0.17709 | 8.623
93 | 0.011885 | 0.0029795 | -0.011885 | -0.0029791 | 8.4164e-07 | 4.4827e-07 | 0.017867 | 0.017867 | 0.017867 | 0.98989 | -0.19471 | 0.98981 | -0.1962 | 4.9084
94 | 0.011402 | 0.0028581 | -0.011401 | -0.0028577 | 6.1346e-07 | 3.2105e-07 | 0.017141 | 0.017141 | 0.017141 | 0.98981 | -0.1962 | 0.98975 | -0.19733 | 4.709
95 | 0.012342 | 0.0030913 | -0.012342 | -0.0030912 | 6.62e-08 | 3.567e-08 | 0.01848 | 0.01848 | 0.01848 | 0.99375 | -0.1197 | 0.99374 | -0.11981 | 5.0768
96 | -0.014087 | -0.0035288 | 0.01409 | 0.0035301 | 2.4684e-06 | 1.3881e-06 | 0.021093 | 0.021093 | 0.021093 | 0.99375 | -0.1197 | 0.99394 | -0.11602 | 5.7949
97 | 0.01043 | 0.002612 | -0.010429 | -0.0026117 | 7.4905e-07 | 3.7329e-07 | 0.015616 | 0.015617 | 0.015617 | 0.99374 | -0.11981 | 0.99366 | -0.12132 | 4.2903
98 | 0.0086925 | 0.0021765 | -0.0086918 | -0.0021762 | 7.7207e-07 | 3.3673e-07 | 0.013016 | 0.013016 | 0.013016 | 0.99366 | -0.12132 | 0.99357 | -0.12319 | 3.576
99 | 0.0073817 | 0.0018478 | -0.0073816 | -0.0018478 | 6.4972e-08 | 2.322e-08 | 0.011054 | 0.011054 | 0.011054 | 0.99357 | -0.12319 | 0.99356 | -0.12337 | 3.0369
100 | 0.064675 | 0.016317 | -0.064674 | -0.016317 | 4.3509e-07 | 2.7684e-07 | 0.096594 | 0.096594 | 0.096594 | 0.9967 | -0.063296 | 0.99669 | -0.063436 | 26.5368
101 | -0.15892 | -0.04009 | 0.15893 | 0.040099 | 1.4355e-05 | 9.1514e-06 | 0.23695 | 0.23695 | 0.23695 | 0.99839 | -0.030881 | 0.99848 | -0.028994 | 32.5479
102 | -0.0066439 | -0.001665 | 0.0066442 | 0.0016651 | 3.2976e-07 | 9.79e-08 | 0.0099915 | 0.0099914 | 0.0099915 | 0.98946 | -0.20294 | 0.98952 | -0.2019 | 2.7449
103 | 0.0026747 | 0.0006702 | -0.0026747 | -0.0006702 | 2.6317e-09 | -3.8867e-09 | 0.0040224 | 0.0040224 | 0.0040224 | 0.98946 | -0.20294 | 0.98946 | -0.20296 | 1.105
104 | -0.0099527 | -0.0024942 | 0.0099549 | 0.0024953 | 2.1657e-06 | 1.0548e-06 | 0.014967 | 0.014967 | 0.014967 | 0.98952 | -0.2019 | 0.98975 | -0.19733 | 4.1117
105 | 0.00097759 | 0.00024486 | -0.00097758 | -0.000245 | 9.6175e-09 | -1.4626e-07 | 0.0014701 | 0.0014702 | 0.0014702 | 0.98946 | -0.20296 | 0.98945 | -0.20316 | 0.40389
106 | 0.056573 | 0.014262 | -0.056538 | -0.01424 | 3.4904e-05 | 2.2169e-05 | 0.084589 | 0.084589 | 0.084589 | 0.99554 | -0.085475 | 0.99487 | -0.098376 | 23.2386
107 | -0.058595 | -0.014769 | 0.058597 | 0.01477 | 1.8415e-06 | 1.1702e-06 | 0.08761 | 0.08761 | 0.08761 | 0.99554 | -0.085475 | 0.99557 | -0.084818 | 24.0687
108 | 0.054396 | 0.013703 | -0.054393 | -0.013701 | 2.6699e-06 | 1.6948e-06 | 0.081384 | 0.081384 | 0.081384 | 0.99487 | -0.098376 | 0.99482 | -0.099402 | 22.3583
109 | -0.059796 | -0.01507 | 0.059823 | 0.015088 | 2.7751e-05 | 1.764e-05 | 0.089402 | 0.089402 | 0.089402 | 0.99557 | -0.084818 | 0.99608 | -0.075123 | 24.561
110 | 0.052268 | 0.013169 | -0.052268 | -0.013168 | 8.0669e-08 | 5.1174e-08 | 0.078205 | 0.078205 | 0.078205 | 0.99482 | -0.099402 | 0.99481 | -0.099435 | 21.4849
111 | -0.061243 | -0.015444 | 0.061277 | 0.015466 | 3.4277e-05 | 2.1795e-05 | 0.091523 | 0.091523 | 0.091523 | 0.99608 | -0.075123 | 0.99669 | -0.063436 | 25.1437
112 | 0.051223 | 0.012907 | -0.051201 | -0.012893 | 2.1491e-05 | 1.3627e-05 | 0.076642 | 0.076642 | 0.076642 | 0.99481 | -0.099435 | 0.99436 | -0.10821 | 21.0555
113 | -0.049494 | -0.012459 | 0.049509 | 0.012469 | 1.4957e-05 | 9.4782e-06 | 0.074109 | 0.074109 | 0.074109 | 0.99403 | -0.11453 | 0.99436 | -0.10821 | 20.3597
114 | 0.048117 | 0.012114 | -0.048069 | -0.012084 | 4.7532e-05 | 3.0104e-05 | 0.072048 | 0.072048 | 0.072048 | 0.99403 | -0.11453 | 0.99296 | -0.13522 | 19.7935
115 | 0.0016063 | 0.00040243 | -0.0016062 | -0.00040256 | 2.4537e-08 | -1.3064e-07 | 0.0024059 | 0.002406 | 0.002406 | 0.99341 | -0.12616 | 0.9934 | -0.12649 | 0.66099
116 | 0.017253 | 0.0043257 | -0.017251 | -0.0043248 | 1.5973e-06 | 9.4001e-07 | 0.025869 | 0.025869 | 0.025869 | 0.99244 | -0.14543 | 0.99234 | -0.14738 | 7.1068
117 | 0.016208 | 0.0040634 | -0.016208 | -0.0040632 | 3.7842e-07 | 2.2012e-07 | 0.024305 | 0.024305 | 0.024305 | 0.99234 | -0.14738 | 0.99232 | -0.14787 | 6.6771
118 | 0.015176 | 0.0038045 | -0.015172 | -0.0038026 | 3.2977e-06 | 1.8912e-06 | 0.022757 | 0.022757 | 0.022757 | 0.99232 | -0.14787 | 0.99208 | -0.15243 | 6.2519
119 | 0.0042093 | 0.0010547 | -0.0042089 | -0.0010548 | 3.5013e-07 | -7.8351e-08 | 0.0063134 | 0.0063135 | 0.0063135 | 0.99208 | -0.15243 | 0.99199 | -0.15417 | 1.7345
120 | 0.010963 | 0.0027479 | -0.010962 | -0.0027471 | 1.5566e-06 | 7.9803e-07 | 0.016444 | 0.016444 | 0.016444 | 0.99208 | -0.15243 | 0.99193 | -0.15541 | 4.5175
121 | 0.0014048 | 0.00035201 | -0.0014048 | -0.00035207 | 8.6574e-09 | -6.2198e-08 | 0.0021024 | 0.0021024 | 0.0021024 | 0.99426 | -0.11035 | 0.99425 | -0.11048 | 0.57758
122 | -0.0016416 | -0.00041144 | 0.0016417 | 0.00041133 | 2.2065e-08 | -1.1111e-07 | 0.0024627 | 0.0024627 | 0.0024627 | 0.99191 | -0.15569 | 0.99193 | -0.15541 | 0.67657
123 | 0.0027948 | 0.00070036 | -0.0027947 | -0.00070041 | 4.1587e-08 | -5.4846e-08 | 0.0041922 | 0.0041922 | 0.0041922 | 0.99199 | -0.15417 | 0.99197 | -0.15449 | 1.1517
124 | 0.001365 | 0.00034209 | -0.001365 | -0.0003421 | 1.4882e-09 | -1.1267e-08 | 0.0020475 | 0.0020475 | 0.0020475 | 0.99197 | -0.15449 | 0.99197 | -0.15451 | 0.56251

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26303 | 0.066179

## res_load
| p_mw | q_mvar
0 | 0.0010085 | 0.00025275
1 | 0.0027357 | 0.00068563
2 | 0.0042337 | 0.0010611
3 | 0.0016258 | 0.00040746
4 | 0.001539 | 0.00038572
5 | 0.0011643 | 0.00029181
6 | 0.0020594 | 0.00051613
7 | 0.0017423 | 0.00043666
8 | 0.0011145 | 0.00027933
9 | 0.00086691 | 0.00021727
10 | 0.001254 | 0.00031429
11 | 0.0005701 | 0.00014288
12 | 0.0025092 | 0.00062888
13 | 0.0013108 | 0.00032851
14 | 0.0040341 | 0.001011
15 | 0.0012498 | 0.00031323
16 | 0.0010156 | 0.00025453
17 | 0.0010169 | 0.00025485
18 | 0.00081899 | 0.00020526
19 | 0.0044277 | 0.0011097
20 | 0.010154 | 0.0025447
21 | 0.0072422 | 0.0018151
22 | 0.0037143 | 0.00093089
23 | 0.0023473 | 0.0005883
24 | 0.008179 | 0.0020499
25 | 0.0027902 | 0.00069928
26 | 0.0010482 | 0.0002627
27 | 0.00077218 | 0.00019353
28 | 0.00084989 | 0.000213
29 | 0.0014264 | 0.0003575
30 | 0.0084276 | 0.0021122
31 | 0.00085403 | 0.00021404
32 | 0.00060567 | 0.0001518
33 | 0.0026645 | 0.00066779
34 | 0.00083148 | 0.00020839
35 | 0.0048659 | 0.0012195
36 | 0.0028212 | 0.00070705
37 | 0.0019753 | 0.00049505
38 | 0.0018775 | 0.00047056
39 | 0.000727 | 0.0001822
40 | 0.0036216 | 0.00090766
41 | 0.0025876 | 0.00064851
42 | 0.0027104 | 0.00067929
43 | 0.012095 | 0.0030313
44 | 0.0021223 | 0.0005319
45 | 0.0056117 | 0.0014064
46 | 0.005517 | 0.0013827
47 | 0.0036463 | 0.00091384
48 | 0.00040723 | 0.00010206
49 | 0.0020023 | 0.00050183
50 | 0.0016646 | 0.0004172
51 | 0.0012201 | 0.0003058
52 | 0.0024789 | 0.00062128
53 | 0.0029396 | 0.00073673
54 | 0.0023986 | 0.00060116
55 | 0.0010882 | 0.00027273
56 | 0.00092745 | 0.00023244
57 | 0.0040788 | 0.0010222
58 | 0.0013054 | 0.00032717
59 | 0.0058243 | 0.0014597
60 | 0.0011549 | 0.00028945
61 | 0.0012969 | 0.00032504
62 | 0.004409 | 0.001105
63 | 0.00048309 | 0.00012107
64 | 0.0012337 | 0.00030919
65 | 0.0024926 | 0.00062471
66 | 0.00037851 | 9.4865e-05
67 | 0.0014725 | 0.00036903
68 | 0.0004829 | 0.00012103
69 | 0.0017456 | 0.00043748
70 | 0.001912 | 0.0004792
71 | 0.0036357 | 0.0009112
72 | 0.0017363 | 0.00043515
73 | 0.0013101 | 0.00032834
74 | 0.0061351 | 0.0015376
75 | 0.0037422 | 0.00093789
76 | 0.0039692 | 0.00099477
77 | 0.0033085 | 0.00082918
78 | 0.0016971 | 0.00042534
79 | 0.0014462 | 0.00036244
80 | 0.00097758 | 0.000245
81 | 0.0020215 | 0.00050663
82 | 0.0021425 | 0.00053696
83 | 0.0011989 | 0.00030048
84 | 0.0021254 | 0.00053268
85 | 0.0014199 | 0.00035585
86 | 0.0010449 | 0.00026187
87 | 0.0033967 | 0.00085129
88 | 0.001377 | 0.0003451
89 | 0.0016925 | 0.00042419
90 | 0.001698 | 0.00042555
91 | 0.0022152 | 0.00055517
92 | 0.0011117 | 0.00027863
93 | 0.00085641 | 0.00021464
94 | 0.0016062 | 0.00040256
95 | 0.0013927 | 0.00034904
96 | 0.001043 | 0.0002614
97 | 0.0010322 | 0.00025868
98 | 0.0018246 | 0.00045728
99 | 0.0014131 | 0.00035416
100 | 0.0014048 | 0.00035207
101 | 0.0016416 | 0.00041144
102 | 0.0093199 | 0.0023358
103 | 0.0014142 | 0.00035442
104 | 0.0014297 | 0.00035833
105 | 0.001365 | 0.0003421
106 | 0.0026758 | 0.00067061

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1