## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_14-5_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_14-5_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_14-5_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_14-5_0_1_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_14-5_0_1_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_14-5_0_1_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_14-5_0_1_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_14-5_0_1_node_169 | 0.4 | n |  | TRUE
8 | bus_LV_14-5_0_1_node_166 | 0.4 | n |  | TRUE
9 | bus_LV_14-5_0_1_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_14-5_0_1_node_171 | 0.4 | n |  | TRUE
11 | bus_LV_14-5_0_1_node_170 | 0.4 | n |  | TRUE
12 | bus_LV_14-5_0_1_node_263 | 0.4 | n |  | TRUE
13 | bus_LV_14-5_0_1_node_218 | 0.4 | n |  | TRUE
14 | bus_LV_14-5_0_1_node_217 | 0.4 | n |  | TRUE
15 | bus_LV_14-5_0_1_node_163 | 0.4 | n |  | TRUE
16 | bus_LV_14-5_0_1_node_162 | 0.4 | n |  | TRUE
17 | bus_LV_14-5_0_1_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_14-5_0_1_node_164 | 0.4 | n |  | TRUE
19 | bus_LV_14-5_0_1_node_165 | 0.4 | n |  | TRUE
20 | bus_LV_14-5_0_1_node_167 | 0.4 | n |  | TRUE
21 | bus_LV_14-5_0_1_node_168 | 0.4 | n |  | TRUE
22 | bus_LV_14-5_0_1_node_172 | 0.4 | n |  | TRUE
23 | bus_MV_358_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_14-5_0_1_load_0 | 0 | 0.0047465 | 0.0011896 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_14-5_0_1_load_1 | 1 | 0.0053556 | 0.0013422 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_14-5_0_1_load_169 | 7 | 0.0093844 | 0.002352 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_14-5_0_1_load_170 | 11 | 0.01192 | 0.0029875 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_14-5_0_1_load_263 | 12 | 0.0047734 | 0.0011963 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_14-5_0_1_load_218 | 13 | 0.01388 | 0.0034786 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_14-5_0_1_load_217 | 14 | 0.0017879 | 0.00044809 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_14-5_0_1_load_163 | 15 | 0.0047343 | 0.0011865 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_14-5_0_1_load_41 | 17 | 0.0051272 | 0.001285 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_14-5_0_1_load_164 | 18 | 0.0042673 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_14-5_0_1_load_165 | 19 | 0.0081069 | 0.0020318 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_14-5_0_1_load_172 | 22 | 0.01393 | 0.0034912 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_14-5_0_1_line_0 |  | 0 | 1 | 0.024436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_14-5_0_1_line_1 |  | 0 | 2 | 0.014692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_14-5_0_1_line_2 |  | 1 | 3 | 0.014118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_14-5_0_1_line_3 |  | 2 | 4 | 0.064505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_14-5_0_1_line_4 |  | 3 | 5 | 0.013326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_14-5_0_1_line_5 |  | 4 | 13 | 0.018956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_14-5_0_1_line_6 |  | 4 | 14 | 0.050853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_14-5_0_1_line_7 |  | 4 | 9 | 0.070933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_14-5_0_1_line_8 |  | 5 | 15 | 0.009954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_14-5_0_1_line_9 |  | 5 | 12 | 0.00221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_14-5_0_1_line_10 |  | 6 | 7 | 0.044614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_14-5_0_1_line_11 |  | 6 | 8 | 0.011679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_14-5_0_1_line_12 |  | 8 | 19 | 0.0068126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_14-5_0_1_line_13 |  | 9 | 10 | 0.026766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_14-5_0_1_line_14 |  | 9 | 11 | 0.030222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_14-5_0_1_line_15 |  | 10 | 22 | 0.009828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_14-5_0_1_line_16 |  | 11 | 21 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_14-5_0_1_line_17 |  | 15 | 18 | 0.004507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_14-5_0_1_line_18 |  | 15 | 16 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_14-5_0_1_line_19 |  | 16 | 17 | 0.031509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_14-5_0_1_line_20 |  | 19 | 20 | 0.0063648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_14-5_0_1_line_21 |  | 20 | 21 | 0.024182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_14-5_0_1_trafo_218 | 0.63 MVA 20/0.4 kV | 23 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2678012.9865 | 1242437.1684 | 2678016.7154 | 1242440.0191 | 2678021.4238 | 1242440.1255 | 2678024.5003 | 1242442.4453 | 2678035.666 | 1242441.8806
1 | 2678002.0712 | 1242427.4399 | 2678005.6308 | 1242431.5451 | 2678012.9865 | 1242437.1684
2 | 2678049.0083 | 1242443.0791 | 2678037.9304 | 1242443.8673 | 2678035.666 | 1242441.8806 | 2678035.666 | 1242441.8806
3 | 2677984.3056 | 1242453.903 | 2677985.2802 | 1242438.9941 | 2677987.5513 | 1242431.8522 | 2677991.7724 | 1242435.0989 | 2677997.2431 | 1242439.3182 | 2677999.0393 | 1242440.6983 | 2678001.684 | 1242443.6685 | 2678004.8284 | 1242439.6737 | 2677996.5255 | 1242432.9487 | 2678000.1976 | 1242429.072 | 2678002.0712 | 1242427.4399
4 | 2678049.0083 | 1242443.0791 | 2678056.7115 | 1242442.5244 | 2678060.4647 | 1242442.2514 | 2678062.0495 | 1242441.316
5 | 2677965.2966 | 1242453.6087 | 2677978.568 | 1242453.8832 | 2677984.3056 | 1242453.903
6 | 2677984.3056 | 1242453.903 | 2677982.7307 | 1242469.6157 | 2677980.6345 | 1242481.2743 | 2677976.1911 | 1242504.0611
7 | 2677940.6221 | 1242425.3757 | 2677973.285 | 1242426.183 | 2677975.2275 | 1242425.6303 | 2677987.5513 | 1242431.8522 | 2677985.2802 | 1242438.9941 | 2677984.3056 | 1242453.903
8 | 2678072.001 | 1242440.5241 | 2678062.0495 | 1242441.316
9 | 2678061.7835 | 1242439.122 | 2678062.0495 | 1242441.316
10 | 2677863.6055 | 1242449.949 | 2677853.0271 | 1242449.5433 | 2677853.5345 | 1242415.4925
11 | 2677853.5345 | 1242415.4925 | 2677865.0994 | 1242417.3455
12 | 2677865.0994 | 1242417.3455 | 2677871.7998 | 1242418.5769
13 | 2677940.6221 | 1242425.3757 | 2677940.0438 | 1242452.1315
14 | 2677940.6221 | 1242425.3757 | 2677910.4152 | 1242424.4304
15 | 2677930.1871 | 1242452.0354 | 2677940.0438 | 1242452.1315
16 | 2677898.3651 | 1242424.0534 | 2677910.4152 | 1242424.4304
17 | 2678071.8864 | 1242436.0194 | 2678072.001 | 1242440.5241
18 | 2678072.001 | 1242440.5241 | 2678086.521 | 1242437.2572
19 | 2678086.521 | 1242437.2572 | 2678088.2473 | 1242468.7193
20 | 2677874.1233 | 1242423.2903 | 2677873.7647 | 1242418.9381 | 2677871.7998 | 1242418.5769
21 | 2677898.3651 | 1242424.0534 | 2677874.1233 | 1242423.2903

## bus_geodata
| x | y | coords
0 | 2678012.9865 | 1242437.1684
1 | 2678035.666 | 1242441.8806
2 | 2678002.0712 | 1242427.4399
3 | 2678049.0083 | 1242443.0791
4 | 2677984.3056 | 1242453.903
5 | 2678062.0495 | 1242441.316
6 | 2677853.5345 | 1242415.4925
7 | 2677863.6055 | 1242449.949
8 | 2677865.0994 | 1242417.3455
9 | 2677940.6221 | 1242425.3757
10 | 2677940.0438 | 1242452.1315
11 | 2677910.4152 | 1242424.4304
12 | 2678061.7835 | 1242439.122
13 | 2677965.2966 | 1242453.6087
14 | 2677976.1911 | 1242504.0611
15 | 2678072.001 | 1242440.5241
16 | 2678086.521 | 1242437.2572
17 | 2678088.2473 | 1242468.7193
18 | 2678071.8864 | 1242436.0194
19 | 2677871.7998 | 1242418.5769
20 | 2677874.1233 | 1242423.2903
21 | 2677898.3651 | 1242424.0534
22 | 2677930.1871 | 1242452.0354
23 | 2677984.3056 | 1242453.903

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99663 | -0.06476 | 0.0047465 | 0.0011896
1 | 0.99609 | -0.075169 | 0.0053556 | 0.0013422
2 | 0.99702 | -0.057285 | 0 | 0
3 | 0.99584 | -0.079859 | 0 | 0
4 | 0.99872 | -0.02453 | 0 | 0
5 | 0.99562 | -0.084288 | 0 | 0
6 | 0.99427 | -0.11023 | 0 | 0
7 | 0.99389 | -0.11762 | 0.0093844 | 0.002352
8 | 0.99437 | -0.1083 | 0 | 0
9 | 0.99592 | -0.078411 | 0 | 0
10 | 0.99558 | -0.084966 | 0 | 0
11 | 0.99511 | -0.094046 | 0.01192 | 0.0029875
12 | 0.99561 | -0.084473 | 0.0047734 | 0.0011963
13 | 1 | 0 | -0.076105 | -0.018779
14 | 0.99864 | -0.02612 | 0.0017879 | 0.00044809
15 | 0.99549 | -0.086761 | 0.0047343 | 0.0011865
16 | 0.99542 | -0.0881 | 0 | 0
17 | 0.99527 | -0.090943 | 0.0051272 | 0.001285
18 | 0.99547 | -0.0871 | 0.0042673 | 0.0010695
19 | 0.99443 | -0.10717 | 0.0081069 | 0.0020318
20 | 0.99453 | -0.10521 | 0 | 0
21 | 0.99491 | -0.097759 | 0 | 0
22 | 0.99545 | -0.087373 | 0.01393 | 0.0034912
23 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024281 | 0.0060928 | -0.024269 | -0.0060855 | 1.2045e-05 | 7.3906e-06 | 0.036255 | 0.036255 | 0.036255 | 0.99663 | -0.06476 | 0.99609 | -0.075169 | 9.9603
1 | -0.029027 | -0.0072824 | 0.029038 | 0.0072889 | 1.035e-05 | 6.4325e-06 | 0.043342 | 0.043342 | 0.043342 | 0.99663 | -0.06476 | 0.99702 | -0.057285 | 11.9071
2 | 0.018913 | 0.0047432 | -0.018909 | -0.0047407 | 4.2267e-06 | 2.5214e-06 | 0.028255 | 0.028255 | 0.028255 | 0.99609 | -0.075169 | 0.99584 | -0.079859 | 7.7623
3 | -0.029038 | -0.0072889 | 0.029083 | 0.0073171 | 4.544e-05 | 2.8239e-05 | 0.043342 | 0.043342 | 0.043342 | 0.99702 | -0.057285 | 0.99872 | -0.02453 | 11.9071
4 | 0.018909 | 0.0047407 | -0.018905 | -0.0047383 | 3.9896e-06 | 2.38e-06 | 0.028255 | 0.028255 | 0.028255 | 0.99584 | -0.079859 | 0.99562 | -0.084288 | 7.7623
5 | -0.074368 | -0.018723 | 0.074455 | 0.018779 | 8.732e-05 | 5.5636e-05 | 0.11083 | 0.11083 | 0.11083 | 0.99872 | -0.02453 | 1 | 0 | 30.4485
6 | 0.001788 | 0.00044751 | -0.0017879 | -0.00044809 | 1.3533e-07 | -5.7878e-07 | 0.0026638 | 0.0026641 | 0.0026641 | 0.99872 | -0.02453 | 0.99864 | -0.02612 | 0.73188
7 | 0.043497 | 0.010959 | -0.043385 | -0.010888 | 0.00011179 | 7.0619e-05 | 0.064827 | 0.064827 | 0.064827 | 0.99872 | -0.02453 | 0.99592 | -0.078411 | 17.8097
8 | 0.014132 | 0.003542 | -0.01413 | -0.003541 | 1.6651e-06 | 9.3625e-07 | 0.021121 | 0.021121 | 0.021121 | 0.99562 | -0.084288 | 0.99549 | -0.086761 | 5.8024
9 | 0.0047734 | 0.0011963 | -0.0047734 | -0.0011963 | 4.2181e-08 | -1.7439e-09 | 0.0071342 | 0.0071342 | 0.0071342 | 0.99562 | -0.084288 | 0.99561 | -0.084473 | 1.96
10 | 0.0093877 | 0.0023535 | -0.0093844 | -0.0023519 | 3.3026e-06 | 1.5352e-06 | 0.01405 | 0.01405 | 0.01405 | 0.99427 | -0.11023 | 0.99389 | -0.11762 | 3.8599
11 | -0.0093877 | -0.0023535 | 0.0093886 | 0.0023539 | 8.6452e-07 | 4.0181e-07 | 0.01405 | 0.01405 | 0.01405 | 0.99427 | -0.11023 | 0.99437 | -0.1083 | 3.8598
12 | -0.0093886 | -0.0023539 | 0.0093891 | 0.0023541 | 5.0429e-07 | 2.3437e-07 | 0.01405 | 0.01405 | 0.01405 | 0.99437 | -0.1083 | 0.99443 | -0.10717 | 3.8598
13 | 0.013936 | 0.0034945 | -0.013932 | -0.0034921 | 4.3519e-06 | 2.4371e-06 | 0.020822 | 0.020823 | 0.020823 | 0.99592 | -0.078411 | 0.99558 | -0.084966 | 5.7205
14 | 0.029449 | 0.0073935 | -0.029427 | -0.0073799 | 2.1946e-05 | 1.3652e-05 | 0.044005 | 0.044005 | 0.044005 | 0.99592 | -0.078411 | 0.99511 | -0.094046 | 12.0893
15 | 0.013932 | 0.0034921 | -0.01393 | -0.0034912 | 1.598e-06 | 8.9491e-07 | 0.020823 | 0.020823 | 0.020823 | 0.99558 | -0.084966 | 0.99545 | -0.087373 | 5.7205
16 | 0.017507 | 0.0043924 | -0.017504 | -0.0043905 | 3.0987e-06 | 1.8266e-06 | 0.02618 | 0.02618 | 0.02618 | 0.99511 | -0.094046 | 0.99491 | -0.097759 | 7.1924
17 | 0.0042674 | 0.0010695 | -0.0042673 | -0.0010695 | 6.8767e-08 | -1.4584e-08 | 0.0063787 | 0.0063787 | 0.0063787 | 0.99549 | -0.086761 | 0.99547 | -0.0871 | 1.7524
18 | 0.0051282 | 0.0012851 | -0.0051279 | -0.001285 | 3.2702e-07 | 1.6354e-08 | 0.0076654 | 0.0076655 | 0.0076655 | 0.99549 | -0.086761 | 0.99542 | -0.0881 | 2.1059
19 | 0.0051279 | 0.001285 | -0.0051272 | -0.001285 | 6.9432e-07 | 3.4824e-08 | 0.0076655 | 0.0076656 | 0.0076656 | 0.99542 | -0.0881 | 0.99527 | -0.090943 | 2.1059
20 | -0.017496 | -0.0043859 | 0.017498 | 0.0043869 | 1.636e-06 | 9.6444e-07 | 0.026181 | 0.026181 | 0.026181 | 0.99443 | -0.10717 | 0.99453 | -0.10521 | 7.1925
21 | -0.017498 | -0.0043869 | 0.017504 | 0.0043905 | 6.2155e-06 | 3.664e-06 | 0.026181 | 0.02618 | 0.026181 | 0.99453 | -0.10521 | 0.99491 | -0.097759 | 7.1924

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.089985 | 0.022258

## res_load
| p_mw | q_mvar
0 | 0.0047465 | 0.0011896
1 | 0.0053556 | 0.0013422
2 | 0.0093844 | 0.002352
3 | 0.01192 | 0.0029875
4 | 0.0047734 | 0.0011963
5 | 0.01388 | 0.0034786
6 | 0.0017879 | 0.00044809
7 | 0.0047343 | 0.0011865
8 | 0.0051272 | 0.001285
9 | 0.0042673 | 0.0010695
10 | 0.0081069 | 0.0020318
11 | 0.01393 | 0.0034912

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1