## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_153-14_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_153-14_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_153-14_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_153-14_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_153-14_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_153-14_0_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_153-14_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_153-14_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_153-14_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_153-14_0_5_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_153-14_0_5_node_137 | 0.4 | n |  | TRUE
11 | bus_LV_153-14_0_5_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_153-14_0_5_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_153-14_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_153-14_0_5_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_153-14_0_5_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_153-14_0_5_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_153-14_0_5_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_153-14_0_5_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_153-14_0_5_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_153-14_0_5_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_153-14_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_153-14_0_5_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_153-14_0_5_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_153-14_0_5_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_153-14_0_5_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_153-14_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_153-14_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_153-14_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_153-14_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_153-14_0_5_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_153-14_0_5_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_153-14_0_5_node_101 | 0.4 | n |  | TRUE
33 | bus_LV_153-14_0_5_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_153-14_0_5_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_153-14_0_5_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_153-14_0_5_node_92 | 0.4 | n |  | TRUE
37 | bus_LV_153-14_0_5_node_135 | 0.4 | n |  | TRUE
38 | bus_LV_153-14_0_5_node_85 | 0.4 | n |  | TRUE
39 | bus_LV_153-14_0_5_node_91 | 0.4 | n |  | TRUE
40 | bus_LV_153-14_0_5_node_138 | 0.4 | n |  | TRUE
41 | bus_LV_153-14_0_5_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_153-14_0_5_node_89 | 0.4 | n |  | TRUE
43 | bus_LV_153-14_0_5_node_102 | 0.4 | n |  | TRUE
44 | bus_LV_153-14_0_5_node_136 | 0.4 | n |  | TRUE
45 | bus_LV_153-14_0_5_node_87 | 0.4 | n |  | TRUE
46 | bus_LV_153-14_0_5_node_83 | 0.4 | n |  | TRUE
47 | bus_LV_153-14_0_5_node_86 | 0.4 | n |  | TRUE
48 | bus_LV_153-14_0_5_node_94 | 0.4 | n |  | TRUE
49 | bus_LV_153-14_0_5_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_153-14_0_5_node_93 | 0.4 | n |  | TRUE
51 | bus_LV_153-14_0_5_node_96 | 0.4 | n |  | TRUE
52 | bus_LV_153-14_0_5_node_97 | 0.4 | n |  | TRUE
53 | bus_LV_153-14_0_5_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_153-14_0_5_node_98 | 0.4 | n |  | TRUE
55 | bus_LV_153-14_0_5_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_153-14_0_5_node_27 | 0.4 | n |  | TRUE
57 | bus_LV_153-14_0_5_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_153-14_0_5_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_153-14_0_5_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_153-14_0_5_node_29 | 0.4 | n |  | TRUE
61 | bus_LV_153-14_0_5_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_153-14_0_5_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_153-14_0_5_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_153-14_0_5_node_105 | 0.4 | n |  | TRUE
65 | bus_LV_153-14_0_5_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_153-14_0_5_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_153-14_0_5_node_99 | 0.4 | n |  | TRUE
68 | bus_LV_153-14_0_5_node_126 | 0.4 | n |  | TRUE
69 | bus_LV_153-14_0_5_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_153-14_0_5_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_153-14_0_5_node_106 | 0.4 | n |  | TRUE
72 | bus_LV_153-14_0_5_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_153-14_0_5_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_153-14_0_5_node_124 | 0.4 | n |  | TRUE
75 | bus_LV_153-14_0_5_node_122 | 0.4 | n |  | TRUE
76 | bus_LV_153-14_0_5_node_45 | 0.4 | n |  | TRUE
77 | bus_LV_153-14_0_5_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_153-14_0_5_node_120 | 0.4 | n |  | TRUE
79 | bus_LV_153-14_0_5_node_42 | 0.4 | n |  | TRUE
80 | bus_LV_153-14_0_5_node_46 | 0.4 | n |  | TRUE
81 | bus_LV_153-14_0_5_node_115 | 0.4 | n |  | TRUE
82 | bus_LV_153-14_0_5_node_112 | 0.4 | n |  | TRUE
83 | bus_LV_153-14_0_5_node_123 | 0.4 | n |  | TRUE
84 | bus_LV_153-14_0_5_node_118 | 0.4 | n |  | TRUE
85 | bus_LV_153-14_0_5_node_113 | 0.4 | n |  | TRUE
86 | bus_LV_153-14_0_5_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_153-14_0_5_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_153-14_0_5_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_153-14_0_5_node_58 | 0.4 | n |  | TRUE
90 | bus_LV_153-14_0_5_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_153-14_0_5_node_125 | 0.4 | n |  | TRUE
92 | bus_LV_153-14_0_5_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_153-14_0_5_node_61 | 0.4 | n |  | TRUE
94 | bus_LV_153-14_0_5_node_62 | 0.4 | n |  | TRUE
95 | bus_LV_153-14_0_5_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_153-14_0_5_node_130 | 0.4 | n |  | TRUE
97 | bus_LV_153-14_0_5_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_153-14_0_5_node_129 | 0.4 | n |  | TRUE
99 | bus_LV_153-14_0_5_node_127 | 0.4 | n |  | TRUE
100 | bus_LV_153-14_0_5_node_64 | 0.4 | n |  | TRUE
101 | bus_LV_153-14_0_5_node_65 | 0.4 | n |  | TRUE
102 | bus_LV_153-14_0_5_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_153-14_0_5_node_68 | 0.4 | n |  | TRUE
104 | bus_LV_153-14_0_5_node_67 | 0.4 | n |  | TRUE
105 | bus_LV_153-14_0_5_node_69 | 0.4 | n |  | TRUE
106 | bus_LV_153-14_0_5_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_153-14_0_5_node_81 | 0.4 | n |  | TRUE
108 | bus_LV_153-14_0_5_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_153-14_0_5_node_72 | 0.4 | n |  | TRUE
110 | bus_LV_153-14_0_5_node_73 | 0.4 | n |  | TRUE
111 | bus_LV_153-14_0_5_node_74 | 0.4 | n |  | TRUE
112 | bus_LV_153-14_0_5_node_75 | 0.4 | n |  | TRUE
113 | bus_LV_153-14_0_5_node_76 | 0.4 | n |  | TRUE
114 | bus_LV_153-14_0_5_node_79 | 0.4 | n |  | TRUE
115 | bus_LV_153-14_0_5_node_134 | 0.4 | n |  | TRUE
116 | bus_LV_153-14_0_5_node_78 | 0.4 | n |  | TRUE
117 | bus_LV_153-14_0_5_node_133 | 0.4 | n |  | TRUE
118 | bus_LV_153-14_0_5_node_82 | 0.4 | n |  | TRUE
119 | bus_LV_153-14_0_5_node_128 | 0.4 | n |  | TRUE
120 | bus_LV_153-14_0_5_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_153-14_0_5_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_153-14_0_5_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_153-14_0_5_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_153-14_0_5_node_139 | 0.4 | n |  | TRUE
125 | bus_LV_153-14_0_5_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_153-14_0_5_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_153-14_0_5_node_119 | 0.4 | n |  | TRUE
128 | bus_LV_153-14_0_5_node_131 | 0.4 | n |  | TRUE
129 | bus_LV_153-14_0_5_node_132 | 0.4 | n |  | TRUE
130 | bus_MV_355_1_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_153-14_0_5_load_0 | 0 | 0.016662 | 0.0041758 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_153-14_0_5_load_1 | 1 | 0.0052724 | 0.0013214 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_153-14_0_5_load_4 | 4 | 0.0070823 | 0.001775 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_153-14_0_5_load_16 | 5 | 0.0040711 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_153-14_0_5_load_137 | 10 | 0.0028422 | 0.00071233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_153-14_0_5_load_25 | 11 | 0.006807 | 0.001706 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_153-14_0_5_load_15 | 12 | 0.0094116 | 0.0023588 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_153-14_0_5_load_11 | 13 | 0.006747 | 0.001691 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_153-14_0_5_load_24 | 14 | 0.011022 | 0.0027624 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_153-14_0_5_load_47 | 17 | 0.0026504 | 0.00066424 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_153-14_0_5_load_37 | 19 | 0.0056464 | 0.0014151 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_153-14_0_5_load_34 | 20 | 0.010821 | 0.0027119 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_153-14_0_5_load_14 | 21 | 0.0076487 | 0.0019169 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_153-14_0_5_load_41 | 22 | 0.0040441 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_153-14_0_5_load_26 | 24 | 0.0024353 | 0.00061034 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_153-14_0_5_load_17 | 25 | 0.031749 | 0.0079571 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_153-14_0_5_load_20 | 28 | 0.0016101 | 0.00040353 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_153-14_0_5_load_53 | 31 | 0.0015771 | 0.00039526 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_153-14_0_5_load_101 | 32 | 0.010086 | 0.0025277 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_153-14_0_5_load_104 | 33 | 0.011585 | 0.0029035 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_153-14_0_5_load_103 | 34 | 0.01102 | 0.002762 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_153-14_0_5_load_38 | 35 | 0.025172 | 0.0063087 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_153-14_0_5_load_135 | 37 | 0.042398 | 0.010626 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_153-14_0_5_load_138 | 40 | 0.046646 | 0.011691 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_153-14_0_5_load_102 | 43 | 0.01009 | 0.0025288 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_153-14_0_5_load_136 | 44 | 0.037203 | 0.0093239 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_153-14_0_5_load_87 | 45 | 0.0045307 | 0.0011355 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_153-14_0_5_load_83 | 46 | 0.0020987 | 0.00052597 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_153-14_0_5_load_84 | 49 | 0.0019573 | 0.00049055 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_153-14_0_5_load_97 | 52 | 0.0020908 | 0.00052399 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_153-14_0_5_load_98 | 54 | 0.010264 | 0.0025724 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_153-14_0_5_load_39 | 55 | 0.0095074 | 0.0023828 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_153-14_0_5_load_27 | 56 | 0.0039719 | 0.00099545 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_153-14_0_5_load_48 | 57 | 0.0025476 | 0.00063849 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_153-14_0_5_load_49 | 58 | 0.0050787 | 0.0012728 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_153-14_0_5_load_28 | 59 | 0.010763 | 0.0026973 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_153-14_0_5_load_29 | 60 | 0.0019843 | 0.00049732 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_153-14_0_5_load_32 | 62 | 0.0010723 | 0.00026875 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_153-14_0_5_load_40 | 63 | 0.0084096 | 0.0021077 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_153-14_0_5_load_105 | 64 | 0.0011062 | 0.00027724 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_153-14_0_5_load_126 | 68 | 0.0030904 | 0.00077453 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_153-14_0_5_load_106 | 71 | 0.0016951 | 0.00042483 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_153-14_0_5_load_124 | 74 | 0.0025829 | 0.00064733 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_153-14_0_5_load_122 | 75 | 0.0042784 | 0.0010723 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_153-14_0_5_load_121 | 77 | 0.0010979 | 0.00027517 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_153-14_0_5_load_120 | 78 | 0.0011538 | 0.00028916 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_153-14_0_5_load_42 | 79 | 0.012305 | 0.0030838 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_153-14_0_5_load_115 | 81 | 0.0025927 | 0.00064979 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_153-14_0_5_load_112 | 82 | 0.0034951 | 0.00087594 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_153-14_0_5_load_123 | 83 | 0.0028489 | 0.000714 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_153-14_0_5_load_118 | 84 | 0.00092842 | 0.00023268 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_153-14_0_5_load_113 | 85 | 0.0041561 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_153-14_0_5_load_50 | 86 | 0.0050982 | 0.0012777 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_153-14_0_5_load_51 | 87 | 0.0064758 | 0.001623 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_153-14_0_5_load_58 | 89 | 0.0069295 | 0.0017367 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_153-14_0_5_load_100 | 90 | 0.020834 | 0.0052215 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_153-14_0_5_load_125 | 91 | 0.0011625 | 0.00029135 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_153-14_0_5_load_77 | 95 | 0.0012949 | 0.00032453 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_153-14_0_5_load_130 | 96 | 0.0024757 | 0.00062047 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_153-14_0_5_load_70 | 97 | 0.001241 | 0.00031103 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_153-14_0_5_load_129 | 98 | 0.017725 | 0.0044423 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_153-14_0_5_load_127 | 99 | 0.0072637 | 0.0018204 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_153-14_0_5_load_64 | 100 | 0.002956 | 0.00074083 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_153-14_0_5_load_65 | 101 | 0.0023842 | 0.00059754 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_153-14_0_5_load_66 | 102 | 0.0027946 | 0.0007004 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_153-14_0_5_load_68 | 103 | 0.002269 | 0.00056866 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_153-14_0_5_load_67 | 104 | 0.0024825 | 0.00062218 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_153-14_0_5_load_71 | 106 | 0.0025613 | 0.00064193 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_153-14_0_5_load_81 | 107 | 0.0017879 | 0.00044809 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_153-14_0_5_load_80 | 108 | 0.002115 | 0.00053008 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_153-14_0_5_load_72 | 109 | 0.0022126 | 0.00055454 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_153-14_0_5_load_73 | 110 | 0.0024533 | 0.00061487 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_153-14_0_5_load_74 | 111 | 0.002376 | 0.00059548 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_153-14_0_5_load_75 | 112 | 0.0019554 | 0.00049008 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_153-14_0_5_load_76 | 113 | 0.0019084 | 0.00047828 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_153-14_0_5_load_79 | 114 | 0.0024646 | 0.00061768 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_153-14_0_5_load_134 | 115 | 0.0019583 | 0.00049079 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_153-14_0_5_load_78 | 116 | 0.0021376 | 0.00053574 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_153-14_0_5_load_133 | 117 | 0.0022655 | 0.00056778 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_153-14_0_5_load_82 | 118 | 0.0022536 | 0.00056482 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_153-14_0_5_load_128 | 119 | 0.0023827 | 0.00059715 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_153-14_0_5_load_108 | 120 | 0.00078235 | 0.00019608 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_153-14_0_5_load_109 | 121 | 0.00080001 | 0.0002005 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_153-14_0_5_load_116 | 123 | 0.0094769 | 0.0023751 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_153-14_0_5_load_139 | 124 | 0.0077839 | 0.0019508 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_153-14_0_5_load_117 | 125 | 0.0049172 | 0.0012324 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_153-14_0_5_load_114 | 126 | 0.0019864 | 0.00049785 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_153-14_0_5_load_119 | 127 | 0.0035438 | 0.00088816 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_153-14_0_5_load_131 | 128 | 0.0019822 | 0.0004968 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_153-14_0_5_load_132 | 129 | 0.0020826 | 0.00052195 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_153-14_0_5_line_0 |  | 0 | 1 | 0.03118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_153-14_0_5_line_1 |  | 0 | 2 | 0.012224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_153-14_0_5_line_2 |  | 1 | 3 | 0.037295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_153-14_0_5_line_3 |  | 2 | 4 | 0.022974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_153-14_0_5_line_4 |  | 3 | 5 | 0.036832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_153-14_0_5_line_5 |  | 4 | 6 | 0.013524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_153-14_0_5_line_6 |  | 5 | 11 | 0.0027243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_153-14_0_5_line_7 |  | 6 | 7 | 0.016555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_153-14_0_5_line_8 |  | 7 | 12 | 0.036142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_153-14_0_5_line_9 |  | 7 | 13 | 0.024294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_153-14_0_5_line_10 |  | 8 | 9 | 0.026333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_153-14_0_5_line_11 |  | 8 | 10 | 0.043997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_153-14_0_5_line_12 |  | 9 | 21 | 0.0018515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_153-14_0_5_line_13 |  | 9 | 13 | 0.0082566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_153-14_0_5_line_14 |  | 11 | 24 | 0.01968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_153-14_0_5_line_15 |  | 12 | 14 | 0.022681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_153-14_0_5_line_16 |  | 15 | 16 | 0.060008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_153-14_0_5_line_17 |  | 15 | 17 | 0.033676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_153-14_0_5_line_18 |  | 15 | 18 | 0.009839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_153-14_0_5_line_19 |  | 16 | 19 | 0.01382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_153-14_0_5_line_20 |  | 16 | 20 | 0.015659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_153-14_0_5_line_21 |  | 17 | 72 | 0.025855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_153-14_0_5_line_22 |  | 18 | 62 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_153-14_0_5_line_23 |  | 18 | 59 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_153-14_0_5_line_24 |  | 21 | 22 | 0.012894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_153-14_0_5_line_25 |  | 22 | 23 | 0.047513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_153-14_0_5_line_26 |  | 23 | 35 | 0.030573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_153-14_0_5_line_27 |  | 23 | 26 | 0.015898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_153-14_0_5_line_28 |  | 24 | 56 | 0.00044515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_153-14_0_5_line_29 |  | 25 | 26 | 0.020823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_153-14_0_5_line_30 |  | 26 | 30 | 0.011152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_153-14_0_5_line_31 |  | 27 | 28 | 0.016617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_153-14_0_5_line_32 |  | 27 | 29 | 0.028131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_153-14_0_5_line_33 |  | 28 | 31 | 0.0078853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_153-14_0_5_line_34 |  | 29 | 32 | 0.019663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_153-14_0_5_line_35 |  | 30 | 33 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_153-14_0_5_line_36 |  | 30 | 34 | 0.013255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_153-14_0_5_line_37 |  | 32 | 42 | 0.017691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_153-14_0_5_line_38 |  | 34 | 43 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_153-14_0_5_line_39 |  | 35 | 55 | 0.018288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_153-14_0_5_line_40 |  | 36 | 37 | 0.0097357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_153-14_0_5_line_41 |  | 36 | 38 | 0.027964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_153-14_0_5_line_42 |  | 37 | 41 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_153-14_0_5_line_43 |  | 38 | 45 | 0.0049642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_153-14_0_5_line_44 |  | 38 | 46 | 0.021072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_153-14_0_5_line_45 |  | 39 | 40 | 0.003437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_153-14_0_5_line_46 |  | 39 | 41 | 0.039197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_153-14_0_5_line_47 |  | 41 | 44 | 0.004895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_153-14_0_5_line_48 |  | 42 | 43 | 0.021038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_153-14_0_5_line_49 |  | 45 | 50 | 0.048823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_153-14_0_5_line_50 |  | 46 | 118 | 0.035779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_153-14_0_5_line_51 |  | 47 | 48 | 0.018514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_153-14_0_5_line_52 |  | 47 | 49 | 0.00067316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_153-14_0_5_line_53 |  | 48 | 52 | 0.0044234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_153-14_0_5_line_54 |  | 49 | 118 | 0.025555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_153-14_0_5_line_55 |  | 50 | 51 | 0.077716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_153-14_0_5_line_56 |  | 51 | 98 | 0.016958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_153-14_0_5_line_57 |  | 51 | 99 | 0.00302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_153-14_0_5_line_58 |  | 52 | 66 | 0.036305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_153-14_0_5_line_59 |  | 53 | 54 | 0.0041566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_153-14_0_5_line_60 |  | 54 | 67 | 0.018779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_153-14_0_5_line_61 |  | 55 | 63 | 0.017125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_153-14_0_5_line_62 |  | 56 | 57 | 0.011877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_153-14_0_5_line_63 |  | 57 | 58 | 0.0036784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_153-14_0_5_line_64 |  | 58 | 86 | 0.0087857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_153-14_0_5_line_65 |  | 59 | 60 | 0.011178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_153-14_0_5_line_66 |  | 60 | 61 | 0.027098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_153-14_0_5_line_67 |  | 61 | 63 | 0.0055165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_153-14_0_5_line_68 |  | 62 | 64 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_153-14_0_5_line_69 |  | 64 | 69 | 0.033068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_153-14_0_5_line_70 |  | 65 | 66 | 0.072282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_153-14_0_5_line_71 |  | 65 | 67 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_153-14_0_5_line_72 |  | 65 | 68 | 0.031249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_153-14_0_5_line_73 |  | 66 | 88 | 0.043194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_153-14_0_5_line_74 |  | 67 | 90 | 0.053869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_153-14_0_5_line_75 |  | 68 | 91 | 0.0091139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_153-14_0_5_line_76 |  | 69 | 70 | 0.031808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_153-14_0_5_line_77 |  | 70 | 71 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_153-14_0_5_line_78 |  | 71 | 92 | 0.026399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_153-14_0_5_line_79 |  | 72 | 79 | 0.024465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_153-14_0_5_line_80 |  | 73 | 74 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_153-14_0_5_line_81 |  | 73 | 75 | 0.018177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_153-14_0_5_line_82 |  | 74 | 77 | 0.0076476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_153-14_0_5_line_83 |  | 75 | 83 | 0.009988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_153-14_0_5_line_84 |  | 76 | 77 | 0.0032222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_153-14_0_5_line_85 |  | 76 | 78 | 0.0043516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_153-14_0_5_line_86 |  | 80 | 81 | 0.026741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_153-14_0_5_line_87 |  | 80 | 82 | 0.018098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_153-14_0_5_line_88 |  | 81 | 84 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_153-14_0_5_line_89 |  | 82 | 85 | 0.010672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_153-14_0_5_line_90 |  | 83 | 127 | 0.0097822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_153-14_0_5_line_91 |  | 84 | 127 | 0.017292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_153-14_0_5_line_92 |  | 85 | 126 | 0.020496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_153-14_0_5_line_93 |  | 86 | 87 | 0.013347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_153-14_0_5_line_94 |  | 88 | 89 | 0.03666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_153-14_0_5_line_95 |  | 91 | 121 | 0.029658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_153-14_0_5_line_96 |  | 92 | 120 | 0.019181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_153-14_0_5_line_97 |  | 92 | 121 | 0.0075726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_153-14_0_5_line_98 |  | 92 | 122 | 0.17191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_153-14_0_5_line_99 |  | 93 | 94 | 0.052118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_153-14_0_5_line_100 |  | 93 | 95 | 0.038282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_153-14_0_5_line_101 |  | 94 | 96 | 0.011003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_153-14_0_5_line_102 |  | 95 | 97 | 0.0064559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_153-14_0_5_line_103 |  | 96 | 98 | 0.014285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_153-14_0_5_line_104 |  | 97 | 105 | 0.00326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_153-14_0_5_line_105 |  | 99 | 119 | 0.013542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_153-14_0_5_line_106 |  | 100 | 101 | 0.015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_153-14_0_5_line_107 |  | 101 | 102 | 0.0082176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_153-14_0_5_line_108 |  | 102 | 103 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_153-14_0_5_line_109 |  | 103 | 104 | 0.0079873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_153-14_0_5_line_110 |  | 104 | 105 | 0.012361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_153-14_0_5_line_111 |  | 105 | 106 | 0.037991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_153-14_0_5_line_112 |  | 106 | 107 | 0.00052533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_153-14_0_5_line_113 |  | 107 | 108 | 0.0078601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_153-14_0_5_line_114 |  | 108 | 116 | 0.0076157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_153-14_0_5_line_115 |  | 109 | 110 | 0.0078105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_153-14_0_5_line_116 |  | 109 | 111 | 0.0074858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_153-14_0_5_line_117 |  | 110 | 112 | 0.0073014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_153-14_0_5_line_118 |  | 111 | 113 | 0.00068709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_153-14_0_5_line_119 |  | 112 | 114 | 0.00058954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_153-14_0_5_line_120 |  | 113 | 115 | 0.006734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_153-14_0_5_line_121 |  | 114 | 116 | 0.0074604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_153-14_0_5_line_122 |  | 115 | 117 | 0.0075488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_153-14_0_5_line_123 |  | 117 | 129 | 0.00071323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_153-14_0_5_line_124 |  | 120 | 123 | 0.016766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_153-14_0_5_line_125 |  | 122 | 124 | 0.047745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_153-14_0_5_line_126 |  | 123 | 125 | 0.00092996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_153-14_0_5_line_127 |  | 125 | 126 | 0.016758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_153-14_0_5_line_128 |  | 128 | 129 | 0.0081372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_153-14_0_5_trafo_95 | 0.63 MVA 20/0.4 kV | 130 | 53 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2700821.4162 | 1234212.2207 | 2700809.3664 | 1234183.4631
1 | 2700826.1401 | 1234223.4948 | 2700821.4162 | 1234212.2207
2 | 2700794.9535 | 1234149.0657 | 2700809.3664 | 1234183.4631
3 | 2700826.1401 | 1234223.4948 | 2700826.7375 | 1234226.6628 | 2700828.7402 | 1234231.7784 | 2700830.8591 | 1234238.9753 | 2700832.2481 | 1234245.5856
4 | 2700794.9535 | 1234149.0657 | 2700784.6901 | 1234164.4921 | 2700773.5082 | 1234175.1549 | 2700771.04 | 1234176.5849
5 | 2700835.0429 | 1234258.7722 | 2700833.2863 | 1234252.9825 | 2700832.5333 | 1234246.943 | 2700832.2481 | 1234245.5856
6 | 2700771.04 | 1234176.5849 | 2700768.6827 | 1234177.9506
7 | 2700835.0429 | 1234258.7722 | 2700821.1254 | 1234267.7983
8 | 2700821.1254 | 1234267.7983 | 2700827.7442 | 1234276.1724 | 2700835.3503 | 1234282.5841 | 2700844.9918 | 1234288.6188 | 2700849.137 | 1234288.6892
9 | 2700821.1254 | 1234267.7983 | 2700801.0978 | 1234281.55
10 | 2700794.2912 | 1234286.2236 | 2700803.187 | 1234298.7283 | 2700813.868 | 1234296.152
11 | 2700813.868 | 1234296.152 | 2700825.3329 | 1234286.6505 | 2700848.3075 | 1234304.5205
12 | 2700794.2912 | 1234286.2236 | 2700792.7799 | 1234287.2931
13 | 2700794.2912 | 1234286.2236 | 2700801.0978 | 1234281.55
14 | 2700750.2313 | 1234184.4684 | 2700756.4285 | 1234183.1379 | 2700765.7701 | 1234179.6381 | 2700768.6827 | 1234177.9506
15 | 2700849.137 | 1234288.6892 | 2700851.4934 | 1234288.7292 | 2700864.1562 | 1234284.4854 | 2700870.3586 | 1234281.3082
16 | 2700851.8771 | 1234412.3615 | 2700871.2621 | 1234391.208 | 2700868.8726 | 1234374.0991 | 2700873.7975 | 1234360.9506
17 | 2700851.8771 | 1234412.3615 | 2700876.7337 | 1234435.0822
18 | 2700851.8771 | 1234412.3615 | 2700844.0599 | 1234406.3577
19 | 2700873.7975 | 1234360.9506 | 2700863.051 | 1234352.262
20 | 2700873.7975 | 1234360.9506 | 2700886.0268 | 1234370.7302
21 | 2700895.8176 | 1234452.5263 | 2700876.7337 | 1234435.0822
22 | 2700844.0599 | 1234406.3577 | 2700835.9016 | 1234415.982 | 2700830.9832 | 1234417.1661 | 2700830.8492 | 1234417.181
23 | 2700844.0599 | 1234406.3577 | 2700833.2852 | 1234398.6675
24 | 2700792.7799 | 1234287.2931 | 2700782.255 | 1234294.7411
25 | 2700748.9963 | 1234328.4649 | 2700756.428 | 1234319.2729 | 2700760.5576 | 1234314.6061 | 2700771.2043 | 1234303.7897 | 2700781.9077 | 1234294.9868 | 2700782.255 | 1234294.7411
26 | 2700748.9963 | 1234328.4649 | 2700753.3164 | 1234332.2076 | 2700761.5047 | 1234339.1072 | 2700771.0956 | 1234347.6762 | 2700772.0756 | 1234348.5131
27 | 2700737.2004 | 1234317.7681 | 2700748.9963 | 1234328.4649
28 | 2700750.2313 | 1234184.4684 | 2700749.7961 | 1234184.5619
29 | 2700737.2004 | 1234317.7681 | 2700721.6711 | 1234303.8966
30 | 2700737.2004 | 1234317.7681 | 2700732.6573 | 1234322.2611 | 2700727.9558 | 1234323.1488
31 | 2700696.0618 | 1234281.0212 | 2700683.4913 | 1234270.1543
32 | 2700675.9667 | 1234300.7622 | 2700696.0618 | 1234281.0212
33 | 2700683.4913 | 1234270.1543 | 2700677.526 | 1234264.9975
34 | 2700675.9667 | 1234300.7622 | 2700679.6006 | 1234320.0869
35 | 2700727.9558 | 1234323.1488 | 2700730.7488 | 1234341.0428
36 | 2700727.9558 | 1234323.1488 | 2700714.9295 | 1234325.6009
37 | 2700682.8699 | 1234337.4732 | 2700679.6006 | 1234320.0869
38 | 2700714.9295 | 1234325.6009 | 2700706.9853 | 1234327.0963 | 2700701.3723 | 1234328.2425
39 | 2700785.9821 | 1234360.3899 | 2700772.0756 | 1234348.5131
40 | 2700507.3867 | 1234403.8636 | 2700514.4427 | 1234397.1557
41 | 2700494.2876 | 1234419.6094 | 2700497.9598 | 1234401.6915 | 2700507.3867 | 1234403.8636
42 | 2700524.6539 | 1234399.508 | 2700514.4427 | 1234397.1557
43 | 2700494.2876 | 1234419.6094 | 2700489.4129 | 1234418.6709
44 | 2700494.2876 | 1234419.6094 | 2700513.0715 | 1234422.7072 | 2700515.0626 | 1234423.1235
45 | 2700556.5777 | 1234401.0047 | 2700557.1952 | 1234397.6237
46 | 2700524.6539 | 1234399.508 | 2700523.6159 | 1234404.0271 | 2700536.8142 | 1234405.6849 | 2700545.4188 | 1234404.9967 | 2700553.5621 | 1234404.2784 | 2700556.5777 | 1234401.0047
47 | 2700525.7869 | 1234394.7458 | 2700524.6539 | 1234399.508
48 | 2700682.8699 | 1234337.4732 | 2700686.5555 | 1234334.4334 | 2700695.0196 | 1234329.5398 | 2700701.3723 | 1234328.2425
49 | 2700441.6012 | 1234408.9107 | 2700450.4987 | 1234410.1509 | 2700480.991 | 1234417.0493 | 2700489.4129 | 1234418.6709
50 | 2700550.0764 | 1234430.4815 | 2700531.7055 | 1234426.603 | 2700515.0626 | 1234423.1235
51 | 2700594.0628 | 1234438.9007 | 2700575.7392 | 1234435.8995
52 | 2700575.0806 | 1234435.7604 | 2700575.7392 | 1234435.8995
53 | 2700594.0628 | 1234438.9007 | 2700598.4721 | 1234439.2536
54 | 2700550.0764 | 1234430.4815 | 2700575.0806 | 1234435.7604
55 | 2700454.2083 | 1234475.051 | 2700441.7251 | 1234474.0948 | 2700441.9084 | 1234462.8117 | 2700442.1314 | 1234423.2193 | 2700441.6012 | 1234408.9107
56 | 2700454.2083 | 1234475.051 | 2700453.1167 | 1234491.9742
57 | 2700454.2083 | 1234475.051 | 2700457.2219 | 1234474.8547
58 | 2700634.7253 | 1234439.3784 | 2700620.4032 | 1234440.1587 | 2700607.808 | 1234440.0009 | 2700598.4721 | 1234439.2536
59 | 2700699.3123 | 1234394.2832 | 2700700.1157 | 1234398.3613
60 | 2700703.7458 | 1234416.7862 | 2700700.1157 | 1234398.3613
61 | 2700798.865 | 1234371.6728 | 2700787.8197 | 1234361.9593 | 2700785.9821 | 1234360.3899
62 | 2700749.7961 | 1234184.5619 | 2700738.1841 | 1234187.0549
63 | 2700738.1841 | 1234187.0549 | 2700737.3249 | 1234187.2394 | 2700734.5569 | 1234187.6591
64 | 2700725.8705 | 1234188.9761 | 2700734.5569 | 1234187.6591
65 | 2700824.1869 | 1234392.1737 | 2700833.2852 | 1234398.6675
66 | 2700803.0075 | 1234375.3158 | 2700814.6475 | 1234385.3652 | 2700824.1869 | 1234392.1737
67 | 2700803.0075 | 1234375.3158 | 2700798.865 | 1234371.6728
68 | 2700814.2803 | 1234419.0183 | 2700830.8492 | 1234417.181
69 | 2700781.4142 | 1234422.6628 | 2700814.2803 | 1234419.0183
70 | 2700634.7253 | 1234439.3784 | 2700640.6864 | 1234438.7678 | 2700657.3494 | 1234436.5594 | 2700706.5244 | 1234431.0662
71 | 2700703.7458 | 1234416.7862 | 2700706.5244 | 1234431.0662
72 | 2700706.5244 | 1234431.0662 | 2700705.9782 | 1234434.7041 | 2700706.3843 | 1234438.436 | 2700707.3796 | 1234442.6894 | 2700708.8854 | 1234447.6519 | 2700711.0536 | 1234451.4915 | 2700713.2141 | 1234454.0078 | 2700716.7729 | 1234457.5485 | 2700717.7999 | 1234458.6634
73 | 2700634.7253 | 1234439.3784 | 2700640.6864 | 1234438.7678 | 2700639.1801 | 1234445.4472 | 2700627.4855 | 1234473.459
74 | 2700703.7458 | 1234416.7862 | 2700749.2063 | 1234408.4616 | 2700747.7309 | 1234400.8198
75 | 2700723.9749 | 1234465.3666 | 2700717.7999 | 1234458.6634
76 | 2700752.7142 | 1234435.0854 | 2700758.8247 | 1234433.6991 | 2700771.1235 | 1234425.0011 | 2700781.4142 | 1234422.6628
77 | 2700752.7142 | 1234435.0854 | 2700754.0253 | 1234439.0217 | 2700755.1802 | 1234447.0253
78 | 2700759.4285 | 1234473.0721 | 2700757.6428 | 1234464.0907 | 2700755.1802 | 1234447.0253
79 | 2700895.8176 | 1234452.5263 | 2700910.1432 | 1234435.946 | 2700911.7101 | 1234433.9296
80 | 2700930.9432 | 1234544.914 | 2700911.1056 | 1234559.3655
81 | 2700930.9432 | 1234544.914 | 2700917.4736 | 1234532.7092
82 | 2700904.9242 | 1234563.8685 | 2700911.1056 | 1234559.3655
83 | 2700917.4736 | 1234532.7092 | 2700910.072 | 1234526.0027
84 | 2700902.3198 | 1234565.7658 | 2700904.9242 | 1234563.8685
85 | 2700902.3198 | 1234565.7658 | 2700898.8939 | 1234568.4491
86 | 2700862.0834 | 1234480.0742 | 2700880.6615 | 1234499.3077
87 | 2700862.0834 | 1234480.0742 | 2700844.0319 | 1234478.7805
88 | 2700880.6615 | 1234499.3077 | 2700883.0492 | 1234501.7797 | 2700889.9161 | 1234507.9272
89 | 2700844.0319 | 1234478.7805 | 2700833.3876 | 1234478.0176
90 | 2700902.7994 | 1234519.4606 | 2700907.1811 | 1234523.3833 | 2700910.072 | 1234526.0027
91 | 2700902.7994 | 1234519.4606 | 2700889.9161 | 1234507.9272
92 | 2700833.3876 | 1234478.0176 | 2700812.9438 | 1234476.5523
93 | 2700725.8705 | 1234188.9761 | 2700712.6747 | 1234190.977
94 | 2700627.4855 | 1234473.459 | 2700622.9059 | 1234485.0346 | 2700627.7712 | 1234487.8746 | 2700625.3282 | 1234506.2908
95 | 2700723.9749 | 1234465.3666 | 2700726.1174 | 1234467.6923 | 2700734.3797 | 1234471.1127 | 2700747.0526 | 1234472.0393 | 2700751.8822 | 1234472.4423
96 | 2700759.4285 | 1234473.0721 | 2700767.9565 | 1234473.328 | 2700778.5782 | 1234474.0893
97 | 2700759.4285 | 1234473.0721 | 2700751.8822 | 1234472.4423
98 | 2700693.5674 | 1234544.6649 | 2700733.3543 | 1234558.3383 | 2700736.7763 | 1234555.6609 | 2700777.0136 | 1234549.0271 | 2700784.2425 | 1234545.08 | 2700778.838 | 1234535.2032 | 2700773.1747 | 1234521.3969 | 2700765.2125 | 1234497.6218 | 2700759.4285 | 1234473.0721
99 | 2700446.2669 | 1234548.4382 | 2700435.9693 | 1234546.7296 | 2700439.1987 | 1234525.8908 | 2700441.226 | 1234505.3987
100 | 2700446.2669 | 1234548.4382 | 2700464.7944 | 1234533.9962 | 2700468.5509 | 1234532.125 | 2700472.515 | 1234530.9578 | 2700478.893 | 1234531.9939
101 | 2700441.226 | 1234505.3987 | 2700452.1971 | 1234506.2292 | 2700452.1971 | 1234506.2292
102 | 2700478.893 | 1234531.9939 | 2700485.2653 | 1234533.0292
103 | 2700453.1167 | 1234491.9742 | 2700452.1971 | 1234506.2292
104 | 2700488.4832 | 1234533.5519 | 2700485.2653 | 1234533.0292
105 | 2700470.2014 | 1234471.263 | 2700460.0367 | 1234474.6715 | 2700457.2219 | 1234474.8547
106 | 2700546.6974 | 1234542.0592 | 2700531.7513 | 1234539.875
107 | 2700523.62 | 1234538.6867 | 2700531.7513 | 1234539.875
108 | 2700523.62 | 1234538.6867 | 2700508.6173 | 1234536.4943
109 | 2700500.7139 | 1234535.3393 | 2700508.6173 | 1234536.4943
110 | 2700488.4832 | 1234533.5519 | 2700500.7139 | 1234535.3393
111 | 2700488.4832 | 1234533.5519 | 2700492.6023 | 1234505.7786 | 2700502.4123 | 1234507.211
112 | 2700502.9321 | 1234507.2869 | 2700502.4123 | 1234507.211
113 | 2700502.9321 | 1234507.2869 | 2700510.7097 | 1234508.4225
114 | 2700518.2455 | 1234509.5229 | 2700510.7097 | 1234508.4225
115 | 2700541.1643 | 1234512.8693 | 2700533.4357 | 1234511.7408
116 | 2700541.1643 | 1234512.8693 | 2700548.5716 | 1234513.9509
117 | 2700526.2109 | 1234510.6859 | 2700533.4357 | 1234511.7408
118 | 2700549.2515 | 1234514.0502 | 2700548.5716 | 1234513.9509
119 | 2700526.2109 | 1234510.6859 | 2700525.6276 | 1234510.6007
120 | 2700549.2515 | 1234514.0502 | 2700555.9148 | 1234515.0231
121 | 2700518.2455 | 1234509.5229 | 2700525.6276 | 1234510.6007
122 | 2700563.3844 | 1234516.1138 | 2700555.9148 | 1234515.0231
123 | 2700564.0902 | 1234516.2168 | 2700563.3844 | 1234516.1138
124 | 2700795.3013 | 1234475.2878 | 2700778.5782 | 1234474.0893
125 | 2700693.5674 | 1234544.6649 | 2700697.3716 | 1234524.8034 | 2700714.2451 | 1234503.0286
126 | 2700795.3013 | 1234475.2878 | 2700796.2289 | 1234475.3543
127 | 2700812.9438 | 1234476.5523 | 2700796.2289 | 1234475.3543
128 | 2700572.142 | 1234517.3925 | 2700564.0902 | 1234516.2168

## bus_geodata
| x | y | coords
0 | 2700821.4162 | 1234212.2207
1 | 2700809.3664 | 1234183.4631
2 | 2700826.1401 | 1234223.4948
3 | 2700794.9535 | 1234149.0657
4 | 2700832.2481 | 1234245.5856
5 | 2700771.04 | 1234176.5849
6 | 2700835.0429 | 1234258.7722
7 | 2700821.1254 | 1234267.7983
8 | 2700813.868 | 1234296.152
9 | 2700794.2912 | 1234286.2236
10 | 2700848.3075 | 1234304.5205
11 | 2700768.6827 | 1234177.9506
12 | 2700849.137 | 1234288.6892
13 | 2700801.0978 | 1234281.55
14 | 2700870.3586 | 1234281.3082
15 | 2700851.8771 | 1234412.3615
16 | 2700873.7975 | 1234360.9506
17 | 2700876.7337 | 1234435.0822
18 | 2700844.0599 | 1234406.3577
19 | 2700863.051 | 1234352.262
20 | 2700886.0268 | 1234370.7302
21 | 2700792.7799 | 1234287.2931
22 | 2700782.255 | 1234294.7411
23 | 2700748.9963 | 1234328.4649
24 | 2700750.2313 | 1234184.4684
25 | 2700721.6711 | 1234303.8966
26 | 2700737.2004 | 1234317.7681
27 | 2700696.0618 | 1234281.0212
28 | 2700683.4913 | 1234270.1543
29 | 2700675.9667 | 1234300.7622
30 | 2700727.9558 | 1234323.1488
31 | 2700677.526 | 1234264.9975
32 | 2700679.6006 | 1234320.0869
33 | 2700730.7488 | 1234341.0428
34 | 2700714.9295 | 1234325.6009
35 | 2700772.0756 | 1234348.5131
36 | 2700507.3867 | 1234403.8636
37 | 2700514.4427 | 1234397.1557
38 | 2700494.2876 | 1234419.6094
39 | 2700556.5777 | 1234401.0047
40 | 2700557.1952 | 1234397.6237
41 | 2700524.6539 | 1234399.508
42 | 2700682.8699 | 1234337.4732
43 | 2700701.3723 | 1234328.2425
44 | 2700525.7869 | 1234394.7458
45 | 2700489.4129 | 1234418.6709
46 | 2700515.0626 | 1234423.1235
47 | 2700575.7392 | 1234435.8995
48 | 2700594.0628 | 1234438.9007
49 | 2700575.0806 | 1234435.7604
50 | 2700441.6012 | 1234408.9107
51 | 2700454.2083 | 1234475.051
52 | 2700598.4721 | 1234439.2536
53 | 2700699.3123 | 1234394.2832
54 | 2700700.1157 | 1234398.3613
55 | 2700785.9821 | 1234360.3899
56 | 2700749.7961 | 1234184.5619
57 | 2700738.1841 | 1234187.0549
58 | 2700734.5569 | 1234187.6591
59 | 2700833.2852 | 1234398.6675
60 | 2700824.1869 | 1234392.1737
61 | 2700803.0075 | 1234375.3158
62 | 2700830.8492 | 1234417.181
63 | 2700798.865 | 1234371.6728
64 | 2700814.2803 | 1234419.0183
65 | 2700706.5244 | 1234431.0662
66 | 2700634.7253 | 1234439.3784
67 | 2700703.7458 | 1234416.7862
68 | 2700717.7999 | 1234458.6634
69 | 2700781.4142 | 1234422.6628
70 | 2700752.7142 | 1234435.0854
71 | 2700755.1802 | 1234447.0253
72 | 2700895.8176 | 1234452.5263
73 | 2700930.9432 | 1234544.914
74 | 2700911.1056 | 1234559.3655
75 | 2700917.4736 | 1234532.7092
76 | 2700902.3198 | 1234565.7658
77 | 2700904.9242 | 1234563.8685
78 | 2700898.8939 | 1234568.4491
79 | 2700911.7101 | 1234433.9296
80 | 2700862.0834 | 1234480.0742
81 | 2700880.6615 | 1234499.3077
82 | 2700844.0319 | 1234478.7805
83 | 2700910.072 | 1234526.0027
84 | 2700889.9161 | 1234507.9272
85 | 2700833.3876 | 1234478.0176
86 | 2700725.8705 | 1234188.9761
87 | 2700712.6747 | 1234190.977
88 | 2700627.4855 | 1234473.459
89 | 2700625.3282 | 1234506.2908
90 | 2700747.7309 | 1234400.8198
91 | 2700723.9749 | 1234465.3666
92 | 2700759.4285 | 1234473.0721
93 | 2700446.2669 | 1234548.4382
94 | 2700441.226 | 1234505.3987
95 | 2700478.893 | 1234531.9939
96 | 2700452.1971 | 1234506.2292
97 | 2700485.2653 | 1234533.0292
98 | 2700453.1167 | 1234491.9742
99 | 2700457.2219 | 1234474.8547
100 | 2700546.6974 | 1234542.0592
101 | 2700531.7513 | 1234539.875
102 | 2700523.62 | 1234538.6867
103 | 2700508.6173 | 1234536.4943
104 | 2700500.7139 | 1234535.3393
105 | 2700488.4832 | 1234533.5519
106 | 2700502.4123 | 1234507.211
107 | 2700502.9321 | 1234507.2869
108 | 2700510.7097 | 1234508.4225
109 | 2700541.1643 | 1234512.8693
110 | 2700533.4357 | 1234511.7408
111 | 2700548.5716 | 1234513.9509
112 | 2700526.2109 | 1234510.6859
113 | 2700549.2515 | 1234514.0502
114 | 2700525.6276 | 1234510.6007
115 | 2700555.9148 | 1234515.0231
116 | 2700518.2455 | 1234509.5229
117 | 2700563.3844 | 1234516.1138
118 | 2700550.0764 | 1234430.4815
119 | 2700470.2014 | 1234471.263
120 | 2700778.5782 | 1234474.0893
121 | 2700751.8822 | 1234472.4423
122 | 2700693.5674 | 1234544.6649
123 | 2700795.3013 | 1234475.2878
124 | 2700714.2451 | 1234503.0286
125 | 2700796.2289 | 1234475.3543
126 | 2700812.9438 | 1234476.5523
127 | 2700902.7994 | 1234519.4606
128 | 2700572.142 | 1234517.3925
129 | 2700564.0902 | 1234516.2168
130 | 2700703.7458 | 1234416.7862

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97627 | -0.4568 | 0.016662 | 0.0041758
1 | 0.97505 | -0.48064 | 0.0052724 | 0.0013214
2 | 0.97693 | -0.44375 | 0 | 0
3 | 0.97378 | -0.50562 | 0 | 0
4 | 0.97725 | -0.43762 | 0.0070823 | 0.001775
5 | 0.97253 | -0.53036 | 0.0040711 | 0.0010203
6 | 0.97741 | -0.43439 | 0 | 0
7 | 0.97761 | -0.43043 | 0 | 0
8 | 0.97807 | -0.4214 | 0 | 0
9 | 0.97814 | -0.42003 | 0 | 0
10 | 0.97796 | -0.42367 | 0.0028422 | 0.00071233
11 | 0.97245 | -0.53199 | 0.006807 | 0.001706
12 | 0.97693 | -0.44391 | 0.0094116 | 0.0023588
13 | 0.978 | -0.42282 | 0.006747 | 0.001691
14 | 0.9767 | -0.44848 | 0.011022 | 0.0027624
15 | 0.984 | -0.30589 | 0 | 0
16 | 0.98309 | -0.3237 | 0 | 0
17 | 0.98353 | -0.31496 | 0.0026504 | 0.00066424
18 | 0.98428 | -0.30032 | 0 | 0
19 | 0.98302 | -0.3251 | 0.0056464 | 0.0014151
20 | 0.98293 | -0.32675 | 0.010821 | 0.0027119
21 | 0.97818 | -0.41939 | 0.0076487 | 0.0019169
22 | 0.97842 | -0.41454 | 0.0040441 | 0.0010135
23 | 0.97937 | -0.396 | 0 | 0
24 | 0.97198 | -0.54128 | 0.0024353 | 0.00061034
25 | 0.97761 | -0.43053 | 0.031749 | 0.0079571
26 | 0.97822 | -0.41848 | 0 | 0
27 | 0.97641 | -0.45421 | 0 | 0
28 | 0.97636 | -0.45518 | 0.0016101 | 0.00040353
29 | 0.97649 | -0.45257 | 0 | 0
30 | 0.97775 | -0.42783 | 0 | 0
31 | 0.97635 | -0.45541 | 0.0015771 | 0.00039526
32 | 0.97655 | -0.45142 | 0.010086 | 0.0025277
33 | 0.97755 | -0.43165 | 0.011585 | 0.0029035
34 | 0.97733 | -0.43614 | 0.01102 | 0.002762
35 | 0.98042 | -0.37547 | 0.025172 | 0.0063087
36 | 0.98428 | -0.30101 | 0 | 0
37 | 0.98315 | -0.32315 | 0.042398 | 0.010626
38 | 0.98754 | -0.2377 | 0 | 0
39 | 0.98064 | -0.37208 | 0 | 0
40 | 0.9805 | -0.37499 | 0.046646 | 0.011691
41 | 0.98234 | -0.339 | 0 | 0
42 | 0.97677 | -0.44713 | 0 | 0
43 | 0.97703 | -0.44203 | 0.01009 | 0.0025288
44 | 0.98217 | -0.34229 | 0.037203 | 0.0093239
45 | 0.98747 | -0.23912 | 0.0045307 | 0.0011355
46 | 0.98835 | -0.22217 | 0.0020987 | 0.00052597
47 | 0.99075 | -0.17595 | 0 | 0
48 | 0.99148 | -0.16198 | 0 | 0
49 | 0.99072 | -0.17646 | 0.0019573 | 0.00049055
50 | 0.98679 | -0.25232 | 0 | 0
51 | 0.98407 | -0.30501 | 0 | 0
52 | 0.99165 | -0.15864 | 0.0020908 | 0.00052399
53 | 1 | 0 | -0.59719 | -0.1531
54 | 0.99955 | -0.0084897 | 0.010264 | 0.0025724
55 | 0.98114 | -0.36154 | 0.0095074 | 0.0023828
56 | 0.97197 | -0.54147 | 0.0039719 | 0.00099545
57 | 0.97176 | -0.54568 | 0.0025476 | 0.00063849
58 | 0.9717 | -0.54681 | 0.0050787 | 0.0012728
59 | 0.98369 | -0.3118 | 0.010763 | 0.0026973
60 | 0.98321 | -0.32107 | 0.0019843 | 0.00049732
61 | 0.98207 | -0.34338 | 0 | 0
62 | 0.98518 | -0.28289 | 0.0010723 | 0.00026875
63 | 0.98183 | -0.34793 | 0.0084096 | 0.0021077
64 | 0.98603 | -0.26654 | 0.0011062 | 0.00027724
65 | 0.99606 | -0.07457 | 0 | 0
66 | 0.99309 | -0.13104 | 0 | 0
67 | 0.99755 | -0.046266 | 0 | 0
68 | 0.99413 | -0.11119 | 0.0030904 | 0.00077453
69 | 0.98771 | -0.23406 | 0 | 0
70 | 0.98933 | -0.20292 | 0 | 0
71 | 0.98995 | -0.19097 | 0.0016951 | 0.00042483
72 | 0.98324 | -0.3207 | 0 | 0
73 | 0.98719 | -0.24499 | 0 | 0
74 | 0.98708 | -0.24712 | 0.0025829 | 0.00064733
75 | 0.98727 | -0.24342 | 0.0042784 | 0.0010723
76 | 0.98706 | -0.24749 | 0 | 0
77 | 0.98707 | -0.24743 | 0.0010979 | 0.00027517
78 | 0.98706 | -0.24758 | 0.0011538 | 0.00028916
79 | 0.98296 | -0.32612 | 0.012305 | 0.0030838
80 | 0.98837 | -0.22211 | 0 | 0
81 | 0.9879 | -0.2312 | 0.0025927 | 0.00064979
82 | 0.98868 | -0.21597 | 0.0034951 | 0.00087594
83 | 0.98735 | -0.2418 | 0.0028489 | 0.000714
84 | 0.98771 | -0.23491 | 0.00092842 | 0.00023268
85 | 0.9889 | -0.21168 | 0.0041561 | 0.0010416
86 | 0.9716 | -0.54869 | 0.0050982 | 0.0012777
87 | 0.97152 | -0.55028 | 0.0064758 | 0.001623
88 | 0.99282 | -0.13633 | 0 | 0
89 | 0.99259 | -0.14083 | 0.0069295 | 0.0017367
90 | 0.99653 | -0.065945 | 0.020834 | 0.0052215
91 | 0.99357 | -0.12179 | 0.0011625 | 0.00029135
92 | 0.99131 | -0.16507 | 0 | 0
93 | 0.97971 | -0.38979 | 0 | 0
94 | 0.98193 | -0.34664 | 0 | 0
95 | 0.97809 | -0.4216 | 0.0012949 | 0.00032453
96 | 0.98239 | -0.33756 | 0.0024757 | 0.00062047
97 | 0.97782 | -0.42682 | 0.001241 | 0.00031103
98 | 0.98303 | -0.32514 | 0.017725 | 0.0044423
99 | 0.98404 | -0.30553 | 0.0072637 | 0.0018204
100 | 0.97727 | -0.43767 | 0.002956 | 0.00074083
101 | 0.97731 | -0.43686 | 0.0023842 | 0.00059754
102 | 0.97735 | -0.43606 | 0.0027946 | 0.0007004
103 | 0.97747 | -0.43381 | 0.002269 | 0.00056866
104 | 0.97755 | -0.43229 | 0.0024825 | 0.00062218
105 | 0.97769 | -0.42939 | 0 | 0
106 | 0.97663 | -0.45037 | 0.0025613 | 0.00064193
107 | 0.97661 | -0.45064 | 0.0017879 | 0.00044809
108 | 0.97642 | -0.45436 | 0.002115 | 0.00053008
109 | 0.97587 | -0.46526 | 0.0022126 | 0.00055454
110 | 0.97598 | -0.46314 | 0.0024533 | 0.00061487
111 | 0.97578 | -0.46698 | 0.002376 | 0.00059548
112 | 0.97609 | -0.46084 | 0.0019554 | 0.00049008
113 | 0.97578 | -0.46711 | 0.0019084 | 0.00047828
114 | 0.9761 | -0.46063 | 0.0024646 | 0.00061768
115 | 0.97572 | -0.46813 | 0.0019583 | 0.00049079
116 | 0.97626 | -0.45768 | 0.0021376 | 0.00053574
117 | 0.97568 | -0.469 | 0.0022655 | 0.00056778
118 | 0.98973 | -0.1956 | 0.0022536 | 0.00056482
119 | 0.98401 | -0.30611 | 0.0023827 | 0.00059715
120 | 0.99054 | -0.18 | 0.00078235 | 0.00019608
121 | 0.99177 | -0.15627 | 0.00080001 | 0.0002005
122 | 0.99008 | -0.18885 | 0 | 0
123 | 0.98987 | -0.19283 | 0.0094769 | 0.0023751
124 | 0.98974 | -0.19546 | 0.0077839 | 0.0019508
125 | 0.98985 | -0.19339 | 0.0049172 | 0.0012324
126 | 0.9894 | -0.20194 | 0.0019864 | 0.00049785
127 | 0.98746 | -0.2397 | 0.0035438 | 0.00088816
128 | 0.97566 | -0.46935 | 0.0019822 | 0.0004968
129 | 0.97568 | -0.46906 | 0.0020826 | 0.00052195
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.041913 | 0.010563 | -0.041865 | -0.010532 | 4.7749e-05 | 3.017e-05 | 0.063904 | 0.063904 | 0.063904 | 0.97627 | -0.4568 | 0.97505 | -0.48064 | 17.5561
1 | -0.058574 | -0.014738 | 0.058611 | 0.014762 | 3.6554e-05 | 2.3241e-05 | 0.089299 | 0.089299 | 0.089299 | 0.97627 | -0.4568 | 0.97693 | -0.44375 | 24.5328
2 | 0.036593 | 0.009211 | -0.036549 | -0.0091835 | 4.3637e-05 | 2.7463e-05 | 0.055858 | 0.055858 | 0.055858 | 0.97505 | -0.48064 | 0.97378 | -0.50562 | 15.3456
3 | -0.058611 | -0.014762 | 0.058628 | 0.014771 | 1.7176e-05 | 9.8413e-06 | 0.089299 | 0.089299 | 0.089299 | 0.97693 | -0.44375 | 0.97725 | -0.43762 | 6.1332
4 | 0.036549 | 0.0091835 | -0.036506 | -0.0091564 | 4.3095e-05 | 2.7123e-05 | 0.055858 | 0.055858 | 0.055858 | 0.97378 | -0.50562 | 0.97253 | -0.53036 | 15.3457
5 | -0.06571 | -0.016546 | 0.065721 | 0.016552 | 1.0159e-05 | 5.6547e-06 | 0.10008 | 0.10008 | 0.10008 | 0.97725 | -0.43762 | 0.97741 | -0.43439 | 5.4991
6 | 0.032435 | 0.0081361 | -0.032432 | -0.0081345 | 2.5163e-06 | 1.5766e-06 | 0.049629 | 0.049629 | 0.049629 | 0.97253 | -0.53036 | 0.97245 | -0.53199 | 13.6344
7 | -0.065721 | -0.016552 | 0.065733 | 0.016559 | 1.2437e-05 | 6.9218e-06 | 0.10008 | 0.10008 | 0.10008 | 0.97741 | -0.43439 | 0.97761 | -0.43043 | 5.499
8 | 0.020449 | 0.0051304 | -0.020436 | -0.0051225 | 1.3132e-05 | 7.9519e-06 | 0.031128 | 0.031128 | 0.031128 | 0.97761 | -0.43043 | 0.97693 | -0.44391 | 8.5517
9 | -0.086182 | -0.021689 | 0.086214 | 0.021708 | 3.1369e-05 | 1.8552e-05 | 0.13121 | 0.13121 | 0.13121 | 0.97761 | -0.43043 | 0.978 | -0.42282 | 7.2093
10 | -0.0028426 | -0.00071198 | 0.0028427 | 0.00071177 | 1.8467e-07 | -2.1233e-07 | 0.0043244 | 0.0043243 | 0.0043244 | 0.97807 | -0.4214 | 0.97814 | -0.42003 | 1.188
11 | 0.0028426 | 0.00071198 | -0.0028422 | -0.00071233 | 3.0855e-07 | -3.5463e-07 | 0.0043244 | 0.0043246 | 0.0043246 | 0.97807 | -0.4214 | 0.97796 | -0.42367 | 1.1881
12 | -0.095816 | -0.024118 | 0.095819 | 0.02412 | 2.9519e-06 | 1.773e-06 | 0.1458 | 0.1458 | 0.1458 | 0.97814 | -0.42003 | 0.97818 | -0.41939 | 8.0109
13 | 0.092973 | 0.023406 | -0.092961 | -0.023399 | 1.2394e-05 | 7.4142e-06 | 0.14147 | 0.14148 | 0.14148 | 0.97814 | -0.42003 | 0.978 | -0.42282 | 7.7734
14 | 0.025625 | 0.0064285 | -0.025614 | -0.0064215 | 1.1348e-05 | 7.0189e-06 | 0.039213 | 0.039213 | 0.039213 | 0.97245 | -0.53199 | 0.97198 | -0.54128 | 10.7729
15 | 0.011025 | 0.0027637 | -0.011022 | -0.0027624 | 2.3984e-06 | 1.2511e-06 | 0.016793 | 0.016793 | 0.016793 | 0.97693 | -0.44391 | 0.9767 | -0.44848 | 4.6134
16 | 0.016483 | 0.0041361 | -0.016469 | -0.0041279 | 1.3983e-05 | 8.1876e-06 | 0.024928 | 0.024928 | 0.024928 | 0.984 | -0.30589 | 0.98309 | -0.3237 | 6.8483
17 | 0.014968 | 0.0037553 | -0.014962 | -0.0037516 | 6.4709e-06 | 3.7138e-06 | 0.022636 | 0.022636 | 0.022636 | 0.984 | -0.30589 | 0.98353 | -0.31496 | 6.2188
18 | -0.031451 | -0.0078914 | 0.031459 | 0.0078966 | 8.3471e-06 | 5.2171e-06 | 0.047564 | 0.047564 | 0.047564 | 0.984 | -0.30589 | 0.98428 | -0.30032 | 13.067
19 | 0.0056468 | 0.0014152 | -0.0056464 | -0.0014151 | 3.7858e-07 | 6.7082e-08 | 0.008547 | 0.0085471 | 0.0085471 | 0.98309 | -0.3237 | 0.98302 | -0.3251 | 2.3481
20 | 0.010822 | 0.0027127 | -0.010821 | -0.0027119 | 1.5757e-06 | 8.0991e-07 | 0.016381 | 0.016381 | 0.016381 | 0.98309 | -0.3237 | 0.98293 | -0.32675 | 4.5002
21 | 0.012311 | 0.0030874 | -0.012308 | -0.0030856 | 3.3639e-06 | 1.8249e-06 | 0.018627 | 0.018627 | 0.018627 | 0.98353 | -0.31496 | 0.98324 | -0.3207 | 5.1172
22 | -0.27379 | -0.069216 | 0.27402 | 0.069362 | 0.00022909 | 0.00014549 | 0.41413 | 0.41413 | 0.41413 | 0.98428 | -0.30032 | 0.98518 | -0.28289 | 22.7542
23 | 0.24233 | 0.06132 | -0.2422 | -0.061235 | 0.0001334 | 8.4538e-05 | 0.36656 | 0.36656 | 0.36656 | 0.98428 | -0.30032 | 0.98369 | -0.3118 | 20.1409
24 | -0.10347 | -0.026037 | 0.10349 | 0.026051 | 2.3968e-05 | 1.453e-05 | 0.15743 | 0.15743 | 0.15743 | 0.97818 | -0.41939 | 0.97842 | -0.41454 | 8.6502
25 | -0.10754 | -0.027065 | 0.10763 | 0.027123 | 9.5357e-05 | 5.8042e-05 | 0.16358 | 0.16358 | 0.16358 | 0.97842 | -0.41454 | 0.97937 | -0.396 | 8.9882
26 | -0.1855 | -0.046695 | 0.18568 | 0.04681 | 0.00018224 | 0.00011471 | 0.28191 | 0.28191 | 0.28191 | 0.97937 | -0.396 | 0.98042 | -0.37547 | 15.4898
27 | 0.077869 | 0.019572 | -0.077785 | -0.019519 | 8.3478e-05 | 5.3226e-05 | 0.11833 | 0.11833 | 0.11833 | 0.97937 | -0.396 | 0.97822 | -0.41848 | 32.5085
28 | 0.023179 | 0.0058112 | -0.023178 | -0.005811 | 2.102e-07 | 1.2901e-07 | 0.035485 | 0.035485 | 0.035485 | 0.97198 | -0.54128 | 0.97197 | -0.54147 | 9.7487
29 | -0.031749 | -0.0079571 | 0.031768 | 0.0079685 | 1.8235e-05 | 1.1409e-05 | 0.048325 | 0.048325 | 0.048325 | 0.97761 | -0.43053 | 0.97822 | -0.41848 | 13.2762
30 | 0.046018 | 0.01155 | -0.045997 | -0.011537 | 2.0495e-05 | 1.2977e-05 | 0.070006 | 0.070006 | 0.070006 | 0.97822 | -0.41848 | 0.97775 | -0.42783 | 19.2323
31 | 0.0031874 | 0.00079859 | -0.0031872 | -0.0007987 | 1.4702e-07 | -1.1373e-07 | 0.0048574 | 0.0048575 | 0.0048575 | 0.97641 | -0.45421 | 0.97636 | -0.45518 | 1.3345
32 | -0.0031874 | -0.00079859 | 0.0031876 | 0.0007984 | 2.4889e-07 | -1.9259e-07 | 0.0048574 | 0.0048573 | 0.0048574 | 0.97641 | -0.45421 | 0.97649 | -0.45257 | 1.3344
33 | 0.0015771 | 0.00039518 | -0.0015771 | -0.00039526 | 1.7083e-08 | -8.7681e-08 | 0.0024036 | 0.0024036 | 0.0024036 | 0.97636 | -0.45518 | 0.97635 | -0.45541 | 0.66034
34 | -0.0031876 | -0.0007984 | 0.0031878 | 0.00079826 | 1.7397e-07 | -1.3466e-07 | 0.0048573 | 0.0048572 | 0.0048573 | 0.97649 | -0.45257 | 0.97655 | -0.45142 | 1.3344
35 | 0.011587 | 0.0029047 | -0.011585 | -0.0029035 | 2.1121e-06 | 1.1246e-06 | 0.017635 | 0.017635 | 0.017635 | 0.97775 | -0.42783 | 0.97755 | -0.43165 | 4.8447
36 | 0.03441 | 0.0086326 | -0.034396 | -0.0086241 | 1.3633e-05 | 8.559e-06 | 0.052371 | 0.052371 | 0.052371 | 0.97775 | -0.42783 | 0.97733 | -0.43614 | 14.3876
37 | -0.013274 | -0.003326 | 0.013276 | 0.0033275 | 2.7138e-06 | 1.5154e-06 | 0.020225 | 0.020225 | 0.020225 | 0.97655 | -0.45142 | 0.97677 | -0.44713 | 5.5564
38 | 0.023376 | 0.0058621 | -0.023369 | -0.0058581 | 6.5616e-06 | 4.0264e-06 | 0.035592 | 0.035592 | 0.035592 | 0.97733 | -0.43614 | 0.97703 | -0.44203 | 9.778
39 | -0.21085 | -0.053118 | 0.21099 | 0.053207 | 0.00014055 | 8.8801e-05 | 0.32012 | 0.32012 | 0.32012 | 0.98042 | -0.37547 | 0.98114 | -0.36154 | 17.5889
40 | 0.12653 | 0.031821 | -0.1264 | -0.031736 | 0.00013364 | 8.5408e-05 | 0.19133 | 0.19133 | 0.19133 | 0.98428 | -0.30101 | 0.98315 | -0.32315 | 52.562
41 | -0.12653 | -0.031821 | 0.12691 | 0.032066 | 0.00038387 | 0.00024532 | 0.19133 | 0.19133 | 0.19133 | 0.98428 | -0.30101 | 0.98754 | -0.2377 | 52.562
42 | 0.083999 | 0.02111 | -0.083935 | -0.021069 | 6.3533e-05 | 4.0528e-05 | 0.12715 | 0.12715 | 0.12715 | 0.98315 | -0.32315 | 0.98234 | -0.339 | 34.9327
43 | 0.080651 | 0.020434 | -0.080646 | -0.02043 | 5.5055e-06 | 3.206e-06 | 0.1216 | 0.1216 | 0.1216 | 0.98754 | -0.2377 | 0.98747 | -0.23912 | 6.6815
44 | -0.20757 | -0.0525 | 0.20772 | 0.052598 | 0.00015476 | 9.7696e-05 | 0.31293 | 0.31293 | 0.31293 | 0.98754 | -0.2377 | 0.98835 | -0.22217 | 17.1939
45 | 0.046653 | 0.011695 | -0.046646 | -0.011691 | 6.4591e-06 | 4.0905e-06 | 0.070791 | 0.070791 | 0.070791 | 0.98064 | -0.37208 | 0.9805 | -0.37499 | 19.4482
46 | -0.046653 | -0.011695 | 0.046727 | 0.011741 | 7.3662e-05 | 4.6648e-05 | 0.070791 | 0.070791 | 0.070791 | 0.98064 | -0.37208 | 0.98234 | -0.339 | 19.4482
47 | 0.037209 | 0.0093276 | -0.037203 | -0.0093239 | 5.8315e-06 | 3.6702e-06 | 0.056364 | 0.056364 | 0.056364 | 0.98234 | -0.339 | 0.98217 | -0.34229 | 15.4845
48 | -0.013276 | -0.0033275 | 0.013279 | 0.0033293 | 3.2272e-06 | 1.802e-06 | 0.020225 | 0.020225 | 0.020225 | 0.97677 | -0.44713 | 0.97703 | -0.44203 | 5.5564
49 | 0.076115 | 0.019295 | -0.076067 | -0.019267 | 4.8238e-05 | 2.7752e-05 | 0.11478 | 0.11478 | 0.11478 | 0.98747 | -0.23912 | 0.98679 | -0.25232 | 6.3064
50 | -0.20982 | -0.053124 | 0.21009 | 0.053293 | 0.0002681 | 0.00016929 | 0.31609 | 0.31609 | 0.31609 | 0.98835 | -0.22217 | 0.98973 | -0.1956 | 17.3674
51 | -0.2145 | -0.054475 | 0.21464 | 0.054566 | 0.00014434 | 9.1185e-05 | 0.32241 | 0.32241 | 0.32241 | 0.99075 | -0.17595 | 0.99148 | -0.16198 | 17.7151
52 | 0.2145 | 0.054475 | -0.21449 | -0.054472 | 5.2482e-06 | 3.3155e-06 | 0.32241 | 0.32241 | 0.32241 | 0.99075 | -0.17595 | 0.99072 | -0.17646 | 17.7151
53 | -0.21464 | -0.054566 | 0.21468 | 0.054588 | 3.4486e-05 | 2.1786e-05 | 0.32241 | 0.32241 | 0.32241 | 0.99148 | -0.16198 | 0.99165 | -0.15864 | 17.715
54 | 0.21254 | 0.053981 | -0.21234 | -0.053858 | 0.00019562 | 0.00012355 | 0.31947 | 0.31947 | 0.31947 | 0.99072 | -0.17646 | 0.98973 | -0.1956 | 17.5536
55 | 0.076067 | 0.019267 | -0.075875 | -0.019146 | 0.00019196 | 0.00012088 | 0.11478 | 0.11478 | 0.11478 | 0.98679 | -0.25232 | 0.98407 | -0.30501 | 15.7661
56 | 0.066228 | 0.016729 | -0.066164 | -0.016688 | 6.3837e-05 | 4.064e-05 | 0.10019 | 0.10019 | 0.10019 | 0.98407 | -0.30501 | 0.98303 | -0.32514 | 27.525
57 | 0.0096466 | 0.0024176 | -0.0096464 | -0.0024175 | 2.4096e-07 | 1.1585e-07 | 0.014587 | 0.014587 | 0.014587 | 0.98407 | -0.30501 | 0.98404 | -0.30553 | 4.0073
58 | -0.21677 | -0.055112 | 0.21706 | 0.055294 | 0.00028858 | 0.00018235 | 0.32555 | 0.32555 | 0.32555 | 0.99165 | -0.15864 | 0.99309 | -0.13104 | 17.8874
59 | 0.59554 | 0.1531 | -0.59529 | -0.15294 | 0.00024557 | 0.00015689 | 0.88754 | 0.88754 | 0.88754 | 1 | 0 | 0.99955 | -0.0084897 | 48.7658
60 | 0.58503 | 0.15037 | -0.58396 | -0.14969 | 0.0010716 | 0.00068459 | 0.87226 | 0.87226 | 0.87226 | 0.99955 | -0.0084897 | 0.99755 | -0.046266 | 47.9263
61 | -0.2205 | -0.05559 | 0.22065 | 0.055681 | 0.00014374 | 9.0914e-05 | 0.33454 | 0.33454 | 0.33454 | 0.98114 | -0.36154 | 0.98183 | -0.34793 | 18.3811
62 | 0.019206 | 0.0048156 | -0.019203 | -0.0048133 | 3.8508e-06 | 2.3174e-06 | 0.029405 | 0.029405 | 0.029405 | 0.97197 | -0.54147 | 0.97176 | -0.54568 | 8.0782
63 | 0.016655 | 0.0041748 | -0.016654 | -0.0041742 | 8.9721e-07 | 5.2864e-07 | 0.025504 | 0.025504 | 0.025504 | 0.97176 | -0.54568 | 0.9717 | -0.54681 | 7.0065
64 | 0.011575 | 0.0029014 | -0.011574 | -0.0029009 | 1.0352e-06 | 5.5374e-07 | 0.017726 | 0.017726 | 0.017726 | 0.9717 | -0.54681 | 0.9716 | -0.54869 | 4.8699
65 | 0.23144 | 0.058538 | -0.23133 | -0.058473 | 0.00010286 | 6.5124e-05 | 0.35028 | 0.35028 | 0.35028 | 0.98369 | -0.3118 | 0.98321 | -0.32107 | 19.2463
66 | 0.22935 | 0.057975 | -0.22911 | -0.05782 | 0.00024511 | 0.00015515 | 0.34728 | 0.34728 | 0.34728 | 0.98321 | -0.32107 | 0.98207 | -0.34338 | 19.0814
67 | 0.22911 | 0.05782 | -0.22906 | -0.057788 | 4.9898e-05 | 3.1586e-05 | 0.34728 | 0.34728 | 0.34728 | 0.98207 | -0.34338 | 0.98183 | -0.34793 | 19.0814
68 | -0.27509 | -0.06963 | 0.27531 | 0.069768 | 0.0002161 | 0.00013724 | 0.41575 | 0.41575 | 0.41575 | 0.98518 | -0.28289 | 0.98603 | -0.26654 | 22.8432
69 | -0.27642 | -0.070045 | 0.27685 | 0.070319 | 0.00043212 | 0.00027444 | 0.41742 | 0.41741 | 0.41742 | 0.98603 | -0.26654 | 0.98771 | -0.23406 | 22.9349
70 | 0.2246 | 0.057419 | -0.22399 | -0.057032 | 0.00061179 | 0.00038686 | 0.33594 | 0.33594 | 0.33594 | 0.99606 | -0.07457 | 0.99309 | -0.13104 | 18.4581
71 | -0.56233 | -0.14396 | 0.56311 | 0.14445 | 0.00077199 | 0.00049313 | 0.84115 | 0.84115 | 0.84115 | 0.99606 | -0.07457 | 0.99755 | -0.046266 | 46.2171
72 | 0.33773 | 0.08654 | -0.33713 | -0.086159 | 0.0005982 | 0.00038082 | 0.50521 | 0.50522 | 0.50522 | 0.99606 | -0.07457 | 0.99413 | -0.11119 | 27.7591
73 | 0.0069327 | 0.0017377 | -0.006931 | -0.0017372 | 1.7479e-06 | 5.5994e-07 | 0.010388 | 0.010388 | 0.010388 | 0.99309 | -0.13104 | 0.99282 | -0.13633 | 2.8539
74 | 0.020854 | 0.0052333 | -0.020834 | -0.0052215 | 1.955e-05 | 1.1809e-05 | 0.031109 | 0.031109 | 0.031109 | 0.99755 | -0.046266 | 0.99653 | -0.065945 | 8.5465
75 | 0.33404 | 0.085385 | -0.33387 | -0.085276 | 0.00017129 | 0.00010904 | 0.50059 | 0.50059 | 0.50059 | 0.99413 | -0.11119 | 0.99357 | -0.12179 | 27.505
76 | -0.27685 | -0.070319 | 0.27726 | 0.070583 | 0.00041565 | 0.00026398 | 0.41741 | 0.41741 | 0.41741 | 0.98771 | -0.23406 | 0.98933 | -0.20292 | 22.9349
77 | -0.27726 | -0.070583 | 0.27742 | 0.070685 | 0.00015989 | 0.00010154 | 0.41741 | 0.41741 | 0.41741 | 0.98933 | -0.20292 | 0.98995 | -0.19097 | 22.9348
78 | -0.27912 | -0.07111 | 0.27947 | 0.071332 | 0.0003492 | 0.00022179 | 0.41996 | 0.41996 | 0.41996 | 0.98995 | -0.19097 | 0.99131 | -0.16507 | 23.0748
79 | 0.012308 | 0.0030856 | -0.012305 | -0.0030838 | 3.1832e-06 | 1.727e-06 | 0.018627 | 0.018627 | 0.018627 | 0.98324 | -0.3207 | 0.98296 | -0.32612 | 5.1173
80 | 0.0048351 | 0.0012115 | -0.0048346 | -0.0012115 | 4.8886e-07 | -8.8829e-10 | 0.007288 | 0.0072881 | 0.0072881 | 0.98719 | -0.24499 | 0.98708 | -0.24712 | 2.0022
81 | -0.0048351 | -0.0012115 | 0.0048355 | 0.0012115 | 3.6204e-07 | -7.0868e-10 | 0.007288 | 0.0072879 | 0.007288 | 0.98719 | -0.24499 | 0.98727 | -0.24342 | 2.0022
82 | 0.0022517 | 0.00056416 | -0.0022517 | -0.00056424 | 3.3044e-08 | -7.6606e-08 | 0.0033944 | 0.0033945 | 0.0033945 | 0.98708 | -0.24712 | 0.98707 | -0.24743 | 0.93254
83 | -0.0091139 | -0.0022838 | 0.0091146 | 0.0022841 | 7.0673e-07 | 3.2457e-07 | 0.013736 | 0.013736 | 0.013736 | 0.98727 | -0.24342 | 0.98735 | -0.2418 | 3.7737
84 | -0.0011538 | -0.00028911 | 0.0011538 | 0.00028907 | 3.6555e-09 | -3.8847e-08 | 0.0017393 | 0.0017393 | 0.0017393 | 0.98706 | -0.24749 | 0.98707 | -0.24743 | 0.47784
85 | 0.0011538 | 0.00028911 | -0.0011538 | -0.00028916 | 4.9368e-09 | -5.2463e-08 | 0.0017393 | 0.0017393 | 0.0017393 | 0.98706 | -0.24749 | 0.98706 | -0.24758 | 0.47784
86 | 0.019044 | 0.0047781 | -0.019036 | -0.0047731 | 8.2447e-06 | 4.9341e-06 | 0.028674 | 0.028674 | 0.028674 | 0.98837 | -0.22211 | 0.9879 | -0.2312 | 7.8774
87 | -0.019044 | -0.0047781 | 0.01905 | 0.0047814 | 5.5798e-06 | 3.3391e-06 | 0.028674 | 0.028674 | 0.028674 | 0.98837 | -0.22211 | 0.98868 | -0.21597 | 7.8774
88 | 0.016443 | 0.0041233 | -0.01644 | -0.0041216 | 2.911e-06 | 1.7011e-06 | 0.024769 | 0.024769 | 0.024769 | 0.9879 | -0.2312 | 0.98771 | -0.23491 | 6.8046
89 | -0.022545 | -0.0056573 | 0.02255 | 0.0056601 | 4.6081e-06 | 2.8123e-06 | 0.033934 | 0.033934 | 0.033934 | 0.98868 | -0.21597 | 0.9889 | -0.21168 | 9.3225
90 | -0.011964 | -0.0029981 | 0.011965 | 0.0029987 | 1.1925e-06 | 6.3807e-07 | 0.01803 | 0.01803 | 0.01803 | 0.98735 | -0.2418 | 0.98746 | -0.2397 | 4.9533
91 | 0.015512 | 0.0038889 | -0.015509 | -0.0038869 | 3.5415e-06 | 2.0453e-06 | 0.02337 | 0.02337 | 0.02337 | 0.98771 | -0.23491 | 0.98746 | -0.2397 | 6.4203
92 | -0.026706 | -0.0067018 | 0.026718 | 0.0067094 | 1.2413e-05 | 7.6814e-06 | 0.040187 | 0.040187 | 0.040187 | 0.9889 | -0.21168 | 0.9894 | -0.20194 | 11.0405
93 | 0.0064762 | 0.0016231 | -0.0064758 | -0.001623 | 4.9237e-07 | 1.4983e-07 | 0.0099184 | 0.0099185 | 0.0099185 | 0.9716 | -0.54869 | 0.97152 | -0.55028 | 2.7249
94 | 0.006931 | 0.0017372 | -0.0069295 | -0.0017367 | 1.4835e-06 | 4.755e-07 | 0.010388 | 0.010388 | 0.010388 | 0.99282 | -0.13633 | 0.99259 | -0.14083 | 2.8539
95 | 0.33271 | 0.084984 | -0.33216 | -0.084632 | 0.00055352 | 0.00035234 | 0.49885 | 0.49885 | 0.49885 | 0.99357 | -0.12179 | 0.99177 | -0.15627 | 27.4093
96 | 0.043951 | 0.011055 | -0.04392 | -0.011035 | 3.132e-05 | 1.9798e-05 | 0.065988 | 0.065988 | 0.065988 | 0.99131 | -0.16507 | 0.99054 | -0.18 | 18.1286
97 | -0.33121 | -0.084342 | 0.33136 | 0.084431 | 0.00014065 | 8.953e-05 | 0.49765 | 0.49765 | 0.49765 | 0.99131 | -0.16507 | 0.99177 | -0.15627 | 27.3434
98 | 0.0077952 | 0.0019552 | -0.0077864 | -0.0019518 | 8.8278e-06 | 3.4362e-06 | 0.011702 | 0.011702 | 0.011702 | 0.99131 | -0.16507 | 0.99008 | -0.18885 | 3.2149
99 | -0.04582 | -0.011534 | 0.045915 | 0.011594 | 9.4705e-05 | 5.9954e-05 | 0.069611 | 0.069611 | 0.069611 | 0.97971 | -0.38979 | 0.98193 | -0.34664 | 19.1239
100 | 0.04582 | 0.011534 | -0.045751 | -0.01149 | 6.9564e-05 | 4.404e-05 | 0.069611 | 0.069611 | 0.069611 | 0.97971 | -0.38979 | 0.97809 | -0.4216 | 19.124
101 | -0.045915 | -0.011594 | 0.045935 | 0.011607 | 1.9993e-05 | 1.2656e-05 | 0.069611 | 0.069611 | 0.069611 | 0.98193 | -0.34664 | 0.98239 | -0.33756 | 19.1239
102 | 0.044456 | 0.011166 | -0.044445 | -0.011159 | 1.1077e-05 | 7.0081e-06 | 0.067641 | 0.067641 | 0.067641 | 0.97809 | -0.4216 | 0.97782 | -0.42682 | 18.5828
103 | -0.048411 | -0.012227 | 0.048439 | 0.012246 | 2.8829e-05 | 1.8269e-05 | 0.073361 | 0.073361 | 0.073361 | 0.98239 | -0.33756 | 0.98303 | -0.32514 | 20.154
104 | 0.043204 | 0.010848 | -0.043198 | -0.010844 | 5.2854e-06 | 3.3418e-06 | 0.065753 | 0.065753 | 0.065753 | 0.97782 | -0.42682 | 0.97769 | -0.42939 | 18.0639
105 | 0.0023827 | 0.00059702 | -0.0023827 | -0.00059715 | 6.5923e-08 | -1.2984e-07 | 0.003603 | 0.0036031 | 0.0036031 | 0.98404 | -0.30553 | 0.98401 | -0.30611 | 0.98985
106 | -0.002956 | -0.00074083 | 0.0029561 | 0.00074072 | 1.1474e-07 | -1.1583e-07 | 0.0045008 | 0.0045007 | 0.0045008 | 0.97727 | -0.43767 | 0.97731 | -0.43686 | 1.2365
107 | -0.0053403 | -0.0013383 | 0.0053405 | 0.0013383 | 2.0373e-07 | 2.7408e-08 | 0.0081309 | 0.0081308 | 0.0081309 | 0.97731 | -0.43686 | 0.97735 | -0.43606 | 2.2338
108 | -0.0081351 | -0.0020387 | 0.008136 | 0.0020391 | 8.7221e-07 | 3.6818e-07 | 0.012386 | 0.012386 | 0.012386 | 0.97735 | -0.43606 | 0.97747 | -0.43381 | 3.4026
109 | -0.010405 | -0.0026077 | 0.010406 | 0.0026081 | 7.5149e-07 | 3.8083e-07 | 0.01584 | 0.01584 | 0.01584 | 0.97747 | -0.43381 | 0.97755 | -0.43229 | 4.3516
110 | -0.012888 | -0.0032303 | 0.01289 | 0.0032313 | 1.784e-06 | 9.868e-07 | 0.019619 | 0.019618 | 0.019619 | 0.97755 | -0.43229 | 0.97769 | -0.42939 | 5.3897
111 | 0.030308 | 0.0076131 | -0.030278 | -0.0075942 | 3.0322e-05 | 1.893e-05 | 0.046134 | 0.046134 | 0.046134 | 0.97769 | -0.42939 | 0.97663 | -0.45037 | 12.6743
112 | 0.027717 | 0.0069522 | -0.027716 | -0.006952 | 3.5136e-07 | 2.1829e-07 | 0.042232 | 0.042232 | 0.042232 | 0.97663 | -0.45037 | 0.97661 | -0.45064 | 11.6022
113 | 0.025928 | 0.0065039 | -0.025924 | -0.0065011 | 4.6007e-06 | 2.8461e-06 | 0.039508 | 0.039508 | 0.039508 | 0.97661 | -0.45064 | 0.97642 | -0.45436 | 10.8538
114 | 0.023809 | 0.005971 | -0.023805 | -0.0059687 | 3.76e-06 | 2.3111e-06 | 0.036285 | 0.036285 | 0.036285 | 0.97642 | -0.45436 | 0.97626 | -0.45768 | 9.9683
115 | -0.014787 | -0.0037064 | 0.014789 | 0.0037072 | 1.4891e-06 | 8.5544e-07 | 0.022548 | 0.022548 | 0.022548 | 0.97587 | -0.46526 | 0.97598 | -0.46314 | 6.1945
116 | 0.012575 | 0.0031518 | -0.012574 | -0.0031513 | 1.0321e-06 | 5.67e-07 | 0.019174 | 0.019174 | 0.019174 | 0.97587 | -0.46526 | 0.97578 | -0.46698 | 5.2676
117 | -0.017242 | -0.0043221 | 0.017244 | 0.0043232 | 1.8922e-06 | 1.1198e-06 | 0.026288 | 0.026288 | 0.026288 | 0.97598 | -0.46314 | 0.97609 | -0.46084 | 7.2221
118 | 0.010198 | 0.0025558 | -0.010198 | -0.0025558 | 6.231e-08 | 3.1296e-08 | 0.015551 | 0.015551 | 0.015551 | 0.97578 | -0.46698 | 0.97578 | -0.46711 | 4.2722
119 | -0.0192 | -0.0048133 | 0.0192 | 0.0048134 | 1.894e-07 | 1.1384e-07 | 0.029269 | 0.029269 | 0.029269 | 0.97609 | -0.46084 | 0.9761 | -0.46063 | 8.041
120 | 0.0082893 | 0.0020775 | -0.0082889 | -0.0020773 | 4.0351e-07 | 1.7413e-07 | 0.012641 | 0.012641 | 0.012641 | 0.97578 | -0.46711 | 0.97572 | -0.46813 | 3.4727
121 | -0.021664 | -0.0054311 | 0.021667 | 0.0054329 | 3.0515e-06 | 1.8597e-06 | 0.033026 | 0.033026 | 0.033026 | 0.9761 | -0.46063 | 0.97626 | -0.45768 | 9.0732
122 | 0.0063306 | 0.0015865 | -0.0063303 | -0.0015864 | 2.6385e-07 | 7.4584e-08 | 0.0096544 | 0.0096544 | 0.0096544 | 0.97572 | -0.46813 | 0.97568 | -0.469 | 2.6523
123 | 0.0040649 | 0.0010187 | -0.0040649 | -0.0010187 | 1.0279e-08 | -2.3289e-09 | 0.0061993 | 0.0061993 | 0.0061993 | 0.97568 | -0.469 | 0.97568 | -0.46906 | 1.7031
124 | 0.043138 | 0.010839 | -0.043111 | -0.010823 | 2.6411e-05 | 1.6687e-05 | 0.064813 | 0.064813 | 0.064813 | 0.99054 | -0.18 | 0.98987 | -0.19283 | 17.8057
125 | 0.0077864 | 0.0019518 | -0.0077839 | -0.0019508 | 2.452e-06 | 9.5546e-07 | 0.011702 | 0.011703 | 0.011703 | 0.99008 | -0.18885 | 0.98974 | -0.19546 | 3.215
126 | 0.033634 | 0.0084475 | -0.033633 | -0.0084469 | 8.9172e-07 | 5.5874e-07 | 0.050567 | 0.050567 | 0.050567 | 0.98987 | -0.19283 | 0.98985 | -0.19339 | 13.892
127 | 0.028716 | 0.0072146 | -0.028705 | -0.0072073 | 1.1714e-05 | 7.2817e-06 | 0.043175 | 0.043175 | 0.043175 | 0.98985 | -0.19339 | 0.9894 | -0.20194 | 11.8612
128 | -0.0019822 | -0.0004968 | 0.0019823 | 0.00049671 | 2.7889e-08 | -8.3774e-08 | 0.0030232 | 0.0030232 | 0.0030232 | 0.97566 | -0.46935 | 0.97568 | -0.46906 | 0.83055

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59719 | 0.1531

## res_load
| p_mw | q_mvar
0 | 0.016662 | 0.0041758
1 | 0.0052724 | 0.0013214
2 | 0.0070823 | 0.001775
3 | 0.0040711 | 0.0010203
4 | 0.0028422 | 0.00071233
5 | 0.006807 | 0.001706
6 | 0.0094116 | 0.0023588
7 | 0.006747 | 0.001691
8 | 0.011022 | 0.0027624
9 | 0.0026504 | 0.00066424
10 | 0.0056464 | 0.0014151
11 | 0.010821 | 0.0027119
12 | 0.0076487 | 0.0019169
13 | 0.0040441 | 0.0010135
14 | 0.0024353 | 0.00061034
15 | 0.031749 | 0.0079571
16 | 0.0016101 | 0.00040353
17 | 0.0015771 | 0.00039526
18 | 0.010086 | 0.0025277
19 | 0.011585 | 0.0029035
20 | 0.01102 | 0.002762
21 | 0.025172 | 0.0063087
22 | 0.042398 | 0.010626
23 | 0.046646 | 0.011691
24 | 0.01009 | 0.0025288
25 | 0.037203 | 0.0093239
26 | 0.0045307 | 0.0011355
27 | 0.0020987 | 0.00052597
28 | 0.0019573 | 0.00049055
29 | 0.0020908 | 0.00052399
30 | 0.010264 | 0.0025724
31 | 0.0095074 | 0.0023828
32 | 0.0039719 | 0.00099545
33 | 0.0025476 | 0.00063849
34 | 0.0050787 | 0.0012728
35 | 0.010763 | 0.0026973
36 | 0.0019843 | 0.00049732
37 | 0.0010723 | 0.00026875
38 | 0.0084096 | 0.0021077
39 | 0.0011062 | 0.00027724
40 | 0.0030904 | 0.00077453
41 | 0.0016951 | 0.00042483
42 | 0.0025829 | 0.00064733
43 | 0.0042784 | 0.0010723
44 | 0.0010979 | 0.00027517
45 | 0.0011538 | 0.00028916
46 | 0.012305 | 0.0030838
47 | 0.0025927 | 0.00064979
48 | 0.0034951 | 0.00087594
49 | 0.0028489 | 0.000714
50 | 0.00092842 | 0.00023268
51 | 0.0041561 | 0.0010416
52 | 0.0050982 | 0.0012777
53 | 0.0064758 | 0.001623
54 | 0.0069295 | 0.0017367
55 | 0.020834 | 0.0052215
56 | 0.0011625 | 0.00029135
57 | 0.0012949 | 0.00032453
58 | 0.0024757 | 0.00062047
59 | 0.001241 | 0.00031103
60 | 0.017725 | 0.0044423
61 | 0.0072637 | 0.0018204
62 | 0.002956 | 0.00074083
63 | 0.0023842 | 0.00059754
64 | 0.0027946 | 0.0007004
65 | 0.002269 | 0.00056866
66 | 0.0024825 | 0.00062218
67 | 0.0025613 | 0.00064193
68 | 0.0017879 | 0.00044809
69 | 0.002115 | 0.00053008
70 | 0.0022126 | 0.00055454
71 | 0.0024533 | 0.00061487
72 | 0.002376 | 0.00059548
73 | 0.0019554 | 0.00049008
74 | 0.0019084 | 0.00047828
75 | 0.0024646 | 0.00061768
76 | 0.0019583 | 0.00049079
77 | 0.0021376 | 0.00053574
78 | 0.0022655 | 0.00056778
79 | 0.0022536 | 0.00056482
80 | 0.0023827 | 0.00059715
81 | 0.00078235 | 0.00019608
82 | 0.00080001 | 0.0002005
83 | 0.0094769 | 0.0023751
84 | 0.0077839 | 0.0019508
85 | 0.0049172 | 0.0012324
86 | 0.0019864 | 0.00049785
87 | 0.0035438 | 0.00088816
88 | 0.0019822 | 0.0004968
89 | 0.0020826 | 0.00052195

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1