## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_153-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_153-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_153-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_153-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_153-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_153-1_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_153-1_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_153-1_0_4_node_97 | 0.4 | n |  | TRUE
8 | bus_LV_153-1_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_153-1_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_153-1_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_153-1_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_153-1_0_4_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_153-1_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_153-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_153-1_0_4_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_153-1_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_153-1_0_4_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_153-1_0_4_node_59 | 0.4 | n |  | TRUE
19 | bus_LV_153-1_0_4_node_355 | 0.4 | n |  | TRUE
20 | bus_LV_153-1_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_153-1_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_153-1_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_153-1_0_4_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_153-1_0_4_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_153-1_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_153-1_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_153-1_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_153-1_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_153-1_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_153-1_0_4_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_153-1_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_153-1_0_4_node_62 | 0.4 | n |  | TRUE
33 | bus_LV_153-1_0_4_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_153-1_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_153-1_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_153-1_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_153-1_0_4_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_153-1_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_153-1_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_153-1_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_153-1_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_153-1_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_153-1_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_153-1_0_4_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_153-1_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_153-1_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_153-1_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_153-1_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_153-1_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_153-1_0_4_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_153-1_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_153-1_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_153-1_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_153-1_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_153-1_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_153-1_0_4_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_153-1_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_153-1_0_4_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_153-1_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_153-1_0_4_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_153-1_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_153-1_0_4_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_153-1_0_4_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_153-1_0_4_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_153-1_0_4_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_153-1_0_4_node_344 | 0.4 | n |  | TRUE
67 | bus_LV_153-1_0_4_node_348 | 0.4 | n |  | TRUE
68 | bus_LV_153-1_0_4_node_66 | 0.4 | n |  | TRUE
69 | bus_LV_153-1_0_4_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_153-1_0_4_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_153-1_0_4_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_153-1_0_4_node_72 | 0.4 | n |  | TRUE
73 | bus_LV_153-1_0_4_node_76 | 0.4 | n |  | TRUE
74 | bus_LV_153-1_0_4_node_83 | 0.4 | n |  | TRUE
75 | bus_LV_153-1_0_4_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_153-1_0_4_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_153-1_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_153-1_0_4_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_153-1_0_4_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_153-1_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_153-1_0_4_node_80 | 0.4 | n |  | TRUE
82 | bus_LV_153-1_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_153-1_0_4_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_153-1_0_4_node_351 | 0.4 | n |  | TRUE
85 | bus_LV_153-1_0_4_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_153-1_0_4_node_229 | 0.4 | n |  | TRUE
87 | bus_LV_153-1_0_4_node_230 | 0.4 | n |  | TRUE
88 | bus_LV_153-1_0_4_node_231 | 0.4 | n |  | TRUE
89 | bus_LV_153-1_0_4_node_232 | 0.4 | n |  | TRUE
90 | bus_LV_153-1_0_4_node_233 | 0.4 | n |  | TRUE
91 | bus_LV_153-1_0_4_node_333 | 0.4 | n |  | TRUE
92 | bus_LV_153-1_0_4_node_336 | 0.4 | n |  | TRUE
93 | bus_LV_153-1_0_4_node_316 | 0.4 | n |  | TRUE
94 | bus_LV_153-1_0_4_node_317 | 0.4 | n |  | TRUE
95 | bus_LV_153-1_0_4_node_318 | 0.4 | n |  | TRUE
96 | bus_LV_153-1_0_4_node_319 | 0.4 | n |  | TRUE
97 | bus_LV_153-1_0_4_node_320 | 0.4 | n |  | TRUE
98 | bus_LV_153-1_0_4_node_321 | 0.4 | n |  | TRUE
99 | bus_LV_153-1_0_4_node_322 | 0.4 | n |  | TRUE
100 | bus_LV_153-1_0_4_node_323 | 0.4 | n |  | TRUE
101 | bus_LV_153-1_0_4_node_324 | 0.4 | n |  | TRUE
102 | bus_LV_153-1_0_4_node_325 | 0.4 | n |  | TRUE
103 | bus_LV_153-1_0_4_node_326 | 0.4 | n |  | TRUE
104 | bus_LV_153-1_0_4_node_327 | 0.4 | n |  | TRUE
105 | bus_LV_153-1_0_4_node_332 | 0.4 | n |  | TRUE
106 | bus_LV_153-1_0_4_node_328 | 0.4 | n |  | TRUE
107 | bus_LV_153-1_0_4_node_329 | 0.4 | n |  | TRUE
108 | bus_LV_153-1_0_4_node_330 | 0.4 | n |  | TRUE
109 | bus_LV_153-1_0_4_node_331 | 0.4 | n |  | TRUE
110 | bus_LV_153-1_0_4_node_334 | 0.4 | n |  | TRUE
111 | bus_LV_153-1_0_4_node_335 | 0.4 | n |  | TRUE
112 | bus_LV_153-1_0_4_node_337 | 0.4 | n |  | TRUE
113 | bus_LV_153-1_0_4_node_338 | 0.4 | n |  | TRUE
114 | bus_LV_153-1_0_4_node_341 | 0.4 | n |  | TRUE
115 | bus_LV_153-1_0_4_node_339 | 0.4 | n |  | TRUE
116 | bus_LV_153-1_0_4_node_340 | 0.4 | n |  | TRUE
117 | bus_LV_153-1_0_4_node_342 | 0.4 | n |  | TRUE
118 | bus_LV_153-1_0_4_node_343 | 0.4 | n |  | TRUE
119 | bus_LV_153-1_0_4_node_349 | 0.4 | n |  | TRUE
120 | bus_MV_361_1_node_179 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_153-1_0_4_load_0 | 0 | 0.0010005 | 0.00025076 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_153-1_0_4_load_1 | 1 | 0.00026517 | 6.6458e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_153-1_0_4_load_2 | 2 | 0.00018513 | 4.6399e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_153-1_0_4_load_3 | 3 | 0.00065922 | 0.00016522 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_153-1_0_4_load_5 | 5 | 0.00074475 | 0.00018665 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_153-1_0_4_load_97 | 7 | 0.0001259 | 3.1553e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_153-1_0_4_load_7 | 9 | 0.00033298 | 8.3454e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_153-1_0_4_load_11 | 10 | 0.00036855 | 9.2367e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_153-1_0_4_load_20 | 13 | 0.00025353 | 6.354e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_153-1_0_4_load_17 | 15 | 0.00028704 | 7.1939e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_153-1_0_4_load_59 | 18 | 0.00042411 | 0.00010629 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_153-1_0_4_load_355 | 19 | 0.00063588 | 0.00015937 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_153-1_0_4_load_13 | 21 | 0.0012801 | 0.00032083 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_153-1_0_4_load_14 | 22 | 0.00079174 | 0.00019843 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_153-1_0_4_load_49 | 24 | 0.00034985 | 8.768e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_153-1_0_4_load_15 | 25 | 0.00037717 | 9.4527e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_153-1_0_4_load_16 | 26 | 0.00058993 | 0.00014785 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_153-1_0_4_load_21 | 28 | 0.00025206 | 6.3171e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_153-1_0_4_load_60 | 30 | 0.00056169 | 0.00014077 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_153-1_0_4_load_26 | 31 | 0.00037858 | 9.488e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_153-1_0_4_load_62 | 32 | 0.00017837 | 4.4704e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_153-1_0_4_load_24 | 34 | 0.00038384 | 9.6198e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_153-1_0_4_load_25 | 35 | 0.00075995 | 0.00019046 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_153-1_0_4_load_27 | 36 | 0.00038462 | 9.6395e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_153-1_0_4_load_28 | 38 | 0.0014847 | 0.00037211 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_153-1_0_4_load_29 | 39 | 0.00039542 | 9.9102e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_153-1_0_4_load_30 | 40 | 0.00016248 | 4.0721e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_153-1_0_4_load_32 | 41 | 0.0001388 | 3.4787e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_153-1_0_4_load_34 | 42 | 0.00014441 | 3.6193e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_153-1_0_4_load_33 | 43 | 0.00046144 | 0.00011565 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_153-1_0_4_load_42 | 44 | 0.00033933 | 8.5045e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_153-1_0_4_load_35 | 45 | 0.00013159 | 3.298e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_153-1_0_4_load_37 | 47 | 0.00016672 | 4.1783e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_153-1_0_4_load_38 | 48 | 0.00062798 | 0.00015739 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_153-1_0_4_load_39 | 49 | 0.00036341 | 9.108e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_153-1_0_4_load_40 | 50 | 0.00031957 | 8.0093e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_153-1_0_4_load_43 | 52 | 0.00013873 | 3.4769e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_153-1_0_4_load_44 | 53 | 0.00077794 | 0.00019497 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_153-1_0_4_load_45 | 54 | 0.00084465 | 0.00021169 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_153-1_0_4_load_47 | 55 | 0.0015053 | 0.00037726 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_153-1_0_4_load_46 | 56 | 0.014406 | 0.0036104 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_153-1_0_4_load_52 | 59 | 0.0014043 | 0.00035196 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_153-1_0_4_load_55 | 60 | 0.0066297 | 0.0016616 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_153-1_0_4_load_53 | 61 | 0.0032529 | 0.00081526 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_153-1_0_4_load_54 | 62 | 0.0055507 | 0.0013911 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_153-1_0_4_load_56 | 63 | 0.0055372 | 0.0013878 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_153-1_0_4_load_57 | 64 | 0.0027387 | 0.00068639 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_153-1_0_4_load_348 | 67 | 0.0052905 | 0.0013259 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_153-1_0_4_load_66 | 68 | 0.00067678 | 0.00016962 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_153-1_0_4_load_69 | 69 | 0.00031844 | 7.9808e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_153-1_0_4_load_70 | 70 | 0.00011021 | 2.7621e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_153-1_0_4_load_71 | 71 | 0.00048624 | 0.00012186 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_153-1_0_4_load_73 | 75 | 0.00032012 | 8.0228e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_153-1_0_4_load_74 | 76 | 0.00026593 | 6.6649e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_153-1_0_4_load_75 | 77 | 0.0020689 | 0.00051852 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_153-1_0_4_load_77 | 78 | 0.0019376 | 0.00048561 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_153-1_0_4_load_79 | 80 | 0.00020878 | 5.2326e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_153-1_0_4_load_80 | 81 | 0.00061359 | 0.00015378 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_153-1_0_4_load_84 | 82 | 0.00029045 | 7.2793e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_153-1_0_4_load_351 | 84 | 0.00082205 | 0.00020603 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_153-1_0_4_load_229 | 86 | 0.0013053 | 0.00032713 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_153-1_0_4_load_230 | 87 | 0.0031997 | 0.00080193 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_153-1_0_4_load_231 | 88 | 0.000561 | 0.0001406 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_153-1_0_4_load_232 | 89 | 0.0014681 | 0.00036793 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_153-1_0_4_load_316 | 93 | 0.00020264 | 5.0786e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_153-1_0_4_load_317 | 94 | 0.00039698 | 9.9494e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_153-1_0_4_load_319 | 96 | 0.00088559 | 0.00022195 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_153-1_0_4_load_320 | 97 | 0.00027669 | 6.9346e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_153-1_0_4_load_321 | 98 | 0.00062269 | 0.00015606 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_153-1_0_4_load_322 | 99 | 0.00029913 | 7.4969e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_153-1_0_4_load_323 | 100 | 0.001595 | 0.00039976 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_153-1_0_4_load_324 | 101 | 0.0010913 | 0.00027351 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_153-1_0_4_load_325 | 102 | 0.00038359 | 9.6136e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_153-1_0_4_load_326 | 103 | 0.00016086 | 4.0316e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_153-1_0_4_load_327 | 104 | 0.00028788 | 7.215e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_153-1_0_4_load_332 | 105 | 0.00027579 | 6.9121e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_153-1_0_4_load_328 | 106 | 0.0010665 | 0.0002673 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_153-1_0_4_load_329 | 107 | 0.00047035 | 0.00011788 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_153-1_0_4_load_331 | 109 | 0.00044768 | 0.0001122 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_153-1_0_4_load_334 | 110 | 0.00047321 | 0.0001186 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_153-1_0_4_load_335 | 111 | 0.0010656 | 0.00026706 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_153-1_0_4_load_337 | 112 | 0.0006699 | 0.00016789 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_153-1_0_4_load_338 | 113 | 0.00029716 | 7.4475e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_153-1_0_4_load_339 | 115 | 0.00041237 | 0.00010335 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_153-1_0_4_load_340 | 116 | 0.00021006 | 5.2646e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_153-1_0_4_load_342 | 117 | 0.00073749 | 0.00018483 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_153-1_0_4_load_343 | 118 | 0.0023103 | 0.00057902 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_153-1_0_4_load_349 | 119 | 0.0088119 | 0.0022085 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_153-1_0_4_line_0 |  | 0 | 1 | 0.0033198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_153-1_0_4_line_1 |  | 0 | 2 | 0.031143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_153-1_0_4_line_2 |  | 1 | 3 | 0.0097563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_153-1_0_4_line_3 |  | 2 | 4 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_153-1_0_4_line_4 |  | 3 | 5 | 0.051618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_153-1_0_4_line_5 |  | 4 | 6 | 0.013777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_153-1_0_4_line_6 |  | 4 | 7 | 0.022116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_153-1_0_4_line_7 |  | 5 | 8 | 0.025418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_153-1_0_4_line_8 |  | 6 | 31 | 0.023683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_153-1_0_4_line_9 |  | 6 | 27 | 0.01576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_153-1_0_4_line_10 |  | 7 | 85 | 0.066416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_153-1_0_4_line_11 |  | 8 | 9 | 0.014704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_153-1_0_4_line_12 |  | 9 | 10 | 0.023356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_153-1_0_4_line_13 |  | 10 | 20 | 0.031461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_153-1_0_4_line_14 |  | 11 | 12 | 0.067369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_153-1_0_4_line_15 |  | 11 | 13 | 0.12743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_153-1_0_4_line_16 |  | 11 | 14 | 0.14538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_153-1_0_4_line_17 |  | 11 | 15 | 0.01068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_153-1_0_4_line_18 |  | 12 | 29 | 0.017237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_153-1_0_4_line_19 |  | 13 | 30 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_153-1_0_4_line_20 |  | 14 | 19 | 0.014226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_153-1_0_4_line_21 |  | 14 | 16 | 0.041372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_153-1_0_4_line_22 |  | 15 | 25 | 0.03302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_153-1_0_4_line_23 |  | 16 | 17 | 0.05717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_153-1_0_4_line_24 |  | 16 | 18 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_153-1_0_4_line_25 |  | 17 | 64 | 0.056373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_153-1_0_4_line_26 |  | 20 | 21 | 0.055694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_153-1_0_4_line_27 |  | 20 | 22 | 0.024212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_153-1_0_4_line_28 |  | 21 | 23 | 0.030646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_153-1_0_4_line_29 |  | 22 | 24 | 0.024809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_153-1_0_4_line_30 |  | 23 | 48 | 0.080865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_153-1_0_4_line_31 |  | 24 | 55 | 0.0078479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_153-1_0_4_line_32 |  | 25 | 26 | 0.052833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_153-1_0_4_line_33 |  | 26 | 27 | 0.0047051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_153-1_0_4_line_34 |  | 27 | 28 | 0.016726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_153-1_0_4_line_35 |  | 29 | 32 | 0.015774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_153-1_0_4_line_36 |  | 29 | 33 | 0.28539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_153-1_0_4_line_37 |  | 31 | 34 | 0.070234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_153-1_0_4_line_38 |  | 33 | 68 | 0.012765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_153-1_0_4_line_39 |  | 34 | 35 | 0.11491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_153-1_0_4_line_40 |  | 35 | 36 | 0.0087815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_153-1_0_4_line_41 |  | 36 | 37 | 0.24083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_153-1_0_4_line_42 |  | 37 | 65 | 0.16214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_153-1_0_4_line_43 |  | 38 | 39 | 0.0053085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_153-1_0_4_line_44 |  | 38 | 40 | 0.016184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_153-1_0_4_line_45 |  | 40 | 41 | 0.026243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_153-1_0_4_line_46 |  | 41 | 42 | 0.028696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_153-1_0_4_line_47 |  | 42 | 45 | 0.016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_153-1_0_4_line_48 |  | 43 | 44 | 0.009776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_153-1_0_4_line_49 |  | 44 | 52 | 0.040139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_153-1_0_4_line_50 |  | 45 | 46 | 0.01699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_153-1_0_4_line_51 |  | 46 | 47 | 0.053053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_153-1_0_4_line_52 |  | 46 | 48 | 0.080247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_153-1_0_4_line_53 |  | 47 | 49 | 0.021761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_153-1_0_4_line_54 |  | 49 | 50 | 0.0045282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_153-1_0_4_line_55 |  | 50 | 51 | 0.01914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_153-1_0_4_line_56 |  | 51 | 52 | 0.011121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_153-1_0_4_line_57 |  | 53 | 54 | 0.016362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_153-1_0_4_line_58 |  | 54 | 55 | 0.027174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_153-1_0_4_line_59 |  | 56 | 57 | 0.022454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_153-1_0_4_line_60 |  | 57 | 58 | 0.010823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_153-1_0_4_line_61 |  | 57 | 59 | 0.008562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_153-1_0_4_line_62 |  | 58 | 60 | 0.004129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_153-1_0_4_line_63 |  | 60 | 61 | 0.10261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_153-1_0_4_line_64 |  | 61 | 62 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_153-1_0_4_line_65 |  | 62 | 63 | 0.06885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_153-1_0_4_line_66 |  | 63 | 64 | 0.0452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_153-1_0_4_line_67 |  | 65 | 66 | 0.19722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_153-1_0_4_line_68 |  | 65 | 67 | 0.067639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_153-1_0_4_line_69 |  | 66 | 117 | 0.00021621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_153-1_0_4_line_70 |  | 66 | 118 | 0.018299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_153-1_0_4_line_71 |  | 67 | 119 | 0.0044605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_153-1_0_4_line_72 |  | 69 | 70 | 0.0010833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_153-1_0_4_line_73 |  | 69 | 71 | 0.01268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_153-1_0_4_line_74 |  | 70 | 72 | 0.044859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_153-1_0_4_line_75 |  | 72 | 73 | 0.025415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_153-1_0_4_line_76 |  | 72 | 74 | 0.42975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_153-1_0_4_line_77 |  | 73 | 76 | 0.068829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_153-1_0_4_line_78 |  | 74 | 83 | 0.58932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_153-1_0_4_line_79 |  | 74 | 82 | 0.022432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_153-1_0_4_line_80 |  | 75 | 76 | 0.01107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_153-1_0_4_line_81 |  | 75 | 77 | 0.0039316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_153-1_0_4_line_82 |  | 78 | 79 | 0.057016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_153-1_0_4_line_83 |  | 78 | 80 | 0.057162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_153-1_0_4_line_84 |  | 79 | 81 | 0.057704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_153-1_0_4_line_85 |  | 81 | 82 | 0.0375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_153-1_0_4_line_86 |  | 83 | 84 | 0.037528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_153-1_0_4_line_87 |  | 83 | 85 | 0.35809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_153-1_0_4_line_88 |  | 86 | 87 | 0.039307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_153-1_0_4_line_89 |  | 87 | 88 | 0.031197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_153-1_0_4_line_90 |  | 88 | 89 | 0.091476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_153-1_0_4_line_91 |  | 89 | 90 | 0.048607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_153-1_0_4_line_92 |  | 90 | 91 | 0.00934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_153-1_0_4_line_93 |  | 90 | 92 | 0.003372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_153-1_0_4_line_94 |  | 91 | 97 | 0.0025005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_153-1_0_4_line_95 |  | 91 | 108 | 0.019008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_153-1_0_4_line_96 |  | 92 | 113 | 0.14577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_153-1_0_4_line_97 |  | 92 | 110 | 0.01932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_153-1_0_4_line_98 |  | 93 | 94 | 0.012573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_153-1_0_4_line_99 |  | 93 | 95 | 0.23762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_153-1_0_4_line_100 |  | 95 | 96 | 0.079867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_153-1_0_4_line_101 |  | 95 | 97 | 0.15359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_153-1_0_4_line_102 |  | 96 | 98 | 0.011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_153-1_0_4_line_103 |  | 98 | 99 | 0.014409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_153-1_0_4_line_104 |  | 99 | 100 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_153-1_0_4_line_105 |  | 100 | 101 | 0.04362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_153-1_0_4_line_106 |  | 102 | 103 | 0.032982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_153-1_0_4_line_107 |  | 103 | 104 | 0.011106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_153-1_0_4_line_108 |  | 104 | 105 | 0.00074702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_153-1_0_4_line_109 |  | 105 | 109 | 0.0016227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_153-1_0_4_line_110 |  | 106 | 107 | 0.026449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_153-1_0_4_line_111 |  | 107 | 108 | 0.015789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_153-1_0_4_line_112 |  | 108 | 109 | 0.020026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_153-1_0_4_line_113 |  | 110 | 111 | 0.044135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_153-1_0_4_line_114 |  | 111 | 112 | 0.0067338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_153-1_0_4_line_115 |  | 113 | 114 | 0.010349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_153-1_0_4_line_116 |  | 114 | 117 | 0.031293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_153-1_0_4_line_117 |  | 114 | 115 | 0.059896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_153-1_0_4_line_118 |  | 115 | 116 | 0.012704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_153-1_0_4_trafo_23 | 0.63 MVA 20/0.4 kV | 120 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50
0 | 2698593.9387 | 1235339.0369 | 2698590.663 | 1235338.4981
1 | 2698593.9387 | 1235339.0369 | 2698598.5426 | 1235339.7942 | 2698624.7353 | 1235343.6658
2 | 2698590.663 | 1235338.4981 | 2698587.1889 | 1235337.9266 | 2698581.053 | 1235336.8163
3 | 2698643.7131 | 1235346.471 | 2698624.7353 | 1235343.6658
4 | 2698530.5983 | 1235326.0004 | 2698545.3848 | 1235328.6263 | 2698570.1684 | 1235334.5195 | 2698579.4759 | 1235336.5309 | 2698581.053 | 1235336.8163
5 | 2698643.7131 | 1235346.471 | 2698643.2377 | 1235351.8449 | 2698642.7279 | 1235360.2093
6 | 2698643.7131 | 1235346.471 | 2698644.8974 | 1235336.6945 | 2698647.1504 | 1235326.3798 | 2698647.6183 | 1235324.7348
7 | 2698505.3396 | 1235324.6371 | 2698520.7275 | 1235324.2475 | 2698530.5983 | 1235326.0004
8 | 2698642.7279 | 1235360.2093 | 2698651.3832 | 1235361.3761 | 2698664.0004 | 1235369.3939
9 | 2698643.3747 | 1235375.954 | 2698642.7279 | 1235360.2093
10 | 2698665.6576 | 1235260.8161 | 2698653.9275 | 1235302.5524 | 2698647.6183 | 1235324.7348
11 | 2698505.3396 | 1235324.6371 | 2698491.4509 | 1235319.809
12 | 2698469.3899 | 1235312.14 | 2698491.4509 | 1235319.809
13 | 2698439.673 | 1235301.8097 | 2698469.3899 | 1235312.14
14 | 2698671.1216 | 1235494.1137 | 2698667.3442 | 1235493.6729 | 2698665.5043 | 1235493.2532 | 2698663.6621 | 1235492.5109 | 2698661.5222 | 1235491.4635 | 2698631.1672 | 1235472.4232 | 2698609.9613 | 1235468.1013
15 | 2698609.9613 | 1235468.1013 | 2698611.4347 | 1235495.6018 | 2698608.1945 | 1235516.1411 | 2698585.0814 | 1235591.7855
16 | 2698483.211 | 1235476.3053 | 2698487.8644 | 1235490.1038 | 2698496.1067 | 1235485.5926 | 2698527.1884 | 1235471.3529 | 2698546.8001 | 1235459.536 | 2698555.3274 | 1235457.9206 | 2698565.0207 | 1235458.5708 | 2698609.9613 | 1235468.1013
17 | 2698609.9613 | 1235468.1013 | 2698610.6439 | 1235457.4428
18 | 2698671.1216 | 1235494.1137 | 2698675.1197 | 1235510.8815
19 | 2698578.5867 | 1235606.7123 | 2698582.8688 | 1235599.027 | 2698585.0814 | 1235591.7855
20 | 2698469.7501 | 1235481.019 | 2698483.211 | 1235476.3053
21 | 2698466.3678 | 1235506.0483 | 2698484.2896 | 1235492.0571 | 2698487.8644 | 1235490.1038 | 2698483.211 | 1235476.3053
22 | 2698615.4832 | 1235425.0834 | 2698613.7909 | 1235428.4798 | 2698612.0664 | 1235435.234 | 2698610.6439 | 1235457.4428
23 | 2698466.3678 | 1235506.0483 | 2698445.2329 | 1235522.5548 | 2698437.5754 | 1235527.4093 | 2698430.1277 | 1235531.0331 | 2698417.5964 | 1235534.9284
24 | 2698466.3678 | 1235506.0483 | 2698459.8196 | 1235499.7017 | 2698458.5494 | 1235495.6622
25 | 2698417.5964 | 1235534.9284 | 2698407.4665 | 1235527.7442 | 2698367.4536 | 1235509.5516
26 | 2698439.673 | 1235301.8097 | 2698420.7867 | 1235273.9539 | 2698415.845 | 1235265.6548 | 2698410.5003 | 1235255.1807 | 2698410.2626 | 1235254.607
27 | 2698439.673 | 1235301.8097 | 2698431.0165 | 1235302.5335 | 2698416.4341 | 1235297.2058
28 | 2698396.7536 | 1235227.3212 | 2698400.1915 | 1235231.359 | 2698403.6584 | 1235238.6662 | 2698410.2626 | 1235254.607
29 | 2698393.0737 | 1235288.9261 | 2698394.1935 | 1235289.0803 | 2698416.4341 | 1235297.2058
30 | 2698396.7536 | 1235227.3212 | 2698392.1171 | 1235225.2652 | 2698386.6632 | 1235224.1185 | 2698345.4924 | 1235225.4268 | 2698316.4875 | 1235224.2646
31 | 2698385.2992 | 1235287.8555 | 2698393.0737 | 1235288.9261
32 | 2698615.4832 | 1235425.0834 | 2698639.0446 | 1235377.7946
33 | 2698643.3747 | 1235375.954 | 2698639.0446 | 1235377.7946 | 2698639.0446 | 1235377.7946
34 | 2698643.3747 | 1235375.954 | 2698645.9973 | 1235388.9517 | 2698646.8028 | 1235392.3233
35 | 2698675.1197 | 1235510.8815 | 2698676.8495 | 1235519.2943 | 2698677.7278 | 1235525.658 | 2698677.8019 | 1235526.416
36 | 2698675.1197 | 1235510.8815 | 2698678.1719 | 1235510.7766 | 2698679.7985 | 1235510.8258 | 2698681.1416 | 1235511.0817 | 2698682.4825 | 1235511.4709 | 2698683.7222 | 1235512.0252 | 2698685.5441 | 1235513.0785 | 2698731.1882 | 1235543.5372 | 2698737.0151 | 1235553.1856 | 2698735.9648 | 1235564.9103 | 2698729.1587 | 1235581.832 | 2698721.6021 | 1235613.8414 | 2698723.1424 | 1235633.6484 | 2698729.3741 | 1235646.7172 | 2698734.371 | 1235652.5602 | 2698746.1097 | 1235656.725 | 2698756.7301 | 1235657.591 | 2698773.4027 | 1235649.9959 | 2698799.4572 | 1235641.734 | 2698820.476 | 1235633.6108 | 2698832.4502 | 1235631.8086
37 | 2698664.0004 | 1235369.3939 | 2698723.2781 | 1235407.0628
38 | 2698832.4502 | 1235631.8086 | 2698837.0878 | 1235643.7009
39 | 2698822.4373 | 1235465.0631 | 2698821.1806 | 1235464.3854 | 2698753.7474 | 1235426.4249 | 2698723.2781 | 1235407.0628
40 | 2698822.4373 | 1235465.0631 | 2698830.1663 | 1235469.2317
41 | 2699057.5704 | 1235546.3381 | 2699038.6225 | 1235539.1836 | 2698950.7329 | 1235512.4772 | 2698864.6627 | 1235487.8373 | 2698830.1663 | 1235469.2317
42 | 2699057.5704 | 1235546.3381 | 2699079.4378 | 1235557.7112 | 2699184.4347 | 1235621.9108 | 2699197.2759 | 1235628.4856
43 | 2698156.5637 | 1235260.125 | 2698159.797 | 1235255.9148
44 | 2698169.6545 | 1235243.0787 | 2698159.797 | 1235255.9148
45 | 2698169.6545 | 1235243.0787 | 2698177.2785 | 1235233.1509 | 2698190.4373 | 1235229.2468
46 | 2698190.4373 | 1235229.2468 | 2698202.0927 | 1235225.7888 | 2698218.3194 | 1235222.5907
47 | 2698218.3194 | 1235222.5907 | 2698226.6078 | 1235220.9571 | 2698230.926 | 1235214.5421
48 | 2698106.1172 | 1235163.6365 | 2698112.0359 | 1235155.8559
49 | 2698112.0359 | 1235155.8559 | 2698115.0815 | 1235151.8522 | 2698117.5325 | 1235149.6577 | 2698121.6803 | 1235148.77 | 2698142.9798 | 1235147.0649 | 2698149.1243 | 1235146.1705
50 | 2698240.4137 | 1235200.4479 | 2698230.926 | 1235214.5421
51 | 2698240.4137 | 1235200.4479 | 2698230.1199 | 1235193.517 | 2698197.8173 | 1235169.8544 | 2698197.3514 | 1235169.4753
52 | 2698240.4137 | 1235200.4479 | 2698266.279 | 1235212.3733 | 2698283.9687 | 1235218.3703 | 2698295.7982 | 1235221.2348 | 2698315.6949 | 1235224.2328 | 2698316.4875 | 1235224.2646
53 | 2698180.473 | 1235155.7404 | 2698197.3514 | 1235169.4753
54 | 2698180.473 | 1235155.7404 | 2698176.9608 | 1235152.8823
55 | 2698160.1289 | 1235144.5685 | 2698164.2303 | 1235145.1145 | 2698172.3768 | 1235149.152 | 2698176.9608 | 1235152.8823
56 | 2698160.1289 | 1235144.5685 | 2698149.1243 | 1235146.1705
57 | 2698346.8665 | 1235302.971 | 2698360.5906 | 1235294.0631
58 | 2698360.5906 | 1235294.0631 | 2698372.805 | 1235286.1351 | 2698385.2992 | 1235287.8555
59 | 2698130.8904 | 1235458.5409 | 2698138.1037 | 1235437.2773
60 | 2698141.1412 | 1235462.1017 | 2698130.8904 | 1235458.5409
61 | 2698130.8904 | 1235458.5409 | 2698122.7403 | 1235455.9174
62 | 2698141.1412 | 1235462.1017 | 2698145.0873 | 1235463.317
63 | 2698245.7013 | 1235482.4691 | 2698167.5828 | 1235470.2446 | 2698145.0873 | 1235463.317
64 | 2698245.7013 | 1235482.4691 | 2698247.5134 | 1235482.7527 | 2698256.8346 | 1235484.0877
65 | 2698256.8346 | 1235484.0877 | 2698313.9667 | 1235492.27 | 2698324.8171 | 1235494.7696
66 | 2698324.8171 | 1235494.7696 | 2698329.1008 | 1235495.7564 | 2698344.4654 | 1235500.403 | 2698361.4508 | 1235506.8223 | 2698367.4536 | 1235509.5516
67 | 2699391.6832 | 1235657.0891 | 2699342.8933 | 1235649.3118 | 2699269.719 | 1235647.6431 | 2699247.5508 | 1235644.3481 | 2699226.3918 | 1235638.6349 | 2699212.0909 | 1235634.2595 | 2699197.2759 | 1235628.4856
68 | 2699197.2759 | 1235628.4856 | 2699202.4556 | 1235636.9562 | 2699224.0444 | 1235648.2029 | 2699233.5791 | 1235663.7515 | 2699236.0785 | 1235673.1669 | 2699235.236 | 1235678.4872
69 | 2699391.6832 | 1235657.0891 | 2699391.8965 | 1235657.1245
70 | 2699391.6832 | 1235657.0891 | 2699388.2197 | 1235673.1765 | 2699389.5834 | 1235674.416
71 | 2699234.5384 | 1235682.8929 | 2699235.236 | 1235678.4872
72 | 2698966.3764 | 1235180.3431 | 2698966.2884 | 1235179.5661 | 2698966.284 | 1235179.2648
73 | 2698966.3764 | 1235180.3431 | 2698966.4929 | 1235181.3709 | 2698966.9687 | 1235182.8021 | 2698967.747 | 1235184.2494 | 2698968.5262 | 1235185.1853 | 2698969.4145 | 1235185.934 | 2698970.3429 | 1235186.5499 | 2698974.7704 | 1235188.8739
74 | 2698984.3226 | 1235138.5248 | 2698969.1305 | 1235168.4607 | 2698967.7201 | 1235171.7842 | 2698966.8016 | 1235174.6599 | 2698966.2567 | 1235177.3751 | 2698966.284 | 1235179.2648
75 | 2698984.3226 | 1235138.5248 | 2698992.6036 | 1235141.2759 | 2698998.1861 | 1235143.3371 | 2699001.3873 | 1235144.7471 | 2699004.261 | 1235146.285 | 2699005.9756 | 1235147.4144 | 2699007.4985 | 1235148.6963
76 | 2698984.3226 | 1235138.5248 | 2698974.523 | 1235135.5927 | 2698967.7841 | 1235133.8792 | 2698963.0465 | 1235132.8996 | 2698958.0395 | 1235132.1935 | 2698952.5844 | 1235131.5688 | 2698943.2316 | 1235130.9015 | 2698921.764 | 1235129.9545 | 2698919.1575 | 1235129.6442 | 2698916.8725 | 1235129.128 | 2698914.9023 | 1235128.3391 | 2698913.0658 | 1235127.2521 | 2698911.5859 | 1235126.1155 | 2698910.3295 | 1235124.738 | 2698909.3181 | 1235123.1978 | 2698908.6917 | 1235121.7196 | 2698908.3795 | 1235120.0132 | 2698908.3591 | 1235118.5117 | 2698908.5175 | 1235117.18 | 2698909.0688 | 1235114.9876 | 2698909.9565 | 1235112.5895 | 2698910.9484 | 1235110.3043 | 2698911.9818 | 1235108.2533 | 2698913.1537 | 1235106.0712 | 2698918.1199 | 1235097.414 | 2698925.3357 | 1235085.5031 | 2698928.7976 | 1235079.901 | 2698932.0087 | 1235075.2732 | 2698936.3598 | 1235069.4636 | 2698954.7998 | 1235047.2319 | 2698976.2901 | 1235019.1355 | 2698978.556 | 1235015.8041 | 2698980.1647 | 1235013.3068 | 2698980.8918 | 1235011.9179 | 2698981.439 | 1235010.4259 | 2698981.8031 | 1235009.0198 | 2698981.9451 | 1235007.7657 | 2698982.0071 | 1235006.3212 | 2698981.9291 | 1235004.6409 | 2698981.765 | 1235002.6811 | 2698987.7139 | 1234999.5668 | 2698994.3497 | 1234995.6744 | 2699004.3021 | 1234988.0902 | 2699018.483 | 1234974.7943 | 2699028.7266 | 1234961.0993 | 2699048.6404 | 1234937.2356 | 2699059.0706 | 1234925.9789 | 2699068.1419 | 1234917.2236 | 2699084.9914 | 1234903.2608 | 2699094.219 | 1234896.4874 | 2699137.0093 | 1234867.2571
77 | 2699007.4985 | 1235148.6963 | 2699009.0342 | 1235151.0236 | 2699009.6598 | 1235152.5463 | 2699010.1022 | 1235154.1659 | 2699010.302 | 1235155.8038 | 2699010.402 | 1235157.9738 | 2699010.4197 | 1235160.9985 | 2699007.373 | 1235216.7838
78 | 2698704.3408 | 1234921.4285 | 2698713.1809 | 1234965.2523 | 2698727.2367 | 1235027.7434 | 2698728.269 | 1235030.7628 | 2698729.5575 | 1235033.3972 | 2698730.9092 | 1235035.4212 | 2698732.3908 | 1235037.3695 | 2698734.3765 | 1235039.5041 | 2698737.7188 | 1235042.9066 | 2698740.4692 | 1235040.0279 | 2698744.2691 | 1235036.3995 | 2698748.8125 | 1235032.6722 | 2698753.6542 | 1235029.2168 | 2698758.6213 | 1235025.9636 | 2698762.969 | 1235023.534 | 2698768.4188 | 1235020.8448 | 2698773.9741 | 1235018.6355 | 2698779.8803 | 1235016.7211 | 2698785.8411 | 1235015.1635 | 2698792.395 | 1235013.9049 | 2698799.1162 | 1235013.0493 | 2698806.0585 | 1235012.5644 | 2698811.3697 | 1235012.2858 | 2698817.9333 | 1235012.2616 | 2698921.1684 | 1235014.3919 | 2698928.354 | 1235014.2892 | 2698935.043 | 1235014.0115 | 2698941.3798 | 1235013.5166 | 2698944.8831 | 1235013.1636 | 2698949.0327 | 1235012.6323 | 2698952.3717 | 1235012.1431 | 2698955.3491 | 1235011.5478 | 2698962.0751 | 1235009.9586 | 2698967.0054 | 1235008.4618 | 2698974.3847 | 1235005.8272 | 2698981.765 | 1235002.6811 | 2698987.7139 | 1234999.5668 | 2698994.3497 | 1234995.6744 | 2699004.3021 | 1234988.0902 | 2699018.483 | 1234974.7943 | 2699028.7266 | 1234961.0993 | 2699048.6404 | 1234937.2356 | 2699059.0706 | 1234925.9789 | 2699068.1419 | 1234917.2236 | 2699084.9914 | 1234903.2608 | 2699094.219 | 1234896.4874 | 2699137.0093 | 1234867.2571
79 | 2699137.0093 | 1234867.2571 | 2699142.4628 | 1234878.412 | 2699142.578 | 1234888.4265
80 | 2699003.1327 | 1235226.7343 | 2699007.2052 | 1235219.8555 | 2699007.373 | 1235216.7838
81 | 2699001.1297 | 1235230.1174 | 2699003.1327 | 1235226.7343
82 | 2699202.6484 | 1234944.4322 | 2699178.7734 | 1234949.3484 | 2699153.3016 | 1234960.5762 | 2699148.5199 | 1234961.0347
83 | 2699143.3721 | 1235006.2223 | 2699136.2977 | 1234991.9492 | 2699134.5463 | 1234975.7857 | 2699135.1839 | 1234967.9794 | 2699137.9931 | 1234962.0441 | 2699148.5199 | 1234961.0347
84 | 2699202.6484 | 1234944.4322 | 2699199.4854 | 1234936.6514 | 2699159.1282 | 1234920.3768 | 2699153.5253 | 1234918.9177
85 | 2699142.578 | 1234888.4265 | 2699142.8703 | 1234913.8563 | 2699146.993 | 1234917.2164 | 2699153.5253 | 1234918.9177
86 | 2698741.0627 | 1234919.2035 | 2698734.0653 | 1234922.5453 | 2698720.5755 | 1234923.4441 | 2698704.3408 | 1234921.4285
87 | 2698665.6576 | 1235260.8161 | 2698674.8872 | 1235228.3452 | 2698713.1249 | 1235093.3911 | 2698715.4067 | 1235085.4564 | 2698717.7721 | 1235078.4127 | 2698720.2618 | 1235072.0827 | 2698722.5797 | 1235066.9841 | 2698724.6872 | 1235062.7048 | 2698726.7581 | 1235058.803 | 2698729.088 | 1235054.8054 | 2698731.6379 | 1235050.7781 | 2698734.6584 | 1235046.6808 | 2698737.7188 | 1235042.9066 | 2698734.3765 | 1235039.5041 | 2698732.3908 | 1235037.3695 | 2698730.9092 | 1235035.4212 | 2698729.5575 | 1235033.3972 | 2698728.269 | 1235030.7628 | 2698727.2367 | 1235027.7434 | 2698713.1809 | 1234965.2523 | 2698704.3408 | 1234921.4285
88 | 2699349.9125 | 1235787.3171 | 2699351.1656 | 1235786.875 | 2699362.3502 | 1235783.8598 | 2699369.2822 | 1235781.6741 | 2699386.2988 | 1235775.721 | 2699387.3192 | 1235775.315
89 | 2699387.3192 | 1235775.315 | 2699404.1368 | 1235768.6252 | 2699410.6137 | 1235765.5979 | 2699415.8491 | 1235762.7751
90 | 2699415.8491 | 1235762.7751 | 2699419.3745 | 1235760.8743 | 2699423.4863 | 1235758.9639 | 2699427.8298 | 1235757.2242 | 2699432.7268 | 1235755.427 | 2699437.5439 | 1235753.8843 | 2699472.1692 | 1235743.7007 | 2699477.5847 | 1235742.1346 | 2699481.7419 | 1235741.1257 | 2699485.8216 | 1235740.2267 | 2699490.0649 | 1235739.4972 | 2699494.281 | 1235739.0452 | 2699498.5905 | 1235738.8839 | 2699503.5272 | 1235739.0853
91 | 2699552.0255 | 1235740.8805 | 2699548.386 | 1235741.2531 | 2699545.8473 | 1235741.4329 | 2699543.2793 | 1235741.5566 | 2699539.8363 | 1235741.4989 | 2699504.1425 | 1235739.1104 | 2699503.5272 | 1235739.0853
92 | 2699552.0255 | 1235740.8805 | 2699552.8433 | 1235741.7615 | 2699555.6023 | 1235744.2429 | 2699559.2846 | 1235746.7287
93 | 2699552.0255 | 1235740.8805 | 2699549.7511 | 1235738.3849
94 | 2699559.2846 | 1235746.7287 | 2699561.5062 | 1235747.8762
95 | 2699554.9877 | 1235765.0926 | 2699555.0593 | 1235762.1805 | 2699555.3949 | 1235759.3174 | 2699555.9094 | 1235756.624 | 2699556.5587 | 1235754.0107 | 2699557.6186 | 1235750.8372 | 2699559.2846 | 1235746.7287
96 | 2699549.7511 | 1235738.3849 | 2699514.3697 | 1235694.326 | 2699507.9695 | 1235687.8028 | 2699498.4158 | 1235680.2038 | 2699489.845 | 1235675.3789 | 2699481.226 | 1235672.5325 | 2699432.9594 | 1235664.0397
97 | 2699549.7511 | 1235738.3849 | 2699553.4388 | 1235731.9753 | 2699554.9425 | 1235729.4208 | 2699557.3394 | 1235725.9583 | 2699559.519 | 1235723.2706 | 2699560.3637 | 1235722.2959
98 | 2699894.8133 | 1235821.9244 | 2699896.2764 | 1235824.1984 | 2699897.6352 | 1235826.2117 | 2699898.7002 | 1235827.6974 | 2699900.0765 | 1235829.1216 | 2699902.0587 | 1235830.5226 | 2699903.1079 | 1235831.1145
99 | 2699712.0066 | 1235726.9304 | 2699716.7818 | 1235734.1938 | 2699720.2055 | 1235738.5545 | 2699724.5141 | 1235743.4082 | 2699728.654 | 1235747.4919 | 2699733.0713 | 1235751.2799 | 2699738.7984 | 1235755.9462 | 2699745.1962 | 1235760.7906 | 2699753.6182 | 1235766.792 | 2699767.3647 | 1235776.1965 | 2699772.5441 | 1235780.1198 | 2699777.1536 | 1235784.178 | 2699781.1164 | 1235788.4366 | 2699785.0765 | 1235792.8509 | 2699789.1271 | 1235798.1895 | 2699805.2519 | 1235821.4445 | 2699807.7599 | 1235824.8892 | 2699809.9233 | 1235827.672 | 2699812.1008 | 1235830.066 | 2699813.6945 | 1235831.6161 | 2699815.2353 | 1235832.7095 | 2699816.8041 | 1235833.492 | 2699818.7843 | 1235834.1146 | 2699821.0113 | 1235834.4634 | 2699823.1372 | 1235834.5214 | 2699825.1024 | 1235834.2319 | 2699827.2619 | 1235833.6456 | 2699829.7081 | 1235832.6637 | 2699848.6166 | 1235823.5969 | 2699852.2253 | 1235821.9007 | 2699855.3112 | 1235820.685 | 2699859.179 | 1235819.3379 | 2699878.8718 | 1235812.6972 | 2699880.8647 | 1235812.1192 | 2699882.6606 | 1235811.9937 | 2699884.3218 | 1235812.2329 | 2699886.029 | 1235812.8844 | 2699887.7516 | 1235813.9697 | 2699889.5059 | 1235815.4225 | 2699890.8669 | 1235816.8575 | 2699892.3978 | 1235818.5401 | 2699894.0488 | 1235820.7362 | 2699894.8133 | 1235821.9244
100 | 2699712.0066 | 1235726.9304 | 2699738.9129 | 1235719.8434 | 2699762.1904 | 1235712.9512 | 2699780.6966 | 1235706.2236 | 2699788.0634 | 1235702.9162
101 | 2699712.0066 | 1235726.9304 | 2699587.5446 | 1235751.428 | 2699583.3055 | 1235751.9018 | 2699579.6469 | 1235752.0628 | 2699576.0382 | 1235751.9578 | 2699571.2733 | 1235751.2885 | 2699567.0142 | 1235750.2497 | 2699563.0892 | 1235748.6939 | 2699561.5062 | 1235747.8762
102 | 2699788.0634 | 1235702.9162 | 2699792.6096 | 1235700.8752 | 2699798.0669 | 1235697.6804
103 | 2699798.0669 | 1235697.6804 | 2699802.9678 | 1235694.8113 | 2699809.9857 | 1235689.6185
104 | 2699809.9857 | 1235689.6185 | 2699827.0652 | 1235676.9806 | 2699827.0652 | 1235676.9806
105 | 2699859.208 | 1235647.5628 | 2699852.9211 | 1235652.2632 | 2699827.0652 | 1235676.9806
106 | 2699493.5805 | 1235789.2352 | 2699505.49 | 1235782.4542 | 2699511.1579 | 1235779.3691 | 2699518.1668 | 1235775.7615 | 2699519.9812 | 1235774.9914 | 2699522.2201 | 1235774.1838 | 2699522.7866 | 1235774.0185
107 | 2699522.7866 | 1235774.0185 | 2699523.8782 | 1235773.7001 | 2699525.7933 | 1235773.243 | 2699533.5331 | 1235771.6381 | 2699533.6261 | 1235771.6178
108 | 2699533.6261 | 1235771.6178 | 2699534.3559 | 1235771.4583
109 | 2699535.9412 | 1235771.1118 | 2699534.3559 | 1235771.4583
110 | 2699565.4957 | 1235805.9354 | 2699558.3416 | 1235780.4727
111 | 2699554.9877 | 1235765.0926 | 2699555.1228 | 1235767.4189 | 2699555.4003 | 1235769.3805 | 2699556.3261 | 1235773.299 | 2699558.3416 | 1235780.4727
112 | 2699554.9877 | 1235765.0926 | 2699551.2071 | 1235766.6638 | 2699547.9612 | 1235767.9437 | 2699545.1901 | 1235768.898 | 2699541.0465 | 1235769.9961 | 2699535.9412 | 1235771.1118
113 | 2699560.3637 | 1235722.2959 | 2699562.1973 | 1235720.1799 | 2699582.9499 | 1235700.4462 | 2699585.0403 | 1235698.1129 | 2699586.8585 | 1235695.7638 | 2699588.6896 | 1235693.0925 | 2699590.3867 | 1235690.1971
114 | 2699590.3867 | 1235690.1971 | 2699591.0195 | 1235689.1175 | 2699593.3212 | 1235685.0196 | 2699593.6462 | 1235684.3079
115 | 2699422.767 | 1235662.2463 | 2699432.9594 | 1235664.0397
116 | 2699422.767 | 1235662.2463 | 2699391.8965 | 1235657.1245
117 | 2699422.767 | 1235662.2463 | 2699427.4667 | 1235669.9752 | 2699450.9646 | 1235696.9108 | 2699452.8038 | 1235704.147 | 2699452.1816 | 1235711.7607
118 | 2699452.1816 | 1235711.7607 | 2699451.1469 | 1235724.4224

## bus_geodata
| x | y | coords
0 | 2698593.9387 | 1235339.0369
1 | 2698590.663 | 1235338.4981
2 | 2698624.7353 | 1235343.6658
3 | 2698581.053 | 1235336.8163
4 | 2698643.7131 | 1235346.471
5 | 2698530.5983 | 1235326.0004
6 | 2698642.7279 | 1235360.2093
7 | 2698647.6183 | 1235324.7348
8 | 2698505.3396 | 1235324.6371
9 | 2698491.4509 | 1235319.809
10 | 2698469.3899 | 1235312.14
11 | 2698609.9613 | 1235468.1013
12 | 2698671.1216 | 1235494.1137
13 | 2698585.0814 | 1235591.7855
14 | 2698483.211 | 1235476.3053
15 | 2698610.6439 | 1235457.4428
16 | 2698466.3678 | 1235506.0483
17 | 2698417.5964 | 1235534.9284
18 | 2698458.5494 | 1235495.6622
19 | 2698469.7501 | 1235481.019
20 | 2698439.673 | 1235301.8097
21 | 2698410.2626 | 1235254.607
22 | 2698416.4341 | 1235297.2058
23 | 2698396.7536 | 1235227.3212
24 | 2698393.0737 | 1235288.9261
25 | 2698615.4832 | 1235425.0834
26 | 2698639.0446 | 1235377.7946
27 | 2698643.3747 | 1235375.954
28 | 2698646.8028 | 1235392.3233
29 | 2698675.1197 | 1235510.8815
30 | 2698578.5867 | 1235606.7123
31 | 2698664.0004 | 1235369.3939
32 | 2698677.8019 | 1235526.416
33 | 2698832.4502 | 1235631.8086
34 | 2698723.2781 | 1235407.0628
35 | 2698822.4373 | 1235465.0631
36 | 2698830.1663 | 1235469.2317
37 | 2699057.5704 | 1235546.3381
38 | 2698159.797 | 1235255.9148
39 | 2698156.5637 | 1235260.125
40 | 2698169.6545 | 1235243.0787
41 | 2698190.4373 | 1235229.2468
42 | 2698218.3194 | 1235222.5907
43 | 2698106.1172 | 1235163.6365
44 | 2698112.0359 | 1235155.8559
45 | 2698230.926 | 1235214.5421
46 | 2698240.4137 | 1235200.4479
47 | 2698197.3514 | 1235169.4753
48 | 2698316.4875 | 1235224.2646
49 | 2698180.473 | 1235155.7404
50 | 2698176.9608 | 1235152.8823
51 | 2698160.1289 | 1235144.5685
52 | 2698149.1243 | 1235146.1705
53 | 2698346.8665 | 1235302.971
54 | 2698360.5906 | 1235294.0631
55 | 2698385.2992 | 1235287.8555
56 | 2698138.1037 | 1235437.2773
57 | 2698130.8904 | 1235458.5409
58 | 2698141.1412 | 1235462.1017
59 | 2698122.7403 | 1235455.9174
60 | 2698145.0873 | 1235463.317
61 | 2698245.7013 | 1235482.4691
62 | 2698256.8346 | 1235484.0877
63 | 2698324.8171 | 1235494.7696
64 | 2698367.4536 | 1235509.5516
65 | 2699197.2759 | 1235628.4856
66 | 2699391.6832 | 1235657.0891
67 | 2699235.236 | 1235678.4872
68 | 2698837.0878 | 1235643.7009
69 | 2698966.3764 | 1235180.3431
70 | 2698966.284 | 1235179.2648
71 | 2698974.7704 | 1235188.8739
72 | 2698984.3226 | 1235138.5248
73 | 2699007.4985 | 1235148.6963
74 | 2699137.0092 | 1234867.2571
75 | 2699003.1327 | 1235226.7343
76 | 2699007.373 | 1235216.7838
77 | 2699001.1297 | 1235230.1174
78 | 2699148.5199 | 1234961.0347
79 | 2699202.6484 | 1234944.4322
80 | 2699143.3721 | 1235006.2223
81 | 2699153.5253 | 1234918.9177
82 | 2699142.578 | 1234888.4265
83 | 2698704.3408 | 1234921.4285
84 | 2698741.0627 | 1234919.2035
85 | 2698665.6576 | 1235260.8161
86 | 2699349.9125 | 1235787.3171
87 | 2699387.3192 | 1235775.315
88 | 2699415.8491 | 1235762.7751
89 | 2699503.5272 | 1235739.0853
90 | 2699552.0255 | 1235740.8805
91 | 2699559.2846 | 1235746.7287
92 | 2699549.7511 | 1235738.3849
93 | 2699894.8133 | 1235821.9244
94 | 2699903.1079 | 1235831.1145
95 | 2699712.0066 | 1235726.9304
96 | 2699788.0634 | 1235702.9162
97 | 2699561.5062 | 1235747.8762
98 | 2699798.0669 | 1235697.6804
99 | 2699809.9857 | 1235689.6185
100 | 2699827.0652 | 1235676.9806
101 | 2699859.208 | 1235647.5628
102 | 2699493.5805 | 1235789.2352
103 | 2699522.7866 | 1235774.0185
104 | 2699533.6261 | 1235771.6178
105 | 2699534.3559 | 1235771.4583
106 | 2699565.4957 | 1235805.9354
107 | 2699558.3416 | 1235780.4727
108 | 2699554.9877 | 1235765.0926
109 | 2699535.9412 | 1235771.1118
110 | 2699560.3637 | 1235722.2959
111 | 2699590.3867 | 1235690.1971
112 | 2699593.6462 | 1235684.3079
113 | 2699432.9594 | 1235664.0397
114 | 2699422.767 | 1235662.2463
115 | 2699452.1816 | 1235711.7607
116 | 2699451.1469 | 1235724.4224
117 | 2699391.8965 | 1235657.1245
118 | 2699389.5834 | 1235674.416
119 | 2699234.5384 | 1235682.8929
120 | 2698671.1216 | 1235494.1137

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99188 | -0.15468 | 0.0010005 | 0.00025076
1 | 0.99184 | -0.15544 | 0.00026517 | 6.6458e-05
2 | 0.99228 | -0.14706 | 0.00018513 | 4.6399e-05
3 | 0.99173 | -0.15761 | 0.00065922 | 0.00016522
4 | 0.99252 | -0.14231 | 0 | 0
5 | 0.99117 | -0.1685 | 0.00074475 | 0.00018665
6 | 0.99279 | -0.13703 | 0 | 0
7 | 0.99237 | -0.14529 | 0.0001259 | 3.1553e-05
8 | 0.99091 | -0.17352 | 0 | 0
9 | 0.99076 | -0.17643 | 0.00033298 | 8.3454e-05
10 | 0.99053 | -0.18092 | 0.00036855 | 9.2367e-05
11 | 0.99602 | -0.07539 | 0 | 0
12 | 0.99919 | -0.015311 | 0 | 0
13 | 0.99593 | -0.077222 | 0.00025353 | 6.354e-05
14 | 0.99056 | -0.17965 | 0 | 0
15 | 0.99572 | -0.081061 | 0.00028704 | 7.1939e-05
16 | 0.98903 | -0.20906 | 0 | 0
17 | 0.98694 | -0.24941 | 0 | 0
18 | 0.98902 | -0.20916 | 0.00042411 | 0.00010629
19 | 0.99055 | -0.17981 | 0.00063588 | 0.00015937
20 | 0.99023 | -0.18676 | 0 | 0
21 | 0.98992 | -0.19287 | 0.0012801 | 0.00032083
22 | 0.99014 | -0.1886 | 0.00079174 | 0.00019843
23 | 0.98978 | -0.19554 | 0 | 0
24 | 0.99006 | -0.19013 | 0.00034985 | 8.768e-05
25 | 0.99481 | -0.098529 | 0.00037717 | 9.4527e-05
26 | 0.99335 | -0.12637 | 0.00058993 | 0.00014785
27 | 0.99322 | -0.12883 | 0 | 0
28 | 0.99322 | -0.1289 | 0.00025206 | 6.3171e-05
29 | 1 | 0 | -0.10595 | -0.02676
30 | 0.99592 | -0.077383 | 0.00056169 | 0.00014077
31 | 0.99238 | -0.14484 | 0.00037858 | 9.488e-05
32 | 1 | -4.9114e-05 | 0.00017837 | 4.4704e-05
33 | 0.99983 | -0.0033931 | 0 | 0
34 | 0.99118 | -0.16779 | 0.00038384 | 9.6198e-05
35 | 0.98924 | -0.20506 | 0.00075995 | 0.00019046
36 | 0.98909 | -0.20786 | 0.00038462 | 9.6395e-05
37 | 0.98514 | -0.28397 | 0 | 0
38 | 0.9889 | -0.21268 | 0.0014847 | 0.00037211
39 | 0.9889 | -0.21272 | 0.00039542 | 9.9102e-05
40 | 0.98893 | -0.21214 | 0.00016248 | 4.0721e-05
41 | 0.98898 | -0.21119 | 0.0001388 | 3.4787e-05
42 | 0.98903 | -0.21007 | 0.00014441 | 3.6193e-05
43 | 0.98892 | -0.21224 | 0.00046144 | 0.00011565
44 | 0.98893 | -0.21216 | 0.00033933 | 8.5045e-05
45 | 0.98907 | -0.2094 | 0.00013159 | 3.298e-05
46 | 0.98911 | -0.20865 | 0 | 0
47 | 0.98902 | -0.21035 | 0.00016672 | 4.1783e-05
48 | 0.98942 | -0.20257 | 0.00062798 | 0.00015739
49 | 0.98899 | -0.21098 | 0.00036341 | 9.108e-05
50 | 0.98898 | -0.21108 | 0.00031957 | 8.0093e-05
51 | 0.98897 | -0.2114 | 0 | 0
52 | 0.98896 | -0.21159 | 0.00013873 | 3.4769e-05
53 | 0.98998 | -0.19158 | 0.00077794 | 0.00019497
54 | 0.98999 | -0.19135 | 0.00084465 | 0.00021169
55 | 0.99004 | -0.19057 | 0.0015053 | 0.00037726
56 | 0.97843 | -0.41537 | 0.014406 | 0.0036104
57 | 0.97873 | -0.40948 | 0 | 0
58 | 0.97888 | -0.40637 | 0 | 0
59 | 0.97871 | -0.4097 | 0.0014043 | 0.00035196
60 | 0.97895 | -0.40518 | 0.0066297 | 0.0016616
61 | 0.98108 | -0.36339 | 0.0032529 | 0.00081526
62 | 0.98135 | -0.35816 | 0.0055507 | 0.0013911
63 | 0.98334 | -0.3193 | 0.0055372 | 0.0013878
64 | 0.98488 | -0.28937 | 0.0027387 | 0.00068639
65 | 0.97982 | -0.38741 | 0 | 0
66 | 0.97593 | -0.46367 | 0 | 0
67 | 0.97894 | -0.40474 | 0.0052905 | 0.0013259
68 | 0.99982 | -0.0035438 | 0.00067678 | 0.00016962
69 | 0.98443 | -0.30028 | 0.00031844 | 7.9808e-05
70 | 0.98443 | -0.30027 | 0.00011021 | 2.7621e-05
71 | 0.98442 | -0.30039 | 0.00048624 | 0.00012186
72 | 0.98446 | -0.29953 | 0 | 0
73 | 0.9844 | -0.30074 | 0 | 0
74 | 0.98588 | -0.27188 | 0 | 0
75 | 0.98421 | -0.30451 | 0.00032012 | 8.0228e-05
76 | 0.98423 | -0.30403 | 0.00026593 | 6.6649e-05
77 | 0.9842 | -0.30465 | 0.0020689 | 0.00051852
78 | 0.98549 | -0.2794 | 0.0019376 | 0.00048561
79 | 0.9856 | -0.2772 | 0 | 0
80 | 0.98548 | -0.27961 | 0.00020878 | 5.2326e-05
81 | 0.98572 | -0.27497 | 0.00061359 | 0.00015378
82 | 0.98581 | -0.27311 | 0.00029045 | 7.2793e-05
83 | 0.98946 | -0.20178 | 0 | 0
84 | 0.98944 | -0.20233 | 0.00082205 | 0.00020603
85 | 0.99191 | -0.15412 | 0 | 0
86 | 0.97193 | -0.54253 | 0.0013053 | 0.00032713
87 | 0.97198 | -0.54158 | 0.0031997 | 0.00080193
88 | 0.97211 | -0.53899 | 0.000561 | 0.0001406
89 | 0.97254 | -0.53044 | 0.0014681 | 0.00036793
90 | 0.97284 | -0.52458 | 0 | 0
91 | 0.97277 | -0.52604 | 0 | 0
92 | 0.97289 | -0.52365 | 0 | 0
93 | 0.97189 | -0.5434 | 0.00020264 | 5.0786e-05
94 | 0.97189 | -0.54349 | 0.00039698 | 9.9494e-05
95 | 0.97202 | -0.54075 | 0 | 0
96 | 0.97169 | -0.54738 | 0.00088559 | 0.00022195
97 | 0.97275 | -0.52629 | 0.00027669 | 6.9346e-05
98 | 0.97165 | -0.54814 | 0.00062269 | 0.00015606
99 | 0.97161 | -0.54893 | 0.00029913 | 7.4969e-05
100 | 0.97156 | -0.54999 | 0.001595 | 0.00039976
101 | 0.97151 | -0.55087 | 0.0010913 | 0.00027351
102 | 0.97266 | -0.52809 | 0.00038359 | 9.6136e-05
103 | 0.97267 | -0.52786 | 0.00016086 | 4.0316e-05
104 | 0.97268 | -0.52775 | 0.00028788 | 7.215e-05
105 | 0.97268 | -0.52773 | 0.00027579 | 6.9121e-05
106 | 0.97266 | -0.52809 | 0.0010665 | 0.0002673
107 | 0.97269 | -0.52757 | 0.00047035 | 0.00011788
108 | 0.97271 | -0.52713 | 0 | 0
109 | 0.97268 | -0.5277 | 0.00044768 | 0.0001122
110 | 0.97285 | -0.52444 | 0.00047321 | 0.0001186
111 | 0.97278 | -0.52585 | 0.0010656 | 0.00026706
112 | 0.97277 | -0.52593 | 0.0006699 | 0.00016789
113 | 0.97523 | -0.47748 | 0.00029716 | 7.4475e-05
114 | 0.97539 | -0.47416 | 0 | 0
115 | 0.97536 | -0.47484 | 0.00041237 | 0.00010335
116 | 0.97536 | -0.47489 | 0.00021006 | 5.2646e-05
117 | 0.97592 | -0.46375 | 0.00073749 | 0.00018483
118 | 0.97589 | -0.46445 | 0.0023103 | 0.00057902
119 | 0.9789 | -0.40546 | 0.0088119 | 0.0022085
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.012819 | 0.0032121 | -0.012818 | -0.0032118 | 4.6039e-07 | 2.518e-07 | 0.019231 | 0.019231 | 0.019231 | 0.99188 | -0.15468 | 0.99184 | -0.15544 | 5.2831
1 | -0.013819 | -0.0034629 | 0.013824 | 0.0034657 | 5.0194e-06 | 2.8103e-06 | 0.020732 | 0.020731 | 0.020732 | 0.99188 | -0.15468 | 0.99228 | -0.14706 | 5.6955
2 | 0.012553 | 0.0031454 | -0.012552 | -0.0031447 | 1.2976e-06 | 7.0457e-07 | 0.018833 | 0.018833 | 0.018833 | 0.99184 | -0.15544 | 0.99173 | -0.15761 | 5.1739
3 | -0.01401 | -0.0035121 | 0.014013 | 0.0035138 | 3.1753e-06 | 1.7843e-06 | 0.021009 | 0.021009 | 0.021009 | 0.99228 | -0.14706 | 0.99252 | -0.14231 | 5.7717
4 | 0.011893 | 0.0029795 | -0.011887 | -0.0029762 | 6.1632e-06 | 3.2788e-06 | 0.017844 | 0.017844 | 0.017844 | 0.99173 | -0.15761 | 0.99117 | -0.1685 | 4.9022
5 | -0.021631 | -0.005418 | 0.021636 | 0.0054213 | 5.4328e-06 | 3.2989e-06 | 0.032428 | 0.032428 | 0.032428 | 0.99252 | -0.14231 | 0.99279 | -0.13703 | 8.9088
6 | 0.0076178 | 0.0019041 | -0.0076167 | -0.0019037 | 1.0814e-06 | 4.0633e-07 | 0.011419 | 0.011419 | 0.011419 | 0.99252 | -0.14231 | 0.99237 | -0.14529 | 3.1371
7 | 0.011142 | 0.0027895 | -0.011139 | -0.0027882 | 2.6666e-06 | 1.3791e-06 | 0.016726 | 0.016726 | 0.016726 | 0.99117 | -0.1685 | 0.99091 | -0.17352 | 4.5951
8 | 0.037767 | 0.0096601 | -0.037753 | -0.0096516 | 1.4264e-05 | 8.5165e-06 | 0.056676 | 0.056676 | 0.056676 | 0.99279 | -0.13703 | 0.99238 | -0.14484 | 7.7852
9 | -0.059403 | -0.015081 | 0.059427 | 0.015096 | 2.3461e-05 | 1.4607e-05 | 0.089103 | 0.089103 | 0.089103 | 0.99279 | -0.13703 | 0.99322 | -0.12883 | 12.2395
10 | 0.0074908 | 0.0018722 | -0.0074876 | -0.001871 | 3.1412e-06 | 1.1527e-06 | 0.01123 | 0.011231 | 0.011231 | 0.99237 | -0.14529 | 0.99191 | -0.15412 | 3.0853
11 | 0.011139 | 0.0027882 | -0.011138 | -0.0027874 | 1.5426e-06 | 7.9787e-07 | 0.016726 | 0.016726 | 0.016726 | 0.99091 | -0.17352 | 0.99076 | -0.17643 | 4.5951
12 | 0.010805 | 0.0027039 | -0.010802 | -0.0027027 | 2.306e-06 | 1.1751e-06 | 0.016226 | 0.016226 | 0.016226 | 0.99076 | -0.17643 | 0.99053 | -0.18092 | 4.4577
13 | 0.010434 | 0.0026104 | -0.010431 | -0.0026089 | 2.8979e-06 | 1.4498e-06 | 0.015672 | 0.015673 | 0.015673 | 0.99053 | -0.18092 | 0.99023 | -0.18676 | 4.3057
14 | -0.10307 | -0.026311 | 0.10337 | 0.026501 | 0.00030017 | 0.00019035 | 0.15415 | 0.15415 | 0.15415 | 0.99602 | -0.07539 | 0.99919 | -0.015311 | 21.1748
15 | 0.00081529 | 0.00020249 | -0.00081522 | -0.0002041 | 7.0852e-08 | -1.613e-06 | 0.0012174 | 0.0012179 | 0.0012179 | 0.99602 | -0.07539 | 0.99593 | -0.077222 | 0.3346
16 | 0.041166 | 0.010538 | -0.040959 | -0.010407 | 0.00020673 | 0.00013042 | 0.061579 | 0.061579 | 0.061579 | 0.99602 | -0.07539 | 0.99056 | -0.17965 | 16.9174
17 | 0.061089 | 0.01557 | -0.061072 | -0.01556 | 1.6713e-05 | 1.0419e-05 | 0.091357 | 0.091357 | 0.091357 | 0.99602 | -0.07539 | 0.99572 | -0.081061 | 12.549
18 | -0.10337 | -0.026501 | 0.10345 | 0.02655 | 7.68e-05 | 4.87e-05 | 0.15415 | 0.15415 | 0.15415 | 0.99919 | -0.015311 | 1 | 0 | 21.1747
19 | 0.00056169 | 0.00014056 | -0.00056169 | -0.00014077 | 4.323e-09 | -2.1024e-07 | 0.00083915 | 0.00083922 | 0.00083922 | 0.99593 | -0.077222 | 0.99592 | -0.077383 | 0.23056
20 | 0.00063588 | 0.00015919 | -0.00063588 | -0.00015937 | 4.8673e-09 | -1.8001e-07 | 0.00095516 | 0.00095522 | 0.00095522 | 0.99056 | -0.17965 | 0.99055 | -0.17981 | 0.26242
21 | 0.040323 | 0.010248 | -0.040266 | -0.010212 | 5.7021e-05 | 3.5962e-05 | 0.060624 | 0.060624 | 0.060624 | 0.99056 | -0.17965 | 0.98903 | -0.20906 | 16.6551
22 | 0.060785 | 0.015488 | -0.060734 | -0.015456 | 5.1189e-05 | 3.1902e-05 | 0.090928 | 0.090928 | 0.090928 | 0.99572 | -0.081061 | 0.99481 | -0.098529 | 12.4901
23 | 0.039842 | 0.010106 | -0.039765 | -0.010058 | 7.7145e-05 | 4.8641e-05 | 0.059986 | 0.059987 | 0.059987 | 0.98903 | -0.20906 | 0.98694 | -0.24941 | 16.4799
24 | 0.00042411 | 0.00010612 | -0.00042411 | -0.00010629 | 2.0387e-09 | -1.7006e-07 | 0.00063802 | 0.00063808 | 0.00063808 | 0.98903 | -0.20906 | 0.98902 | -0.20916 | 0.1753
25 | 0.039765 | 0.010058 | -0.039689 | -0.01001 | 7.6071e-05 | 4.7966e-05 | 0.059987 | 0.059987 | 0.059987 | 0.98694 | -0.24941 | 0.98488 | -0.28937 | 16.4799
26 | 0.0061607 | 0.0015397 | -0.0061589 | -0.0015393 | 1.7894e-06 | 4.2898e-07 | 0.0092561 | 0.0092564 | 0.0092564 | 0.99023 | -0.18676 | 0.98992 | -0.19287 | 2.543
27 | 0.0042702 | 0.0010692 | -0.0042699 | -0.0010693 | 3.7382e-07 | -7.2192e-08 | 0.0064165 | 0.0064166 | 0.0064166 | 0.99023 | -0.18676 | 0.99014 | -0.1886 | 1.7628
28 | 0.0048788 | 0.0012184 | -0.0048781 | -0.0012184 | 6.1782e-07 | 1.4784e-09 | 0.0073321 | 0.0073322 | 0.0073322 | 0.98992 | -0.19287 | 0.98978 | -0.19554 | 2.0143
29 | 0.0034781 | 0.00087087 | -0.0034779 | -0.00087103 | 2.5416e-07 | -1.564e-07 | 0.0052268 | 0.0052269 | 0.0052269 | 0.99014 | -0.1886 | 0.99006 | -0.19013 | 1.436
30 | 0.0048781 | 0.0012184 | -0.0048765 | -0.0012184 | 1.6304e-06 | 4.4961e-09 | 0.0073322 | 0.0073326 | 0.0073326 | 0.98978 | -0.19554 | 0.98942 | -0.20257 | 2.0144
31 | 0.003128 | 0.00078335 | -0.0031279 | -0.0007834 | 6.5039e-08 | -5.9294e-08 | 0.0047011 | 0.0047011 | 0.0047011 | 0.99006 | -0.19013 | 0.99004 | -0.19057 | 1.2915
32 | 0.060357 | 0.015362 | -0.060276 | -0.015311 | 8.0891e-05 | 5.0401e-05 | 0.090364 | 0.090364 | 0.090364 | 0.99481 | -0.098529 | 0.99335 | -0.12637 | 12.4127
33 | 0.059686 | 0.015163 | -0.059679 | -0.015159 | 7.0636e-06 | 4.3989e-06 | 0.089481 | 0.089481 | 0.089481 | 0.99335 | -0.12637 | 0.99322 | -0.12883 | 12.2913
34 | 0.00025206 | 6.2955e-05 | -0.00025206 | -6.3171e-05 | 8.9425e-10 | -2.159e-07 | 0.00037755 | 0.00037762 | 0.00037762 | 0.99322 | -0.12883 | 0.99322 | -0.1289 | 0.10374
35 | 0.00017837 | 4.4497e-05 | -0.00017837 | -4.4704e-05 | 4.1661e-10 | -2.0668e-07 | 0.00026535 | 0.00026542 | 0.00026542 | 1 | 0 | 1 | -4.9114e-05 | 0.072917
36 | 0.0006769 | 0.00016578 | -0.00067679 | -0.00016945 | 1.0843e-07 | -3.6741e-06 | 0.0010059 | 0.0010072 | 0.0010072 | 1 | 0 | 0.99983 | -0.0033931 | 0.2767
37 | 0.037375 | 0.0095567 | -0.037333 | -0.009532 | 4.1458e-05 | 2.472e-05 | 0.056108 | 0.056109 | 0.056109 | 0.99238 | -0.14484 | 0.99118 | -0.16779 | 7.7073
38 | 0.00067679 | 0.00016945 | -0.00067678 | -0.00016962 | 4.8561e-09 | -1.6429e-07 | 0.0010072 | 0.0010073 | 0.0010073 | 0.99983 | -0.0033931 | 0.99982 | -0.0035438 | 0.27672
39 | 0.036949 | 0.0094358 | -0.036883 | -0.0093962 | 6.6447e-05 | 3.957e-05 | 0.055533 | 0.055534 | 0.055534 | 0.99118 | -0.16779 | 0.98924 | -0.20506 | 7.6283
40 | 0.036123 | 0.0092058 | -0.036118 | -0.0092029 | 4.871e-06 | 2.892e-06 | 0.054391 | 0.054391 | 0.054391 | 0.98924 | -0.20506 | 0.98909 | -0.20786 | 7.4713
41 | 0.035733 | 0.0091065 | -0.035603 | -0.009029 | 0.00013077 | 7.7533e-05 | 0.053812 | 0.053814 | 0.053814 | 0.98909 | -0.20786 | 0.98514 | -0.28397 | 7.3921
42 | 0.035603 | 0.009029 | -0.035426 | -0.0089183 | 0.00017609 | 0.00011064 | 0.053814 | 0.053815 | 0.053815 | 0.98514 | -0.28397 | 0.97982 | -0.38741 | 14.7844
43 | 0.00039542 | 9.9034e-05 | -0.00039542 | -9.9102e-05 | 7.047e-10 | -6.7655e-08 | 0.00059497 | 0.000595 | 0.000595 | 0.9889 | -0.21268 | 0.9889 | -0.21272 | 0.16346
44 | -0.0018802 | -0.00047114 | 0.0018802 | 0.00047097 | 4.8574e-08 | -1.7656e-07 | 0.0028291 | 0.002829 | 0.0028291 | 0.9889 | -0.21268 | 0.98893 | -0.21214 | 0.77722
45 | -0.0020427 | -0.00051169 | 0.0020428 | 0.00051141 | 9.2959e-08 | -2.7723e-07 | 0.0030735 | 0.0030734 | 0.0030735 | 0.98893 | -0.21214 | 0.98898 | -0.21119 | 0.84436
46 | -0.0021816 | -0.0005462 | 0.0021817 | 0.0005459 | 1.1592e-07 | -2.9405e-07 | 0.0032822 | 0.0032821 | 0.0032822 | 0.98898 | -0.21119 | 0.98903 | -0.21007 | 0.9017
47 | -0.0023261 | -0.0005821 | 0.0023262 | 0.00058194 | 7.4301e-08 | -1.6011e-07 | 0.0034993 | 0.0034993 | 0.0034993 | 0.98903 | -0.21007 | 0.98907 | -0.2094 | 0.96136
48 | -0.00046144 | -0.00011565 | 0.00046144 | 0.00011552 | 1.7672e-09 | -1.243e-07 | 0.00069432 | 0.00069427 | 0.00069432 | 0.98892 | -0.21224 | 0.98893 | -0.21216 | 0.19075
49 | -0.00080077 | -0.00020057 | 0.00080079 | 0.00020007 | 2.1848e-08 | -5.0103e-07 | 0.0012049 | 0.0012047 | 0.0012049 | 0.98893 | -0.21216 | 0.98896 | -0.21159 | 0.33101
50 | -0.0024578 | -0.00061492 | 0.0024579 | 0.00061475 | 8.7091e-08 | -1.6232e-07 | 0.0036972 | 0.0036972 | 0.0036972 | 0.98907 | -0.2094 | 0.98911 | -0.20865 | 1.0157
51 | 0.0017895 | 0.00044653 | -0.0017893 | -0.00044712 | 1.4412e-07 | -5.8863e-07 | 0.0026914 | 0.0026916 | 0.0026916 | 0.98911 | -0.20865 | 0.98902 | -0.21035 | 0.73945
52 | -0.0042473 | -0.0010613 | 0.0042485 | 0.001061 | 1.2281e-06 | -2.4431e-07 | 0.0063885 | 0.0063882 | 0.0063885 | 0.98911 | -0.20865 | 0.98942 | -0.20257 | 1.7551
53 | 0.0016226 | 0.00040533 | -0.0016225 | -0.00040558 | 4.8616e-08 | -2.4813e-07 | 0.0024408 | 0.0024409 | 0.0024409 | 0.98902 | -0.21035 | 0.98899 | -0.21098 | 0.67057
54 | 0.0012591 | 0.0003145 | -0.0012591 | -0.00031455 | 6.0919e-09 | -5.4206e-08 | 0.0018941 | 0.0018941 | 0.0018941 | 0.98899 | -0.21098 | 0.98898 | -0.21108 | 0.52036
55 | 0.00093955 | 0.00023446 | -0.00093953 | -0.0002347 | 1.4337e-08 | -2.3642e-07 | 0.0014133 | 0.0014134 | 0.0014134 | 0.98898 | -0.21108 | 0.98897 | -0.2114 | 0.38829
56 | 0.00093953 | 0.0002347 | -0.00093952 | -0.00023484 | 8.3307e-09 | -1.3736e-07 | 0.0014134 | 0.0014134 | 0.0014134 | 0.98897 | -0.2114 | 0.98896 | -0.21159 | 0.3883
57 | -0.00077794 | -0.00019497 | 0.00077795 | 0.00019477 | 8.3885e-09 | -2.0501e-07 | 0.0011693 | 0.0011692 | 0.0011693 | 0.98998 | -0.19158 | 0.98999 | -0.19135 | 0.32124
58 | -0.0016226 | -0.00040646 | 0.0016227 | 0.00040614 | 6.0605e-08 | -3.1063e-07 | 0.0024388 | 0.0024387 | 0.0024388 | 0.98999 | -0.19135 | 0.99004 | -0.19057 | 0.67
59 | -0.014406 | -0.0036104 | 0.01441 | 0.0036127 | 4.0415e-06 | 2.3045e-06 | 0.021908 | 0.021908 | 0.021908 | 0.97843 | -0.41537 | 0.97873 | -0.40948 | 6.0188
60 | -0.015814 | -0.0039646 | 0.015816 | 0.0039659 | 2.3462e-06 | 1.3655e-06 | 0.024043 | 0.024043 | 0.024043 | 0.97873 | -0.40948 | 0.97888 | -0.40637 | 6.6053
61 | 0.0014043 | 0.00035186 | -0.0014043 | -0.00035196 | 1.4637e-08 | -9.823e-08 | 0.0021351 | 0.0021351 | 0.0021351 | 0.97873 | -0.40948 | 0.97871 | -0.4097 | 0.58657
62 | -0.015816 | -0.0039659 | 0.015817 | 0.0039664 | 8.951e-07 | 5.2095e-07 | 0.024043 | 0.024043 | 0.024043 | 0.97888 | -0.40637 | 0.97895 | -0.40518 | 6.6053
63 | -0.022447 | -0.005628 | 0.022492 | 0.0056554 | 4.4796e-05 | 2.7377e-05 | 0.034121 | 0.03412 | 0.034121 | 0.97895 | -0.40518 | 0.98108 | -0.36339 | 9.3738
64 | -0.025745 | -0.0064706 | 0.025751 | 0.0064746 | 6.4348e-06 | 3.9761e-06 | 0.039054 | 0.039054 | 0.039054 | 0.98108 | -0.36339 | 0.98135 | -0.35816 | 10.7291
65 | -0.031302 | -0.0078658 | 0.03136 | 0.0079021 | 5.8181e-05 | 3.6364e-05 | 0.04747 | 0.04747 | 0.04747 | 0.98135 | -0.35816 | 0.98334 | -0.3193 | 13.0413
66 | -0.036897 | -0.0092899 | 0.03695 | 0.0093232 | 5.2869e-05 | 3.3262e-05 | 0.055849 | 0.055849 | 0.055849 | 0.98334 | -0.3193 | 0.98488 | -0.28937 | 15.3432
67 | 0.021312 | 0.0053772 | -0.021235 | -0.00533 | 7.7537e-05 | 4.715e-05 | 0.032379 | 0.03238 | 0.03238 | 0.97982 | -0.38741 | 0.97593 | -0.46367 | 8.8955
68 | 0.014114 | 0.0035411 | -0.014103 | -0.0035345 | 1.1656e-05 | 6.6084e-06 | 0.021436 | 0.021437 | 0.021437 | 0.97982 | -0.38741 | 0.97894 | -0.40474 | 5.8892
69 | 0.018924 | 0.0047512 | -0.018924 | -0.0047511 | 6.7516e-08 | 4.0509e-08 | 0.028857 | 0.028857 | 0.028857 | 0.97593 | -0.46367 | 0.97592 | -0.46375 | 7.9278
70 | 0.0023104 | 0.00057885 | -0.0023103 | -0.00057902 | 8.5155e-08 | -1.7414e-07 | 0.0035227 | 0.0035227 | 0.0035227 | 0.97593 | -0.46367 | 0.97589 | -0.46445 | 0.96779
71 | 0.0088122 | 0.0022086 | -0.0088119 | -0.0022085 | 3.0012e-07 | 1.36e-07 | 0.013395 | 0.013395 | 0.013395 | 0.97894 | -0.40474 | 0.9789 | -0.40546 | 3.6799
72 | -0.00080468 | -0.00020151 | 0.00080468 | 0.0002015 | 6.0083e-10 | -1.3388e-08 | 0.0012163 | 0.0012163 | 0.0012163 | 0.98443 | -0.30028 | 0.98443 | -0.30027 | 0.33414
73 | 0.00048625 | 0.0001217 | -0.00048624 | -0.00012186 | 2.5685e-09 | -1.5957e-07 | 0.00073493 | 0.00073499 | 0.00073499 | 0.98443 | -0.30028 | 0.98442 | -0.30039 | 0.20192
74 | -0.00091489 | -0.00022912 | 0.00091492 | 0.00022857 | 3.2164e-08 | -5.4976e-07 | 0.0013828 | 0.0013826 | 0.0013828 | 0.98443 | -0.30027 | 0.98446 | -0.29953 | 0.3799
75 | 0.0026556 | 0.00066442 | -0.0026554 | -0.00066464 | 1.5353e-07 | -2.2487e-07 | 0.0040135 | 0.0040136 | 0.0040136 | 0.98446 | -0.29953 | 0.9844 | -0.30074 | 1.1027
76 | -0.0035705 | -0.00089299 | 0.0035752 | 0.00089052 | 4.691e-06 | -2.4698e-06 | 0.0053962 | 0.0053942 | 0.0053962 | 0.98446 | -0.29953 | 0.98588 | -0.27188 | 1.4825
77 | 0.0026554 | 0.00066464 | -0.002655 | -0.00066525 | 4.1583e-07 | -6.0876e-07 | 0.0040136 | 0.004014 | 0.004014 | 0.9844 | -0.30074 | 0.98423 | -0.30403 | 1.1027
78 | -0.0066265 | -0.0016526 | 0.0066486 | 0.0016592 | 2.2088e-05 | 6.5944e-06 | 0.0099988 | 0.0099961 | 0.0099988 | 0.98588 | -0.27188 | 0.98946 | -0.20178 | 2.7469
79 | 0.0030513 | 0.00076212 | -0.0030511 | -0.00076229 | 1.7835e-07 | -1.7187e-07 | 0.0046045 | 0.0046046 | 0.0046046 | 0.98588 | -0.27188 | 0.98581 | -0.27311 | 1.265
80 | -0.002389 | -0.00059871 | 0.0023891 | 0.0005986 | 5.4158e-08 | -1.0602e-07 | 0.003612 | 0.0036119 | 0.003612 | 0.98421 | -0.30451 | 0.98423 | -0.30403 | 0.9923
81 | 0.0020689 | 0.00051848 | -0.0020689 | -0.00051852 | 1.4426e-08 | -4.0731e-08 | 0.003128 | 0.003128 | 0.003128 | 0.98421 | -0.30451 | 0.9842 | -0.30465 | 0.85934
82 | -0.0021464 | -0.00053721 | 0.0021466 | 0.00053663 | 2.2452e-07 | -5.8285e-07 | 0.0032406 | 0.0032404 | 0.0032406 | 0.98549 | -0.2794 | 0.9856 | -0.2772 | 0.89029
83 | 0.00020879 | 5.1599e-05 | -0.00020878 | -5.2326e-05 | 2.1286e-09 | -7.2695e-07 | 0.00031499 | 0.00031525 | 0.00031525 | 0.98549 | -0.2794 | 0.98548 | -0.27961 | 0.086608
84 | -0.0021466 | -0.00053663 | 0.0021469 | 0.00053604 | 2.2719e-07 | -5.9008e-07 | 0.0032404 | 0.0032401 | 0.0032404 | 0.9856 | -0.2772 | 0.98572 | -0.27497 | 0.89022
85 | -0.0027604 | -0.00068982 | 0.0027607 | 0.0006895 | 2.441e-07 | -3.2185e-07 | 0.0041664 | 0.0041662 | 0.0041664 | 0.98572 | -0.27497 | 0.98581 | -0.27311 | 1.1446
86 | 0.00082207 | 0.00020556 | -0.00082205 | -0.00020603 | 2.1506e-08 | -4.6824e-07 | 0.0012361 | 0.0012363 | 0.0012363 | 0.98946 | -0.20178 | 0.98944 | -0.20233 | 0.33964
87 | -0.0074707 | -0.0018648 | 0.0074876 | 0.001871 | 1.6939e-05 | 6.2303e-06 | 0.011232 | 0.011231 | 0.011232 | 0.98946 | -0.20178 | 0.99191 | -0.15412 | 3.0858
88 | -0.0013053 | -0.00032713 | 0.0013053 | 0.00032668 | 5.8859e-08 | -4.495e-07 | 0.0019984 | 0.0019982 | 0.0019984 | 0.97193 | -0.54253 | 0.97198 | -0.54158 | 0.549
89 | -0.0045051 | -0.0011286 | 0.0045056 | 0.0011286 | 5.5643e-07 | -3.0599e-08 | 0.0068967 | 0.0068966 | 0.0068967 | 0.97198 | -0.54158 | 0.97211 | -0.53899 | 1.8947
90 | -0.0050666 | -0.0012692 | 0.0050687 | 0.0012694 | 2.0631e-06 | 1.8575e-07 | 0.0077553 | 0.0077549 | 0.0077553 | 0.97211 | -0.53899 | 0.97254 | -0.53044 | 2.1306
91 | -0.0065368 | -0.0016373 | 0.0065386 | 0.0016379 | 1.8231e-06 | 5.6346e-07 | 0.010001 | 0.010001 | 0.010001 | 0.97254 | -0.53044 | 0.97284 | -0.52458 | 2.7475
92 | 0.0084691 | 0.0021162 | -0.0084685 | -0.0021159 | 5.8754e-07 | 2.6006e-07 | 0.012952 | 0.012952 | 0.012952 | 0.97284 | -0.52458 | 0.97277 | -0.52604 | 3.5582
93 | -0.015008 | -0.003754 | 0.015008 | 0.0037544 | 6.6616e-07 | 3.8447e-07 | 0.022953 | 0.022953 | 0.022953 | 0.97284 | -0.52458 | 0.97289 | -0.52365 | 6.3056
94 | 0.0053756 | 0.0013422 | -0.0053755 | -0.0013422 | 6.3375e-08 | 9.5179e-09 | 0.0082211 | 0.0082211 | 0.0082211 | 0.97277 | -0.52604 | 0.97275 | -0.52629 | 2.2585
95 | 0.003093 | 0.00077369 | -0.0030928 | -0.00077382 | 1.5952e-07 | -1.3387e-07 | 0.0047307 | 0.0047308 | 0.0047308 | 0.97277 | -0.52604 | 0.97271 | -0.52713 | 1.2997
96 | -0.017217 | -0.0043072 | 0.017255 | 0.0043297 | 3.7899e-05 | 2.2441e-05 | 0.026331 | 0.02633 | 0.026331 | 0.97289 | -0.52365 | 0.97523 | -0.47748 | 7.2337
97 | 0.0022089 | 0.00055281 | -0.0022088 | -0.000553 | 8.2685e-08 | -1.8698e-07 | 0.0033782 | 0.0033783 | 0.0033783 | 0.97289 | -0.52365 | 0.97285 | -0.52444 | 0.9281
98 | 0.00039699 | 9.9339e-05 | -0.00039698 | -9.9494e-05 | 1.7417e-09 | -1.547e-07 | 0.00060775 | 0.00060781 | 0.00060781 | 0.97189 | -0.5434 | 0.97189 | -0.54349 | 0.16698
99 | -0.00059962 | -0.00015012 | 0.0005997 | 0.00014723 | 7.5007e-08 | -2.897e-06 | 0.000918 | 0.00091695 | 0.000918 | 0.97189 | -0.5434 | 0.97202 | -0.54075 | 0.2522
100 | 0.0044956 | 0.0011253 | -0.0044942 | -0.0011254 | 1.4184e-06 | -8.1877e-08 | 0.0068816 | 0.0068819 | 0.0068819 | 0.97202 | -0.54075 | 0.97169 | -0.54738 | 1.8906
101 | -0.0050953 | -0.0012725 | 0.0050988 | 0.0012729 | 3.5025e-06 | 3.3635e-07 | 0.0077985 | 0.0077978 | 0.0077985 | 0.97202 | -0.54075 | 0.97275 | -0.52629 | 2.1425
102 | 0.0036086 | 0.00090345 | -0.0036085 | -0.0009035 | 1.2947e-07 | -5.7193e-08 | 0.0055258 | 0.0055258 | 0.0055258 | 0.97169 | -0.54738 | 0.97165 | -0.54814 | 1.5181
103 | 0.0029858 | 0.00074744 | -0.0029857 | -0.00074755 | 1.1296e-07 | -1.0617e-07 | 0.0045722 | 0.0045723 | 0.0045723 | 0.97165 | -0.54814 | 0.97161 | -0.54893 | 1.2561
104 | 0.0026866 | 0.00067258 | -0.0026864 | -0.00067276 | 1.3486e-07 | -1.7681e-07 | 0.0041142 | 0.0041143 | 0.0041143 | 0.97161 | -0.54893 | 0.97156 | -0.54999 | 1.1303
105 | 0.0010914 | 0.000273 | -0.0010913 | -0.00027351 | 4.5697e-08 | -5.109e-07 | 0.0016713 | 0.0016715 | 0.0016715 | 0.97156 | -0.54999 | 0.97151 | -0.55087 | 0.45921
106 | -0.00038359 | -9.6136e-05 | 0.00038359 | 9.573e-05 | 4.2582e-09 | -4.0665e-07 | 0.00058683 | 0.00058668 | 0.00058683 | 0.97266 | -0.52809 | 0.97267 | -0.52786 | 0.16122
107 | -0.00054445 | -0.00013605 | 0.00054446 | 0.00013591 | 2.888e-09 | -1.36e-07 | 0.00083277 | 0.00083272 | 0.00083277 | 0.97267 | -0.52786 | 0.97268 | -0.52775 | 0.22878
108 | -0.00083234 | -0.00020806 | 0.00083234 | 0.00020805 | 4.5402e-10 | -8.9816e-09 | 0.0012731 | 0.0012731 | 0.0012731 | 0.97268 | -0.52775 | 0.97268 | -0.52773 | 0.34976
109 | -0.0011081 | -0.00027717 | 0.0011081 | 0.00027715 | 1.7483e-09 | -1.9022e-08 | 0.001695 | 0.001695 | 0.001695 | 0.97268 | -0.52773 | 0.97268 | -0.5277 | 0.46567
110 | -0.0010665 | -0.0002673 | 0.0010666 | 0.00026699 | 2.6402e-08 | -3.1139e-07 | 0.0016316 | 0.0016315 | 0.0016316 | 0.97266 | -0.52809 | 0.97269 | -0.52757 | 0.44825
111 | -0.0015369 | -0.00038487 | 0.0015369 | 0.00038469 | 3.2726e-08 | -1.7504e-07 | 0.002351 | 0.002351 | 0.002351 | 0.97269 | -0.52757 | 0.97271 | -0.52713 | 0.64589
112 | 0.0015559 | 0.00038913 | -0.0015558 | -0.00038935 | 4.2534e-08 | -2.2136e-07 | 0.0023798 | 0.0023799 | 0.0023799 | 0.97271 | -0.52713 | 0.97268 | -0.5277 | 0.65382
113 | 0.0017356 | 0.0004344 | -0.0017355 | -0.00043487 | 1.1663e-07 | -4.7332e-07 | 0.0026545 | 0.0026547 | 0.0026547 | 0.97285 | -0.52444 | 0.97278 | -0.52585 | 0.72931
114 | 0.0006699 | 0.00016781 | -0.0006699 | -0.00016789 | 2.6515e-09 | -8.1901e-08 | 0.0010247 | 0.0010247 | 0.0010247 | 0.97278 | -0.52585 | 0.97277 | -0.52593 | 0.28152
115 | -0.017552 | -0.0044042 | 0.017555 | 0.0044058 | 2.784e-06 | 1.6526e-06 | 0.026784 | 0.026783 | 0.026784 | 0.97523 | -0.47748 | 0.97539 | -0.47416 | 7.3581
116 | -0.018178 | -0.0045609 | 0.018187 | 0.0045663 | 9.0251e-06 | 5.3853e-06 | 0.027733 | 0.027733 | 0.027733 | 0.97539 | -0.47416 | 0.97592 | -0.46375 | 7.6189
117 | 0.00062245 | 0.0001551 | -0.00062243 | -0.00015584 | 2.0245e-08 | -7.3461e-07 | 0.00094925 | 0.00094952 | 0.00094952 | 0.97539 | -0.47416 | 0.97536 | -0.47484 | 0.26086
118 | 0.00021006 | 5.2488e-05 | -0.00021006 | -5.2646e-05 | 4.8918e-10 | -1.5824e-07 | 0.00032041 | 0.00032047 | 0.00032047 | 0.97536 | -0.47484 | 0.97536 | -0.47489 | 0.088042

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.10595 | 0.02676

## res_load
| p_mw | q_mvar
0 | 0.0010005 | 0.00025076
1 | 0.00026517 | 6.6458e-05
2 | 0.00018513 | 4.6399e-05
3 | 0.00065922 | 0.00016522
4 | 0.00074475 | 0.00018665
5 | 0.0001259 | 3.1553e-05
6 | 0.00033298 | 8.3454e-05
7 | 0.00036855 | 9.2367e-05
8 | 0.00025353 | 6.354e-05
9 | 0.00028704 | 7.1939e-05
10 | 0.00042411 | 0.00010629
11 | 0.00063588 | 0.00015937
12 | 0.0012801 | 0.00032083
13 | 0.00079174 | 0.00019843
14 | 0.00034985 | 8.768e-05
15 | 0.00037717 | 9.4527e-05
16 | 0.00058993 | 0.00014785
17 | 0.00025206 | 6.3171e-05
18 | 0.00056169 | 0.00014077
19 | 0.00037858 | 9.488e-05
20 | 0.00017837 | 4.4704e-05
21 | 0.00038384 | 9.6198e-05
22 | 0.00075995 | 0.00019046
23 | 0.00038462 | 9.6395e-05
24 | 0.0014847 | 0.00037211
25 | 0.00039542 | 9.9102e-05
26 | 0.00016248 | 4.0721e-05
27 | 0.0001388 | 3.4787e-05
28 | 0.00014441 | 3.6193e-05
29 | 0.00046144 | 0.00011565
30 | 0.00033933 | 8.5045e-05
31 | 0.00013159 | 3.298e-05
32 | 0.00016672 | 4.1783e-05
33 | 0.00062798 | 0.00015739
34 | 0.00036341 | 9.108e-05
35 | 0.00031957 | 8.0093e-05
36 | 0.00013873 | 3.4769e-05
37 | 0.00077794 | 0.00019497
38 | 0.00084465 | 0.00021169
39 | 0.0015053 | 0.00037726
40 | 0.014406 | 0.0036104
41 | 0.0014043 | 0.00035196
42 | 0.0066297 | 0.0016616
43 | 0.0032529 | 0.00081526
44 | 0.0055507 | 0.0013911
45 | 0.0055372 | 0.0013878
46 | 0.0027387 | 0.00068639
47 | 0.0052905 | 0.0013259
48 | 0.00067678 | 0.00016962
49 | 0.00031844 | 7.9808e-05
50 | 0.00011021 | 2.7621e-05
51 | 0.00048624 | 0.00012186
52 | 0.00032012 | 8.0228e-05
53 | 0.00026593 | 6.6649e-05
54 | 0.0020689 | 0.00051852
55 | 0.0019376 | 0.00048561
56 | 0.00020878 | 5.2326e-05
57 | 0.00061359 | 0.00015378
58 | 0.00029045 | 7.2793e-05
59 | 0.00082205 | 0.00020603
60 | 0.0013053 | 0.00032713
61 | 0.0031997 | 0.00080193
62 | 0.000561 | 0.0001406
63 | 0.0014681 | 0.00036793
64 | 0.00020264 | 5.0786e-05
65 | 0.00039698 | 9.9494e-05
66 | 0.00088559 | 0.00022195
67 | 0.00027669 | 6.9346e-05
68 | 0.00062269 | 0.00015606
69 | 0.00029913 | 7.4969e-05
70 | 0.001595 | 0.00039976
71 | 0.0010913 | 0.00027351
72 | 0.00038359 | 9.6136e-05
73 | 0.00016086 | 4.0316e-05
74 | 0.00028788 | 7.215e-05
75 | 0.00027579 | 6.9121e-05
76 | 0.0010665 | 0.0002673
77 | 0.00047035 | 0.00011788
78 | 0.00044768 | 0.0001122
79 | 0.00047321 | 0.0001186
80 | 0.0010656 | 0.00026706
81 | 0.0006699 | 0.00016789
82 | 0.00029716 | 7.4475e-05
83 | 0.00041237 | 0.00010335
84 | 0.00021006 | 5.2646e-05
85 | 0.00073749 | 0.00018483
86 | 0.0023103 | 0.00057902
87 | 0.0088119 | 0.0022085

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1