## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_153-5_1_4_node_192 | 0.4 | n |  | TRUE
1 | bus_LV_153-5_1_4_node_193 | 0.4 | n |  | TRUE
2 | bus_LV_153-5_1_4_node_194 | 0.4 | n |  | TRUE
3 | bus_LV_153-5_1_4_node_195 | 0.4 | n |  | TRUE
4 | bus_LV_153-5_1_4_node_196 | 0.4 | n |  | TRUE
5 | bus_LV_153-5_1_4_node_197 | 0.4 | n |  | TRUE
6 | bus_LV_153-5_1_4_node_198 | 0.4 | n |  | TRUE
7 | bus_LV_153-5_1_4_node_232 | 0.4 | n |  | TRUE
8 | bus_LV_153-5_1_4_node_248 | 0.4 | n |  | TRUE
9 | bus_LV_153-5_1_4_node_203 | 0.4 | n |  | TRUE
10 | bus_LV_153-5_1_4_node_204 | 0.4 | n |  | TRUE
11 | bus_LV_153-5_1_4_node_205 | 0.4 | n |  | TRUE
12 | bus_LV_153-5_1_4_node_206 | 0.4 | n |  | TRUE
13 | bus_LV_153-5_1_4_node_207 | 0.4 | n |  | TRUE
14 | bus_LV_153-5_1_4_node_303 | 0.4 | n |  | TRUE
15 | bus_LV_153-5_1_4_node_209 | 0.4 | n |  | TRUE
16 | bus_LV_153-5_1_4_node_309 | 0.4 | n |  | TRUE
17 | bus_LV_153-5_1_4_node_302 | 0.4 | n |  | TRUE
18 | bus_LV_153-5_1_4_node_285 | 0.4 | n |  | TRUE
19 | bus_LV_153-5_1_4_node_306 | 0.4 | n |  | TRUE
20 | bus_LV_153-5_1_4_node_211 | 0.4 | n |  | TRUE
21 | bus_LV_153-5_1_4_node_212 | 0.4 | n |  | TRUE
22 | bus_LV_153-5_1_4_node_213 | 0.4 | n |  | TRUE
23 | bus_LV_153-5_1_4_node_345 | 0.4 | n |  | TRUE
24 | bus_LV_153-5_1_4_node_217 | 0.4 | n |  | TRUE
25 | bus_LV_153-5_1_4_node_218 | 0.4 | n |  | TRUE
26 | bus_LV_153-5_1_4_node_219 | 0.4 | n |  | TRUE
27 | bus_LV_153-5_1_4_node_220 | 0.4 | n |  | TRUE
28 | bus_LV_153-5_1_4_node_221 | 0.4 | n |  | TRUE
29 | bus_LV_153-5_1_4_node_223 | 0.4 | n |  | TRUE
30 | bus_LV_153-5_1_4_node_224 | 0.4 | n |  | TRUE
31 | bus_LV_153-5_1_4_node_222 | 0.4 | n |  | TRUE
32 | bus_LV_153-5_1_4_node_239 | 0.4 | n |  | TRUE
33 | bus_LV_153-5_1_4_node_277 | 0.4 | n |  | TRUE
34 | bus_LV_153-5_1_4_node_234 | 0.4 | n |  | TRUE
35 | bus_LV_153-5_1_4_node_231 | 0.4 | n |  | TRUE
36 | bus_LV_153-5_1_4_node_225 | 0.4 | n |  | TRUE
37 | bus_LV_153-5_1_4_node_226 | 0.4 | n |  | TRUE
38 | bus_LV_153-5_1_4_node_227 | 0.4 | n |  | TRUE
39 | bus_LV_153-5_1_4_node_228 | 0.4 | n |  | TRUE
40 | bus_LV_153-5_1_4_node_229 | 0.4 | n |  | TRUE
41 | bus_LV_153-5_1_4_node_230 | 0.4 | n |  | TRUE
42 | bus_LV_153-5_1_4_node_233 | 0.4 | n |  | TRUE
43 | bus_LV_153-5_1_4_node_235 | 0.4 | n |  | TRUE
44 | bus_LV_153-5_1_4_node_243 | 0.4 | n |  | TRUE
45 | bus_LV_153-5_1_4_node_236 | 0.4 | n |  | TRUE
46 | bus_LV_153-5_1_4_node_237 | 0.4 | n |  | TRUE
47 | bus_LV_153-5_1_4_node_238 | 0.4 | n |  | TRUE
48 | bus_LV_153-5_1_4_node_240 | 0.4 | n |  | TRUE
49 | bus_LV_153-5_1_4_node_241 | 0.4 | n |  | TRUE
50 | bus_LV_153-5_1_4_node_242 | 0.4 | n |  | TRUE
51 | bus_LV_153-5_1_4_node_250 | 0.4 | n |  | TRUE
52 | bus_LV_153-5_1_4_node_244 | 0.4 | n |  | TRUE
53 | bus_LV_153-5_1_4_node_245 | 0.4 | n |  | TRUE
54 | bus_LV_153-5_1_4_node_246 | 0.4 | n |  | TRUE
55 | bus_LV_153-5_1_4_node_247 | 0.4 | n |  | TRUE
56 | bus_LV_153-5_1_4_node_249 | 0.4 | n |  | TRUE
57 | bus_LV_153-5_1_4_node_336 | 0.4 | n |  | TRUE
58 | bus_LV_153-5_1_4_node_318 | 0.4 | n |  | TRUE
59 | bus_LV_153-5_1_4_node_256 | 0.4 | n |  | TRUE
60 | bus_LV_153-5_1_4_node_257 | 0.4 | n |  | TRUE
61 | bus_LV_153-5_1_4_node_258 | 0.4 | n |  | TRUE
62 | bus_LV_153-5_1_4_node_259 | 0.4 | n |  | TRUE
63 | bus_LV_153-5_1_4_node_260 | 0.4 | n |  | TRUE
64 | bus_LV_153-5_1_4_node_272 | 0.4 | n |  | TRUE
65 | bus_LV_153-5_1_4_node_271 | 0.4 | n |  | TRUE
66 | bus_LV_153-5_1_4_node_261 | 0.4 | n |  | TRUE
67 | bus_LV_153-5_1_4_node_262 | 0.4 | n |  | TRUE
68 | bus_LV_153-5_1_4_node_263 | 0.4 | n |  | TRUE
69 | bus_LV_153-5_1_4_node_264 | 0.4 | n |  | TRUE
70 | bus_LV_153-5_1_4_node_265 | 0.4 | n |  | TRUE
71 | bus_LV_153-5_1_4_node_274 | 0.4 | n |  | TRUE
72 | bus_LV_153-5_1_4_node_266 | 0.4 | n |  | TRUE
73 | bus_LV_153-5_1_4_node_267 | 0.4 | n |  | TRUE
74 | bus_LV_153-5_1_4_node_268 | 0.4 | n |  | TRUE
75 | bus_LV_153-5_1_4_node_269 | 0.4 | n |  | TRUE
76 | bus_LV_153-5_1_4_node_270 | 0.4 | n |  | TRUE
77 | bus_LV_153-5_1_4_node_273 | 0.4 | n |  | TRUE
78 | bus_LV_153-5_1_4_node_289 | 0.4 | n |  | TRUE
79 | bus_LV_153-5_1_4_node_275 | 0.4 | n |  | TRUE
80 | bus_LV_153-5_1_4_node_293 | 0.4 | n |  | TRUE
81 | bus_LV_153-5_1_4_node_276 | 0.4 | n |  | TRUE
82 | bus_LV_153-5_1_4_node_278 | 0.4 | n |  | TRUE
83 | bus_LV_153-5_1_4_node_280 | 0.4 | n |  | TRUE
84 | bus_LV_153-5_1_4_node_281 | 0.4 | n |  | TRUE
85 | bus_LV_153-5_1_4_node_283 | 0.4 | n |  | TRUE
86 | bus_LV_153-5_1_4_node_284 | 0.4 | n |  | TRUE
87 | bus_LV_153-5_1_4_node_329 | 0.4 | n |  | TRUE
88 | bus_LV_153-5_1_4_node_326 | 0.4 | n |  | TRUE
89 | bus_LV_153-5_1_4_node_319 | 0.4 | n |  | TRUE
90 | bus_LV_153-5_1_4_node_286 | 0.4 | n |  | TRUE
91 | bus_LV_153-5_1_4_node_287 | 0.4 | n |  | TRUE
92 | bus_LV_153-5_1_4_node_288 | 0.4 | n |  | TRUE
93 | bus_LV_153-5_1_4_node_290 | 0.4 | n |  | TRUE
94 | bus_LV_153-5_1_4_node_291 | 0.4 | n |  | TRUE
95 | bus_LV_153-5_1_4_node_294 | 0.4 | n |  | TRUE
96 | bus_LV_153-5_1_4_node_292 | 0.4 | n |  | TRUE
97 | bus_LV_153-5_1_4_node_295 | 0.4 | n |  | TRUE
98 | bus_LV_153-5_1_4_node_296 | 0.4 | n |  | TRUE
99 | bus_LV_153-5_1_4_node_313 | 0.4 | n |  | TRUE
100 | bus_LV_153-5_1_4_node_297 | 0.4 | n |  | TRUE
101 | bus_LV_153-5_1_4_node_298 | 0.4 | n |  | TRUE
102 | bus_LV_153-5_1_4_node_299 | 0.4 | n |  | TRUE
103 | bus_LV_153-5_1_4_node_300 | 0.4 | n |  | TRUE
104 | bus_LV_153-5_1_4_node_301 | 0.4 | n |  | TRUE
105 | bus_LV_153-5_1_4_node_304 | 0.4 | n |  | TRUE
106 | bus_LV_153-5_1_4_node_317 | 0.4 | n |  | TRUE
107 | bus_LV_153-5_1_4_node_305 | 0.4 | n |  | TRUE
108 | bus_LV_153-5_1_4_node_307 | 0.4 | n |  | TRUE
109 | bus_LV_153-5_1_4_node_308 | 0.4 | n |  | TRUE
110 | bus_LV_153-5_1_4_node_310 | 0.4 | n |  | TRUE
111 | bus_LV_153-5_1_4_node_320 | 0.4 | n |  | TRUE
112 | bus_LV_153-5_1_4_node_321 | 0.4 | n |  | TRUE
113 | bus_LV_153-5_1_4_node_311 | 0.4 | n |  | TRUE
114 | bus_LV_153-5_1_4_node_312 | 0.4 | n |  | TRUE
115 | bus_LV_153-5_1_4_node_314 | 0.4 | n |  | TRUE
116 | bus_LV_153-5_1_4_node_315 | 0.4 | n |  | TRUE
117 | bus_LV_153-5_1_4_node_316 | 0.4 | n |  | TRUE
118 | bus_LV_153-5_1_4_node_322 | 0.4 | n |  | TRUE
119 | bus_LV_153-5_1_4_node_323 | 0.4 | n |  | TRUE
120 | bus_LV_153-5_1_4_node_325 | 0.4 | n |  | TRUE
121 | bus_LV_153-5_1_4_node_328 | 0.4 | n |  | TRUE
122 | bus_LV_153-5_1_4_node_324 | 0.4 | n |  | TRUE
123 | bus_LV_153-5_1_4_node_330 | 0.4 | n |  | TRUE
124 | bus_LV_153-5_1_4_node_327 | 0.4 | n |  | TRUE
125 | bus_LV_153-5_1_4_node_331 | 0.4 | n |  | TRUE
126 | bus_LV_153-5_1_4_node_333 | 0.4 | n |  | TRUE
127 | bus_LV_153-5_1_4_node_334 | 0.4 | n |  | TRUE
128 | bus_LV_153-5_1_4_node_335 | 0.4 | n |  | TRUE
129 | bus_LV_153-5_1_4_node_337 | 0.4 | n |  | TRUE
130 | bus_MV_355_1_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_153-5_1_4_load_192 | 0 | 0.00096347 | 0.00024147 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_153-5_1_4_load_193 | 1 | 0.0012342 | 0.00030931 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_153-5_1_4_load_194 | 2 | 0.0024805 | 0.00062168 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_153-5_1_4_load_195 | 3 | 0.0018157 | 0.00045505 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_153-5_1_4_load_196 | 4 | 0.0024072 | 0.0006033 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_153-5_1_4_load_197 | 5 | 0.0072882 | 0.0018266 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_153-5_1_4_load_198 | 6 | 0.0019138 | 0.00047965 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_153-5_1_4_load_248 | 8 | 0.0012402 | 0.00031081 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_153-5_1_4_load_203 | 9 | 0.0037714 | 0.00094521 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_153-5_1_4_load_204 | 10 | 0.0026091 | 0.00065391 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_153-5_1_4_load_205 | 11 | 0.0084855 | 0.0021267 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_153-5_1_4_load_207 | 13 | 0.0046296 | 0.0011603 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_153-5_1_4_load_303 | 14 | 0.0024251 | 0.00060778 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_153-5_1_4_load_309 | 16 | 0.00031864 | 7.9859e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_153-5_1_4_load_306 | 19 | 0.0003402 | 8.5263e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_153-5_1_4_load_211 | 20 | 0.00083189 | 0.00020849 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_153-5_1_4_load_212 | 21 | 0.001508 | 0.00037794 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_153-5_1_4_load_213 | 22 | 0.00093883 | 0.00023529 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_153-5_1_4_load_345 | 23 | 0.0026077 | 0.00065356 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_153-5_1_4_load_217 | 24 | 0.0011893 | 0.00029808 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_153-5_1_4_load_218 | 25 | 0.00061777 | 0.00015483 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_153-5_1_4_load_219 | 26 | 0.001359 | 0.0003406 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_153-5_1_4_load_221 | 28 | 0.0011711 | 0.0002935 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_153-5_1_4_load_224 | 30 | 0.0012149 | 0.00030448 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_153-5_1_4_load_239 | 32 | 0.0026763 | 0.00067075 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_153-5_1_4_load_277 | 33 | 0.0011015 | 0.00027605 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_153-5_1_4_load_234 | 34 | 0.014905 | 0.0037355 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_153-5_1_4_load_231 | 35 | 0.00096018 | 0.00024064 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_153-5_1_4_load_225 | 36 | 0.0015256 | 0.00038235 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_153-5_1_4_load_229 | 40 | 0.002842 | 0.00071226 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_153-5_1_4_load_230 | 41 | 0.0026219 | 0.00065711 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_153-5_1_4_load_233 | 42 | 0.0186 | 0.0046616 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_153-5_1_4_load_235 | 43 | 0.0066383 | 0.0016637 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_153-5_1_4_load_243 | 44 | 0.0050329 | 0.0012614 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_153-5_1_4_load_236 | 45 | 0.0013699 | 0.00034332 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_153-5_1_4_load_237 | 46 | 0.002622 | 0.00065715 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_153-5_1_4_load_238 | 47 | 0.0029391 | 0.00073662 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_153-5_1_4_load_241 | 49 | 0.0011082 | 0.00027775 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_153-5_1_4_load_242 | 50 | 0.0039418 | 0.00098792 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_153-5_1_4_load_250 | 51 | 0.0012128 | 0.00030395 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_153-5_1_4_load_244 | 52 | 0.01818 | 0.0045563 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_153-5_1_4_load_245 | 53 | 0.019428 | 0.004869 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_153-5_1_4_load_247 | 55 | 0.025199 | 0.0063155 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_153-5_1_4_load_249 | 56 | 0.010486 | 0.002628 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_153-5_1_4_load_318 | 58 | 0.0026651 | 0.00066795 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_153-5_1_4_load_256 | 59 | 0.00017162 | 4.3013e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_153-5_1_4_load_257 | 60 | 0.00033389 | 8.3682e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_153-5_1_4_load_259 | 62 | 0.00013902 | 3.4843e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_153-5_1_4_load_260 | 63 | 0.00016136 | 4.044e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_153-5_1_4_load_272 | 64 | 0.0010086 | 0.00025279 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_153-5_1_4_load_261 | 66 | 0.00023435 | 5.8735e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_153-5_1_4_load_262 | 67 | 0.00014813 | 3.7126e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_153-5_1_4_load_264 | 69 | 0.00018456 | 4.6254e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_153-5_1_4_load_265 | 70 | 0.00027041 | 6.777e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_153-5_1_4_load_274 | 71 | 0.00018848 | 4.7237e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_153-5_1_4_load_266 | 72 | 0.00019971 | 5.0051e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_153-5_1_4_load_267 | 73 | 0.00016617 | 4.1646e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_153-5_1_4_load_268 | 74 | 7.7621e-05 | 1.9454e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_153-5_1_4_load_269 | 75 | 0.00025321 | 6.346e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_153-5_1_4_load_273 | 77 | 0.00032982 | 8.266e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_153-5_1_4_load_289 | 78 | 0.00023117 | 5.7936e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_153-5_1_4_load_293 | 80 | 0.0014608 | 0.0003661 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_153-5_1_4_load_276 | 81 | 0.0021342 | 0.00053487 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_153-5_1_4_load_278 | 82 | 0.0023624 | 0.00059207 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_153-5_1_4_load_280 | 83 | 0.00028124 | 7.0484e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_153-5_1_4_load_281 | 84 | 0.00045363 | 0.00011369 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_153-5_1_4_load_283 | 85 | 0.00065289 | 0.00016363 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_153-5_1_4_load_329 | 87 | 0.0015778 | 0.00039545 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_153-5_1_4_load_326 | 88 | 0.00046629 | 0.00011686 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_153-5_1_4_load_319 | 89 | 0.00065376 | 0.00016385 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_153-5_1_4_load_286 | 90 | 0.00068927 | 0.00017275 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_153-5_1_4_load_287 | 91 | 0.0017407 | 0.00043627 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_153-5_1_4_load_288 | 92 | 0.0012201 | 0.0003058 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_153-5_1_4_load_290 | 93 | 0.00097296 | 0.00024385 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_153-5_1_4_load_291 | 94 | 0.0013263 | 0.00033241 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_153-5_1_4_load_295 | 97 | 0.00030136 | 7.5529e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_153-5_1_4_load_296 | 98 | 0.0014006 | 0.00035102 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_153-5_1_4_load_313 | 99 | 0.0051448 | 0.0012894 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_153-5_1_4_load_297 | 100 | 0.0020701 | 0.00051881 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_153-5_1_4_load_298 | 101 | 0.0027226 | 0.00068235 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_153-5_1_4_load_299 | 102 | 0.0015793 | 0.00039582 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_153-5_1_4_load_300 | 103 | 0.0021418 | 0.0005368 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_153-5_1_4_load_304 | 105 | 0.0013819 | 0.00034634 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_153-5_1_4_load_317 | 106 | 0.0028245 | 0.0007079 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_153-5_1_4_load_305 | 107 | 0.0003426 | 8.5865e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_153-5_1_4_load_307 | 108 | 0.0010017 | 0.00025104 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_153-5_1_4_load_308 | 109 | 0.0004852 | 0.0001216 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_153-5_1_4_load_310 | 110 | 0.0003753 | 9.4058e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_153-5_1_4_load_311 | 113 | 0.0057551 | 0.0014424 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_153-5_1_4_load_312 | 114 | 0.0012943 | 0.00032437 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_153-5_1_4_load_314 | 115 | 0.0018493 | 0.00046349 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_153-5_1_4_load_315 | 116 | 0.001034 | 0.00025914 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_153-5_1_4_load_316 | 117 | 0.0029394 | 0.00073667 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_153-5_1_4_load_322 | 118 | 0.00039058 | 9.7888e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_153-5_1_4_load_325 | 120 | 0.00084556 | 0.00021192 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_153-5_1_4_load_328 | 121 | 0.00044379 | 0.00011122 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_153-5_1_4_load_324 | 122 | 0.00023574 | 5.9082e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_153-5_1_4_load_330 | 123 | 0.0010983 | 0.00027526 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_153-5_1_4_load_327 | 124 | 0.00032648 | 8.1824e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_153-5_1_4_load_331 | 125 | 0.00049473 | 0.00012399 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_153-5_1_4_load_333 | 126 | 0.0024677 | 0.00061847 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_153-5_1_4_load_334 | 127 | 0.0018614 | 0.00046652 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_153-5_1_4_load_337 | 129 | 0.0046242 | 0.0011589 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_153-5_1_4_line_0 |  | 0 | 1 | 0.0038779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_153-5_1_4_line_1 |  | 0 | 2 | 0.013545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_153-5_1_4_line_2 |  | 1 | 3 | 0.002259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_153-5_1_4_line_3 |  | 2 | 4 | 0.034927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_153-5_1_4_line_4 |  | 3 | 5 | 0.027604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_153-5_1_4_line_5 |  | 4 | 6 | 0.0213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_153-5_1_4_line_6 |  | 5 | 7 | 0.018277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_153-5_1_4_line_7 |  | 6 | 8 | 0.03361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_153-5_1_4_line_8 |  | 7 | 42 | 0.01682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_153-5_1_4_line_9 |  | 7 | 29 | 0.067169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_153-5_1_4_line_10 |  | 8 | 50 | 0.019103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_153-5_1_4_line_11 |  | 9 | 10 | 0.12304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_153-5_1_4_line_12 |  | 9 | 11 | 0.00014223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_153-5_1_4_line_13 |  | 10 | 12 | 0.19053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_153-5_1_4_line_14 |  | 12 | 13 | 0.12825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_153-5_1_4_line_15 |  | 13 | 14 | 0.0020363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_153-5_1_4_line_16 |  | 14 | 104 | 0.016879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_153-5_1_4_line_17 |  | 15 | 16 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_153-5_1_4_line_18 |  | 15 | 17 | 0.057558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_153-5_1_4_line_19 |  | 15 | 18 | 0.053158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_153-5_1_4_line_20 |  | 15 | 19 | 0.022443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_153-5_1_4_line_21 |  | 16 | 111 | 0.12169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_153-5_1_4_line_22 |  | 17 | 103 | 0.059675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_153-5_1_4_line_23 |  | 18 | 89 | 0.047588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_153-5_1_4_line_24 |  | 18 | 85 | 0.018366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_153-5_1_4_line_25 |  | 19 | 107 | 0.020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_153-5_1_4_line_26 |  | 20 | 21 | 0.053395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_153-5_1_4_line_27 |  | 21 | 22 | 0.32622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_153-5_1_4_line_28 |  | 22 | 23 | 0.16846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_153-5_1_4_line_29 |  | 23 | 82 | 0.19559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_153-5_1_4_line_30 |  | 24 | 25 | 0.020484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_153-5_1_4_line_31 |  | 24 | 26 | 0.029902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_153-5_1_4_line_32 |  | 25 | 27 | 0.0087629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_153-5_1_4_line_33 |  | 26 | 28 | 0.020661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_153-5_1_4_line_34 |  | 27 | 29 | 0.34509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_153-5_1_4_line_35 |  | 28 | 30 | 0.024484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_153-5_1_4_line_36 |  | 29 | 34 | 0.058955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_153-5_1_4_line_37 |  | 30 | 35 | 0.0052665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_153-5_1_4_line_38 |  | 31 | 32 | 0.037992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_153-5_1_4_line_39 |  | 31 | 33 | 0.48748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_153-5_1_4_line_40 |  | 32 | 46 | 0.022196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_153-5_1_4_line_41 |  | 33 | 81 | 0.024997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_153-5_1_4_line_42 |  | 35 | 40 | 0.018841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_153-5_1_4_line_43 |  | 36 | 37 | 0.038322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_153-5_1_4_line_44 |  | 36 | 38 | 0.028764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_153-5_1_4_line_45 |  | 37 | 39 | 0.040164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_153-5_1_4_line_46 |  | 38 | 40 | 0.017283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_153-5_1_4_line_47 |  | 39 | 41 | 0.055145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_153-5_1_4_line_48 |  | 42 | 43 | 0.018554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_153-5_1_4_line_49 |  | 43 | 44 | 0.003837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_153-5_1_4_line_50 |  | 44 | 52 | 0.023199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_153-5_1_4_line_51 |  | 45 | 46 | 0.060885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_153-5_1_4_line_52 |  | 45 | 47 | 0.042737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_153-5_1_4_line_53 |  | 47 | 48 | 0.005146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_153-5_1_4_line_54 |  | 48 | 49 | 0.024669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_153-5_1_4_line_55 |  | 48 | 50 | 0.016464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_153-5_1_4_line_56 |  | 49 | 51 | 0.042111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_153-5_1_4_line_57 |  | 51 | 58 | 0.0024626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_153-5_1_4_line_58 |  | 52 | 53 | 0.024143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_153-5_1_4_line_59 |  | 53 | 54 | 0.037696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_153-5_1_4_line_60 |  | 54 | 55 | 0.020328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_153-5_1_4_line_61 |  | 55 | 56 | 0.0044731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_153-5_1_4_line_62 |  | 56 | 57 | 0.094306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_153-5_1_4_line_63 |  | 57 | 129 | 0.034401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_153-5_1_4_line_64 |  | 57 | 128 | 0.034362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_153-5_1_4_line_65 |  | 58 | 117 | 0.0080049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_153-5_1_4_line_66 |  | 59 | 60 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_153-5_1_4_line_67 |  | 60 | 61 | 0.018887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_153-5_1_4_line_68 |  | 61 | 62 | 0.016255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_153-5_1_4_line_69 |  | 61 | 63 | 0.017709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_153-5_1_4_line_70 |  | 62 | 64 | 0.078232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_153-5_1_4_line_71 |  | 63 | 65 | 0.030129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_153-5_1_4_line_72 |  | 64 | 78 | 0.00027406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_153-5_1_4_line_73 |  | 65 | 70 | 0.017254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_153-5_1_4_line_74 |  | 65 | 76 | 0.023497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_153-5_1_4_line_75 |  | 66 | 67 | 0.024756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_153-5_1_4_line_76 |  | 67 | 68 | 0.037043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_153-5_1_4_line_77 |  | 68 | 69 | 0.0087284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_153-5_1_4_line_78 |  | 68 | 70 | 0.020469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_153-5_1_4_line_79 |  | 69 | 71 | 0.01865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_153-5_1_4_line_80 |  | 72 | 73 | 0.0081326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_153-5_1_4_line_81 |  | 72 | 74 | 0.034839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_153-5_1_4_line_82 |  | 73 | 75 | 0.0039177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_153-5_1_4_line_83 |  | 75 | 76 | 0.039979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_153-5_1_4_line_84 |  | 76 | 77 | 0.051633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_153-5_1_4_line_85 |  | 77 | 79 | 0.081987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_153-5_1_4_line_86 |  | 78 | 91 | 0.0066713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_153-5_1_4_line_87 |  | 79 | 80 | 0.039649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_153-5_1_4_line_88 |  | 80 | 98 | 0.012492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_153-5_1_4_line_89 |  | 81 | 82 | 0.20226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_153-5_1_4_line_90 |  | 83 | 84 | 0.26456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_153-5_1_4_line_91 |  | 84 | 85 | 0.050131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_153-5_1_4_line_92 |  | 86 | 87 | 0.052733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_153-5_1_4_line_93 |  | 86 | 88 | 0.088428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_153-5_1_4_line_94 |  | 88 | 124 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_153-5_1_4_line_95 |  | 89 | 97 | 0.049177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_153-5_1_4_line_96 |  | 90 | 91 | 0.025599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_153-5_1_4_line_97 |  | 90 | 92 | 0.0054204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_153-5_1_4_line_98 |  | 92 | 93 | 0.065442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_153-5_1_4_line_99 |  | 93 | 94 | 0.087972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_153-5_1_4_line_100 |  | 94 | 95 | 0.018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_153-5_1_4_line_101 |  | 95 | 99 | 0.029101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_153-5_1_4_line_102 |  | 95 | 96 | 0.02701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_153-5_1_4_line_103 |  | 96 | 97 | 0.019109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_153-5_1_4_line_104 |  | 99 | 113 | 0.073929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_153-5_1_4_line_105 |  | 100 | 101 | 0.022919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_153-5_1_4_line_106 |  | 100 | 102 | 0.035725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_153-5_1_4_line_107 |  | 101 | 103 | 0.028239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_153-5_1_4_line_108 |  | 102 | 104 | 0.0054799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_153-5_1_4_line_109 |  | 104 | 105 | 0.0031172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_153-5_1_4_line_110 |  | 105 | 106 | 0.01432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_153-5_1_4_line_111 |  | 106 | 116 | 0.0065707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_153-5_1_4_line_112 |  | 107 | 108 | 0.0046747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_153-5_1_4_line_113 |  | 109 | 110 | 0.00049138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_153-5_1_4_line_114 |  | 110 | 112 | 0.013286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_153-5_1_4_line_115 |  | 111 | 118 | 0.058647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_153-5_1_4_line_116 |  | 111 | 119 | 0.070417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_153-5_1_4_line_117 |  | 112 | 120 | 0.079873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_153-5_1_4_line_118 |  | 112 | 121 | 0.010781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_153-5_1_4_line_119 |  | 113 | 114 | 0.070286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_153-5_1_4_line_120 |  | 115 | 116 | 0.060428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_153-5_1_4_line_121 |  | 115 | 117 | 0.022743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_153-5_1_4_line_122 |  | 118 | 122 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_153-5_1_4_line_123 |  | 119 | 120 | 0.062205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_153-5_1_4_line_124 |  | 121 | 124 | 0.0023913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_153-5_1_4_line_125 |  | 122 | 123 | 0.010341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_153-5_1_4_line_126 |  | 123 | 125 | 0.0072877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_153-5_1_4_line_127 |  | 126 | 127 | 0.034934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_153-5_1_4_line_128 |  | 126 | 128 | 0.034495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_153-5_1_4_trafo_198 | 0.63 MVA 20/0.4 kV | 130 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2700883.5643 | 1233297.4894 | 2700880.1309 | 1233295.6869
1 | 2700867.6991 | 1233290.3249 | 2700878.3987 | 1233294.7774 | 2700880.1309 | 1233295.6869
2 | 2700885.5644 | 1233298.5395 | 2700883.5643 | 1233297.4894
3 | 2700867.6991 | 1233290.3249 | 2700864.5258 | 1233289.0044 | 2700845.5897 | 1233282.178 | 2700834.7589 | 1233278.7473
4 | 2700910.0045 | 1233311.3705 | 2700885.5644 | 1233298.5395
5 | 2700814.0768 | 1233273.7299 | 2700819.3285 | 1233274.6158 | 2700834.7589 | 1233278.7473 | 2700834.7589 | 1233278.7473
6 | 2700924.8465 | 1233322.0084 | 2700918.7272 | 1233317.1565 | 2700910.0488 | 1233311.3937 | 2700910.0045 | 1233311.3705
7 | 2700814.0768 | 1233273.7299 | 2700798.3677 | 1233271.0799 | 2700780.8169 | 1233268.955
8 | 2700924.8465 | 1233322.0084 | 2700926.6974 | 1233323.5966 | 2700937.1991 | 1233333.46
9 | 2700924.8465 | 1233322.0084 | 2700926.8244 | 1233318.7952 | 2700935.8843 | 1233298.9898 | 2700941.6486 | 1233287.746 | 2700945.6071 | 1233278.4952 | 2700952.3219 | 1233260.7849
10 | 2700761.7483 | 1233268.4976 | 2700776.1506 | 1233268.3901 | 2700780.8169 | 1233268.955
11 | 2700728.9514 | 1233357.2896 | 2700819.804 | 1233366.6035 | 2700850.5897 | 1233374.2218
12 | 2700850.7278 | 1233374.256 | 2700850.5897 | 1233374.2218
13 | 2700625.4905 | 1233475.8255 | 2700631.403 | 1233458.0234 | 2700654.5791 | 1233415.2506 | 2700655.5974 | 1233404.7601 | 2700645.1573 | 1233389.0049 | 2700647.6479 | 1233380.1071 | 2700728.9514 | 1233357.2896 | 2700728.9514 | 1233357.2896
14 | 2700625.4905 | 1233475.8255 | 2700623.0839 | 1233456.5259 | 2700580.5003 | 1233358.043 | 2700580.1648 | 1233356.5715
15 | 2700580.1648 | 1233356.5715 | 2700579.7123 | 1233354.5862
16 | 2700575.9609 | 1233338.1291 | 2700579.7123 | 1233354.5862
17 | 2700400.9772 | 1233450.8214 | 2700399.9887 | 1233453.7513 | 2700399.6264 | 1233469.5607
18 | 2700448.1724 | 1233420.474 | 2700430.859 | 1233430.5333 | 2700421.8496 | 1233434.9288 | 2700410.1171 | 1233439.6008 | 2700406.6418 | 1233441.8215 | 2700404.5383 | 1233443.5206 | 2700403.2354 | 1233445.3443 | 2700402.314 | 1233447.4415 | 2700400.9772 | 1233450.8214
19 | 2700400.9772 | 1233450.8214 | 2700389.7518 | 1233448.3411 | 2700378.2706 | 1233444.8668 | 2700372.2254 | 1233442.3406 | 2700365.818 | 1233439.2857 | 2700359.4981 | 1233435.5317 | 2700354.0778 | 1233431.8708 | 2700352.3068 | 1233430.4732
20 | 2700400.9772 | 1233450.8214 | 2700381.482 | 1233461.9403
21 | 2700397.2637 | 1233591.2187 | 2700397.0442 | 1233582.2528 | 2700399.6264 | 1233469.5607
22 | 2700448.1724 | 1233420.474 | 2700498.5333 | 1233388.4597
23 | 2700352.3068 | 1233430.4732 | 2700345.533 | 1233424.4544 | 2700340.5669 | 1233418.9998 | 2700336.4605 | 1233413.76 | 2700332.519 | 1233407.7223 | 2700328.8692 | 1233401.4449 | 2700324.4246 | 1233392.4632
24 | 2700352.3068 | 1233430.4732 | 2700344.8383 | 1233438.2307 | 2700337.8638 | 1233441.2439
25 | 2700363.0121 | 1233466.9365 | 2700368.564 | 1233468.1202 | 2700372.7642 | 1233466.9124 | 2700381.482 | 1233461.9403
26 | 2701100.8135 | 1232623.9219 | 2701110.9958 | 1232631.5799 | 2701148.6214 | 1232646.9777
27 | 2700816.6189 | 1232466.9357 | 2700835.2133 | 1232473.5226 | 2700866.3261 | 1232485.0368 | 2700905.7656 | 1232503.909 | 2700977.3844 | 1232541.4641 | 2701034.6503 | 1232574.1614 | 2701100.8135 | 1232623.9219
28 | 2700816.6189 | 1232466.9357 | 2700648.6562 | 1232454.0023
29 | 2700648.6562 | 1232454.0023 | 2700642.1105 | 1232649.4811
30 | 2701164.8919 | 1233266.9293 | 2701147.7094 | 1233255.7779
31 | 2701164.8919 | 1233266.9293 | 2701189.9748 | 1233283.208
32 | 2701140.3589 | 1233251.0075 | 2701147.7094 | 1233255.7779
33 | 2701207.8383 | 1233293.3452 | 2701203.2787 | 1233291.8422 | 2701189.9748 | 1233283.208
34 | 2701140.3589 | 1233251.0075 | 2701077.3433 | 1233209.9605 | 2701058.9111 | 1233196.2147 | 2701047.0358 | 1233179.845 | 2701036.5119 | 1233157.4828 | 2701025.0721 | 1233140.876 | 2701011.7573 | 1233127.2062 | 2701003.1403 | 1233122.7231 | 2700995.8479 | 1233122.2767 | 2700992.5833 | 1233127.6696 | 2700990.1646 | 1233135.868 | 2700985.2633 | 1233156.4667 | 2700983.6449 | 1233161.2428 | 2700981.3213 | 1233165.6288 | 2700980.5826 | 1233171.2204 | 2700975.5071 | 1233192.7169 | 2700969.9932 | 1233211.048 | 2700965.7933 | 1233222.0182 | 2700952.3219 | 1233260.7849
35 | 2701207.8383 | 1233293.3452 | 2701231.0917 | 1233301.0105
36 | 2700952.3219 | 1233260.7849 | 2700961.3944 | 1233274.1045 | 2700973.5672 | 1233297.9179 | 2700976.8945 | 1233306.6476 | 2700978.7951 | 1233313.1277
37 | 2701231.0917 | 1233301.0105 | 2701236.0935 | 1233302.6593
38 | 2700885.4474 | 1233182.4912 | 2700872.8997 | 1233188.2937 | 2700850.6892 | 1233197.8215
39 | 2700854.4902 | 1232695.9964 | 2700885.4474 | 1233182.4912
40 | 2700830.2501 | 1233206.4737 | 2700833.2799 | 1233205.2897 | 2700850.6892 | 1233197.8215
41 | 2700833.386 | 1232682.5992 | 2700854.4902 | 1232695.9964
42 | 2701253.9872 | 1233308.5578 | 2701236.0935 | 1233302.6593
43 | 2701285.5482 | 1233358.6822 | 2701272.2661 | 1233354.7085 | 2701256.5667 | 1233346.8352 | 2701259.2418 | 1233340.48
44 | 2701270.4013 | 1233313.9686 | 2701259.2418 | 1233340.48
45 | 2701285.5482 | 1233358.6822 | 2701282.123 | 1233391.693 | 2701281.9587 | 1233398.662
46 | 2701270.4013 | 1233313.9686 | 2701253.9872 | 1233308.5578
47 | 2701238.342 | 1233372.4995 | 2701238.5745 | 1233376.6287 | 2701243.1627 | 1233385.5469 | 2701262.3459 | 1233393.8243 | 2701281.9587 | 1233398.662
48 | 2700937.1991 | 1233333.46 | 2700945.5791 | 1233343.4098 | 2700948.1864 | 1233348.3038
49 | 2700948.1864 | 1233348.3038 | 2700949.9905 | 1233351.6903
50 | 2700958.6102 | 1233373.1378 | 2700958.5778 | 1233372.9859 | 2700957.0006 | 1233366.8768 | 2700951.7065 | 1233354.9113 | 2700949.9905 | 1233351.6903
51 | 2700775.5829 | 1233232.7859 | 2700777.1946 | 1233231.4024 | 2700784.1881 | 1233227.1401 | 2700793.7288 | 1233221.8201 | 2700803.6112 | 1233216.884 | 2700830.2501 | 1233206.4737
52 | 2700775.5829 | 1233232.7859 | 2700765.9525 | 1233241.0524 | 2700753.7894 | 1233254.5562 | 2700748.1083 | 1233263.1441 | 2700747.4543 | 1233264.576
53 | 2700745.3164 | 1233269.2569 | 2700747.4543 | 1233264.576
54 | 2700745.3164 | 1233269.2569 | 2700733.9248 | 1233273.8895 | 2700721.7957 | 1233276.3245
55 | 2700745.3164 | 1233269.2569 | 2700752.9384 | 1233268.5634 | 2700761.7483 | 1233268.4976
56 | 2700721.7957 | 1233276.3245 | 2700717.5811 | 1233277.1706 | 2700697.5827 | 1233280.7344 | 2700689.8562 | 1233282.6827 | 2700680.7804 | 1233285.593
57 | 2700678.4354 | 1233286.3449 | 2700680.7804 | 1233285.593
58 | 2700958.6102 | 1233373.1378 | 2700963.2912 | 1233395.0491 | 2700963.6597 | 1233396.747
59 | 2700973.404 | 1233433.127 | 2700971.9146 | 1233426.7525 | 2700968.8738 | 1233417.6608 | 2700965.8754 | 1233406.9574 | 2700963.6597 | 1233396.747
60 | 2700973.404 | 1233433.127 | 2700973.9243 | 1233435.9268 | 2700974.5526 | 1233440.8412 | 2700975.1923 | 1233452.205 | 2700975.2469 | 1233453.3477
61 | 2700975.2469 | 1233453.3477 | 2700975.4604 | 1233457.8157
62 | 2700984.1319 | 1233551.6977 | 2700976.3819 | 1233477.0993 | 2700975.4604 | 1233457.8157
63 | 2701017.8296 | 1233544.4427 | 2700991.137 | 1233550.7494 | 2700984.1319 | 1233551.6977
64 | 2700984.1319 | 1233551.6977 | 2700988.2845 | 1233585.8048
65 | 2700678.4354 | 1233286.3449 | 2700676.7149 | 1233286.8966 | 2700670.9645 | 1233289.2094
66 | 2700027.1071 | 1233125.3619 | 2700031.9802 | 1233137.067 | 2700032.1332 | 1233137.7014
67 | 2700035.4356 | 1233156.2616 | 2700034.3797 | 1233147.0148 | 2700032.1332 | 1233137.7014
68 | 2700035.4356 | 1233156.2616 | 2700042.0983 | 1233156.7741 | 2700050.7612 | 1233160.8465
69 | 2700035.4356 | 1233156.2616 | 2700034.2734 | 1233164.5704 | 2700032.3198 | 1233173.6828
70 | 2700050.7612 | 1233160.8465 | 2700055.6892 | 1233163.1632 | 2700072.3688 | 1233177.6992 | 2700110.8159 | 1233210.6903
71 | 2700027.592 | 1233203.3868 | 2700028.1217 | 1233195.7679 | 2700029.2686 | 1233187.9147 | 2700032.3198 | 1233173.6828
72 | 2700111.0239 | 1233210.8687 | 2700110.8159 | 1233210.6903
73 | 2700027.592 | 1233203.3868 | 2700017.678 | 1233203.042 | 2700014.1371 | 1233202.4153 | 2700010.8738 | 1233200.5923
74 | 2700033.0568 | 1233226.0178 | 2700030.5259 | 1233219.8262 | 2700028.2133 | 1233212.3595 | 2700027.592 | 1233203.3868
75 | 2699935.556 | 1233186.2371 | 2699945.989 | 1233187.3578 | 2699960.2462 | 1233186.9476
76 | 2699997.2354 | 1233185.3293 | 2699990.5743 | 1233186.0734 | 2699987.4377 | 1233186.1651 | 2699973.5432 | 1233186.5651 | 2699960.2462 | 1233186.9476
77 | 2699997.2354 | 1233185.3293 | 2699990.0994 | 1233180.3031
78 | 2699997.2354 | 1233185.3293 | 2700010.8738 | 1233200.5923
79 | 2699990.0994 | 1233180.3031 | 2699974.8516 | 1233169.5633
80 | 2700001.9315 | 1233262.4462 | 2699999.7872 | 1233254.6015 | 2699999.7872 | 1233254.6015
81 | 2700001.9315 | 1233262.4462 | 2700005.9643 | 1233277.1999 | 2700005.7299 | 1233281.2323 | 2700003.1483 | 1233284.3468 | 2699994.93 | 1233292.3337
82 | 2699999.7872 | 1233254.6015 | 2700002.6871 | 1233251.9672
83 | 2700033.0568 | 1233226.0178 | 2700021.6959 | 1233234.6997 | 2700002.6871 | 1233251.9672
84 | 2700033.0568 | 1233226.0178 | 2700053.1768 | 1233251.1751 | 2700065.7648 | 1233261.3501 | 2700068.5771 | 1233262.9456
85 | 2700145.7641 | 1233289.7852 | 2700093.2262 | 1233273.6883 | 2700083.3841 | 1233270.8761 | 2700075.9657 | 1233267.1373 | 2700068.5771 | 1233262.9456
86 | 2700111.0239 | 1233210.8687 | 2700116.0868 | 1233215.2131
87 | 2700145.7641 | 1233289.7852 | 2700132.7927 | 1233327.2525
88 | 2700128.7061 | 1233339.0567 | 2700132.7927 | 1233327.2525
89 | 2700833.386 | 1232682.5992 | 2700815.664 | 1232671.3492 | 2700779.7757 | 1232652.1153 | 2700734.6842 | 1232639.6751 | 2700699.2113 | 1232637.9061 | 2700642.1105 | 1232649.4811
90 | 2700037.4111 | 1233363.2384 | 2700048.2796 | 1233361.6414 | 2700061.075 | 1233362.6353 | 2700210.8801 | 1233420.2796 | 2700223.0345 | 1233424.2542 | 2700243.4693 | 1233429.3248 | 2700289.1198 | 1233437.5326
91 | 2700337.8638 | 1233441.2439 | 2700329.6057 | 1233444.8118 | 2700289.1198 | 1233437.5326
92 | 2700167.0283 | 1233525.4409 | 2700173.4217 | 1233520.3448 | 2700179.0603 | 1233511.0663 | 2700197.9248 | 1233483.0857
93 | 2700167.0283 | 1233525.4409 | 2700172.8305 | 1233535.6463 | 2700177.814 | 1233542.313 | 2700185.6853 | 1233550.1515 | 2700194.4563 | 1233557.6271 | 2700201.5595 | 1233562.0724 | 2700215.578 | 1233565.9449 | 2700232.1751 | 1233566.4251 | 2700238.2047 | 1233564.9616
94 | 2700238.2047 | 1233564.9616 | 2700254.6781 | 1233560.9631
95 | 2700304.5573 | 1233347.5195 | 2700305.5926 | 1233348.9686 | 2700324.4246 | 1233392.4632 | 2700324.4246 | 1233392.4632
96 | 2700138.8658 | 1233225.8443 | 2700122.4777 | 1233220.6971 | 2700116.0868 | 1233215.2131
97 | 2700138.8658 | 1233225.8443 | 2700144.0372 | 1233227.4686
98 | 2700144.0372 | 1233227.4686 | 2700206.472 | 1233247.0781
99 | 2700277.0886 | 1233292.7198 | 2700272.1828 | 1233283.1004 | 2700265.9983 | 1233274.4563 | 2700262.0631 | 1233269.8309 | 2700256.8383 | 1233265.7842 | 2700248.0718 | 1233261.1663 | 2700238.4173 | 1233257.1115 | 2700206.472 | 1233247.0781
100 | 2700284.3197 | 1233309.2023 | 2700277.3136 | 1233293.1611 | 2700277.0886 | 1233292.7198
101 | 2700284.3197 | 1233309.2023 | 2700293.0056 | 1233306.0354 | 2700308.5106 | 1233302.6278 | 2700312.316 | 1233301.4605
102 | 2700290.6803 | 1233334.7731 | 2700291.7531 | 1233329.0869 | 2700284.3197 | 1233309.2023
103 | 2700290.6803 | 1233334.7731 | 2700296.1363 | 1233338.1232 | 2700300.6068 | 1233341.9904 | 2700304.5573 | 1233347.5195
104 | 2700374.0032 | 1233292.7945 | 2700372.1731 | 1233293.0843 | 2700362.7726 | 1233292.8253 | 2700356.6123 | 1233287.2394 | 2700347.8479 | 1233280.7088 | 2700339.3746 | 1233282.0445 | 2700333.3805 | 1233284.1004 | 2700328.617 | 1233286.8221 | 2700322.4472 | 1233297.0366 | 2700315.932 | 1233300.3514 | 2700312.316 | 1233301.4605
105 | 2700541.706 | 1233361.0148 | 2700522.3642 | 1233373.3104
106 | 2700541.706 | 1233361.0148 | 2700555.0525 | 1233352.5305 | 2700563.2469 | 1233347.0873 | 2700571.4813 | 1233341.2854
107 | 2700498.5333 | 1233388.4597 | 2700522.3642 | 1233373.3104
108 | 2700575.9609 | 1233338.1291 | 2700571.4813 | 1233341.2854
109 | 2700575.9609 | 1233338.1291 | 2700578.5276 | 1233336.3601
110 | 2700590.3181 | 1233328.2338 | 2700578.5276 | 1233336.3601
111 | 2700590.3181 | 1233328.2338 | 2700590.5105 | 1233328.1012 | 2700595.9482 | 1233324.847
112 | 2700363.0121 | 1233466.9365 | 2700358.4401 | 1233465.9618
113 | 2700270.3897 | 1233549.8907 | 2700270.693 | 1233549.5041
114 | 2700267.4149 | 1233562.8391 | 2700270.3897 | 1233549.8907
115 | 2700397.2637 | 1233591.2187 | 2700402.7299 | 1233590.8107 | 2700411.0053 | 1233588.6156 | 2700416.857 | 1233587.8027 | 2700422.3265 | 1233588.0953 | 2700428.4974 | 1233589.4562 | 2700435.7487 | 1233591.8471 | 2700447.9057 | 1233596.5338 | 2700453.8566 | 1233598.3953
116 | 2700369.9978 | 1233656.151 | 2700395.0535 | 1233597.4416 | 2700397.2637 | 1233591.2187
117 | 2700267.4149 | 1233562.8391 | 2700273.341 | 1233567.0422 | 2700283.4412 | 1233577.398 | 2700293.0364 | 1233584.0315 | 2700324.1056 | 1233599.1783 | 2700333.2378 | 1233606.827
118 | 2700267.4149 | 1233562.8391 | 2700263.3473 | 1233561.1358 | 2700257.0087 | 1233560.4973
119 | 2700374.0032 | 1233292.7945 | 2700389.879 | 1233290.2812 | 2700394.8706 | 1233298.2603 | 2700406.7714 | 1233314.1064 | 2700421.2468 | 1233332.1867 | 2700422.3113 | 1233333.6659
120 | 2700649.8642 | 1233297.6957 | 2700648.7796 | 1233298.1319 | 2700639.3439 | 1233302.1863 | 2700623.9795 | 1233309.3537 | 2700614.2701 | 1233314.3709 | 2700599.5449 | 1233322.6945 | 2700595.9482 | 1233324.847
121 | 2700649.8642 | 1233297.6957 | 2700670.9645 | 1233289.2094
122 | 2700465.7543 | 1233602.1168 | 2700453.8566 | 1233598.3953
123 | 2700369.9978 | 1233656.151 | 2700364.8485 | 1233653.0395 | 2700345.2732 | 1233620.8962 | 2700335.1483 | 1233608.4271 | 2700333.2378 | 1233606.827
124 | 2700254.6781 | 1233560.9631 | 2700256.7179 | 1233560.468 | 2700257.0087 | 1233560.4973
125 | 2700465.7543 | 1233602.1168 | 2700475.624 | 1233605.204
126 | 2700475.624 | 1233605.204 | 2700482.5794 | 1233607.3796
127 | 2700953.8688 | 1233583.7479 | 2700943.5379 | 1233583.3651 | 2700918.9442 | 1233583.0357
128 | 2700988.2845 | 1233585.8048 | 2700976.8032 | 1233584.5978 | 2700953.8688 | 1233583.7479

## bus_geodata
| x | y | coords
0 | 2700880.1309 | 1233295.6869
1 | 2700883.5643 | 1233297.4894
2 | 2700867.6991 | 1233290.3249
3 | 2700885.5644 | 1233298.5395
4 | 2700834.7589 | 1233278.7473
5 | 2700910.0045 | 1233311.3705
6 | 2700814.0768 | 1233273.7299
7 | 2700924.8465 | 1233322.0084
8 | 2700780.8169 | 1233268.955
9 | 2700850.5897 | 1233374.2218
10 | 2700728.9514 | 1233357.2896
11 | 2700850.7278 | 1233374.256
12 | 2700625.4905 | 1233475.8255
13 | 2700580.1648 | 1233356.5715
14 | 2700579.7123 | 1233354.5862
15 | 2700400.9772 | 1233450.8214
16 | 2700399.6264 | 1233469.5607
17 | 2700448.1724 | 1233420.474
18 | 2700352.3068 | 1233430.4732
19 | 2700381.482 | 1233461.9403
20 | 2701148.6214 | 1232646.9777
21 | 2701100.8135 | 1232623.9219
22 | 2700816.6189 | 1232466.9357
23 | 2700648.6562 | 1232454.0023
24 | 2701164.8919 | 1233266.9293
25 | 2701147.7094 | 1233255.7779
26 | 2701189.9748 | 1233283.208
27 | 2701140.3589 | 1233251.0075
28 | 2701207.8383 | 1233293.3452
29 | 2700952.3219 | 1233260.7849
30 | 2701231.0917 | 1233301.0105
31 | 2700885.4474 | 1233182.4912
32 | 2700850.6892 | 1233197.8215
33 | 2700854.4902 | 1232695.9964
34 | 2700978.7951 | 1233313.1277
35 | 2701236.0935 | 1233302.6593
36 | 2701259.2418 | 1233340.48
37 | 2701285.5482 | 1233358.6822
38 | 2701270.4013 | 1233313.9686
39 | 2701281.9587 | 1233398.662
40 | 2701253.9872 | 1233308.5578
41 | 2701238.342 | 1233372.4995
42 | 2700937.1991 | 1233333.46
43 | 2700948.1864 | 1233348.3038
44 | 2700949.9905 | 1233351.6903
45 | 2700775.5829 | 1233232.7859
46 | 2700830.2501 | 1233206.4737
47 | 2700747.4543 | 1233264.576
48 | 2700745.3164 | 1233269.2569
49 | 2700721.7957 | 1233276.3245
50 | 2700761.7483 | 1233268.4976
51 | 2700680.7804 | 1233285.593
52 | 2700958.6102 | 1233373.1378
53 | 2700963.6597 | 1233396.747
54 | 2700973.404 | 1233433.127
55 | 2700975.2469 | 1233453.3477
56 | 2700975.4604 | 1233457.8157
57 | 2700984.1319 | 1233551.6977
58 | 2700678.4354 | 1233286.3449
59 | 2700027.1071 | 1233125.3619
60 | 2700032.1332 | 1233137.7014
61 | 2700035.4356 | 1233156.2616
62 | 2700050.7612 | 1233160.8465
63 | 2700032.3198 | 1233173.6828
64 | 2700110.8159 | 1233210.6903
65 | 2700027.592 | 1233203.3868
66 | 2699935.556 | 1233186.2371
67 | 2699960.2462 | 1233186.9476
68 | 2699997.2354 | 1233185.3293
69 | 2699990.0994 | 1233180.3031
70 | 2700010.8738 | 1233200.5923
71 | 2699974.8516 | 1233169.5633
72 | 2700001.9315 | 1233262.4462
73 | 2699999.7872 | 1233254.6015
74 | 2699994.93 | 1233292.3337
75 | 2700002.6871 | 1233251.9672
76 | 2700033.0568 | 1233226.0178
77 | 2700068.5771 | 1233262.9456
78 | 2700111.0239 | 1233210.8687
79 | 2700145.7641 | 1233289.7852
80 | 2700132.7927 | 1233327.2525
81 | 2700833.386 | 1232682.5992
82 | 2700642.1105 | 1232649.4811
83 | 2700037.4111 | 1233363.2384
84 | 2700289.1198 | 1233437.5326
85 | 2700337.8638 | 1233441.2439
86 | 2700167.0283 | 1233525.4409
87 | 2700197.9248 | 1233483.0857
88 | 2700238.2047 | 1233564.9616
89 | 2700324.4246 | 1233392.4632
90 | 2700138.8658 | 1233225.8443
91 | 2700116.0868 | 1233215.2131
92 | 2700144.0372 | 1233227.4686
93 | 2700206.472 | 1233247.0781
94 | 2700277.0886 | 1233292.7198
95 | 2700284.3197 | 1233309.2023
96 | 2700290.6803 | 1233334.7731
97 | 2700304.5573 | 1233347.5195
98 | 2700128.7061 | 1233339.0567
99 | 2700312.316 | 1233301.4605
100 | 2700541.706 | 1233361.0148
101 | 2700522.3642 | 1233373.3104
102 | 2700571.4813 | 1233341.2854
103 | 2700498.5333 | 1233388.4597
104 | 2700575.9609 | 1233338.1291
105 | 2700578.5276 | 1233336.3601
106 | 2700590.3181 | 1233328.2338
107 | 2700363.0121 | 1233466.9365
108 | 2700358.4401 | 1233465.9618
109 | 2700270.693 | 1233549.5041
110 | 2700270.3897 | 1233549.8907
111 | 2700397.2637 | 1233591.2187
112 | 2700267.4149 | 1233562.8391
113 | 2700374.0032 | 1233292.7945
114 | 2700422.3113 | 1233333.6659
115 | 2700649.8642 | 1233297.6957
116 | 2700595.9482 | 1233324.847
117 | 2700670.9645 | 1233289.2094
118 | 2700453.8566 | 1233598.3953
119 | 2700369.9978 | 1233656.151
120 | 2700333.2378 | 1233606.827
121 | 2700257.0087 | 1233560.4973
122 | 2700465.7543 | 1233602.1168
123 | 2700475.624 | 1233605.204
124 | 2700254.6781 | 1233560.9631
125 | 2700482.5794 | 1233607.3796
126 | 2700953.8688 | 1233583.7479
127 | 2700918.9442 | 1233583.0357
128 | 2700988.2845 | 1233585.8048
129 | 2701017.8296 | 1233544.4427
130 | 2700745.3164 | 1233269.2569

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99502 | -0.09472 | 0.00096347 | 0.00024147
1 | 0.99475 | -0.099886 | 0.0012342 | 0.00030931
2 | 0.99597 | -0.076583 | 0.0024805 | 0.00062168
3 | 0.9946 | -0.10287 | 0.0018157 | 0.00045505
4 | 0.99846 | -0.029217 | 0.0024072 | 0.0006033
5 | 0.99272 | -0.13899 | 0.0072882 | 0.0018266
6 | 1 | 0 | -0.27035 | -0.068696
7 | 0.99153 | -0.1618 | 0 | 0
8 | 0.99833 | -0.031707 | 0.0012402 | 0.00031081
9 | 0.98008 | -0.38298 | 0.0037714 | 0.00094521
10 | 0.98148 | -0.35565 | 0.0026091 | 0.00065391
11 | 0.98008 | -0.383 | 0.0084855 | 0.0021267
12 | 0.9841 | -0.30451 | 0 | 0
13 | 0.98586 | -0.27023 | 0.0046296 | 0.0011603
14 | 0.9859 | -0.26952 | 0.0024251 | 0.00060778
15 | 0.97875 | -0.40854 | 0 | 0
16 | 0.97862 | -0.41097 | 0.00031864 | 7.9859e-05
17 | 0.98069 | -0.37064 | 0 | 0
18 | 0.97739 | -0.43516 | 0 | 0
19 | 0.97871 | -0.40922 | 0.0003402 | 8.5263e-05
20 | 0.98495 | -0.2906 | 0.00083189 | 0.00020849
21 | 0.98499 | -0.2898 | 0.001508 | 0.00037794
22 | 0.98569 | -0.27605 | 0.00093883 | 0.00023529
23 | 0.9862 | -0.2661 | 0.0026077 | 0.00065356
24 | 0.98513 | -0.28594 | 0.0011893 | 0.00029808
25 | 0.98538 | -0.2812 | 0.00061777 | 0.00015483
26 | 0.98481 | -0.29223 | 0.001359 | 0.0003406
27 | 0.98549 | -0.27907 | 0 | 0
28 | 0.98461 | -0.29607 | 0.0011711 | 0.0002935
29 | 0.98978 | -0.19572 | 0 | 0
30 | 0.98441 | -0.30011 | 0.0012149 | 0.00030448
31 | 0.99417 | -0.11131 | 0 | 0
32 | 0.99457 | -0.10358 | 0.0026763 | 0.00067075
33 | 0.98903 | -0.21089 | 0.0011015 | 0.00027605
34 | 0.98897 | -0.21137 | 0.014905 | 0.0037355
35 | 0.98437 | -0.30086 | 0.00096018 | 0.00024064
36 | 0.98407 | -0.30667 | 0.0015256 | 0.00038235
37 | 0.98398 | -0.30848 | 0 | 0
38 | 0.98418 | -0.30452 | 0 | 0
39 | 0.98388 | -0.31038 | 0 | 0
40 | 0.98425 | -0.30323 | 0.002842 | 0.00071226
41 | 0.98375 | -0.31298 | 0.0026219 | 0.00065711
42 | 0.98979 | -0.19542 | 0.0186 | 0.0046616
43 | 0.98818 | -0.22647 | 0.0066383 | 0.0016637
44 | 0.98787 | -0.23245 | 0.0050329 | 0.0012614
45 | 0.99579 | -0.079994 | 0.0013699 | 0.00034332
46 | 0.99486 | -0.098026 | 0.002622 | 0.00065715
47 | 0.9965 | -0.066328 | 0.0029391 | 0.00073662
48 | 0.9966 | -0.064418 | 0 | 0
49 | 0.99567 | -0.082127 | 0.0011082 | 0.00027775
50 | 0.99738 | -0.049568 | 0.0039418 | 0.00098792
51 | 0.9941 | -0.11202 | 0.0012128 | 0.00030395
52 | 0.98611 | -0.26659 | 0.01818 | 0.0045563
53 | 0.98469 | -0.29436 | 0.019428 | 0.004869
54 | 0.98313 | -0.32466 | 0 | 0
55 | 0.9823 | -0.34104 | 0.025199 | 0.0063155
56 | 0.98221 | -0.34262 | 0.010486 | 0.002628
57 | 0.98143 | -0.35789 | 0 | 0
58 | 0.99392 | -0.11547 | 0.0026651 | 0.00066795
59 | 0.97136 | -0.55405 | 0.00017162 | 4.3013e-05
60 | 0.97136 | -0.55401 | 0.00033389 | 8.3682e-05
61 | 0.97137 | -0.55383 | 0 | 0
62 | 0.97146 | -0.55215 | 0.00013902 | 3.4843e-05
63 | 0.97129 | -0.55549 | 0.00016136 | 4.044e-05
64 | 0.97187 | -0.54386 | 0.0010086 | 0.00025279
65 | 0.97115 | -0.55824 | 0 | 0
66 | 0.9711 | -0.55922 | 0.00023435 | 5.8735e-05
67 | 0.9711 | -0.55912 | 0.00014813 | 3.7126e-05
68 | 0.97112 | -0.55885 | 0 | 0
69 | 0.97112 | -0.55891 | 0.00018456 | 4.6254e-05
70 | 0.97113 | -0.55857 | 0.00027041 | 6.777e-05
71 | 0.97111 | -0.55898 | 0.00018848 | 4.7237e-05
72 | 0.97103 | -0.56052 | 0.00019971 | 5.0051e-05
73 | 0.97104 | -0.56048 | 0.00016617 | 4.1646e-05
74 | 0.97103 | -0.56057 | 7.7621e-05 | 1.9454e-05
75 | 0.97104 | -0.56045 | 0.00025321 | 6.346e-05
76 | 0.97106 | -0.55993 | 0 | 0
77 | 0.97091 | -0.56298 | 0.00032982 | 8.266e-05
78 | 0.97188 | -0.54383 | 0.00023117 | 5.7936e-05
79 | 0.97069 | -0.56732 | 0 | 0
80 | 0.97058 | -0.56942 | 0.0014608 | 0.0003661
81 | 0.98879 | -0.21553 | 0.0021342 | 0.00053487
82 | 0.98725 | -0.24542 | 0.0023624 | 0.00059207
83 | 0.97726 | -0.43769 | 0.00028124 | 7.0484e-05
84 | 0.97733 | -0.43631 | 0.00045363 | 0.00011369
85 | 0.97737 | -0.43563 | 0.00065289 | 0.00016363
86 | 0.97684 | -0.44612 | 0 | 0
87 | 0.97676 | -0.44764 | 0.0015778 | 0.00039545
88 | 0.97697 | -0.44357 | 0.00046629 | 0.00011686
89 | 0.97623 | -0.45785 | 0.00065376 | 0.00016385
90 | 0.97213 | -0.53885 | 0.00068927 | 0.00017275
91 | 0.97192 | -0.54297 | 0.0017407 | 0.00043627
92 | 0.97217 | -0.53791 | 0.0012201 | 0.0003058
93 | 0.97282 | -0.52509 | 0.00097296 | 0.00024385
94 | 0.97377 | -0.5063 | 0.0013263 | 0.00033241
95 | 0.97399 | -0.50203 | 0 | 0
96 | 0.97462 | -0.48956 | 0 | 0
97 | 0.97507 | -0.48075 | 0.00030136 | 7.5529e-05
98 | 0.97057 | -0.56975 | 0.0014006 | 0.00035102
99 | 0.97366 | -0.50855 | 0.0051448 | 0.0012894
100 | 0.98458 | -0.29499 | 0.0020701 | 0.00051881
101 | 0.98371 | -0.31195 | 0.0027226 | 0.00068235
102 | 0.98601 | -0.26728 | 0.0015793 | 0.00039582
103 | 0.9827 | -0.3315 | 0.0021418 | 0.0005368
104 | 0.98624 | -0.26288 | 0 | 0
105 | 0.98643 | -0.25915 | 0.0013819 | 0.00034634
106 | 0.98734 | -0.2417 | 0.0028245 | 0.0007079
107 | 0.97869 | -0.40972 | 0.0003426 | 8.5865e-05
108 | 0.97868 | -0.4098 | 0.0010017 | 0.00025104
109 | 0.97702 | -0.44249 | 0.0004852 | 0.0001216
110 | 0.97703 | -0.44248 | 0.0003753 | 9.4058e-05
111 | 0.97786 | -0.42595 | 0 | 0
112 | 0.97704 | -0.44228 | 0 | 0
113 | 0.97317 | -0.51814 | 0.0057551 | 0.0014424
114 | 0.97309 | -0.51982 | 0.0012943 | 0.00032437
115 | 0.9918 | -0.15601 | 0.0018493 | 0.00046349
116 | 0.98777 | -0.23337 | 0.001034 | 0.00025914
117 | 0.99335 | -0.12632 | 0.0029394 | 0.00073667
118 | 0.97774 | -0.42832 | 0.00039058 | 9.7888e-05
119 | 0.97757 | -0.43177 | 0 | 0
120 | 0.97731 | -0.43691 | 0.00084556 | 0.00021192
121 | 0.97701 | -0.44283 | 0.00044379 | 0.00011122
122 | 0.97772 | -0.42874 | 0.00023574 | 5.9082e-05
123 | 0.97771 | -0.42904 | 0.0010983 | 0.00027526
124 | 0.977 | -0.44293 | 0.00032648 | 8.1824e-05
125 | 0.9777 | -0.4291 | 0.00049473 | 0.00012399
126 | 0.98116 | -0.36329 | 0.0024677 | 0.00061847
127 | 0.9811 | -0.36447 | 0.0018614 | 0.00046652
128 | 0.9813 | -0.36059 | 0 | 0
129 | 0.98129 | -0.36077 | 0.0046242 | 0.0011589
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.15254 | 0.03871 | -0.1525 | -0.038686 | 3.7892e-05 | 2.415e-05 | 0.22828 | 0.22828 | 0.22828 | 0.99502 | -0.09472 | 0.99475 | -0.099886 | 31.3577
1 | -0.1535 | -0.038952 | 0.15364 | 0.039037 | 0.00013403 | 8.5429e-05 | 0.22973 | 0.22972 | 0.22973 | 0.99502 | -0.09472 | 0.99597 | -0.076583 | 31.5556
2 | 0.15127 | 0.038377 | -0.15124 | -0.038363 | 2.1718e-05 | 1.3841e-05 | 0.22644 | 0.22644 | 0.22644 | 0.99475 | -0.099886 | 0.9946 | -0.10287 | 31.1041
3 | -0.15612 | -0.039659 | 0.15647 | 0.039886 | 0.00035685 | 0.00022747 | 0.23343 | 0.23343 | 0.23343 | 0.99597 | -0.076583 | 0.99846 | -0.029217 | 32.0647
4 | 0.14943 | 0.037908 | -0.14917 | -0.037743 | 0.00025905 | 0.00016508 | 0.22372 | 0.22372 | 0.22372 | 0.9946 | -0.10287 | 0.99272 | -0.13899 | 30.731
5 | -0.15888 | -0.04049 | 0.1591 | 0.040633 | 0.00022436 | 0.00014303 | 0.23702 | 0.23702 | 0.23702 | 0.99846 | -0.029217 | 1 | 0 | 32.5574
6 | 0.14188 | 0.035916 | -0.14173 | -0.035817 | 0.00015518 | 9.8843e-05 | 0.2128 | 0.2128 | 0.2128 | 0.99272 | -0.13899 | 0.99153 | -0.1618 | 29.2304
7 | 0.1096 | 0.028063 | -0.10943 | -0.027956 | 0.00016804 | 0.00010667 | 0.1633 | 0.1633 | 0.1633 | 1 | 0 | 0.99833 | -0.031707 | 22.4308
8 | 0.11319 | 0.028628 | -0.11301 | -0.028511 | 0.00018221 | 0.0001164 | 0.16997 | 0.16997 | 0.16997 | 0.99153 | -0.1618 | 0.98979 | -0.19542 | 46.6938
9 | 0.028532 | 0.0071896 | -0.028486 | -0.0071608 | 4.6211e-05 | 2.871e-05 | 0.042832 | 0.042833 | 0.042833 | 0.99153 | -0.1618 | 0.98978 | -0.19572 | 11.7672
10 | 0.10819 | 0.027646 | -0.1081 | -0.027586 | 9.3362e-05 | 5.9253e-05 | 0.16145 | 0.16145 | 0.16145 | 0.99833 | -0.031707 | 0.99738 | -0.049568 | 22.177
11 | -0.012257 | -0.0030719 | 0.012273 | 0.0030806 | 1.5978e-05 | 8.6733e-06 | 0.018609 | 0.018609 | 0.018609 | 0.98008 | -0.38298 | 0.98148 | -0.35565 | 5.1124
12 | 0.0084855 | 0.0021267 | -0.0084855 | -0.0021267 | 8.8524e-09 | 3.8732e-09 | 0.012883 | 0.012883 | 0.012883 | 0.98008 | -0.38298 | 0.98008 | -0.383 | 3.5393
13 | -0.014882 | -0.0037345 | 0.014918 | 0.0037553 | 3.6377e-05 | 2.0867e-05 | 0.022564 | 0.022563 | 0.022564 | 0.98148 | -0.35565 | 0.9841 | -0.30451 | 6.199
14 | -0.014918 | -0.0037553 | 0.014943 | 0.0037694 | 2.4485e-05 | 1.4038e-05 | 0.022563 | 0.022563 | 0.022563 | 0.9841 | -0.30451 | 0.98586 | -0.27023 | 6.1987
15 | -0.019573 | -0.0049297 | 0.019573 | 0.0049301 | 6.6681e-07 | 4.0079e-07 | 0.029551 | 0.029551 | 0.029551 | 0.98586 | -0.27023 | 0.9859 | -0.26952 | 8.1183
16 | -0.021998 | -0.0055378 | 0.022005 | 0.0055421 | 6.9813e-06 | 4.2527e-06 | 0.033211 | 0.033211 | 0.033211 | 0.9859 | -0.26952 | 0.98624 | -0.26288 | 9.1238
17 | 0.0070681 | 0.0017674 | -0.0070673 | -0.0017671 | 8.1845e-07 | 2.8624e-07 | 0.010744 | 0.010745 | 0.010745 | 0.97875 | -0.40854 | 0.97862 | -0.41097 | 2.9518
18 | -0.03635 | -0.0091457 | 0.036416 | 0.0091872 | 6.5951e-05 | 4.1484e-05 | 0.055277 | 0.055276 | 0.055277 | 0.97875 | -0.40854 | 0.98069 | -0.37064 | 15.1859
19 | 0.027597 | 0.0069567 | -0.027562 | -0.0069349 | 3.5116e-05 | 2.1807e-05 | 0.041971 | 0.041972 | 0.041972 | 0.97875 | -0.40854 | 0.97739 | -0.43516 | 11.5307
20 | 0.0016846 | 0.00042163 | -0.0016845 | -0.00042188 | 5.5196e-08 | -2.4672e-07 | 0.0025609 | 0.002561 | 0.002561 | 0.97875 | -0.40854 | 0.97871 | -0.40922 | 0.70356
21 | 0.0067487 | 0.0016872 | -0.0067439 | -0.0016857 | 4.804e-06 | 1.5468e-06 | 0.01026 | 0.010261 | 0.010261 | 0.97862 | -0.41097 | 0.97786 | -0.42595 | 2.8188
22 | -0.036416 | -0.0091872 | 0.036484 | 0.0092302 | 6.8376e-05 | 4.3006e-05 | 0.055276 | 0.055276 | 0.055276 | 0.98069 | -0.37064 | 0.9827 | -0.3315 | 15.1858
23 | 0.026174 | 0.0065913 | -0.026146 | -0.0065737 | 2.8354e-05 | 1.7551e-05 | 0.03986 | 0.039861 | 0.039861 | 0.97739 | -0.43516 | 0.97623 | -0.45785 | 10.9507
24 | 0.0013878 | 0.00034368 | -0.0013878 | -0.00034389 | 3.0705e-08 | -2.1052e-07 | 0.0021114 | 0.0021115 | 0.0021115 | 0.97739 | -0.43516 | 0.97737 | -0.43563 | 0.58008
25 | 0.0013443 | 0.00033662 | -0.0013443 | -0.00033685 | 3.1458e-08 | -2.3224e-07 | 0.0020437 | 0.0020438 | 0.0020438 | 0.97871 | -0.40922 | 0.97869 | -0.40972 | 0.56149
26 | -0.00083189 | -0.00020849 | 0.00083193 | 0.00020783 | 3.1621e-08 | -6.5936e-07 | 0.0012568 | 0.0012565 | 0.0012568 | 0.98495 | -0.2906 | 0.98499 | -0.2898 | 0.34527
27 | -0.0023399 | -0.00058577 | 0.0023415 | 0.0005826 | 1.5278e-06 | -3.1774e-06 | 0.0035347 | 0.0035332 | 0.0035347 | 0.98499 | -0.2898 | 0.98569 | -0.27605 | 0.97107
28 | -0.0032803 | -0.00081789 | 0.0032818 | 0.00081673 | 1.5479e-06 | -1.1577e-06 | 0.0049505 | 0.0049497 | 0.0049505 | 0.98569 | -0.27605 | 0.9862 | -0.2661 | 1.36
29 | -0.0058896 | -0.0014703 | 0.0058954 | 0.0014715 | 5.7888e-06 | 1.2065e-06 | 0.0088844 | 0.0088835 | 0.0088844 | 0.9862 | -0.2661 | 0.98725 | -0.24542 | 2.4408
30 | -0.012894 | -0.0032317 | 0.012897 | 0.0032333 | 2.9136e-06 | 1.6038e-06 | 0.019476 | 0.019475 | 0.019476 | 0.98513 | -0.28594 | 0.98538 | -0.2812 | 5.3504
31 | 0.011704 | 0.0029336 | -0.011701 | -0.0029317 | 3.5048e-06 | 1.8625e-06 | 0.017679 | 0.017679 | 0.017679 | 0.98513 | -0.28594 | 0.98481 | -0.29223 | 4.8569
32 | -0.013514 | -0.0033881 | 0.013516 | 0.0033889 | 1.3686e-06 | 7.643e-07 | 0.020408 | 0.020408 | 0.020408 | 0.98538 | -0.2812 | 0.98549 | -0.27907 | 5.6067
33 | 0.010342 | 0.0025911 | -0.01034 | -0.0025902 | 1.8918e-06 | 9.4791e-07 | 0.015626 | 0.015626 | 0.015626 | 0.98481 | -0.29223 | 0.98461 | -0.29607 | 4.2928
34 | -0.013516 | -0.0033889 | 0.01357 | 0.003419 | 5.3895e-05 | 3.0077e-05 | 0.020408 | 0.020407 | 0.020408 | 0.98549 | -0.27907 | 0.98978 | -0.19572 | 5.6067
35 | 0.0091688 | 0.0022967 | -0.009167 | -0.0022959 | 1.7628e-06 | 8.1684e-07 | 0.013856 | 0.013856 | 0.013856 | 0.98461 | -0.29607 | 0.98441 | -0.30011 | 3.8066
36 | 0.014916 | 0.0037419 | -0.014905 | -0.0037355 | 1.1119e-05 | 6.3589e-06 | 0.022426 | 0.022426 | 0.022426 | 0.98978 | -0.19572 | 0.98897 | -0.21137 | 6.161
37 | 0.0079522 | 0.0019914 | -0.0079519 | -0.0019913 | 2.8533e-07 | 1.1566e-07 | 0.01202 | 0.01202 | 0.01202 | 0.98441 | -0.30011 | 0.98437 | -0.30086 | 3.3021
38 | -0.011562 | -0.0029093 | 0.011566 | 0.0029116 | 4.2688e-06 | 2.2392e-06 | 0.01731 | 0.01731 | 0.01731 | 0.99417 | -0.11131 | 0.99457 | -0.10358 | 4.7554
39 | 0.011562 | 0.0029093 | -0.011507 | -0.0028806 | 5.4781e-05 | 2.8771e-05 | 0.01731 | 0.017312 | 0.017312 | 0.99417 | -0.11131 | 0.98903 | -0.21089 | 4.756
40 | -0.014243 | -0.0035823 | 0.014247 | 0.0035845 | 3.7812e-06 | 2.1319e-06 | 0.021314 | 0.021314 | 0.021314 | 0.99457 | -0.10358 | 0.99486 | -0.098026 | 5.8554
41 | 0.010406 | 0.0026045 | -0.010404 | -0.0026034 | 2.2973e-06 | 1.1496e-06 | 0.015655 | 0.015655 | 0.015655 | 0.98903 | -0.21089 | 0.98879 | -0.21553 | 4.3008
42 | 0.0069917 | 0.0017506 | -0.0069909 | -0.0017504 | 7.8914e-07 | 2.6556e-07 | 0.010568 | 0.010568 | 0.010568 | 0.98437 | -0.30086 | 0.98425 | -0.30323 | 2.9034
43 | 0.0026227 | 0.00065592 | -0.0026225 | -0.00065626 | 2.2597e-07 | -3.4221e-07 | 0.0039653 | 0.0039654 | 0.0039654 | 0.98407 | -0.30667 | 0.98398 | -0.30848 | 1.0894
44 | -0.0041483 | -0.0010383 | 0.0041487 | 0.0010382 | 4.2433e-07 | -9.3911e-08 | 0.0062721 | 0.006272 | 0.0062721 | 0.98407 | -0.30667 | 0.98418 | -0.30452 | 1.7231
45 | 0.0026225 | 0.00065626 | -0.0026222 | -0.00065662 | 2.3685e-07 | -3.5854e-07 | 0.0039654 | 0.0039656 | 0.0039656 | 0.98398 | -0.30848 | 0.98388 | -0.31038 | 1.0895
46 | -0.0041487 | -0.0010382 | 0.004149 | 0.0010381 | 2.5495e-07 | -5.647e-08 | 0.006272 | 0.0062719 | 0.006272 | 0.98418 | -0.30452 | 0.98425 | -0.30323 | 1.7231
47 | 0.0026222 | 0.00065662 | -0.0026219 | -0.00065711 | 3.2523e-07 | -4.9209e-07 | 0.0039656 | 0.0039659 | 0.0039659 | 0.98388 | -0.31038 | 0.98375 | -0.31298 | 1.0895
48 | 0.094412 | 0.02385 | -0.094272 | -0.02376 | 0.0001403 | 8.9554e-05 | 0.142 | 0.142 | 0.142 | 0.98979 | -0.19542 | 0.98818 | -0.22647 | 39.0119
49 | 0.087633 | 0.022097 | -0.087608 | -0.022081 | 2.5074e-05 | 1.5998e-05 | 0.13201 | 0.13201 | 0.13201 | 0.98818 | -0.22647 | 0.98787 | -0.23245 | 36.2657
50 | 0.082575 | 0.020819 | -0.082441 | -0.020733 | 0.00013468 | 8.5902e-05 | 0.12443 | 0.12443 | 0.12443 | 0.98787 | -0.23245 | 0.98611 | -0.26659 | 34.183
51 | 0.016883 | 0.0042501 | -0.016869 | -0.0042416 | 1.454e-05 | 8.5142e-06 | 0.025235 | 0.025235 | 0.025235 | 0.99579 | -0.079994 | 0.99486 | -0.098026 | 6.9328
52 | -0.018253 | -0.0045935 | 0.018265 | 0.0046005 | 1.1929e-05 | 7.0779e-06 | 0.027282 | 0.027282 | 0.027282 | 0.99579 | -0.079994 | 0.9965 | -0.066328 | 7.4951
53 | -0.021204 | -0.0053371 | 0.021206 | 0.0053383 | 1.9356e-06 | 1.1717e-06 | 0.031671 | 0.031671 | 0.031671 | 0.9965 | -0.066328 | 0.9966 | -0.064418 | 8.7008
54 | 0.082875 | 0.021213 | -0.082804 | -0.021168 | 7.1002e-05 | 4.4799e-05 | 0.1239 | 0.1239 | 0.1239 | 0.9966 | -0.064418 | 0.99567 | -0.082127 | 17.0188
55 | -0.10408 | -0.026551 | 0.10416 | 0.026599 | 7.4707e-05 | 4.7383e-05 | 0.15557 | 0.15557 | 0.15557 | 0.9966 | -0.064418 | 0.99738 | -0.049568 | 21.3692
56 | 0.081696 | 0.02089 | -0.081578 | -0.020816 | 0.00011799 | 7.4418e-05 | 0.12224 | 0.12224 | 0.12224 | 0.99567 | -0.082127 | 0.9941 | -0.11202 | 16.7914
57 | 0.080365 | 0.020512 | -0.080352 | -0.020503 | 1.3393e-05 | 8.5395e-06 | 0.12043 | 0.12043 | 0.12043 | 0.9941 | -0.11202 | 0.99392 | -0.11547 | 33.0841
58 | 0.064261 | 0.016177 | -0.064176 | -0.016123 | 8.5174e-05 | 5.4204e-05 | 0.096993 | 0.096993 | 0.096993 | 0.98611 | -0.26659 | 0.98469 | -0.29436 | 26.6465
59 | 0.044748 | 0.011254 | -0.044683 | -0.011213 | 6.4666e-05 | 4.0907e-05 | 0.067635 | 0.067635 | 0.067635 | 0.98469 | -0.29436 | 0.98313 | -0.32466 | 18.5811
60 | 0.044683 | 0.011213 | -0.044648 | -0.011191 | 3.4871e-05 | 2.206e-05 | 0.067635 | 0.067635 | 0.067635 | 0.98313 | -0.32466 | 0.9823 | -0.34104 | 18.5811
61 | 0.019449 | 0.0048752 | -0.019448 | -0.0048744 | 1.4561e-06 | 8.7526e-07 | 0.029463 | 0.029463 | 0.029463 | 0.9823 | -0.34104 | 0.98221 | -0.34262 | 8.0941
62 | 0.0089618 | 0.0022464 | -0.0089553 | -0.0022434 | 6.519e-06 | 2.9795e-06 | 0.013577 | 0.013577 | 0.013577 | 0.98221 | -0.34262 | 0.98143 | -0.35789 | 3.73
63 | 0.0046249 | 0.0011589 | -0.0046242 | -0.0011589 | 6.343e-07 | -2.8695e-08 | 0.007012 | 0.0070122 | 0.0070122 | 0.98143 | -0.35789 | 0.98129 | -0.36077 | 1.9264
64 | 0.0043304 | 0.0010845 | -0.0043298 | -0.0010845 | 5.5542e-07 | -7.869e-08 | 0.0065653 | 0.0065654 | 0.0065654 | 0.98143 | -0.35789 | 0.9813 | -0.36059 | 1.8037
65 | 0.077686 | 0.019835 | -0.077646 | -0.019809 | 4.0697e-05 | 2.5942e-05 | 0.11644 | 0.11644 | 0.11644 | 0.99392 | -0.11547 | 0.99335 | -0.12632 | 31.9879
66 | -0.00017162 | -4.3013e-05 | 0.00017162 | 4.2848e-05 | 3.4549e-10 | -1.648e-07 | 0.00026291 | 0.00026285 | 0.00026291 | 0.97136 | -0.55405 | 0.97136 | -0.55401 | 0.072228
67 | -0.00050552 | -0.00012653 | 0.00050552 | 0.0001263 | 4.2464e-09 | -2.3108e-07 | 0.00077434 | 0.00077425 | 0.00077434 | 0.97136 | -0.55401 | 0.97137 | -0.55383 | 0.21273
68 | -0.0055835 | -0.0013942 | 0.0055839 | 0.0013943 | 4.4573e-07 | 8.4036e-08 | 0.0085513 | 0.0085512 | 0.0085513 | 0.97137 | -0.55383 | 0.97146 | -0.55215 | 2.3493
69 | 0.005078 | 0.0012679 | -0.0050775 | -0.0012679 | 4.0167e-07 | 3.7866e-08 | 0.0077771 | 0.0077771 | 0.0077771 | 0.97137 | -0.55383 | 0.97129 | -0.55549 | 2.1366
70 | -0.0057229 | -0.0014291 | 0.0057252 | 0.0014296 | 2.2533e-06 | 4.7311e-07 | 0.0087642 | 0.0087638 | 0.0087642 | 0.97146 | -0.55215 | 0.97187 | -0.54386 | 2.4077
71 | 0.0049162 | 0.0012274 | -0.0049156 | -0.0012274 | 6.4063e-07 | 3.7157e-08 | 0.0075299 | 0.0075301 | 0.0075301 | 0.97129 | -0.55549 | 0.97115 | -0.55824 | 2.0687
72 | -0.0067338 | -0.0016824 | 0.0067338 | 0.0016824 | 1.0921e-08 | 3.5934e-09 | 0.010308 | 0.010308 | 0.010308 | 0.97187 | -0.54386 | 0.97188 | -0.54383 | 2.8319
73 | 0.001026 | 0.00025557 | -0.0010259 | -0.00025578 | 1.5978e-08 | -2.0326e-07 | 0.0015714 | 0.0015715 | 0.0015715 | 0.97115 | -0.55824 | 0.97113 | -0.55857 | 0.43173
74 | 0.0038896 | 0.00097182 | -0.0038893 | -0.00097191 | 3.1286e-07 | -9.048e-08 | 0.0059586 | 0.0059587 | 0.0059587 | 0.97115 | -0.55824 | 0.97106 | -0.55993 | 1.637
75 | -0.00023435 | -5.8735e-05 | 0.00023435 | 5.8429e-05 | 1.1968e-09 | -3.0552e-07 | 0.0003591 | 0.00035899 | 0.0003591 | 0.9711 | -0.55922 | 0.9711 | -0.55912 | 0.098654
76 | -0.00038249 | -9.5555e-05 | 0.00038249 | 9.51e-05 | 4.7684e-09 | -4.5526e-07 | 0.00058597 | 0.00058581 | 0.00058597 | 0.9711 | -0.55912 | 0.97112 | -0.55885 | 0.16098
77 | 0.00037304 | 9.3153e-05 | -0.00037303 | -9.3261e-05 | 1.069e-09 | -1.0731e-07 | 0.00057147 | 0.00057151 | 0.00057151 | 0.97112 | -0.55885 | 0.97112 | -0.55891 | 0.15701
78 | -0.00075553 | -0.00018825 | 0.00075554 | 0.00018801 | 1.0279e-08 | -2.4667e-07 | 0.0011573 | 0.0011572 | 0.0011573 | 0.97112 | -0.55885 | 0.97113 | -0.55857 | 0.31793
79 | 0.00018848 | 4.7007e-05 | -0.00018848 | -4.7237e-05 | 5.8317e-10 | -2.3038e-07 | 0.00028872 | 0.0002888 | 0.0002888 | 0.97112 | -0.55891 | 0.97111 | -0.55898 | 0.079341
80 | -0.00027733 | -6.9074e-05 | 0.00027733 | 6.8974e-05 | 5.5035e-10 | -1.0025e-07 | 0.00042482 | 0.00042479 | 0.00042482 | 0.97103 | -0.56052 | 0.97104 | -0.56048 | 0.11671
81 | 7.7621e-05 | 1.9023e-05 | -7.7621e-05 | -1.9454e-05 | 1.846e-10 | -4.3085e-07 | 0.00011879 | 0.00011895 | 0.00011895 | 0.97103 | -0.56052 | 0.97103 | -0.56057 | 0.032678
82 | -0.0004435 | -0.00011062 | 0.0004435 | 0.00011057 | 6.7814e-10 | -4.803e-08 | 0.00067942 | 0.00067941 | 0.00067942 | 0.97104 | -0.56048 | 0.97104 | -0.56045 | 0.18665
83 | -0.00069671 | -0.00017403 | 0.00069672 | 0.00017355 | 1.7079e-08 | -4.8364e-07 | 0.0010674 | 0.0010672 | 0.0010674 | 0.97104 | -0.56045 | 0.97106 | -0.55993 | 0.29325
84 | 0.0031926 | 0.00079836 | -0.0031921 | -0.00079871 | 4.633e-07 | -3.4214e-07 | 0.0048915 | 0.0048917 | 0.0048917 | 0.97106 | -0.55993 | 0.97091 | -0.56298 | 1.3439
85 | 0.0028623 | 0.00071604 | -0.0028617 | -0.00071668 | 5.9156e-07 | -6.3511e-07 | 0.0043862 | 0.0043866 | 0.0043866 | 0.97091 | -0.56298 | 0.97069 | -0.56732 | 1.2051
86 | -0.006965 | -0.0017403 | 0.0069653 | 0.0017404 | 2.844e-07 | 9.9341e-08 | 0.010662 | 0.010662 | 0.010662 | 0.97188 | -0.54383 | 0.97192 | -0.54297 | 2.9291
87 | 0.0028617 | 0.00071668 | -0.0028614 | -0.00071699 | 2.8611e-07 | -3.0696e-07 | 0.0043866 | 0.0043868 | 0.0043868 | 0.97069 | -0.56732 | 0.97058 | -0.56942 | 1.2052
88 | 0.0014006 | 0.00035088 | -0.0014006 | -0.00035102 | 2.1599e-08 | -1.4056e-07 | 0.0021473 | 0.0021473 | 0.0021473 | 0.97058 | -0.56942 | 0.97057 | -0.56975 | 0.58992
89 | 0.0082695 | 0.0020685 | -0.0082578 | -0.0020636 | 1.1745e-05 | 4.9264e-06 | 0.012443 | 0.012444 | 0.012444 | 0.98879 | -0.21553 | 0.98725 | -0.24542 | 3.4187
90 | -0.00028124 | -7.0484e-05 | 0.00028125 | 6.7181e-05 | 1.8142e-08 | -3.3034e-06 | 0.00042822 | 0.00042706 | 0.00042822 | 0.97726 | -0.43769 | 0.97733 | -0.43631 | 0.11764
91 | -0.00073489 | -0.00018087 | 0.00073491 | 0.00018026 | 2.3481e-08 | -6.132e-07 | 0.0011177 | 0.0011175 | 0.0011177 | 0.97733 | -0.43631 | 0.97737 | -0.43563 | 0.30706
92 | 0.001578 | 0.00039486 | -0.0015778 | -0.00039545 | 1.1425e-07 | -5.8698e-07 | 0.0024035 | 0.0024037 | 0.0024037 | 0.97684 | -0.44612 | 0.97676 | -0.44764 | 0.66036
93 | -0.001578 | -0.00039486 | 0.0015782 | 0.00039387 | 1.9153e-07 | -9.8457e-07 | 0.0024035 | 0.0024031 | 0.0024035 | 0.97684 | -0.44612 | 0.97697 | -0.44357 | 0.6603
94 | -0.0020444 | -0.00051074 | 0.0020445 | 0.00051057 | 6.1613e-08 | -1.7284e-07 | 0.0031133 | 0.0031132 | 0.0031133 | 0.97697 | -0.44357 | 0.977 | -0.44293 | 0.8553
95 | 0.025492 | 0.0064099 | -0.025464 | -0.0063926 | 2.7854e-05 | 1.7213e-05 | 0.038864 | 0.038864 | 0.038864 | 0.97623 | -0.45785 | 0.97507 | -0.48075 | 10.677
96 | 0.0087077 | 0.0021775 | -0.008706 | -0.0021767 | 1.705e-06 | 7.7388e-07 | 0.013327 | 0.013327 | 0.013327 | 0.97213 | -0.53885 | 0.97192 | -0.54297 | 3.6613
97 | -0.009397 | -0.0023502 | 0.0093974 | 0.0023504 | 4.2044e-07 | 2.0188e-07 | 0.014382 | 0.014382 | 0.014382 | 0.97213 | -0.53885 | 0.97217 | -0.53791 | 3.9511
98 | -0.010618 | -0.0026562 | 0.010624 | 0.0026596 | 6.4798e-06 | 3.3351e-06 | 0.01625 | 0.016249 | 0.01625 | 0.97217 | -0.53791 | 0.97282 | -0.52509 | 4.4642
99 | -0.011597 | -0.0029034 | 0.011607 | 0.002909 | 1.0379e-05 | 5.5492e-06 | 0.017738 | 0.017737 | 0.017738 | 0.97282 | -0.52509 | 0.97377 | -0.5063 | 4.8729
100 | -0.012934 | -0.0032414 | 0.012936 | 0.0032428 | 2.6366e-06 | 1.4634e-06 | 0.019764 | 0.019764 | 0.019764 | 0.97377 | -0.5063 | 0.97399 | -0.50203 | 5.4296
101 | 0.012201 | 0.0030585 | -0.012197 | -0.0030565 | 3.792e-06 | 2.0648e-06 | 0.018641 | 0.018641 | 0.018641 | 0.97399 | -0.50203 | 0.97366 | -0.50855 | 5.1211
102 | -0.025138 | -0.0063014 | 0.025153 | 0.0063106 | 1.4939e-05 | 9.2246e-06 | 0.038405 | 0.038404 | 0.038405 | 0.97399 | -0.50203 | 0.97462 | -0.48956 | 10.5507
103 | -0.025153 | -0.0063106 | 0.025163 | 0.0063171 | 1.0569e-05 | 6.5259e-06 | 0.038404 | 0.038404 | 0.038404 | 0.97462 | -0.48956 | 0.97507 | -0.48075 | 10.5507
104 | 0.0070527 | 0.0017671 | -0.0070494 | -0.0017659 | 3.2207e-06 | 1.1422e-06 | 0.010778 | 0.010779 | 0.010779 | 0.97366 | -0.50855 | 0.97317 | -0.51814 | 2.9611
105 | 0.041419 | 0.010494 | -0.041385 | -0.010472 | 3.3721e-05 | 2.129e-05 | 0.062638 | 0.062638 | 0.062638 | 0.98458 | -0.29499 | 0.98371 | -0.31195 | 17.2082
106 | -0.043489 | -0.011012 | 0.043547 | 0.011049 | 5.7945e-05 | 3.663e-05 | 0.065766 | 0.065766 | 0.065766 | 0.98458 | -0.29499 | 0.98601 | -0.26728 | 18.0676
107 | 0.038663 | 0.0097899 | -0.038626 | -0.009767 | 3.6264e-05 | 2.2851e-05 | 0.058519 | 0.058519 | 0.058519 | 0.98371 | -0.31195 | 0.9827 | -0.3315 | 16.0768
108 | -0.045126 | -0.011445 | 0.045136 | 0.011451 | 9.544e-06 | 6.0382e-06 | 0.068149 | 0.068149 | 0.068149 | 0.98601 | -0.26728 | 0.98624 | -0.26288 | 18.7223
109 | -0.067141 | -0.016993 | 0.067153 | 0.017001 | 1.201e-05 | 7.6464e-06 | 0.10136 | 0.10136 | 0.10136 | 0.98624 | -0.26288 | 0.98643 | -0.25915 | 27.8461
110 | -0.068535 | -0.017347 | 0.068592 | 0.017383 | 5.7462e-05 | 3.6592e-05 | 0.10344 | 0.10344 | 0.10344 | 0.98643 | -0.25915 | 0.98734 | -0.2417 | 28.4188
111 | -0.071417 | -0.018091 | 0.071446 | 0.01811 | 2.8582e-05 | 1.8208e-05 | 0.1077 | 0.1077 | 0.1077 | 0.98734 | -0.2417 | 0.98777 | -0.23337 | 29.5882
112 | 0.0010017 | 0.00025098 | -0.0010017 | -0.00025104 | 4.0658e-09 | -5.6141e-08 | 0.0015229 | 0.0015229 | 0.0015229 | 0.97869 | -0.40972 | 0.97868 | -0.4098 | 0.41839
113 | -0.0004852 | -0.0001216 | 0.0004852 | 0.0001216 | 1.0042e-10 | -6.0893e-09 | 0.00073896 | 0.00073896 | 0.00073896 | 0.97702 | -0.44249 | 0.97703 | -0.44248 | 0.20301
114 | -0.0008605 | -0.00021565 | 0.00086051 | 0.00021549 | 8.5565e-09 | -1.6091e-07 | 0.0013105 | 0.0013105 | 0.0013105 | 0.97703 | -0.44248 | 0.97704 | -0.44228 | 0.36004
115 | 0.0022197 | 0.00055531 | -0.0022194 | -0.00055588 | 2.5087e-07 | -5.7507e-07 | 0.0033773 | 0.0033776 | 0.0033776 | 0.97786 | -0.42595 | 0.97774 | -0.42832 | 0.9279
116 | 0.0045242 | 0.0011304 | -0.004523 | -0.0011304 | 1.2512e-06 | -8.2359e-08 | 0.0068833 | 0.0068836 | 0.0068836 | 0.97786 | -0.42595 | 0.97757 | -0.43177 | 1.8911
117 | -0.0036754 | -0.000919 | 0.0036763 | 0.0009186 | 9.3817e-07 | -4.0015e-07 | 0.0055968 | 0.0055964 | 0.0055968 | 0.97704 | -0.44228 | 0.97731 | -0.43691 | 1.5376
118 | 0.0028149 | 0.0007035 | -0.0028148 | -0.00070359 | 7.4275e-08 | -8.7472e-08 | 0.0042863 | 0.0042864 | 0.0042864 | 0.97704 | -0.44228 | 0.97701 | -0.44283 | 1.1776
119 | 0.0012944 | 0.00032357 | -0.0012943 | -0.00032437 | 1.0323e-07 | -8.0715e-07 | 0.0019788 | 0.0019792 | 0.0019792 | 0.97317 | -0.51814 | 0.97309 | -0.51982 | 0.54372
120 | 0.07275 | 0.018541 | -0.072479 | -0.018369 | 0.00027051 | 0.00017235 | 0.10926 | 0.10926 | 0.10926 | 0.9918 | -0.15601 | 0.98777 | -0.23337 | 30.0162
121 | -0.074599 | -0.019005 | 0.074706 | 0.019073 | 0.00010705 | 6.8215e-05 | 0.11203 | 0.11203 | 0.11203 | 0.9918 | -0.15601 | 0.99335 | -0.12632 | 30.7783
122 | 0.0018288 | 0.00045799 | -0.0018288 | -0.00045813 | 3.6211e-08 | -1.3317e-07 | 0.0027832 | 0.0027832 | 0.0027832 | 0.97774 | -0.42832 | 0.97772 | -0.42874 | 0.76462
123 | 0.004523 | 0.0011304 | -0.0045219 | -0.0011305 | 1.1054e-06 | -7.225e-08 | 0.0068836 | 0.0068838 | 0.0068838 | 0.97757 | -0.43177 | 0.97731 | -0.43691 | 1.8912
124 | 0.002371 | 0.00059237 | -0.002371 | -0.00059239 | 1.1689e-08 | -2.2465e-08 | 0.0036104 | 0.0036105 | 0.0036105 | 0.97701 | -0.44283 | 0.977 | -0.44293 | 0.99188
125 | 0.0015931 | 0.00039905 | -0.001593 | -0.00039916 | 2.2795e-08 | -1.151e-07 | 0.0024244 | 0.0024245 | 0.0024245 | 0.97772 | -0.42874 | 0.97771 | -0.42904 | 0.66606
126 | 0.00049473 | 0.0001239 | -0.00049473 | -0.00012399 | 1.5493e-09 | -9.0403e-08 | 0.00075292 | 0.00075296 | 0.00075296 | 0.97771 | -0.42904 | 0.9777 | -0.4291 | 0.20686
127 | 0.0018615 | 0.00046614 | -0.0018614 | -0.00046652 | 1.0441e-07 | -3.7435e-07 | 0.002823 | 0.0028232 | 0.0028232 | 0.98116 | -0.36329 | 0.9811 | -0.36447 | 0.7756
128 | -0.0043293 | -0.0010846 | 0.0043298 | 0.0010845 | 5.5759e-07 | -7.8855e-08 | 0.0065656 | 0.0065654 | 0.0065656 | 0.98116 | -0.36329 | 0.9813 | -0.36059 | 1.8037

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27227 | 0.069176

## res_load
| p_mw | q_mvar
0 | 0.00096347 | 0.00024147
1 | 0.0012342 | 0.00030931
2 | 0.0024805 | 0.00062168
3 | 0.0018157 | 0.00045505
4 | 0.0024072 | 0.0006033
5 | 0.0072882 | 0.0018266
6 | 0.0019138 | 0.00047965
7 | 0.0012402 | 0.00031081
8 | 0.0037714 | 0.00094521
9 | 0.0026091 | 0.00065391
10 | 0.0084855 | 0.0021267
11 | 0.0046296 | 0.0011603
12 | 0.0024251 | 0.00060778
13 | 0.00031864 | 7.9859e-05
14 | 0.0003402 | 8.5263e-05
15 | 0.00083189 | 0.00020849
16 | 0.001508 | 0.00037794
17 | 0.00093883 | 0.00023529
18 | 0.0026077 | 0.00065356
19 | 0.0011893 | 0.00029808
20 | 0.00061777 | 0.00015483
21 | 0.001359 | 0.0003406
22 | 0.0011711 | 0.0002935
23 | 0.0012149 | 0.00030448
24 | 0.0026763 | 0.00067075
25 | 0.0011015 | 0.00027605
26 | 0.014905 | 0.0037355
27 | 0.00096018 | 0.00024064
28 | 0.0015256 | 0.00038235
29 | 0.002842 | 0.00071226
30 | 0.0026219 | 0.00065711
31 | 0.0186 | 0.0046616
32 | 0.0066383 | 0.0016637
33 | 0.0050329 | 0.0012614
34 | 0.0013699 | 0.00034332
35 | 0.002622 | 0.00065715
36 | 0.0029391 | 0.00073662
37 | 0.0011082 | 0.00027775
38 | 0.0039418 | 0.00098792
39 | 0.0012128 | 0.00030395
40 | 0.01818 | 0.0045563
41 | 0.019428 | 0.004869
42 | 0.025199 | 0.0063155
43 | 0.010486 | 0.002628
44 | 0.0026651 | 0.00066795
45 | 0.00017162 | 4.3013e-05
46 | 0.00033389 | 8.3682e-05
47 | 0.00013902 | 3.4843e-05
48 | 0.00016136 | 4.044e-05
49 | 0.0010086 | 0.00025279
50 | 0.00023435 | 5.8735e-05
51 | 0.00014813 | 3.7126e-05
52 | 0.00018456 | 4.6254e-05
53 | 0.00027041 | 6.777e-05
54 | 0.00018848 | 4.7237e-05
55 | 0.00019971 | 5.0051e-05
56 | 0.00016617 | 4.1646e-05
57 | 7.7621e-05 | 1.9454e-05
58 | 0.00025321 | 6.346e-05
59 | 0.00032982 | 8.266e-05
60 | 0.00023117 | 5.7936e-05
61 | 0.0014608 | 0.0003661
62 | 0.0021342 | 0.00053487
63 | 0.0023624 | 0.00059207
64 | 0.00028124 | 7.0484e-05
65 | 0.00045363 | 0.00011369
66 | 0.00065289 | 0.00016363
67 | 0.0015778 | 0.00039545
68 | 0.00046629 | 0.00011686
69 | 0.00065376 | 0.00016385
70 | 0.00068927 | 0.00017275
71 | 0.0017407 | 0.00043627
72 | 0.0012201 | 0.0003058
73 | 0.00097296 | 0.00024385
74 | 0.0013263 | 0.00033241
75 | 0.00030136 | 7.5529e-05
76 | 0.0014006 | 0.00035102
77 | 0.0051448 | 0.0012894
78 | 0.0020701 | 0.00051881
79 | 0.0027226 | 0.00068235
80 | 0.0015793 | 0.00039582
81 | 0.0021418 | 0.0005368
82 | 0.0013819 | 0.00034634
83 | 0.0028245 | 0.0007079
84 | 0.0003426 | 8.5865e-05
85 | 0.0010017 | 0.00025104
86 | 0.0004852 | 0.0001216
87 | 0.0003753 | 9.4058e-05
88 | 0.0057551 | 0.0014424
89 | 0.0012943 | 0.00032437
90 | 0.0018493 | 0.00046349
91 | 0.001034 | 0.00025914
92 | 0.0029394 | 0.00073667
93 | 0.00039058 | 9.7888e-05
94 | 0.00084556 | 0.00021192
95 | 0.00044379 | 0.00011122
96 | 0.00023574 | 5.9082e-05
97 | 0.0010983 | 0.00027526
98 | 0.00032648 | 8.1824e-05
99 | 0.00049473 | 0.00012399
100 | 0.0024677 | 0.00061847
101 | 0.0018614 | 0.00046652
102 | 0.0046242 | 0.0011589

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1