## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_153-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_153-9_0_3_node_203 | 0.4 | n |  | TRUE
2 | bus_LV_153-9_0_3_node_64 | 0.4 | n |  | TRUE
3 | bus_LV_153-9_0_3_node_204 | 0.4 | n |  | TRUE
4 | bus_LV_153-9_0_3_node_65 | 0.4 | n |  | TRUE
5 | bus_LV_153-9_0_3_node_66 | 0.4 | n |  | TRUE
6 | bus_LV_153-9_0_3_node_1 | 0.4 | n |  | TRUE
7 | bus_LV_153-9_0_3_node_2 | 0.4 | n |  | TRUE
8 | bus_LV_153-9_0_3_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_153-9_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_153-9_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_153-9_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_153-9_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_153-9_0_3_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_153-9_0_3_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_153-9_0_3_node_116 | 0.4 | n |  | TRUE
16 | bus_LV_153-9_0_3_node_60 | 0.4 | n |  | TRUE
17 | bus_LV_153-9_0_3_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_153-9_0_3_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_153-9_0_3_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_153-9_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_153-9_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_153-9_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_153-9_0_3_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_153-9_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_153-9_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_153-9_0_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_153-9_0_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_153-9_0_3_node_102 | 0.4 | n |  | TRUE
29 | bus_LV_153-9_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_153-9_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_153-9_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_153-9_0_3_node_201 | 0.4 | n |  | TRUE
33 | bus_LV_153-9_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_153-9_0_3_node_202 | 0.4 | n |  | TRUE
35 | bus_LV_153-9_0_3_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_153-9_0_3_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_153-9_0_3_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_153-9_0_3_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_153-9_0_3_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_153-9_0_3_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_153-9_0_3_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_153-9_0_3_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_153-9_0_3_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_153-9_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_153-9_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_153-9_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_153-9_0_3_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_153-9_0_3_node_100 | 0.4 | n |  | TRUE
49 | bus_LV_153-9_0_3_node_156 | 0.4 | n |  | TRUE
50 | bus_LV_153-9_0_3_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_153-9_0_3_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_153-9_0_3_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_153-9_0_3_node_152 | 0.4 | n |  | TRUE
54 | bus_LV_153-9_0_3_node_200 | 0.4 | n |  | TRUE
55 | bus_LV_153-9_0_3_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_153-9_0_3_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_153-9_0_3_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_153-9_0_3_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_153-9_0_3_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_153-9_0_3_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_153-9_0_3_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_153-9_0_3_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_153-9_0_3_node_83 | 0.4 | n |  | TRUE
64 | bus_LV_153-9_0_3_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_153-9_0_3_node_84 | 0.4 | n |  | TRUE
66 | bus_LV_153-9_0_3_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_153-9_0_3_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_153-9_0_3_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_153-9_0_3_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_153-9_0_3_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_153-9_0_3_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_153-9_0_3_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_153-9_0_3_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_153-9_0_3_node_95 | 0.4 | n |  | TRUE
75 | bus_LV_153-9_0_3_node_92 | 0.4 | n |  | TRUE
76 | bus_LV_153-9_0_3_node_78 | 0.4 | n |  | TRUE
77 | bus_LV_153-9_0_3_node_97 | 0.4 | n |  | TRUE
78 | bus_LV_153-9_0_3_node_93 | 0.4 | n |  | TRUE
79 | bus_LV_153-9_0_3_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_153-9_0_3_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_153-9_0_3_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_153-9_0_3_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_153-9_0_3_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_153-9_0_3_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_153-9_0_3_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_153-9_0_3_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_153-9_0_3_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_153-9_0_3_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_153-9_0_3_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_153-9_0_3_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_153-9_0_3_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_153-9_0_3_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_153-9_0_3_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_153-9_0_3_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_153-9_0_3_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_153-9_0_3_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_153-9_0_3_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_153-9_0_3_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_153-9_0_3_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_153-9_0_3_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_153-9_0_3_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_153-9_0_3_node_109 | 0.4 | n |  | TRUE
103 | bus_LV_153-9_0_3_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_153-9_0_3_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_153-9_0_3_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_153-9_0_3_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_153-9_0_3_node_111 | 0.4 | n |  | TRUE
108 | bus_LV_153-9_0_3_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_153-9_0_3_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_153-9_0_3_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_153-9_0_3_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_153-9_0_3_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_153-9_0_3_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_153-9_0_3_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_153-9_0_3_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_153-9_0_3_node_108 | 0.4 | n |  | TRUE
117 | bus_LV_153-9_0_3_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_153-9_0_3_node_124 | 0.4 | n |  | TRUE
119 | bus_MV_355_1_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_153-9_0_3_load_0 | 0 | 0.0013247 | 0.00033201 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_153-9_0_3_load_64 | 2 | 0.0048329 | 0.0012112 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_153-9_0_3_load_204 | 3 | 0.0025081 | 0.00062858 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_153-9_0_3_load_65 | 4 | 0.00095972 | 0.00024053 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_153-9_0_3_load_66 | 5 | 0.0016997 | 0.00042599 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_153-9_0_3_load_1 | 6 | 0.0013163 | 0.00032989 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_153-9_0_3_load_2 | 7 | 0.0049132 | 0.0012314 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_153-9_0_3_load_3 | 8 | 0.0030779 | 0.00077139 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_153-9_0_3_load_4 | 9 | 0.0010554 | 0.00026451 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_153-9_0_3_load_6 | 11 | 0.0016231 | 0.00040679 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_153-9_0_3_load_39 | 14 | 0.0020469 | 0.00051301 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_153-9_0_3_load_116 | 15 | 0.0011952 | 0.00029954 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_153-9_0_3_load_60 | 16 | 0.0041746 | 0.0010463 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_153-9_0_3_load_40 | 17 | 0.0025768 | 0.00064581 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_153-9_0_3_load_8 | 18 | 0.0056932 | 0.0014269 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_153-9_0_3_load_9 | 19 | 0.0058237 | 0.0014596 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_153-9_0_3_load_10 | 20 | 0.0053014 | 0.0013286 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_153-9_0_3_load_12 | 22 | 0.0057195 | 0.0014334 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_153-9_0_3_load_27 | 25 | 0.0056786 | 0.0014232 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_153-9_0_3_load_28 | 26 | 0.0015706 | 0.00039362 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_153-9_0_3_load_102 | 28 | 0.0019518 | 0.00048916 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_153-9_0_3_load_29 | 29 | 0.0017792 | 0.0004459 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_153-9_0_3_load_30 | 31 | 0.0049341 | 0.0012366 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_153-9_0_3_load_202 | 34 | 0.0049123 | 0.0012311 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_153-9_0_3_load_15 | 35 | 0.0019414 | 0.00048655 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_153-9_0_3_load_16 | 36 | 0.00014166 | 3.5503e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_153-9_0_3_load_19 | 39 | 0.0060866 | 0.0015254 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_153-9_0_3_load_20 | 40 | 0.00069985 | 0.0001754 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_153-9_0_3_load_21 | 41 | 9.3403e-05 | 2.3409e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_153-9_0_3_load_22 | 42 | 0.0001445 | 3.6215e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_153-9_0_3_load_42 | 43 | 0.0044845 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_153-9_0_3_load_32 | 44 | 0.0037029 | 0.00092803 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_153-9_0_3_load_41 | 45 | 0.0024358 | 0.00061048 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_153-9_0_3_load_34 | 46 | 0.0011523 | 0.00028879 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_153-9_0_3_load_33 | 47 | 0.0018838 | 0.00047213 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_153-9_0_3_load_100 | 48 | 0.0013872 | 0.00034767 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_153-9_0_3_load_156 | 49 | 0.0038334 | 0.00096075 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_153-9_0_3_load_36 | 50 | 0.0042133 | 0.0010559 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_153-9_0_3_load_37 | 51 | 0.0012634 | 0.00031664 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_153-9_0_3_load_152 | 53 | 0.0059268 | 0.0014854 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_153-9_0_3_load_200 | 54 | 0.0015686 | 0.00039313 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_153-9_0_3_load_47 | 55 | 0.0020907 | 0.00052399 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_153-9_0_3_load_48 | 56 | 0.0018877 | 0.0004731 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_153-9_0_3_load_49 | 57 | 0.0034632 | 0.00086797 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_153-9_0_3_load_50 | 58 | 0.0010818 | 0.00027112 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_153-9_0_3_load_52 | 60 | 0.0013931 | 0.00034914 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_153-9_0_3_load_86 | 62 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_153-9_0_3_load_83 | 63 | 0.0012556 | 0.00031468 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_153-9_0_3_load_88 | 64 | 0.0012556 | 0.00031468 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_153-9_0_3_load_84 | 65 | 0.0026991 | 0.00067646 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_153-9_0_3_load_54 | 66 | 0.0031317 | 0.00078489 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_153-9_0_3_load_55 | 67 | 0.0030118 | 0.00075483 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_153-9_0_3_load_56 | 68 | 0.0016996 | 0.00042595 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_153-9_0_3_load_58 | 70 | 0.0022222 | 0.00055694 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_153-9_0_3_load_59 | 71 | 0.0041159 | 0.0010316 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_153-9_0_3_load_61 | 72 | 0.0034019 | 0.00085259 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_153-9_0_3_load_62 | 73 | 0.0020739 | 0.00051977 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_153-9_0_3_load_95 | 74 | 0.0022212 | 0.00055669 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_153-9_0_3_load_92 | 75 | 0.0069724 | 0.0017475 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_153-9_0_3_load_78 | 76 | 0.001982 | 0.00049674 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_153-9_0_3_load_97 | 77 | 0.0022558 | 0.00056536 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_153-9_0_3_load_93 | 78 | 0.0034997 | 0.00087711 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_153-9_0_3_load_75 | 79 | 0.00061188 | 0.00015335 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_153-9_0_3_load_117 | 80 | 0.0032308 | 0.00080972 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_153-9_0_3_load_67 | 81 | 0.0020032 | 0.00050204 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_153-9_0_3_load_68 | 82 | 0.001593 | 0.00039925 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_153-9_0_3_load_69 | 83 | 0.0018571 | 0.00046544 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_153-9_0_3_load_77 | 84 | 0.0014227 | 0.00035656 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_153-9_0_3_load_79 | 85 | 0.0023456 | 0.00058786 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_153-9_0_3_load_96 | 86 | 0.0025077 | 0.00062849 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_153-9_0_3_load_80 | 87 | 0.0018395 | 0.00046102 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_153-9_0_3_load_70 | 88 | 0.0013211 | 0.0003311 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_153-9_0_3_load_71 | 89 | 0.001329 | 0.00033307 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_153-9_0_3_load_72 | 90 | 0.0017647 | 0.00044228 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_153-9_0_3_load_73 | 91 | 0.0018019 | 0.0004516 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_153-9_0_3_load_74 | 92 | 0.0012863 | 0.00032239 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_153-9_0_3_load_76 | 93 | 0.0017837 | 0.00044704 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_153-9_0_3_load_89 | 94 | 0.0017644 | 0.0004422 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_153-9_0_3_load_90 | 95 | 0.0023103 | 0.00057902 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_153-9_0_3_load_81 | 96 | 0.0026364 | 0.00066074 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_153-9_0_3_load_91 | 98 | 0.0019935 | 0.00049961 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_153-9_0_3_load_105 | 99 | 0.0017983 | 0.00045069 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_153-9_0_3_load_85 | 100 | 0.0032685 | 0.00081915 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_153-9_0_3_load_87 | 101 | 0.0033176 | 0.00083148 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_153-9_0_3_load_109 | 102 | 0.0012924 | 0.00032392 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_153-9_0_3_load_94 | 103 | 0.003545 | 0.00088845 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_153-9_0_3_load_114 | 104 | 0.00157 | 0.00039349 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_153-9_0_3_load_115 | 105 | 0.0027849 | 0.00069797 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_153-9_0_3_load_98 | 106 | 0.0019989 | 0.00050098 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_153-9_0_3_load_111 | 107 | 0.0022152 | 0.00055517 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_153-9_0_3_load_112 | 108 | 0.023031 | 0.0057721 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_153-9_0_3_load_99 | 109 | 0.00088184 | 0.00022101 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_153-9_0_3_load_101 | 110 | 0.0011135 | 0.00027907 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_153-9_0_3_load_103 | 111 | 0.0021412 | 0.00053664 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_153-9_0_3_load_104 | 112 | 0.0026433 | 0.00066247 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_153-9_0_3_load_123 | 113 | 0.0011952 | 0.00029955 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_153-9_0_3_load_107 | 114 | 0.0019105 | 0.00047882 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_153-9_0_3_load_106 | 115 | 0.0016186 | 0.00040565 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_153-9_0_3_load_108 | 116 | 0.0016341 | 0.00040956 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_153-9_0_3_load_110 | 117 | 0.0013902 | 0.00034842 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_153-9_0_3_load_124 | 118 | 0.0018507 | 0.00046383 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_153-9_0_3_line_0 |  | 0 | 1 | 0.17026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_153-9_0_3_line_1 |  | 0 | 2 | 0.36337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_153-9_0_3_line_2 |  | 1 | 3 | 0.020894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_153-9_0_3_line_3 |  | 2 | 4 | 0.0091902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_153-9_0_3_line_4 |  | 2 | 5 | 0.0025191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_153-9_0_3_line_5 |  | 4 | 81 | 0.0012688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_153-9_0_3_line_6 |  | 5 | 82 | 0.011223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_153-9_0_3_line_7 |  | 6 | 7 | 0.024388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_153-9_0_3_line_8 |  | 6 | 8 | 0.0027981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_153-9_0_3_line_9 |  | 7 | 9 | 0.0093829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_153-9_0_3_line_10 |  | 8 | 10 | 0.010628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_153-9_0_3_line_11 |  | 9 | 11 | 0.02519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_153-9_0_3_line_12 |  | 10 | 12 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_153-9_0_3_line_13 |  | 11 | 13 | 0.044327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_153-9_0_3_line_14 |  | 12 | 14 | 0.020586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_153-9_0_3_line_15 |  | 13 | 15 | 0.018534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_153-9_0_3_line_16 |  | 13 | 16 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_153-9_0_3_line_17 |  | 14 | 17 | 0.035929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_153-9_0_3_line_18 |  | 15 | 80 | 0.0040407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_153-9_0_3_line_19 |  | 16 | 69 | 0.033068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_153-9_0_3_line_20 |  | 17 | 45 | 0.0079619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_153-9_0_3_line_21 |  | 18 | 19 | 0.041808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_153-9_0_3_line_22 |  | 18 | 20 | 0.0010253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_153-9_0_3_line_23 |  | 19 | 21 | 0.023588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_153-9_0_3_line_24 |  | 20 | 22 | 0.034449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_153-9_0_3_line_25 |  | 21 | 23 | 0.017736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_153-9_0_3_line_26 |  | 21 | 24 | 0.062003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_153-9_0_3_line_27 |  | 22 | 25 | 0.054449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_153-9_0_3_line_28 |  | 23 | 26 | 0.037765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_153-9_0_3_line_29 |  | 24 | 27 | 0.036174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_153-9_0_3_line_30 |  | 26 | 28 | 0.0053105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_153-9_0_3_line_31 |  | 27 | 33 | 0.0070177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_153-9_0_3_line_32 |  | 27 | 34 | 0.040191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_153-9_0_3_line_33 |  | 28 | 48 | 0.01767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_153-9_0_3_line_34 |  | 29 | 30 | 0.011838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_153-9_0_3_line_35 |  | 30 | 45 | 0.015544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_153-9_0_3_line_36 |  | 30 | 40 | 0.019499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_153-9_0_3_line_37 |  | 31 | 32 | 0.042875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_153-9_0_3_line_38 |  | 32 | 34 | 0.0073848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_153-9_0_3_line_39 |  | 32 | 49 | 0.01047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_153-9_0_3_line_40 |  | 33 | 50 | 0.024047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_153-9_0_3_line_41 |  | 33 | 51 | 0.027483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_153-9_0_3_line_42 |  | 33 | 47 | 0.025296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_153-9_0_3_line_43 |  | 35 | 36 | 0.026434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_153-9_0_3_line_44 |  | 35 | 37 | 0.017182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_153-9_0_3_line_45 |  | 36 | 38 | 0.013078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_153-9_0_3_line_46 |  | 37 | 39 | 0.013443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_153-9_0_3_line_47 |  | 37 | 40 | 0.015474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_153-9_0_3_line_48 |  | 38 | 41 | 0.021135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_153-9_0_3_line_49 |  | 39 | 42 | 0.015695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_153-9_0_3_line_50 |  | 41 | 43 | 0.054878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_153-9_0_3_line_51 |  | 42 | 44 | 0.052525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_153-9_0_3_line_52 |  | 46 | 47 | 0.031879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_153-9_0_3_line_53 |  | 48 | 109 | 0.018851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_153-9_0_3_line_54 |  | 51 | 52 | 0.0077321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_153-9_0_3_line_55 |  | 52 | 53 | 0.021616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_153-9_0_3_line_56 |  | 52 | 54 | 0.018635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_153-9_0_3_line_57 |  | 55 | 56 | 0.0076318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_153-9_0_3_line_58 |  | 55 | 57 | 0.031238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_153-9_0_3_line_59 |  | 56 | 58 | 0.0041227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_153-9_0_3_line_60 |  | 57 | 59 | 0.018265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_153-9_0_3_line_61 |  | 59 | 60 | 0.001854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_153-9_0_3_line_62 |  | 59 | 61 | 0.017433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_153-9_0_3_line_63 |  | 61 | 62 | 0.012107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_153-9_0_3_line_64 |  | 61 | 63 | 0.016914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_153-9_0_3_line_65 |  | 62 | 64 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_153-9_0_3_line_66 |  | 63 | 65 | 0.0047312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_153-9_0_3_line_67 |  | 64 | 86 | 0.0091186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_153-9_0_3_line_68 |  | 65 | 100 | 0.037218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_153-9_0_3_line_69 |  | 66 | 67 | 0.011611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_153-9_0_3_line_70 |  | 66 | 68 | 0.0036617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_153-9_0_3_line_71 |  | 67 | 69 | 0.022959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_153-9_0_3_line_72 |  | 68 | 70 | 0.0018656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_153-9_0_3_line_73 |  | 69 | 71 | 0.023804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_153-9_0_3_line_74 |  | 69 | 72 | 0.014095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_153-9_0_3_line_75 |  | 70 | 73 | 0.008159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_153-9_0_3_line_76 |  | 71 | 74 | 0.027612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_153-9_0_3_line_77 |  | 72 | 75 | 0.016754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_153-9_0_3_line_78 |  | 73 | 76 | 0.005198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_153-9_0_3_line_79 |  | 74 | 77 | 0.00075256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_153-9_0_3_line_80 |  | 75 | 78 | 0.0069196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_153-9_0_3_line_81 |  | 76 | 79 | 0.0029053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_153-9_0_3_line_82 |  | 77 | 106 | 0.0018224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_153-9_0_3_line_83 |  | 78 | 103 | 0.01806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_153-9_0_3_line_84 |  | 79 | 91 | 0.0088187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_153-9_0_3_line_85 |  | 80 | 113 | 0.0053553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_153-9_0_3_line_86 |  | 81 | 83 | 0.021541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_153-9_0_3_line_87 |  | 82 | 84 | 0.013112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_153-9_0_3_line_88 |  | 83 | 85 | 0.015285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_153-9_0_3_line_89 |  | 84 | 86 | 0.011807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_153-9_0_3_line_90 |  | 85 | 87 | 0.0082806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_153-9_0_3_line_91 |  | 87 | 96 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_153-9_0_3_line_92 |  | 88 | 89 | 0.0037611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_153-9_0_3_line_93 |  | 88 | 90 | 0.00089728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_153-9_0_3_line_94 |  | 89 | 91 | 0.0053899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_153-9_0_3_line_95 |  | 90 | 92 | 0.0074296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_153-9_0_3_line_96 |  | 92 | 93 | 0.0011858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_153-9_0_3_line_97 |  | 93 | 94 | 0.002763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_153-9_0_3_line_98 |  | 94 | 95 | 0.021324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_153-9_0_3_line_99 |  | 95 | 97 | 0.013643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_153-9_0_3_line_100 |  | 96 | 97 | 0.004261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_153-9_0_3_line_101 |  | 97 | 98 | 0.023178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_153-9_0_3_line_102 |  | 98 | 99 | 0.0010113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_153-9_0_3_line_103 |  | 99 | 102 | 0.007969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_153-9_0_3_line_104 |  | 100 | 101 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_153-9_0_3_line_105 |  | 102 | 114 | 0.0029872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_153-9_0_3_line_106 |  | 103 | 104 | 0.0094367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_153-9_0_3_line_107 |  | 104 | 105 | 0.016973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_153-9_0_3_line_108 |  | 105 | 118 | 0.003381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_153-9_0_3_line_109 |  | 106 | 107 | 0.0013611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_153-9_0_3_line_110 |  | 107 | 108 | 0.036953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_153-9_0_3_line_111 |  | 109 | 110 | 0.0025027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_153-9_0_3_line_112 |  | 110 | 111 | 0.021613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_153-9_0_3_line_113 |  | 111 | 112 | 0.0027714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_153-9_0_3_line_114 |  | 112 | 113 | 0.017077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_153-9_0_3_line_115 |  | 114 | 115 | 0.0073344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_153-9_0_3_line_116 |  | 115 | 116 | 0.019615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_153-9_0_3_line_117 |  | 116 | 117 | 0.0059089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_153-9_0_3_trafo_61 | 0.63 MVA 20/0.4 kV | 119 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2702143.2326 | 1233996.893 | 2702064.5365 | 1233845.9114
1 | 2701778.7627 | 1234070.3509 | 2702064.5365 | 1233845.9114
2 | 2702143.2326 | 1233996.893 | 2702147.963 | 1234017.2451
3 | 2701784.184 | 1234077.7718 | 2701778.7627 | 1234070.3509
4 | 2701776.2454 | 1234070.2546 | 2701778.7627 | 1234070.3509 | 2701778.7627 | 1234070.3509
5 | 2701784.184 | 1234077.7718 | 2701784.9325 | 1234078.7963
6 | 2701776.2454 | 1234070.2546 | 2701765.0302 | 1234069.8251
7 | 2701604.4524 | 1233993.5503 | 2701613.6825 | 1234016.1241
8 | 2701604.4524 | 1233993.5503 | 2701603.3934 | 1233990.9603
9 | 2701613.6825 | 1234016.1241 | 2701616.0064 | 1234021.8074 | 2701617.1338 | 1234024.848
10 | 2701597.4053 | 1233982.3043 | 2701602.2202 | 1233988.0909 | 2701603.3934 | 1233990.9603
11 | 2701625.891 | 1234048.4664 | 2701617.1338 | 1234024.848
12 | 2701597.4053 | 1233982.3043 | 2701587.5364 | 1233983.8256 | 2701580.0543 | 1233984.3537 | 2701578.9885 | 1233991.3296
13 | 2701645.6583 | 1234088.0307 | 2701640.1256 | 1234078.6291 | 2701638.6969 | 1234076.7254 | 2701627.4125 | 1234052.5699 | 2701625.891 | 1234048.4664
14 | 2701578.9885 | 1233991.3296 | 2701575.9721 | 1234008.7688 | 2701575.2984 | 1234011.5764
15 | 2701645.6583 | 1234088.0307 | 2701636.9204 | 1234087.1806 | 2701627.8294 | 1234090.7174
16 | 2701645.6583 | 1234088.0307 | 2701647.6999 | 1234102.7878
17 | 2701575.2984 | 1234011.5764 | 2701572.972 | 1234021.2714 | 2701569.456 | 1234028.9615 | 2701562.0816 | 1234043.1239 | 2701561.3021 | 1234044.447
18 | 2701624.0637 | 1234092.1824 | 2701627.8294 | 1234090.7174
19 | 2701646.1427 | 1234135.8193 | 2701647.6999 | 1234102.7878
20 | 2701561.3021 | 1234044.447 | 2701557.261 | 1234051.3072
21 | 2701445.2007 | 1234135.3415 | 2701454.2945 | 1234128.7025 | 2701465.0461 | 1234122.0366 | 2701470.535 | 1234119.395 | 2701476.6564 | 1234118.2876 | 2701481.0192 | 1234118.629 | 2701482.1866 | 1234118.9458
22 | 2701444.3726 | 1234135.9461 | 2701445.2007 | 1234135.3415
23 | 2701500.6925 | 1234132.6199 | 2701490.4411 | 1234121.9813 | 2701485.2621 | 1234119.7801 | 2701482.1866 | 1234118.9458
24 | 2701444.3726 | 1234135.9461 | 2701430.7649 | 1234145.8805 | 2701416.5195 | 1234156.2185
25 | 2701511.5924 | 1234118.6067 | 2701500.6925 | 1234132.6199
26 | 2701476.9427 | 1234187.4888 | 2701476.3269 | 1234182.3188 | 2701476.4552 | 1234177.473 | 2701477.0967 | 1234171.3905 | 2701478.4375 | 1234166.4763 | 2701480.3217 | 1234161.6605 | 2701482.6813 | 1234156.4969 | 2701487.1846 | 1234149.9467 | 2701495.6708 | 1234138.9389 | 2701500.6925 | 1234132.6199
27 | 2701416.5195 | 1234156.2185 | 2701364.9536 | 1234138.7366
28 | 2701511.5924 | 1234118.6067 | 2701516.3876 | 1234122.0023 | 2701519.0202 | 1234118.5891 | 2701526.5093 | 1234130.0367 | 2701538.3327 | 1234125.78 | 2701539.5472 | 1234125.2315
29 | 2701476.9427 | 1234187.4888 | 2701477.6973 | 1234191.627 | 2701485.4198 | 1234222.6487
30 | 2701543.7782 | 1234122.1369 | 2701541.3696 | 1234124.4086 | 2701539.5472 | 1234125.2315
31 | 2701485.4198 | 1234222.6487 | 2701486.1747 | 1234225.8752 | 2701487.0217 | 1234229.4812
32 | 2701485.4198 | 1234222.6487 | 2701501.7607 | 1234215.4224 | 2701519.7904 | 1234202.26
33 | 2701543.7782 | 1234122.1369 | 2701543.7782 | 1234122.1369 | 2701548.3523 | 1234121.6369 | 2701560.5316 | 1234116.8987
34 | 2701549.3713 | 1234064.7006 | 2701542.8014 | 1234074.5478
35 | 2701549.3713 | 1234064.7006 | 2701557.261 | 1234051.3072
36 | 2701549.3713 | 1234064.7006 | 2701533.5706 | 1234058.0145 | 2701531.5031 | 1234056.9149
37 | 2701526.4101 | 1234199.1757 | 2701531.1311 | 1234197.5996 | 2701535.7294 | 1234190.8064 | 2701529.0356 | 1234172.2559 | 2701522.4523 | 1234167.173 | 2701520.9404 | 1234167.8479
38 | 2701526.4101 | 1234199.1757 | 2701522.0012 | 1234200.6459 | 2701519.7904 | 1234202.26
39 | 2701526.4101 | 1234199.1757 | 2701529.5854 | 1234207.4139 | 2701529.643 | 1234209.0535
40 | 2701487.0217 | 1234229.4812 | 2701496.5487 | 1234224.0176 | 2701499.2408 | 1234223.3186 | 2701503.7631 | 1234223.1846 | 2701507.6164 | 1234224.5403 | 2701509.108 | 1234225.422
41 | 2701487.0217 | 1234229.4812 | 2701493.3657 | 1234256.2224
42 | 2701487.0217 | 1234229.4812 | 2701478.8437 | 1234228.2184 | 2701464.4608 | 1234237.3202
43 | 2701484.5745 | 1234022.6448 | 2701491.1508 | 1234025.0764 | 2701507.0339 | 1234036.2545
44 | 2701518.6058 | 1234048.4851 | 2701515.4032 | 1234042.7261 | 2701511.7321 | 1234039.561 | 2701507.0339 | 1234036.2545
45 | 2701473.4475 | 1234016.2898 | 2701477.2466 | 1234019.9352 | 2701484.5745 | 1234022.6448
46 | 2701518.6058 | 1234048.4851 | 2701514.9884 | 1234050.6027 | 2701507.8408 | 1234056.4766
47 | 2701518.6058 | 1234048.4851 | 2701524.4767 | 1234053.1778 | 2701531.5031 | 1234056.9149
48 | 2701473.4475 | 1234016.2898 | 2701455.3337 | 1234020.4504 | 2701452.8617 | 1234021.073
49 | 2701495.7155 | 1234066.4413 | 2701507.8408 | 1234056.4766
50 | 2701452.8617 | 1234021.073 | 2701450.4138 | 1234021.6895 | 2701437.536 | 1234024.7275 | 2701418.9645 | 1234029.0917 | 2701399.4533 | 1234033.6852
51 | 2701495.7155 | 1234066.4413 | 2701482.1827 | 1234077.5626 | 2701452.8345 | 1234096.6497
52 | 2701464.4608 | 1234237.3202 | 2701439.0817 | 1234253.3807 | 2701437.4814 | 1234254.3
53 | 2701578.0997 | 1234110.0641 | 2701560.5316 | 1234116.8987
54 | 2701495.1505 | 1234263.7457 | 2701493.3657 | 1234256.2224
55 | 2701495.1505 | 1234263.7457 | 2701515.3167 | 1234255.9621
56 | 2701495.1505 | 1234263.7457 | 2701483.5297 | 1234278.3137
57 | 2701682.2311 | 1234028.1605 | 2701684.1334 | 1234022.7288 | 2701686.0082 | 1234022.6462
58 | 2701682.2311 | 1234028.1605 | 2701680.8855 | 1234032.0024 | 2701672.1627 | 1234038.6693 | 2701671.1184 | 1234045.2675 | 2701673.9231 | 1234054.353
59 | 2701690.1269 | 1234022.4645 | 2701686.0082 | 1234022.6462
60 | 2701679.3106 | 1234071.8053 | 2701673.9231 | 1234054.353
61 | 2701679.3106 | 1234071.8053 | 2701677.6244 | 1234072.5762
62 | 2701679.3106 | 1234071.8053 | 2701689.9482 | 1234066.9503 | 2701695.7289 | 1234067.1716
63 | 2701695.7289 | 1234067.1716 | 2701707.8273 | 1234067.6349
64 | 2701695.7289 | 1234067.1716 | 2701698.8581 | 1234050.5498
65 | 2701707.8273 | 1234067.6349 | 2701731.0174 | 1234068.5228
66 | 2701698.8581 | 1234050.5498 | 2701699.7334 | 1234045.9003
67 | 2701740.1294 | 1234068.8717 | 2701731.0174 | 1234068.5228
68 | 2701699.7334 | 1234045.9003 | 2701701.7592 | 1234035.1397 | 2701708.7593 | 1234029.5887 | 2701725.909 | 1234032.1134
69 | 2701680.3383 | 1234140.8968 | 2701668.8531 | 1234139.1914
70 | 2701680.3383 | 1234140.8968 | 2701683.9603 | 1234141.4346
71 | 2701646.1427 | 1234135.8193 | 2701668.8531 | 1234139.1914
72 | 2701685.8057 | 1234141.7087 | 2701683.9603 | 1234141.4346
73 | 2701646.1427 | 1234135.8193 | 2701645.531 | 1234159.6151
74 | 2701646.1427 | 1234135.8193 | 2701633.045 | 1234141.0262
75 | 2701693.8762 | 1234142.907 | 2701685.8057 | 1234141.7087
76 | 2701645.531 | 1234159.6151 | 2701645.3044 | 1234168.4294 | 2701646.0219 | 1234176.9369 | 2701646.8308 | 1234187.1623
77 | 2701617.4765 | 1234147.2155 | 2701633.045 | 1234141.0262
78 | 2701693.8762 | 1234142.907 | 2701699.0178 | 1234143.6705
79 | 2701646.8308 | 1234187.1623 | 2701646.8901 | 1234187.9125
80 | 2701617.4765 | 1234147.2155 | 2701611.0464 | 1234149.7718
81 | 2701701.8916 | 1234144.0972 | 2701699.0178 | 1234143.6705
82 | 2701646.8901 | 1234187.9125 | 2701647.0339 | 1234189.7293
83 | 2701594.2639 | 1234156.4437 | 2701611.0464 | 1234149.7718
84 | 2701710.6146 | 1234145.3924 | 2701701.8916 | 1234144.0972
85 | 2701624.0637 | 1234092.1824 | 2701619.0727 | 1234094.1241
86 | 2701784.9325 | 1234078.7963 | 2701784.9325 | 1234078.7963 | 2701783.4001 | 1234088.6886 | 2701780.3371 | 1234099.8049
87 | 2701751.9278 | 1234069.3235 | 2701765.0302 | 1234069.8251
88 | 2701776.2768 | 1234114.5411 | 2701780.3371 | 1234099.8049
89 | 2701740.1294 | 1234068.8717 | 2701751.9278 | 1234069.3235
90 | 2701776.2768 | 1234114.5411 | 2701774.0771 | 1234122.5242
91 | 2701774.0771 | 1234122.5242 | 2701767.6504 | 1234145.8485
92 | 2701719.6663 | 1234146.7365 | 2701715.946 | 1234146.1841
93 | 2701720.5539 | 1234146.8683 | 2701719.6663 | 1234146.7365
94 | 2701710.6146 | 1234145.3924 | 2701715.946 | 1234146.1841
95 | 2701727.9029 | 1234147.9595 | 2701720.5539 | 1234146.8683
96 | 2701727.9029 | 1234147.9595 | 2701729.0758 | 1234148.1337
97 | 2701731.8088 | 1234148.5395 | 2701729.0758 | 1234148.1337
98 | 2701731.8088 | 1234148.5395 | 2701740.3547 | 1234149.8084 | 2701753.0018 | 1234150.7793
99 | 2701766.5185 | 1234149.9565 | 2701759.001 | 1234151.2399 | 2701753.0018 | 1234150.7793
100 | 2701766.5185 | 1234149.9565 | 2701767.6504 | 1234145.8485
101 | 2701766.5185 | 1234149.9565 | 2701760.3698 | 1234160.17 | 2701759.1126 | 1234171.3556
102 | 2701758.9997 | 1234172.3606 | 2701759.1126 | 1234171.3556
103 | 2701758.1097 | 1234180.2797 | 2701758.9997 | 1234172.3606
104 | 2701739.4771 | 1234026.4676 | 2701738.3344 | 1234033.9426 | 2701725.909 | 1234032.1134
105 | 2701758.1097 | 1234180.2797 | 2701758.1097 | 1234180.2797 | 2701759.6099 | 1234182.8629
106 | 2701594.2639 | 1234156.4437 | 2701585.4947 | 1234159.9299
107 | 2701569.7221 | 1234166.2003 | 2701585.4947 | 1234159.9299
108 | 2701566.5803 | 1234167.4494 | 2701569.7221 | 1234166.2003
109 | 2701647.1412 | 1234191.0861 | 2701647.0339 | 1234189.7293
110 | 2701647.1412 | 1234191.0861 | 2701647.4224 | 1234194.6408 | 2701649.371 | 1234227.9716
111 | 2701580.4321 | 1234109.1567 | 2701578.0997 | 1234110.0641
112 | 2701580.4321 | 1234109.1567 | 2701600.5745 | 1234101.3205
113 | 2701603.1573 | 1234100.3157 | 2701600.5745 | 1234101.3205
114 | 2701603.1573 | 1234100.3157 | 2701619.0727 | 1234094.1241
115 | 2701766.6831 | 1234184.4932 | 2701762.7682 | 1234184.129 | 2701759.6099 | 1234182.8629 | 2701759.6099 | 1234182.8629
116 | 2701766.6831 | 1234184.4932 | 2701786.2136 | 1234186.3103
117 | 2701786.506 | 1234191.0741 | 2701787.3808 | 1234186.4189 | 2701786.2136 | 1234186.3103

## bus_geodata
| x | y | coords
0 | 2702064.5365 | 1233845.9114
1 | 2702143.2326 | 1233996.893
2 | 2701778.7627 | 1234070.3509
3 | 2702147.963 | 1234017.2451
4 | 2701784.184 | 1234077.7718
5 | 2701776.2454 | 1234070.2546
6 | 2701604.4524 | 1233993.5503
7 | 2701613.6825 | 1234016.1241
8 | 2701603.3934 | 1233990.9603
9 | 2701617.1338 | 1234024.848
10 | 2701597.4053 | 1233982.3043
11 | 2701625.891 | 1234048.4664
12 | 2701578.9885 | 1233991.3296
13 | 2701645.6583 | 1234088.0307
14 | 2701575.2984 | 1234011.5764
15 | 2701627.8294 | 1234090.7174
16 | 2701647.6999 | 1234102.7878
17 | 2701561.3021 | 1234044.447
18 | 2701445.2007 | 1234135.3415
19 | 2701482.1866 | 1234118.9458
20 | 2701444.3726 | 1234135.9461
21 | 2701500.6925 | 1234132.6199
22 | 2701416.5195 | 1234156.2185
23 | 2701511.5924 | 1234118.6067
24 | 2701476.9427 | 1234187.4888
25 | 2701364.9536 | 1234138.7366
26 | 2701539.5472 | 1234125.2315
27 | 2701485.4198 | 1234222.6488
28 | 2701543.7782 | 1234122.1369
29 | 2701542.8014 | 1234074.5478
30 | 2701549.3713 | 1234064.7006
31 | 2701520.9404 | 1234167.8479
32 | 2701526.4101 | 1234199.1757
33 | 2701487.0217 | 1234229.4812
34 | 2701519.7904 | 1234202.26
35 | 2701507.0339 | 1234036.2545
36 | 2701484.5745 | 1234022.6448
37 | 2701518.6058 | 1234048.4851
38 | 2701473.4475 | 1234016.2898
39 | 2701507.8408 | 1234056.4766
40 | 2701531.5031 | 1234056.9149
41 | 2701452.8617 | 1234021.073
42 | 2701495.7154 | 1234066.4413
43 | 2701399.4533 | 1234033.6852
44 | 2701452.8345 | 1234096.6497
45 | 2701557.261 | 1234051.3072
46 | 2701437.4814 | 1234254.3
47 | 2701464.4608 | 1234237.3202
48 | 2701560.5316 | 1234116.8987
49 | 2701529.643 | 1234209.0535
50 | 2701509.108 | 1234225.422
51 | 2701493.3657 | 1234256.2224
52 | 2701495.1505 | 1234263.7457
53 | 2701515.3167 | 1234255.9621
54 | 2701483.5297 | 1234278.3137
55 | 2701682.231 | 1234028.1605
56 | 2701686.0082 | 1234022.6462
57 | 2701673.9231 | 1234054.353
58 | 2701690.1269 | 1234022.4645
59 | 2701679.3106 | 1234071.8053
60 | 2701677.6244 | 1234072.5763
61 | 2701695.7289 | 1234067.1716
62 | 2701707.8273 | 1234067.6349
63 | 2701698.8581 | 1234050.5498
64 | 2701731.0174 | 1234068.5228
65 | 2701699.7334 | 1234045.9003
66 | 2701680.3383 | 1234140.8968
67 | 2701668.8531 | 1234139.1914
68 | 2701683.9603 | 1234141.4346
69 | 2701646.1427 | 1234135.8193
70 | 2701685.8057 | 1234141.7087
71 | 2701645.531 | 1234159.6151
72 | 2701633.045 | 1234141.0262
73 | 2701693.8762 | 1234142.907
74 | 2701646.8308 | 1234187.1623
75 | 2701617.4765 | 1234147.2155
76 | 2701699.0178 | 1234143.6705
77 | 2701646.8901 | 1234187.9125
78 | 2701611.0464 | 1234149.7718
79 | 2701701.8916 | 1234144.0972
80 | 2701624.0637 | 1234092.1824
81 | 2701784.9325 | 1234078.7963
82 | 2701765.0302 | 1234069.8251
83 | 2701780.3371 | 1234099.8049
84 | 2701751.9278 | 1234069.3235
85 | 2701776.2768 | 1234114.5411
86 | 2701740.1294 | 1234068.8717
87 | 2701774.0771 | 1234122.5242
88 | 2701719.6663 | 1234146.7365
89 | 2701715.946 | 1234146.1841
90 | 2701720.5539 | 1234146.8683
91 | 2701710.6146 | 1234145.3924
92 | 2701727.9029 | 1234147.9595
93 | 2701729.0758 | 1234148.1337
94 | 2701731.8088 | 1234148.5395
95 | 2701753.0018 | 1234150.7793
96 | 2701767.6504 | 1234145.8485
97 | 2701766.5185 | 1234149.9565
98 | 2701759.1126 | 1234171.3556
99 | 2701758.9997 | 1234172.3606
100 | 2701725.909 | 1234032.1134
101 | 2701739.4771 | 1234026.4676
102 | 2701758.1097 | 1234180.2797
103 | 2701594.2639 | 1234156.4437
104 | 2701585.4947 | 1234159.9299
105 | 2701569.7222 | 1234166.2003
106 | 2701647.0339 | 1234189.7293
107 | 2701647.1412 | 1234191.0861
108 | 2701649.371 | 1234227.9716
109 | 2701578.0997 | 1234110.0641
110 | 2701580.4321 | 1234109.1567
111 | 2701600.5745 | 1234101.3205
112 | 2701603.1573 | 1234100.3157
113 | 2701619.0727 | 1234094.1241
114 | 2701759.6099 | 1234182.8629
115 | 2701766.6831 | 1234184.4932
116 | 2701786.2136 | 1234186.3103
117 | 2701786.506 | 1234191.0741
118 | 2701566.5803 | 1234167.4494
119 | 2701646.1427 | 1234135.8193

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98515 | -0.286 | 0.0013247 | 0.00033201
1 | 0.98476 | -0.29368 | 0 | 0
2 | 0.98643 | -0.26094 | 0.0048329 | 0.0012112
3 | 0.98471 | -0.29463 | 0.0025081 | 0.00062858
4 | 0.98677 | -0.25447 | 0.00095972 | 0.00024053
5 | 0.98636 | -0.26232 | 0.0016997 | 0.00042599
6 | 0.9899 | -0.19339 | 0.0013163 | 0.00032989
7 | 0.99058 | -0.18015 | 0.0049132 | 0.0012314
8 | 0.98982 | -0.19485 | 0.0030779 | 0.00077139
9 | 0.99089 | -0.17425 | 0.0010554 | 0.00026451
10 | 0.98957 | -0.19979 | 0 | 0
11 | 0.99173 | -0.15794 | 0.0016231 | 0.00040679
12 | 0.98898 | -0.21122 | 0 | 0
13 | 0.99328 | -0.12803 | 0 | 0
14 | 0.98849 | -0.22082 | 0.0020469 | 0.00051301
15 | 0.992 | -0.15269 | 0.0011952 | 0.00029954
16 | 0.99484 | -0.098236 | 0.0041746 | 0.0010463
17 | 0.98769 | -0.23627 | 0.0025768 | 0.00064581
18 | 0.98182 | -0.34983 | 0.0056932 | 0.0014269
19 | 0.98268 | -0.33292 | 0.0058237 | 0.0014596
20 | 0.9818 | -0.35014 | 0.0053014 | 0.0013286
21 | 0.9833 | -0.32091 | 0 | 0
22 | 0.98144 | -0.35725 | 0.0057195 | 0.0014334
23 | 0.98425 | -0.30241 | 0 | 0
24 | 0.98159 | -0.35416 | 0 | 0
25 | 0.98115 | -0.36285 | 0.0056786 | 0.0014232
26 | 0.98627 | -0.26314 | 0.0015706 | 0.00039362
27 | 0.9806 | -0.37362 | 0 | 0
28 | 0.98656 | -0.25748 | 0.0019518 | 0.00048916
29 | 0.98724 | -0.24501 | 0.0017792 | 0.0004459
30 | 0.98726 | -0.24464 | 0 | 0
31 | 0.97984 | -0.3886 | 0.0049341 | 0.0012366
32 | 0.98003 | -0.38476 | 0 | 0
33 | 0.9805 | -0.37565 | 0 | 0
34 | 0.98009 | -0.38359 | 0.0049123 | 0.0012311
35 | 0.98661 | -0.25732 | 0.0019414 | 0.00048655
36 | 0.98649 | -0.25955 | 0.00014166 | 3.5503e-05
37 | 0.98671 | -0.25527 | 0 | 0
38 | 0.98644 | -0.26063 | 0 | 0
39 | 0.98659 | -0.25766 | 0.0060866 | 0.0015254
40 | 0.98695 | -0.25067 | 0.00069985 | 0.0001754
41 | 0.98635 | -0.26236 | 9.3403e-05 | 2.3409e-05
42 | 0.98654 | -0.25874 | 0.0001445 | 3.6215e-05
43 | 0.98612 | -0.26677 | 0.0044845 | 0.0011239
44 | 0.98636 | -0.26223 | 0.0037029 | 0.00092803
45 | 0.98753 | -0.23933 | 0.0024358 | 0.00061048
46 | 0.98039 | -0.37771 | 0.0011523 | 0.00028879
47 | 0.98043 | -0.37705 | 0.0018838 | 0.00047213
48 | 0.98756 | -0.23805 | 0.0013872 | 0.00034767
49 | 0.98 | -0.38549 | 0.0038334 | 0.00096075
50 | 0.9804 | -0.37749 | 0.0042133 | 0.0010559
51 | 0.98027 | -0.38002 | 0.0012634 | 0.00031664
52 | 0.98022 | -0.38107 | 0 | 0
53 | 0.9801 | -0.3834 | 0.0059268 | 0.0014854
54 | 0.98019 | -0.3816 | 0.0015686 | 0.00039313
55 | 0.98411 | -0.30631 | 0.0020907 | 0.00052399
56 | 0.98409 | -0.30672 | 0.0018877 | 0.0004731
57 | 0.98425 | -0.30347 | 0.0034632 | 0.00086797
58 | 0.98408 | -0.3068 | 0.0010818 | 0.00027112
59 | 0.9844 | -0.30067 | 0 | 0
60 | 0.98439 | -0.30071 | 0.0013931 | 0.00034914
61 | 0.98456 | -0.29756 | 0 | 0
62 | 0.98478 | -0.29311 | 0.0016707 | 0.00041871
63 | 0.98439 | -0.30077 | 0.0012556 | 0.00031468
64 | 0.98526 | -0.28388 | 0.0012556 | 0.00031468
65 | 0.98435 | -0.30156 | 0.0026991 | 0.00067646
66 | 0.99558 | -0.084383 | 0.0031317 | 0.00078489
67 | 0.99651 | -0.066499 | 0.0030118 | 0.00075483
68 | 0.99529 | -0.089827 | 0.0016996 | 0.00042595
69 | 0.99842 | -0.030027 | 0 | 0
70 | 0.99515 | -0.092547 | 0.0022222 | 0.00055694
71 | 0.99764 | -0.044955 | 0.0041159 | 0.0010316
72 | 1 | 0 | -0.26859 | -0.067928
73 | 0.99455 | -0.10413 | 0.0020739 | 0.00051977
74 | 0.99685 | -0.060308 | 0.0022212 | 0.00055669
75 | 0.99969 | -0.0059076 | 0.0069724 | 0.0017475
76 | 0.99417 | -0.11133 | 0.001982 | 0.00049674
77 | 0.99683 | -0.060697 | 0.0022558 | 0.00056536
78 | 0.99961 | -0.007507 | 0.0034997 | 0.00087711
79 | 0.99397 | -0.11525 | 0.00061188 | 0.00015335
80 | 0.99172 | -0.15799 | 0.0032308 | 0.00080972
81 | 0.98681 | -0.25356 | 0.0020032 | 0.00050204
82 | 0.98606 | -0.26814 | 0.001593 | 0.00039925
83 | 0.98765 | -0.23728 | 0.0018571 | 0.00046544
84 | 0.98573 | -0.27456 | 0.0014227 | 0.00035656
85 | 0.98827 | -0.22524 | 0.0023456 | 0.00058786
86 | 0.98545 | -0.28005 | 0.0025077 | 0.00062849
87 | 0.98862 | -0.21837 | 0.0018395 | 0.00046102
88 | 0.99273 | -0.13898 | 0.0013211 | 0.0003311
89 | 0.99299 | -0.13413 | 0.001329 | 0.00033307
90 | 0.99267 | -0.14011 | 0.0017647 | 0.00044228
91 | 0.99335 | -0.12707 | 0.0018019 | 0.0004516
92 | 0.9922 | -0.14928 | 0.0012863 | 0.00032239
93 | 0.99212 | -0.15071 | 0.0017837 | 0.00044704
94 | 0.99196 | -0.15398 | 0.0017644 | 0.0004422
95 | 0.99068 | -0.17852 | 0.0023103 | 0.00057902
96 | 0.9897 | -0.19756 | 0.0026364 | 0.00066074
97 | 0.9899 | -0.19369 | 0 | 0
98 | 0.98965 | -0.19849 | 0.0019935 | 0.00049961
99 | 0.98964 | -0.19867 | 0.0017983 | 0.00045069
100 | 0.98412 | -0.30597 | 0.0032685 | 0.00081915
101 | 0.98406 | -0.30717 | 0.0033176 | 0.00083148
102 | 0.98959 | -0.19978 | 0.0012924 | 0.00032392
103 | 0.99945 | -0.01058 | 0.003545 | 0.00088845
104 | 0.9994 | -0.011602 | 0.00157 | 0.00039349
105 | 0.99933 | -0.012975 | 0.0027849 | 0.00069797
106 | 0.99678 | -0.061568 | 0.0019989 | 0.00050098
107 | 0.99675 | -0.062171 | 0.0022152 | 0.00055517
108 | 0.99598 | -0.077114 | 0.023031 | 0.0057721
109 | 0.98866 | -0.21691 | 0.00088184 | 0.00022101
110 | 0.98881 | -0.21407 | 0.0011135 | 0.00027907
111 | 0.9901 | -0.18912 | 0.0021412 | 0.00053664
112 | 0.99027 | -0.18582 | 0.0026433 | 0.00066247
113 | 0.99137 | -0.16472 | 0.0011952 | 0.00029955
114 | 0.98957 | -0.20013 | 0.0019105 | 0.00047882
115 | 0.98954 | -0.20074 | 0.0016186 | 0.00040565
116 | 0.98948 | -0.20179 | 0.0016341 | 0.00040956
117 | 0.98947 | -0.20194 | 0.0013902 | 0.00034842
118 | 0.99932 | -0.013084 | 0.0018507 | 0.00046383
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0025091 | 0.0006268 | -0.0025082 | -0.00062838 | 9.1687e-07 | -1.5802e-06 | 0.0037891 | 0.0037899 | 0.0037899 | 0.98515 | -0.286 | 0.98476 | -0.29368 | 1.0412
1 | -0.0038338 | -0.00095882 | 0.0038384 | 0.00095711 | 4.567e-06 | -1.7099e-06 | 0.0057901 | 0.0057884 | 0.0057901 | 0.98515 | -0.286 | 0.98643 | -0.26094 | 1.5907
2 | 0.0025082 | 0.00062838 | -0.0025081 | -0.00062858 | 1.1254e-07 | -1.9378e-07 | 0.0037899 | 0.00379 | 0.00379 | 0.98476 | -0.29368 | 0.98471 | -0.29463 | 1.0412
3 | -0.039328 | -0.0098683 | 0.039341 | 0.009876 | 1.2131e-05 | 7.6467e-06 | 0.05933 | 0.05933 | 0.05933 | 0.98643 | -0.26094 | 0.98677 | -0.25447 | 16.2996
4 | 0.030657 | 0.0077 | -0.030655 | -0.0076987 | 2.0208e-06 | 1.2612e-06 | 0.046252 | 0.046252 | 0.046252 | 0.98643 | -0.26094 | 0.98636 | -0.26232 | 12.7065
5 | -0.0403 | -0.010116 | 0.040302 | 0.010118 | 1.7575e-06 | 1.1086e-06 | 0.060778 | 0.060778 | 0.060778 | 0.98677 | -0.25447 | 0.98681 | -0.25356 | 16.6971
6 | 0.028955 | 0.0072727 | -0.028947 | -0.0072677 | 8.0329e-06 | 4.9978e-06 | 0.043687 | 0.043688 | 0.043688 | 0.98636 | -0.26232 | 0.98606 | -0.26814 | 12.0021
7 | -0.030601 | -0.0076931 | 0.03062 | 0.0077052 | 1.9359e-05 | 1.2076e-05 | 0.046008 | 0.046008 | 0.046008 | 0.9899 | -0.19339 | 0.99058 | -0.18015 | 12.6396
8 | 0.029285 | 0.0073633 | -0.029283 | -0.007362 | 2.0342e-06 | 1.2659e-06 | 0.044029 | 0.044029 | 0.044029 | 0.9899 | -0.19339 | 0.98982 | -0.19485 | 12.096
9 | -0.035534 | -0.0089366 | 0.035544 | 0.0089429 | 1.0029e-05 | 6.2978e-06 | 0.053388 | 0.053388 | 0.053388 | 0.99058 | -0.18015 | 0.99089 | -0.17425 | 14.6671
10 | 0.026205 | 0.0065906 | -0.026199 | -0.0065868 | 6.1876e-06 | 3.8235e-06 | 0.039402 | 0.039402 | 0.039402 | 0.98982 | -0.19485 | 0.98957 | -0.19979 | 10.8248
11 | -0.036599 | -0.0092074 | 0.036628 | 0.0092253 | 2.8547e-05 | 1.7945e-05 | 0.054973 | 0.054973 | 0.054973 | 0.99089 | -0.17425 | 0.99173 | -0.15794 | 15.1025
12 | 0.026199 | 0.0065868 | -0.026184 | -0.0065779 | 1.4289e-05 | 8.8299e-06 | 0.039402 | 0.039403 | 0.039403 | 0.98957 | -0.19979 | 0.98898 | -0.21122 | 10.8249
13 | -0.038251 | -0.0096321 | 0.038305 | 0.0096666 | 5.4783e-05 | 3.4488e-05 | 0.057408 | 0.057408 | 0.057408 | 0.99173 | -0.15794 | 0.99328 | -0.12803 | 15.7715
14 | 0.026184 | 0.0065779 | -0.026172 | -0.0065705 | 1.1985e-05 | 7.4065e-06 | 0.039403 | 0.039403 | 0.039403 | 0.98898 | -0.21122 | 0.98849 | -0.22082 | 10.8249
15 | 0.075942 | 0.019307 | -0.075852 | -0.01925 | 9.0111e-05 | 5.7432e-05 | 0.11387 | 0.11387 | 0.11387 | 0.99328 | -0.12803 | 0.992 | -0.15269 | 31.2817
16 | -0.11425 | -0.028974 | 0.11441 | 0.029079 | 0.00016388 | 0.00010469 | 0.17127 | 0.17127 | 0.17127 | 0.99328 | -0.12803 | 0.99484 | -0.098236 | 47.0531
17 | 0.024126 | 0.0060575 | -0.024108 | -0.0060466 | 1.7775e-05 | 1.0916e-05 | 0.036321 | 0.036321 | 0.036321 | 0.98849 | -0.22082 | 0.98769 | -0.23627 | 9.9784
18 | 0.074657 | 0.01895 | -0.074638 | -0.018938 | 1.9032e-05 | 1.2128e-05 | 0.11207 | 0.11207 | 0.11207 | 0.992 | -0.15269 | 0.99172 | -0.15799 | 30.7891
19 | -0.11859 | -0.030125 | 0.11898 | 0.030375 | 0.00039077 | 0.00024966 | 0.17752 | 0.17752 | 0.17752 | 0.99484 | -0.098236 | 0.99842 | -0.030027 | 48.7685
20 | 0.021531 | 0.0054008 | -0.021528 | -0.0053989 | 3.1419e-06 | 1.9089e-06 | 0.032439 | 0.032439 | 0.032439 | 0.98769 | -0.23627 | 0.98753 | -0.23933 | 8.9119
21 | -0.022398 | -0.0056146 | 0.022416 | 0.0056256 | 1.8067e-05 | 1.1034e-05 | 0.033947 | 0.033947 | 0.033947 | 0.98182 | -0.34983 | 0.98268 | -0.33292 | 9.326
22 | 0.016705 | 0.0041878 | -0.016705 | -0.0041876 | 2.4647e-07 | 1.4477e-07 | 0.025318 | 0.025318 | 0.025318 | 0.98182 | -0.34983 | 0.9818 | -0.35014 | 6.9555
23 | -0.02824 | -0.0070852 | 0.028256 | 0.0070953 | 1.6177e-05 | 1.0054e-05 | 0.042765 | 0.042765 | 0.042765 | 0.98268 | -0.33292 | 0.9833 | -0.32091 | 11.7486
24 | 0.011404 | 0.002859 | -0.0114 | -0.0028569 | 3.859e-06 | 2.0343e-06 | 0.017283 | 0.017284 | 0.017284 | 0.9818 | -0.35014 | 0.98144 | -0.35725 | 4.7483
25 | -0.058032 | -0.014587 | 0.058084 | 0.01462 | 5.1313e-05 | 3.2615e-05 | 0.087835 | 0.087835 | 0.087835 | 0.9833 | -0.32091 | 0.98425 | -0.30241 | 24.1305
26 | 0.029776 | 0.0074922 | -0.029729 | -0.0074627 | 4.7231e-05 | 2.9443e-05 | 0.04507 | 0.04507 | 0.04507 | 0.9833 | -0.32091 | 0.98159 | -0.35416 | 12.382
27 | 0.0056801 | 0.0014235 | -0.0056786 | -0.0014232 | 1.5144e-06 | 2.8134e-07 | 0.008612 | 0.0086122 | 0.0086122 | 0.98144 | -0.35725 | 0.98115 | -0.36285 | 2.366
28 | -0.058084 | -0.01462 | 0.058193 | 0.014689 | 0.00010926 | 6.9444e-05 | 0.087835 | 0.087835 | 0.087835 | 0.98425 | -0.30241 | 0.98627 | -0.26314 | 24.1305
29 | 0.029729 | 0.0074627 | -0.029701 | -0.0074456 | 2.7556e-05 | 1.7179e-05 | 0.04507 | 0.045071 | 0.045071 | 0.98159 | -0.35416 | 0.9806 | -0.37362 | 12.382
30 | -0.059763 | -0.015083 | 0.05978 | 0.015093 | 1.6204e-05 | 1.0303e-05 | 0.090204 | 0.090204 | 0.090204 | 0.98627 | -0.26314 | 0.98656 | -0.25748 | 24.7815
31 | 0.016013 | 0.0040132 | -0.016012 | -0.0040123 | 1.5539e-06 | 9.0597e-07 | 0.024299 | 0.024299 | 0.024299 | 0.9806 | -0.37362 | 0.9805 | -0.37565 | 6.6757
32 | 0.013688 | 0.0034323 | -0.013681 | -0.0034287 | 6.5026e-06 | 3.6549e-06 | 0.020771 | 0.020771 | 0.020771 | 0.9806 | -0.37362 | 0.98009 | -0.38359 | 5.7064
33 | -0.061731 | -0.015583 | 0.061789 | 0.015619 | 5.7493e-05 | 3.6569e-05 | 0.093148 | 0.093148 | 0.093148 | 0.98656 | -0.25748 | 0.98756 | -0.23805 | 25.5902
34 | -0.0017792 | -0.0004459 | 0.0017792 | 0.00044577 | 3.1922e-08 | -1.3094e-07 | 0.0026816 | 0.0026816 | 0.0026816 | 0.98724 | -0.24501 | 0.98726 | -0.24464 | 0.73671
35 | -0.019087 | -0.0047855 | 0.019092 | 0.0047884 | 4.8246e-06 | 2.8889e-06 | 0.028769 | 0.028769 | 0.028769 | 0.98726 | -0.24464 | 0.98753 | -0.23933 | 7.9036
36 | 0.017308 | 0.0043398 | -0.017303 | -0.0043368 | 4.9763e-06 | 2.9356e-06 | 0.026088 | 0.026088 | 0.026088 | 0.98726 | -0.24464 | 0.98695 | -0.25067 | 7.1669
37 | -0.0049341 | -0.0012366 | 0.004935 | 0.0012366 | 9.0269e-07 | 3.7586e-08 | 0.0074931 | 0.0074929 | 0.0074931 | 0.97984 | -0.3886 | 0.98003 | -0.38476 | 2.0585
38 | -0.0087686 | -0.0021973 | 0.0087691 | 0.0021976 | 4.9086e-07 | 2.2109e-07 | 0.013314 | 0.013313 | 0.013314 | 0.98003 | -0.38476 | 0.98009 | -0.38359 | 3.6576
39 | 0.0038336 | 0.0009607 | -0.0038334 | -0.00096075 | 1.3302e-07 | -4.6788e-08 | 0.0058206 | 0.0058207 | 0.0058207 | 0.98003 | -0.38476 | 0.98 | -0.38549 | 1.5991
40 | 0.0042136 | 0.0010559 | -0.0042133 | -0.0010559 | 3.6875e-07 | -6.7267e-08 | 0.0063946 | 0.0063947 | 0.0063947 | 0.9805 | -0.37565 | 0.9804 | -0.37749 | 1.7568
41 | 0.0087617 | 0.0021961 | -0.0087599 | -0.0021952 | 1.8223e-06 | 8.1969e-07 | 0.013297 | 0.013297 | 0.013297 | 0.9805 | -0.37565 | 0.98027 | -0.38002 | 3.653
42 | 0.0030364 | 0.00076036 | -0.0030362 | -0.00076055 | 2.0141e-07 | -1.9012e-07 | 0.0046078 | 0.0046079 | 0.0046079 | 0.9805 | -0.37565 | 0.98043 | -0.37705 | 1.2659
43 | 0.0047216 | 0.0011827 | -0.0047211 | -0.0011827 | 5.0265e-07 | -1.5831e-08 | 0.0071209 | 0.007121 | 0.007121 | 0.98661 | -0.25732 | 0.98649 | -0.25955 | 1.9563
44 | -0.0066629 | -0.0016692 | 0.0066636 | 0.0016694 | 6.5063e-07 | 1.9696e-07 | 0.010049 | 0.010049 | 0.010049 | 0.98661 | -0.25732 | 0.98671 | -0.25527 | 2.7607
45 | 0.0045794 | 0.0011472 | -0.0045792 | -0.0011472 | 2.3399e-07 | -1.7208e-08 | 0.0069073 | 0.0069074 | 0.0069074 | 0.98649 | -0.25955 | 0.98644 | -0.26063 | 1.8976
46 | 0.0099359 | 0.0024899 | -0.0099348 | -0.0024893 | 1.1318e-06 | 5.5268e-07 | 0.014984 | 0.014984 | 0.014984 | 0.98671 | -0.25527 | 0.98659 | -0.25766 | 4.1164
47 | -0.0166 | -0.0041593 | 0.016603 | 0.0041614 | 3.6362e-06 | 2.1295e-06 | 0.025033 | 0.025032 | 0.025033 | 0.98671 | -0.25527 | 0.98695 | -0.25067 | 6.8771
48 | 0.0045792 | 0.0011472 | -0.0045788 | -0.0011472 | 3.7815e-07 | -2.7764e-08 | 0.0069074 | 0.0069075 | 0.0069075 | 0.98644 | -0.26063 | 0.98635 | -0.26236 | 1.8977
49 | 0.0038482 | 0.00096389 | -0.003848 | -0.00096396 | 1.9825e-07 | -7.3527e-08 | 0.0058038 | 0.0058039 | 0.0058039 | 0.98659 | -0.25766 | 0.98654 | -0.25874 | 1.5945
50 | 0.0044854 | 0.0011238 | -0.0044845 | -0.0011239 | 9.4229e-07 | -9.7214e-08 | 0.0067666 | 0.0067668 | 0.0067668 | 0.98635 | -0.26236 | 0.98612 | -0.26677 | 1.859
51 | 0.0037035 | 0.00092775 | -0.0037029 | -0.00092803 | 6.1462e-07 | -2.7719e-07 | 0.0055859 | 0.0055861 | 0.0055861 | 0.98654 | -0.25874 | 0.98636 | -0.26223 | 1.5347
52 | -0.0011523 | -0.00028879 | 0.0011523 | 0.00028841 | 3.6563e-08 | -3.7861e-07 | 0.0017489 | 0.0017488 | 0.0017489 | 0.98039 | -0.37771 | 0.98043 | -0.37705 | 0.48047
53 | -0.063176 | -0.015967 | 0.06324 | 0.016008 | 6.4119e-05 | 4.0794e-05 | 0.095238 | 0.095238 | 0.095238 | 0.98756 | -0.23805 | 0.98866 | -0.21691 | 26.1644
54 | 0.0074965 | 0.0018786 | -0.0074961 | -0.0018785 | 3.7546e-07 | 1.4282e-07 | 0.011379 | 0.011379 | 0.011379 | 0.98027 | -0.38002 | 0.98022 | -0.38107 | 3.1262
55 | 0.0059275 | 0.0014855 | -0.0059268 | -0.0014854 | 6.5633e-07 | 1.476e-07 | 0.0089981 | 0.0089982 | 0.0089982 | 0.98022 | -0.38107 | 0.9801 | -0.3834 | 2.472
56 | 0.0015686 | 0.00039292 | -0.0015686 | -0.00039313 | 3.9624e-08 | -2.0954e-07 | 0.0023812 | 0.0023813 | 0.0023813 | 0.98022 | -0.38107 | 0.98019 | -0.3816 | 0.65419
57 | 0.0029695 | 0.00074411 | -0.0029695 | -0.00074417 | 5.7698e-08 | -6.0038e-08 | 0.00449 | 0.0044901 | 0.0044901 | 0.98411 | -0.30631 | 0.98409 | -0.30672 | 1.2335
58 | -0.0050603 | -0.0012681 | 0.005061 | 0.0012681 | 6.8578e-07 | 4.1939e-08 | 0.0076513 | 0.0076512 | 0.0076513 | 0.98411 | -0.30631 | 0.98425 | -0.30347 | 2.102
59 | 0.0010818 | 0.00027107 | -0.0010818 | -0.00027112 | 4.1366e-09 | -4.9731e-08 | 0.0016357 | 0.0016357 | 0.0016357 | 0.98409 | -0.30672 | 0.98408 | -0.3068 | 0.44938
60 | -0.0085242 | -0.0021361 | 0.0085253 | 0.0021366 | 1.1375e-06 | 4.9583e-07 | 0.012887 | 0.012887 | 0.012887 | 0.98425 | -0.30347 | 0.9844 | -0.30067 | 3.5404
61 | 0.0013931 | 0.00034911 | -0.0013931 | -0.00034914 | 3.0829e-09 | -2.1597e-08 | 0.0021058 | 0.0021058 | 0.0021058 | 0.9844 | -0.30067 | 0.98439 | -0.30071 | 0.57851
62 | -0.0099184 | -0.0024857 | 0.0099199 | 0.0024864 | 1.4695e-06 | 7.188e-07 | 0.014993 | 0.014993 | 0.014993 | 0.9844 | -0.30067 | 0.98456 | -0.29756 | 4.1189
63 | -0.020464 | -0.0051295 | 0.020469 | 0.0051321 | 4.3432e-06 | 2.6256e-06 | 0.030929 | 0.030929 | 0.030929 | 0.98456 | -0.29756 | 0.98478 | -0.29311 | 8.497
64 | 0.010544 | 0.002643 | -0.010543 | -0.0026422 | 1.6109e-06 | 8.1589e-07 | 0.015936 | 0.015936 | 0.015936 | 0.98456 | -0.29756 | 0.98439 | -0.30077 | 4.3782
65 | -0.022139 | -0.0055508 | 0.022149 | 0.0055567 | 9.7394e-06 | 5.9378e-06 | 0.033453 | 0.033453 | 0.033453 | 0.98478 | -0.29311 | 0.98526 | -0.28388 | 9.1905
66 | 0.0092871 | 0.0023275 | -0.0092868 | -0.0023274 | 3.4966e-07 | 1.6364e-07 | 0.014039 | 0.014039 | 0.014039 | 0.98439 | -0.30077 | 0.98435 | -0.30156 | 3.8567
67 | -0.023405 | -0.0058714 | 0.023409 | 0.005874 | 4.2729e-06 | 2.6185e-06 | 0.03535 | 0.03535 | 0.03535 | 0.98526 | -0.28388 | 0.98545 | -0.28005 | 9.7114
68 | 0.0065877 | 0.0016509 | -0.0065863 | -0.0016505 | 1.3841e-06 | 4.1282e-07 | 0.0099583 | 0.0099585 | 0.0099585 | 0.98435 | -0.30156 | 0.98412 | -0.30597 | 2.7359
69 | -0.088216 | -0.022323 | 0.088292 | 0.022371 | 7.5783e-05 | 4.835e-05 | 0.13193 | 0.13193 | 0.13193 | 0.99558 | -0.084383 | 0.99651 | -0.066499 | 36.2435
70 | 0.085085 | 0.021538 | -0.085062 | -0.021523 | 2.2233e-05 | 1.4181e-05 | 0.12725 | 0.12725 | 0.12725 | 0.99558 | -0.084383 | 0.99529 | -0.089827 | 34.9576
71 | -0.091304 | -0.023126 | 0.091464 | 0.023228 | 0.00016024 | 0.00010225 | 0.13642 | 0.13642 | 0.13642 | 0.99651 | -0.066499 | 0.99842 | -0.030027 | 37.479
72 | 0.083363 | 0.021098 | -0.083352 | -0.021091 | 1.088e-05 | 6.9387e-06 | 0.1247 | 0.1247 | 0.1247 | 0.99529 | -0.089827 | 0.99515 | -0.092547 | 34.2595
73 | 0.035906 | 0.009024 | -0.03588 | -0.0090079 | 2.557e-05 | 1.6054e-05 | 0.053522 | 0.053522 | 0.053522 | 0.99842 | -0.030027 | 0.99764 | -0.044955 | 14.7038
74 | -0.24635 | -0.062627 | 0.2467 | 0.062855 | 0.00035685 | 0.00022801 | 0.36746 | 0.36746 | 0.36746 | 0.99842 | -0.030027 | 1 | 0 | 50.4755
75 | 0.08113 | 0.020534 | -0.081085 | -0.020505 | 4.5079e-05 | 2.8745e-05 | 0.12138 | 0.12138 | 0.12138 | 0.99515 | -0.092547 | 0.99455 | -0.10413 | 33.3467
76 | 0.031764 | 0.0079764 | -0.031741 | -0.0079618 | 2.3247e-05 | 1.4518e-05 | 0.047383 | 0.047383 | 0.047383 | 0.99764 | -0.044955 | 0.99685 | -0.060308 | 13.0173
77 | 0.020231 | 0.005073 | -0.020226 | -0.0050695 | 5.6943e-06 | 3.4246e-06 | 0.030106 | 0.030106 | 0.030106 | 1 | 0 | 0.99969 | -0.0059076 | 8.2708
78 | 0.079011 | 0.019985 | -0.078984 | -0.019968 | 2.727e-05 | 1.7385e-05 | 0.11828 | 0.11828 | 0.11828 | 0.99455 | -0.10413 | 0.99417 | -0.11133 | 32.4942
79 | 0.02952 | 0.0074051 | -0.029519 | -0.0074048 | 5.4803e-07 | 3.4093e-07 | 0.044067 | 0.044067 | 0.044067 | 0.99685 | -0.060308 | 0.99683 | -0.060697 | 12.1064
80 | 0.013253 | 0.0033221 | -0.013252 | -0.0033215 | 1.0098e-06 | 5.5558e-07 | 0.019727 | 0.019728 | 0.019728 | 0.99969 | -0.0059076 | 0.99961 | -0.007507 | 5.4196
81 | 0.077002 | 0.019471 | -0.076987 | -0.019462 | 1.4487e-05 | 9.2339e-06 | 0.11531 | 0.11531 | 0.11531 | 0.99417 | -0.11133 | 0.99397 | -0.11525 | 31.6792
82 | 0.027263 | 0.0068394 | -0.027262 | -0.0068387 | 1.1321e-06 | 7.0077e-07 | 0.0407 | 0.0407 | 0.0407 | 0.99683 | -0.060697 | 0.99678 | -0.061568 | 11.1813
83 | 0.0097527 | 0.0024444 | -0.0097512 | -0.0024437 | 1.4274e-06 | 6.7685e-07 | 0.014518 | 0.014518 | 0.014518 | 0.99961 | -0.007507 | 0.99945 | -0.01058 | 3.9884
84 | 0.076375 | 0.019308 | -0.076332 | -0.019281 | 4.3277e-05 | 2.7583e-05 | 0.1144 | 0.1144 | 0.1144 | 0.99397 | -0.11525 | 0.99335 | -0.12707 | 31.4276
85 | 0.071407 | 0.018129 | -0.071384 | -0.018114 | 2.3089e-05 | 1.4708e-05 | 0.10722 | 0.10722 | 0.10722 | 0.99172 | -0.15799 | 0.99137 | -0.16472 | 29.4574
86 | -0.042305 | -0.01062 | 0.042338 | 0.01064 | 3.2878e-05 | 2.0767e-05 | 0.063798 | 0.063798 | 0.063798 | 0.98681 | -0.25356 | 0.98765 | -0.23728 | 17.527
87 | 0.027354 | 0.0068685 | -0.027346 | -0.0068633 | 8.3802e-06 | 5.1962e-06 | 0.041284 | 0.041284 | 0.041284 | 0.98606 | -0.26814 | 0.98573 | -0.27456 | 11.3417
88 | -0.044195 | -0.011106 | 0.044221 | 0.011122 | 2.5422e-05 | 1.6074e-05 | 0.066596 | 0.066596 | 0.066596 | 0.98765 | -0.23728 | 0.98827 | -0.22524 | 18.2956
89 | 0.025923 | 0.0065067 | -0.025917 | -0.0065025 | 6.7815e-06 | 4.1897e-06 | 0.039136 | 0.039136 | 0.039136 | 0.98573 | -0.27456 | 0.98545 | -0.28005 | 10.7517
90 | -0.046566 | -0.01171 | 0.046582 | 0.011719 | 1.5271e-05 | 9.6674e-06 | 0.070128 | 0.070128 | 0.070128 | 0.98827 | -0.22524 | 0.98862 | -0.21837 | 19.2658
91 | -0.048421 | -0.01218 | 0.048469 | 0.012211 | 4.821e-05 | 3.0544e-05 | 0.072896 | 0.072896 | 0.072896 | 0.98862 | -0.21837 | 0.9897 | -0.19756 | 20.0265
92 | -0.073159 | -0.018469 | 0.073176 | 0.01848 | 1.6975e-05 | 1.0815e-05 | 0.10971 | 0.10971 | 0.10971 | 0.99273 | -0.13898 | 0.99299 | -0.13413 | 30.139
93 | 0.071838 | 0.018138 | -0.071834 | -0.018136 | 3.9048e-06 | 2.4875e-06 | 0.10773 | 0.10773 | 0.10773 | 0.99273 | -0.13898 | 0.99267 | -0.14011 | 29.5949
94 | -0.074505 | -0.018813 | 0.07453 | 0.018829 | 2.5217e-05 | 1.6069e-05 | 0.1117 | 0.1117 | 0.1117 | 0.99299 | -0.13413 | 0.99335 | -0.12707 | 30.6861
95 | 0.070069 | 0.017693 | -0.070038 | -0.017674 | 3.0764e-05 | 1.9593e-05 | 0.10508 | 0.10508 | 0.10508 | 0.99267 | -0.14011 | 0.9922 | -0.14928 | 28.8682
96 | 0.068752 | 0.017351 | -0.068747 | -0.017348 | 4.7313e-06 | 3.0127e-06 | 0.10315 | 0.10315 | 0.10315 | 0.9922 | -0.14928 | 0.99212 | -0.15071 | 28.3382
97 | 0.066964 | 0.016901 | -0.066953 | -0.016895 | 1.046e-05 | 6.6587e-06 | 0.10048 | 0.10048 | 0.10048 | 0.99212 | -0.15071 | 0.99196 | -0.15398 | 27.6033
98 | 0.065189 | 0.016453 | -0.065112 | -0.016404 | 7.653e-05 | 4.8705e-05 | 0.097829 | 0.097829 | 0.097829 | 0.99196 | -0.15398 | 0.99068 | -0.17852 | 26.8762
99 | 0.062802 | 0.015825 | -0.062756 | -0.015796 | 4.5553e-05 | 2.8978e-05 | 0.094359 | 0.094359 | 0.094359 | 0.99068 | -0.17852 | 0.9899 | -0.19369 | 25.9229
100 | -0.051106 | -0.012872 | 0.051115 | 0.012878 | 9.4395e-06 | 5.9865e-06 | 0.07686 | 0.07686 | 0.07686 | 0.9897 | -0.19756 | 0.9899 | -0.19369 | 21.1154
101 | 0.011641 | 0.0029181 | -0.011639 | -0.0029167 | 2.6616e-06 | 1.4055e-06 | 0.017499 | 0.017499 | 0.017499 | 0.9899 | -0.19369 | 0.98965 | -0.19849 | 4.8075
102 | 0.009645 | 0.0024171 | -0.009645 | -0.002417 | 7.9755e-08 | 3.8049e-08 | 0.014502 | 0.014502 | 0.014502 | 0.98965 | -0.19849 | 0.98964 | -0.19867 | 3.9841
103 | 0.0078467 | 0.0019663 | -0.0078463 | -0.0019662 | 4.1597e-07 | 1.6383e-07 | 0.011798 | 0.011798 | 0.011798 | 0.98964 | -0.19867 | 0.98959 | -0.19978 | 3.2412
104 | 0.0033178 | 0.00083134 | -0.0033176 | -0.00083148 | 1.8989e-07 | -1.3411e-07 | 0.0050165 | 0.0050166 | 0.0050166 | 0.98412 | -0.30597 | 0.98406 | -0.30717 | 1.3782
105 | 0.0065538 | 0.0016422 | -0.0065537 | -0.0016422 | 1.0879e-07 | 3.1248e-08 | 0.0098547 | 0.0098547 | 0.0098547 | 0.98959 | -0.19978 | 0.98957 | -0.20013 | 2.7073
106 | 0.0062063 | 0.0015553 | -0.006206 | -0.0015552 | 3.0214e-07 | 6.9708e-08 | 0.0092401 | 0.0092401 | 0.0092401 | 0.99945 | -0.01058 | 0.9994 | -0.011602 | 2.5385
107 | 0.0046359 | 0.0011617 | -0.0046356 | -0.0011618 | 3.0326e-07 | -2.8308e-08 | 0.0069025 | 0.0069026 | 0.0069026 | 0.9994 | -0.011602 | 0.99933 | -0.012975 | 1.8963
108 | 0.0018507 | 0.00046379 | -0.0018507 | -0.00046383 | 9.6286e-09 | -3.8135e-08 | 0.0027557 | 0.0027557 | 0.0027557 | 0.99933 | -0.012975 | 0.99932 | -0.013084 | 0.75707
109 | 0.025263 | 0.0063378 | -0.025263 | -0.0063373 | 7.2604e-07 | 4.4692e-07 | 0.037716 | 0.037716 | 0.037716 | 0.99678 | -0.061568 | 0.99675 | -0.062171 | 10.3615
110 | 0.023047 | 0.0057821 | -0.023031 | -0.0057721 | 1.6407e-05 | 1.0019e-05 | 0.034409 | 0.034409 | 0.034409 | 0.99675 | -0.062171 | 0.99598 | -0.077114 | 9.453
111 | -0.064122 | -0.016229 | 0.064131 | 0.016234 | 8.7517e-06 | 5.569e-06 | 0.096566 | 0.096566 | 0.096566 | 0.98866 | -0.21691 | 0.98881 | -0.21407 | 26.529
112 | -0.065244 | -0.016513 | 0.065322 | 0.016563 | 7.8223e-05 | 4.9785e-05 | 0.098241 | 0.098241 | 0.098241 | 0.98881 | -0.21407 | 0.9901 | -0.18912 | 26.9893
113 | -0.067464 | -0.0171 | 0.067474 | 0.017106 | 1.0698e-05 | 6.8112e-06 | 0.10146 | 0.10146 | 0.10146 | 0.9901 | -0.18912 | 0.99027 | -0.18582 | 27.8734
114 | -0.070118 | -0.017769 | 0.070189 | 0.017814 | 7.1185e-05 | 4.5338e-05 | 0.10543 | 0.10543 | 0.10543 | 0.99027 | -0.18582 | 0.99137 | -0.16472 | 28.9645
115 | 0.0046432 | 0.0011634 | -0.0046431 | -0.0011634 | 1.3407e-07 | -8.4143e-09 | 0.0069819 | 0.0069819 | 0.0069819 | 0.98957 | -0.20013 | 0.98954 | -0.20074 | 1.9181
116 | 0.0030245 | 0.00075775 | -0.0030244 | -0.0007579 | 1.5215e-07 | -1.5459e-07 | 0.004548 | 0.0045481 | 0.0045481 | 0.98954 | -0.20074 | 0.98948 | -0.20179 | 1.2495
117 | 0.0013902 | 0.00034835 | -0.0013902 | -0.00034842 | 9.6848e-09 | -6.9699e-08 | 0.0020906 | 0.0020906 | 0.0020906 | 0.98948 | -0.20179 | 0.98947 | -0.20194 | 0.57435

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27199 | 0.06878

## res_load
| p_mw | q_mvar
0 | 0.0013247 | 0.00033201
1 | 0.0048329 | 0.0012112
2 | 0.0025081 | 0.00062858
3 | 0.00095972 | 0.00024053
4 | 0.0016997 | 0.00042599
5 | 0.0013163 | 0.00032989
6 | 0.0049132 | 0.0012314
7 | 0.0030779 | 0.00077139
8 | 0.0010554 | 0.00026451
9 | 0.0016231 | 0.00040679
10 | 0.0020469 | 0.00051301
11 | 0.0011952 | 0.00029954
12 | 0.0041746 | 0.0010463
13 | 0.0025768 | 0.00064581
14 | 0.0056932 | 0.0014269
15 | 0.0058237 | 0.0014596
16 | 0.0053014 | 0.0013286
17 | 0.0057195 | 0.0014334
18 | 0.0056786 | 0.0014232
19 | 0.0015706 | 0.00039362
20 | 0.0019518 | 0.00048916
21 | 0.0017792 | 0.0004459
22 | 0.0049341 | 0.0012366
23 | 0.0049123 | 0.0012311
24 | 0.0019414 | 0.00048655
25 | 0.00014166 | 3.5503e-05
26 | 0.0060866 | 0.0015254
27 | 0.00069985 | 0.0001754
28 | 9.3403e-05 | 2.3409e-05
29 | 0.0001445 | 3.6215e-05
30 | 0.0044845 | 0.0011239
31 | 0.0037029 | 0.00092803
32 | 0.0024358 | 0.00061048
33 | 0.0011523 | 0.00028879
34 | 0.0018838 | 0.00047213
35 | 0.0013872 | 0.00034767
36 | 0.0038334 | 0.00096075
37 | 0.0042133 | 0.0010559
38 | 0.0012634 | 0.00031664
39 | 0.0059268 | 0.0014854
40 | 0.0015686 | 0.00039313
41 | 0.0020907 | 0.00052399
42 | 0.0018877 | 0.0004731
43 | 0.0034632 | 0.00086797
44 | 0.0010818 | 0.00027112
45 | 0.0013931 | 0.00034914
46 | 0.0016707 | 0.00041871
47 | 0.0012556 | 0.00031468
48 | 0.0012556 | 0.00031468
49 | 0.0026991 | 0.00067646
50 | 0.0031317 | 0.00078489
51 | 0.0030118 | 0.00075483
52 | 0.0016996 | 0.00042595
53 | 0.0022222 | 0.00055694
54 | 0.0041159 | 0.0010316
55 | 0.0034019 | 0.00085259
56 | 0.0020739 | 0.00051977
57 | 0.0022212 | 0.00055669
58 | 0.0069724 | 0.0017475
59 | 0.001982 | 0.00049674
60 | 0.0022558 | 0.00056536
61 | 0.0034997 | 0.00087711
62 | 0.00061188 | 0.00015335
63 | 0.0032308 | 0.00080972
64 | 0.0020032 | 0.00050204
65 | 0.001593 | 0.00039925
66 | 0.0018571 | 0.00046544
67 | 0.0014227 | 0.00035656
68 | 0.0023456 | 0.00058786
69 | 0.0025077 | 0.00062849
70 | 0.0018395 | 0.00046102
71 | 0.0013211 | 0.0003311
72 | 0.001329 | 0.00033307
73 | 0.0017647 | 0.00044228
74 | 0.0018019 | 0.0004516
75 | 0.0012863 | 0.00032239
76 | 0.0017837 | 0.00044704
77 | 0.0017644 | 0.0004422
78 | 0.0023103 | 0.00057902
79 | 0.0026364 | 0.00066074
80 | 0.0019935 | 0.00049961
81 | 0.0017983 | 0.00045069
82 | 0.0032685 | 0.00081915
83 | 0.0033176 | 0.00083148
84 | 0.0012924 | 0.00032392
85 | 0.003545 | 0.00088845
86 | 0.00157 | 0.00039349
87 | 0.0027849 | 0.00069797
88 | 0.0019989 | 0.00050098
89 | 0.0022152 | 0.00055517
90 | 0.023031 | 0.0057721
91 | 0.00088184 | 0.00022101
92 | 0.0011135 | 0.00027907
93 | 0.0021412 | 0.00053664
94 | 0.0026433 | 0.00066247
95 | 0.0011952 | 0.00029955
96 | 0.0019105 | 0.00047882
97 | 0.0016186 | 0.00040565
98 | 0.0016341 | 0.00040956
99 | 0.0013902 | 0.00034842
100 | 0.0018507 | 0.00046383

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1