## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_157-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_157-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_157-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_157-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_157-5_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_157-5_0_4_node_130 | 0.4 | n |  | TRUE
6 | bus_LV_157-5_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_157-5_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_157-5_0_4_node_115 | 0.4 | n |  | TRUE
9 | bus_LV_157-5_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_157-5_0_4_node_110 | 0.4 | n |  | TRUE
11 | bus_LV_157-5_0_4_node_108 | 0.4 | n |  | TRUE
12 | bus_LV_157-5_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_157-5_0_4_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_157-5_0_4_node_94 | 0.4 | n |  | TRUE
15 | bus_LV_157-5_0_4_node_95 | 0.4 | n |  | TRUE
16 | bus_LV_157-5_0_4_node_88 | 0.4 | n |  | TRUE
17 | bus_LV_157-5_0_4_node_99 | 0.4 | n |  | TRUE
18 | bus_LV_157-5_0_4_node_96 | 0.4 | n |  | TRUE
19 | bus_LV_157-5_0_4_node_97 | 0.4 | n |  | TRUE
20 | bus_LV_157-5_0_4_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_157-5_0_4_node_100 | 0.4 | n |  | TRUE
22 | bus_LV_157-5_0_4_node_101 | 0.4 | n |  | TRUE
23 | bus_LV_157-5_0_4_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_157-5_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_157-5_0_4_node_116 | 0.4 | n |  | TRUE
26 | bus_LV_157-5_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_157-5_0_4_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_157-5_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_157-5_0_4_node_114 | 0.4 | n |  | TRUE
30 | bus_LV_157-5_0_4_node_7 | 0.4 | n |  | TRUE
31 | bus_LV_157-5_0_4_node_8 | 0.4 | n |  | TRUE
32 | bus_LV_157-5_0_4_node_87 | 0.4 | n |  | TRUE
33 | bus_LV_157-5_0_4_node_89 | 0.4 | n |  | TRUE
34 | bus_LV_157-5_0_4_node_91 | 0.4 | n |  | TRUE
35 | bus_LV_157-5_0_4_node_92 | 0.4 | n |  | TRUE
36 | bus_LV_157-5_0_4_node_93 | 0.4 | n |  | TRUE
37 | bus_LV_157-5_0_4_node_104 | 0.4 | n |  | TRUE
38 | bus_LV_157-5_0_4_node_103 | 0.4 | n |  | TRUE
39 | bus_LV_157-5_0_4_node_109 | 0.4 | n |  | TRUE
40 | bus_LV_157-5_0_4_node_118 | 0.4 | n |  | TRUE
41 | bus_LV_157-5_0_4_node_119 | 0.4 | n |  | TRUE
42 | bus_LV_157-5_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_157-5_0_4_node_12 | 0.4 | n |  | TRUE
44 | bus_LV_157-5_0_4_node_13 | 0.4 | n |  | TRUE
45 | bus_LV_157-5_0_4_node_15 | 0.4 | n |  | TRUE
46 | bus_LV_157-5_0_4_node_16 | 0.4 | n |  | TRUE
47 | bus_LV_157-5_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_157-5_0_4_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_157-5_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_157-5_0_4_node_21 | 0.4 | n |  | TRUE
51 | bus_LV_157-5_0_4_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_157-5_0_4_node_25 | 0.4 | n |  | TRUE
53 | bus_LV_157-5_0_4_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_157-5_0_4_node_20 | 0.4 | n |  | TRUE
55 | bus_LV_157-5_0_4_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_157-5_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_157-5_0_4_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_157-5_0_4_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_157-5_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_157-5_0_4_node_117 | 0.4 | n |  | TRUE
61 | bus_LV_157-5_0_4_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_157-5_0_4_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_157-5_0_4_node_107 | 0.4 | n |  | TRUE
64 | bus_LV_157-5_0_4_node_26 | 0.4 | n |  | TRUE
65 | bus_LV_157-5_0_4_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_157-5_0_4_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_157-5_0_4_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_157-5_0_4_node_84 | 0.4 | n |  | TRUE
69 | bus_LV_157-5_0_4_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_157-5_0_4_node_105 | 0.4 | n |  | TRUE
71 | bus_LV_157-5_0_4_node_106 | 0.4 | n |  | TRUE
72 | bus_LV_157-5_0_4_node_42 | 0.4 | n |  | TRUE
73 | bus_LV_157-5_0_4_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_157-5_0_4_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_157-5_0_4_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_157-5_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_157-5_0_4_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_157-5_0_4_node_49 | 0.4 | n |  | TRUE
79 | bus_LV_157-5_0_4_node_46 | 0.4 | n |  | TRUE
80 | bus_LV_157-5_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_157-5_0_4_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_157-5_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_157-5_0_4_node_59 | 0.4 | n |  | TRUE
84 | bus_LV_157-5_0_4_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_157-5_0_4_node_47 | 0.4 | n |  | TRUE
86 | bus_LV_157-5_0_4_node_48 | 0.4 | n |  | TRUE
87 | bus_LV_157-5_0_4_node_50 | 0.4 | n |  | TRUE
88 | bus_LV_157-5_0_4_node_51 | 0.4 | n |  | TRUE
89 | bus_LV_157-5_0_4_node_63 | 0.4 | n |  | TRUE
90 | bus_LV_157-5_0_4_node_52 | 0.4 | n |  | TRUE
91 | bus_LV_157-5_0_4_node_53 | 0.4 | n |  | TRUE
92 | bus_LV_157-5_0_4_node_54 | 0.4 | n |  | TRUE
93 | bus_LV_157-5_0_4_node_55 | 0.4 | n |  | TRUE
94 | bus_LV_157-5_0_4_node_127 | 0.4 | n |  | TRUE
95 | bus_LV_157-5_0_4_node_57 | 0.4 | n |  | TRUE
96 | bus_LV_157-5_0_4_node_58 | 0.4 | n |  | TRUE
97 | bus_LV_157-5_0_4_node_129 | 0.4 | n |  | TRUE
98 | bus_LV_157-5_0_4_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_157-5_0_4_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_157-5_0_4_node_72 | 0.4 | n |  | TRUE
101 | bus_LV_157-5_0_4_node_61 | 0.4 | n |  | TRUE
102 | bus_LV_157-5_0_4_node_66 | 0.4 | n |  | TRUE
103 | bus_LV_157-5_0_4_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_157-5_0_4_node_69 | 0.4 | n |  | TRUE
105 | bus_LV_157-5_0_4_node_68 | 0.4 | n |  | TRUE
106 | bus_LV_157-5_0_4_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_157-5_0_4_node_71 | 0.4 | n |  | TRUE
108 | bus_LV_157-5_0_4_node_73 | 0.4 | n |  | TRUE
109 | bus_LV_157-5_0_4_node_76 | 0.4 | n |  | TRUE
110 | bus_LV_157-5_0_4_node_77 | 0.4 | n |  | TRUE
111 | bus_LV_157-5_0_4_node_75 | 0.4 | n |  | TRUE
112 | bus_LV_157-5_0_4_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_157-5_0_4_node_78 | 0.4 | n |  | TRUE
114 | bus_LV_157-5_0_4_node_128 | 0.4 | n |  | TRUE
115 | bus_LV_157-5_0_4_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_157-5_0_4_node_82 | 0.4 | n |  | TRUE
117 | bus_LV_157-5_0_4_node_124 | 0.4 | n |  | TRUE
118 | bus_LV_157-5_0_4_node_79 | 0.4 | n |  | TRUE
119 | bus_LV_157-5_0_4_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_157-5_0_4_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_157-5_0_4_node_125 | 0.4 | n |  | TRUE
122 | bus_LV_157-5_0_4_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_157-5_0_4_node_85 | 0.4 | n |  | TRUE
124 | bus_LV_157-5_0_4_node_86 | 0.4 | n |  | TRUE
125 | bus_LV_157-5_0_4_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_157-5_0_4_node_112 | 0.4 | n |  | TRUE
127 | bus_LV_157-5_0_4_node_111 | 0.4 | n |  | TRUE
128 | bus_LV_157-5_0_4_node_123 | 0.4 | n |  | TRUE
129 | bus_MV_361_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_157-5_0_4_load_0 | 0 | 0.010509 | 0.0026338 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_157-5_0_4_load_130 | 5 | 0.0014396 | 0.0003608 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_157-5_0_4_load_115 | 8 | 0.036839 | 0.0092327 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_157-5_0_4_load_110 | 10 | 0.00022255 | 5.5776e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_157-5_0_4_load_9 | 12 | 0.00083187 | 0.00020849 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_157-5_0_4_load_95 | 15 | 0.00078691 | 0.00019722 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_157-5_0_4_load_88 | 16 | 0.0031716 | 0.00079487 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_157-5_0_4_load_99 | 17 | 0.00030707 | 7.696e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_157-5_0_4_load_96 | 18 | 0.00011127 | 2.7886e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_157-5_0_4_load_97 | 19 | 0.00030539 | 7.6539e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_157-5_0_4_load_98 | 20 | 0.00044945 | 0.00011264 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_157-5_0_4_load_101 | 22 | 0.00026384 | 6.6126e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_157-5_0_4_load_102 | 23 | 0.0023426 | 0.00058711 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_157-5_0_4_load_116 | 25 | 0.00059283 | 0.00014858 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_157-5_0_4_load_10 | 27 | 0.00082906 | 0.00020778 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_157-5_0_4_load_18 | 28 | 0.00032237 | 8.0793e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_157-5_0_4_load_114 | 29 | 0.02287 | 0.0057316 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_157-5_0_4_load_7 | 30 | 0.0018454 | 0.0004625 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_157-5_0_4_load_8 | 31 | 0.00028867 | 7.2349e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_157-5_0_4_load_87 | 32 | 0.0020255 | 0.00050764 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_157-5_0_4_load_89 | 33 | 0.0017754 | 0.00044495 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_157-5_0_4_load_91 | 34 | 0.0014617 | 0.00036635 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_157-5_0_4_load_92 | 35 | 0.00067946 | 0.00017029 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_157-5_0_4_load_93 | 36 | 0.00068921 | 0.00017273 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_157-5_0_4_load_104 | 37 | 0.00035749 | 8.9595e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_157-5_0_4_load_103 | 38 | 0.00014016 | 3.5127e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_157-5_0_4_load_118 | 40 | 0.00070045 | 0.00017555 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_157-5_0_4_load_119 | 41 | 0.00073922 | 0.00018527 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_157-5_0_4_load_24 | 42 | 0.0012803 | 0.00032086 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_157-5_0_4_load_12 | 43 | 0.0006114 | 0.00015323 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_157-5_0_4_load_13 | 44 | 0.00036634 | 9.1813e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_157-5_0_4_load_16 | 46 | 0.00025965 | 6.5074e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_157-5_0_4_load_21 | 50 | 0.00036554 | 9.1612e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_157-5_0_4_load_25 | 52 | 0.0012083 | 0.00030282 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_157-5_0_4_load_30 | 53 | 0.00054222 | 0.00013589 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_157-5_0_4_load_20 | 54 | 0.0010776 | 0.00027007 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_157-5_0_4_load_32 | 56 | 0.00071607 | 0.00017946 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_157-5_0_4_load_40 | 58 | 0.0038204 | 0.00095748 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_157-5_0_4_load_37 | 59 | 0.001229 | 0.00030801 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_157-5_0_4_load_117 | 60 | 0.00098185 | 0.00024607 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_157-5_0_4_load_34 | 61 | 0.00085038 | 0.00021313 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_157-5_0_4_load_35 | 62 | 0.0010016 | 0.00025102 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_157-5_0_4_load_107 | 63 | 0.001499 | 0.00037568 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_157-5_0_4_load_26 | 64 | 0.0006043 | 0.00015145 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_157-5_0_4_load_38 | 66 | 0.0019203 | 0.00048126 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_157-5_0_4_load_84 | 68 | 0.00042402 | 0.00010627 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_157-5_0_4_load_83 | 69 | 0.00084843 | 0.00021264 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_157-5_0_4_load_105 | 70 | 0.001006 | 0.00025213 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_157-5_0_4_load_41 | 73 | 0.00087325 | 0.00021886 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_157-5_0_4_load_39 | 74 | 0.00037573 | 9.4168e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_157-5_0_4_load_46 | 79 | 0.0026677 | 0.00066858 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_157-5_0_4_load_60 | 81 | 0.040662 | 0.010191 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_157-5_0_4_load_65 | 82 | 0.042963 | 0.010768 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_157-5_0_4_load_59 | 83 | 0.0054374 | 0.0013627 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_157-5_0_4_load_56 | 84 | 0.032868 | 0.0082374 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_157-5_0_4_load_47 | 85 | 0.0015513 | 0.00038878 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_157-5_0_4_load_48 | 86 | 0.0015788 | 0.00039568 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_157-5_0_4_load_50 | 87 | 0.0015148 | 0.00037964 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_157-5_0_4_load_51 | 88 | 0.0019364 | 0.00048531 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_157-5_0_4_load_63 | 89 | 0.0034563 | 0.00086623 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_157-5_0_4_load_52 | 90 | 0.002671 | 0.00066941 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_157-5_0_4_load_53 | 91 | 0.0033445 | 0.00083821 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_157-5_0_4_load_54 | 92 | 0.0041159 | 0.0010315 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_157-5_0_4_load_127 | 94 | 0.0014742 | 0.00036948 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_157-5_0_4_load_129 | 97 | 0.007595 | 0.0019035 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_157-5_0_4_load_81 | 99 | 0.0044774 | 0.0011221 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_157-5_0_4_load_72 | 100 | 0.0043918 | 0.0011007 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_157-5_0_4_load_61 | 101 | 0.0066519 | 0.0016671 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_157-5_0_4_load_66 | 102 | 0.01857 | 0.004654 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_157-5_0_4_load_67 | 103 | 0.0048061 | 0.0012045 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_157-5_0_4_load_70 | 106 | 0.0015656 | 0.00039239 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_157-5_0_4_load_71 | 107 | 0.0046256 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_157-5_0_4_load_80 | 112 | 0.0015002 | 0.00037598 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_157-5_0_4_load_78 | 113 | 0.010602 | 0.0026572 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_157-5_0_4_load_128 | 114 | 0.0050952 | 0.001277 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_157-5_0_4_load_82 | 116 | 0.0065629 | 0.0016448 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_157-5_0_4_load_124 | 117 | 0.0028323 | 0.00070984 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_157-5_0_4_load_79 | 118 | 0.0029606 | 0.00074199 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_157-5_0_4_load_120 | 120 | 0.0014956 | 0.00037483 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_157-5_0_4_load_125 | 121 | 0.0041414 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_157-5_0_4_load_126 | 122 | 0.00054008 | 0.00013536 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_157-5_0_4_load_86 | 124 | 0.00050587 | 0.00012678 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_157-5_0_4_load_112 | 126 | 0.00022975 | 5.758e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_157-5_0_4_load_111 | 127 | 0.00038089 | 9.5461e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_157-5_0_4_line_0 |  | 0 | 1 | 0.01788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_157-5_0_4_line_1 |  | 0 | 2 | 0.066324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_157-5_0_4_line_2 |  | 1 | 3 | 0.095498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_157-5_0_4_line_3 |  | 2 | 4 | 0.064065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_157-5_0_4_line_4 |  | 3 | 5 | 0.028726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_157-5_0_4_line_5 |  | 3 | 6 | 0.098768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_157-5_0_4_line_6 |  | 4 | 8 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_157-5_0_4_line_7 |  | 6 | 7 | 0.05045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_157-5_0_4_line_8 |  | 7 | 27 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_157-5_0_4_line_9 |  | 7 | 28 | 0.04039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_157-5_0_4_line_10 |  | 8 | 29 | 0.031388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_157-5_0_4_line_11 |  | 9 | 10 | 0.026302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_157-5_0_4_line_12 |  | 9 | 11 | 0.1918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_157-5_0_4_line_13 |  | 9 | 12 | 0.050722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_157-5_0_4_line_14 |  | 11 | 39 | 0.061806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_157-5_0_4_line_15 |  | 11 | 37 | 0.188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_157-5_0_4_line_16 |  | 12 | 30 | 0.0081008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_157-5_0_4_line_17 |  | 13 | 14 | 0.051507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_157-5_0_4_line_18 |  | 13 | 15 | 0.11021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_157-5_0_4_line_19 |  | 13 | 16 | 0.044403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_157-5_0_4_line_20 |  | 14 | 17 | 0.014769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_157-5_0_4_line_21 |  | 14 | 18 | 0.014228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_157-5_0_4_line_22 |  | 16 | 32 | 0.005478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_157-5_0_4_line_23 |  | 18 | 19 | 0.01652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_157-5_0_4_line_24 |  | 19 | 20 | 0.03196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_157-5_0_4_line_25 |  | 20 | 21 | 0.014454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_157-5_0_4_line_26 |  | 21 | 22 | 0.021129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_157-5_0_4_line_27 |  | 21 | 23 | 0.065244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_157-5_0_4_line_28 |  | 22 | 38 | 0.0013443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_157-5_0_4_line_29 |  | 24 | 25 | 0.088503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_157-5_0_4_line_30 |  | 24 | 26 | 0.007625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_157-5_0_4_line_31 |  | 25 | 47 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_157-5_0_4_line_32 |  | 26 | 46 | 0.0044123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_157-5_0_4_line_33 |  | 26 | 43 | 0.0077496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_157-5_0_4_line_34 |  | 27 | 31 | 0.033099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_157-5_0_4_line_35 |  | 28 | 46 | 0.0031252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_157-5_0_4_line_36 |  | 30 | 31 | 0.017951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_157-5_0_4_line_37 |  | 32 | 33 | 0.019607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_157-5_0_4_line_38 |  | 33 | 34 | 0.015992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_157-5_0_4_line_39 |  | 34 | 35 | 0.0011995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_157-5_0_4_line_40 |  | 35 | 36 | 0.017779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_157-5_0_4_line_41 |  | 36 | 37 | 0.0044187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_157-5_0_4_line_42 |  | 39 | 40 | 0.089849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_157-5_0_4_line_43 |  | 40 | 41 | 0.0061844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_157-5_0_4_line_44 |  | 41 | 42 | 0.18579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_157-5_0_4_line_45 |  | 42 | 60 | 0.036428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_157-5_0_4_line_46 |  | 44 | 45 | 0.0019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_157-5_0_4_line_47 |  | 45 | 47 | 0.006263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_157-5_0_4_line_48 |  | 47 | 51 | 0.037835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_157-5_0_4_line_49 |  | 48 | 49 | 0.01543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_157-5_0_4_line_50 |  | 48 | 50 | 0.024089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_157-5_0_4_line_51 |  | 49 | 53 | 0.031945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_157-5_0_4_line_52 |  | 49 | 51 | 0.018534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_157-5_0_4_line_53 |  | 50 | 54 | 0.014372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_157-5_0_4_line_54 |  | 51 | 52 | 0.050385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_157-5_0_4_line_55 |  | 52 | 64 | 0.0014562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_157-5_0_4_line_56 |  | 53 | 55 | 0.045915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_157-5_0_4_line_57 |  | 55 | 56 | 0.029279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_157-5_0_4_line_58 |  | 56 | 57 | 0.010833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_157-5_0_4_line_59 |  | 57 | 58 | 0.02429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_157-5_0_4_line_60 |  | 57 | 59 | 0.018244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_157-5_0_4_line_61 |  | 58 | 65 | 0.080191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_157-5_0_4_line_62 |  | 59 | 66 | 0.0038178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_157-5_0_4_line_63 |  | 60 | 63 | 0.01772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_157-5_0_4_line_64 |  | 61 | 62 | 0.0073941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_157-5_0_4_line_65 |  | 62 | 67 | 0.0085229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_157-5_0_4_line_66 |  | 63 | 71 | 0.064288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_157-5_0_4_line_67 |  | 65 | 75 | 0.01424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_157-5_0_4_line_68 |  | 66 | 74 | 0.0093512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_157-5_0_4_line_69 |  | 67 | 72 | 0.07043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_157-5_0_4_line_70 |  | 67 | 68 | 0.14554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_157-5_0_4_line_71 |  | 68 | 69 | 0.031979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_157-5_0_4_line_72 |  | 69 | 123 | 0.021545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_157-5_0_4_line_73 |  | 70 | 71 | 0.042299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_157-5_0_4_line_74 |  | 72 | 73 | 0.18989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_157-5_0_4_line_75 |  | 73 | 74 | 0.04851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_157-5_0_4_line_76 |  | 75 | 76 | 0.026729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_157-5_0_4_line_77 |  | 76 | 80 | 0.01668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_157-5_0_4_line_78 |  | 76 | 81 | 0.017458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_157-5_0_4_line_79 |  | 77 | 78 | 0.026466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_157-5_0_4_line_80 |  | 77 | 79 | 0.034127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_157-5_0_4_line_81 |  | 78 | 83 | 0.022773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_157-5_0_4_line_82 |  | 78 | 84 | 0.029588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_157-5_0_4_line_83 |  | 79 | 85 | 0.019688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_157-5_0_4_line_84 |  | 80 | 102 | 0.016972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_157-5_0_4_line_85 |  | 80 | 82 | 0.02846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_157-5_0_4_line_86 |  | 81 | 101 | 0.010138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_157-5_0_4_line_87 |  | 83 | 89 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_157-5_0_4_line_88 |  | 85 | 86 | 0.013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_157-5_0_4_line_89 |  | 86 | 87 | 0.0095323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_157-5_0_4_line_90 |  | 87 | 88 | 0.0051196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_157-5_0_4_line_91 |  | 88 | 90 | 0.016083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_157-5_0_4_line_92 |  | 89 | 101 | 0.010078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_157-5_0_4_line_93 |  | 90 | 91 | 0.014845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_157-5_0_4_line_94 |  | 91 | 92 | 0.012413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_157-5_0_4_line_95 |  | 92 | 93 | 0.015225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_157-5_0_4_line_96 |  | 93 | 94 | 0.076527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_157-5_0_4_line_97 |  | 93 | 95 | 0.007989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_157-5_0_4_line_98 |  | 95 | 96 | 0.017159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_157-5_0_4_line_99 |  | 96 | 97 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_157-5_0_4_line_100 |  | 96 | 98 | 0.011589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_157-5_0_4_line_101 |  | 98 | 99 | 0.019178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_157-5_0_4_line_102 |  | 98 | 100 | 0.016112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_157-5_0_4_line_103 |  | 99 | 116 | 0.03283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_157-5_0_4_line_104 |  | 100 | 107 | 0.015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_157-5_0_4_line_105 |  | 100 | 106 | 0.034204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_157-5_0_4_line_106 |  | 103 | 104 | 0.010229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_157-5_0_4_line_107 |  | 104 | 105 | 0.004917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_157-5_0_4_line_108 |  | 105 | 106 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_157-5_0_4_line_109 |  | 107 | 108 | 0.0052952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_157-5_0_4_line_110 |  | 108 | 109 | 0.013298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_157-5_0_4_line_111 |  | 108 | 110 | 0.10887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_157-5_0_4_line_112 |  | 109 | 114 | 0.011701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_157-5_0_4_line_113 |  | 109 | 111 | 0.037144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_157-5_0_4_line_114 |  | 110 | 115 | 0.097526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_157-5_0_4_line_115 |  | 111 | 112 | 0.019259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_157-5_0_4_line_116 |  | 111 | 113 | 0.015294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_157-5_0_4_line_117 |  | 112 | 117 | 0.0094633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_157-5_0_4_line_118 |  | 113 | 118 | 0.0016809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_157-5_0_4_line_119 |  | 115 | 119 | 0.065752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_157-5_0_4_line_120 |  | 115 | 120 | 0.018553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_157-5_0_4_line_121 |  | 119 | 128 | 0.019948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_157-5_0_4_line_122 |  | 121 | 122 | 0.021843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_157-5_0_4_line_123 |  | 122 | 128 | 0.03739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_157-5_0_4_line_124 |  | 123 | 124 | 0.0097667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_157-5_0_4_line_125 |  | 124 | 125 | 0.015509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_157-5_0_4_line_126 |  | 125 | 126 | 0.12454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_157-5_0_4_line_127 |  | 126 | 127 | 0.00020036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_157-5_0_4_trafo_39 | 0.63 MVA 20/0.4 kV | 129 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2698583.9003 | 1236417.543 | 2698589.9413 | 1236410.16 | 2698595.2253 | 1236403.7072
1 | 2698609.9276 | 1236347.8229 | 2698596.7758 | 1236377.3267 | 2698596.5768 | 1236377.9127 | 2698596.491 | 1236378.5229 | 2698596.5259 | 1236379.1572 | 2698596.6661 | 1236379.8267 | 2698596.9356 | 1236380.465 | 2698597.2891 | 1236381.0491 | 2698597.7795 | 1236381.6021 | 2698604.8774 | 1236387.591 | 2698605.4122 | 1236388.2004 | 2698605.6817 | 1236388.8386 | 2698605.8062 | 1236389.5412 | 2698605.7495 | 1236390.2186 | 2698605.5731 | 1236390.8161 | 2698605.3303 | 1236391.3124 | 2698604.9972 | 1236391.7739 | 2698595.2253 | 1236403.7072
2 | 2698512.2925 | 1236415.0867 | 2698518.5318 | 1236411.254 | 2698524.4318 | 1236406.893 | 2698530.3429 | 1236401.854 | 2698534.8505 | 1236397.481 | 2698542.4754 | 1236389.0568 | 2698556.0986 | 1236401.3475 | 2698570.9583 | 1236413.9145 | 2698580.5627 | 1236421.6463 | 2698583.9003 | 1236417.543
3 | 2698581.8858 | 1236338.3172 | 2698586.7978 | 1236334.6626 | 2698588.3495 | 1236333.2873 | 2698596.799 | 1236322.6085 | 2698597.6206 | 1236321.8993 | 2698598.6821 | 1236321.3276 | 2698599.8604 | 1236321.0136 | 2698600.9524 | 1236320.8872 | 2698602.382 | 1236320.9332 | 2698603.6718 | 1236321.1993 | 2698604.7992 | 1236321.6739 | 2698615.4602 | 1236328.6783 | 2698616.2458 | 1236329.6809 | 2698616.6807 | 1236330.8335 | 2698616.7252 | 1236331.8016 | 2698616.4993 | 1236333.0988 | 2698609.9276 | 1236347.8229
4 | 2698498.0853 | 1236390.0992 | 2698509.7241 | 1236410.6964 | 2698512.2925 | 1236415.0867
5 | 2698501.5711 | 1236346.9581 | 2698502.7832 | 1236348.257 | 2698542.4754 | 1236389.0568 | 2698534.8505 | 1236397.481 | 2698530.3429 | 1236401.854 | 2698524.4318 | 1236406.893 | 2698518.5318 | 1236411.254 | 2698512.2925 | 1236415.0867
6 | 2698581.8858 | 1236338.3172 | 2698579.2419 | 1236340.297 | 2698577.4814 | 1236341.9468 | 2698569.6322 | 1236351.3894
7 | 2698467.0814 | 1236310.0478 | 2698477.4957 | 1236320.9841 | 2698501.5711 | 1236346.9581
8 | 2698467.0814 | 1236310.0478 | 2698462.368 | 1236314.5063 | 2698456.2185 | 1236316.5726 | 2698450.6819 | 1236321.6991
9 | 2698467.0814 | 1236310.0478 | 2698456.3262 | 1236298.6722 | 2698451.6848 | 1236293.7694 | 2698447.7399 | 1236289.3118 | 2698443.6734 | 1236283.9737 | 2698440.6719 | 1236279.5802
10 | 2698547.1127 | 1236346.2529 | 2698562.739 | 1236359.6821 | 2698569.6322 | 1236351.3894
11 | 2698426.5507 | 1236415.1657 | 2698446.007 | 1236397.4676
12 | 2698426.5507 | 1236415.1657 | 2698292.1364 | 1236551.9868
13 | 2698426.5507 | 1236415.1657 | 2698425.3524 | 1236412.5772 | 2698423.2928 | 1236408.0731 | 2698421.7631 | 1236404.4784 | 2698418.1176 | 1236393.8323 | 2698417.5752 | 1236391.8551 | 2698417.2598 | 1236389.8818 | 2698417.1701 | 1236387.99 | 2698417.2204 | 1236386.3229 | 2698417.5125 | 1236384.6821 | 2698418.1751 | 1236382.6026 | 2698419.1956 | 1236379.9398 | 2698420.279 | 1236377.5893 | 2698421.4354 | 1236375.3957 | 2698422.4402 | 1236373.6777 | 2698423.6727 | 1236371.9191 | 2698425.014 | 1236370.4513 | 2698426.7556 | 1236369.0235
14 | 2698253.939 | 1236509.5455 | 2698272.0789 | 1236526.5138 | 2698276.9223 | 1236530.6414 | 2698294.8454 | 1236544.6928 | 2698293.3672 | 1236547.5817 | 2698292.5565 | 1236549.9255 | 2698292.1364 | 1236551.9868
15 | 2698372.3844 | 1236722.0029 | 2698292.1364 | 1236551.9868
16 | 2698433.409 | 1236364.4081 | 2698431.3243 | 1236365.9859 | 2698426.7556 | 1236369.0235 | 2698426.7556 | 1236369.0235
17 | 2698416.2599 | 1236846.4282 | 2698425.2072 | 1236833.0553 | 2698437.9505 | 1236814.8418 | 2698440.2825 | 1236811.1221 | 2698442.2591 | 1236807.3854 | 2698444.2428 | 1236803.2263
18 | 2698444.2428 | 1236803.2263 | 2698464.3523 | 1236775.7279 | 2698498.5486 | 1236737.1104 | 2698516.3629 | 1236720.204
19 | 2698444.2428 | 1236803.2263 | 2698431.932 | 1236793.5261 | 2698427.3438 | 1236789.0912 | 2698412.5164 | 1236772.3692
20 | 2698423.5922 | 1236859.2593 | 2698416.2599 | 1236846.4282
21 | 2698416.2599 | 1236846.4282 | 2698412.2926 | 1236852.4781 | 2698408.7084 | 1236858.4826
22 | 2698408.882 | 1236768.2704 | 2698412.5164 | 1236772.3692
23 | 2698408.7084 | 1236858.4826 | 2698408.1126 | 1236859.4808 | 2698405.8646 | 1236863.6133 | 2698404.8073 | 1236865.764 | 2698403.8528 | 1236868.1055 | 2698401.9657 | 1236873.5135
24 | 2698401.9657 | 1236873.5135 | 2698395.0259 | 1236893.4004 | 2698391.6851 | 1236903.773
25 | 2698386.6308 | 1236917.3015 | 2698388.5263 | 1236912.9741 | 2698390.231 | 1236908.2877 | 2698391.6851 | 1236903.773
26 | 2698386.6308 | 1236917.3015 | 2698385.0642 | 1236920.5001 | 2698384.0359 | 1236922.2733 | 2698383.077 | 1236923.5139 | 2698382.0857 | 1236924.4204 | 2698381.5052 | 1236924.7444 | 2698380.8207 | 1236924.9554 | 2698380.2298 | 1236924.9901 | 2698379.4827 | 1236924.8665 | 2698378.6158 | 1236924.6631 | 2698377.7057 | 1236924.3256 | 2698375.8274 | 1236923.505 | 2698372.1267 | 1236921.6868 | 2698370.5033 | 1236920.8176
27 | 2698386.6308 | 1236917.3015 | 2698404.2923 | 1236938.8323 | 2698407.1038 | 1236942.2481 | 2698409.2736 | 1236944.6525 | 2698411.4675 | 1236946.9795 | 2698413.6128 | 1236949.0388 | 2698415.7974 | 1236951.0098 | 2698419.8795 | 1236954.4689 | 2698424.7195 | 1236958.3186 | 2698429.5323 | 1236961.9789 | 2698431.934 | 1236963.8382
28 | 2698370.5033 | 1236920.8176 | 2698369.3181 | 1236920.1831
29 | 2698443.1492 | 1236269.0317 | 2698440.9995 | 1236264.9375 | 2698438.7491 | 1236260.0743 | 2698436.2882 | 1236254.207 | 2698433.7279 | 1236247.4929 | 2698412.9449 | 1236185.9344
30 | 2698443.1492 | 1236269.0317 | 2698441.5894 | 1236269.9843 | 2698440.4873 | 1236270.7222 | 2698436.7232 | 1236273.1616
31 | 2698406.8259 | 1236167.8101 | 2698412.9449 | 1236185.9344
32 | 2698436.7232 | 1236273.1616 | 2698439.0019 | 1236276.94
33 | 2698436.7232 | 1236273.1616 | 2698433.3682 | 1236266.9014 | 2698433.0883 | 1236266.3181
34 | 2698442.0591 | 1236348.8243 | 2698444.345 | 1236343.8851 | 2698443.7014 | 1236338.8818 | 2698442.0989 | 1236334.6521 | 2698440.1617 | 1236331.4398 | 2698450.6819 | 1236321.6991
35 | 2698439.0019 | 1236276.94 | 2698440.0084 | 1236278.609 | 2698440.6719 | 1236279.5802
36 | 2698433.409 | 1236364.4081 | 2698433.409 | 1236364.4081 | 2698435.0876 | 1236362.6791 | 2698436.6152 | 1236360.4694 | 2698439.2584 | 1236354.8757 | 2698442.0591 | 1236348.8243
37 | 2698408.882 | 1236768.2704 | 2698395.8741 | 1236753.6002
38 | 2698386.1539 | 1236740.9191 | 2698393.1411 | 1236750.5181 | 2698395.8741 | 1236753.6002
39 | 2698386.1539 | 1236740.9191 | 2698385.448 | 1236739.9493
40 | 2698385.448 | 1236739.9493 | 2698374.9849 | 1236725.5753
41 | 2698372.3844 | 1236722.0029 | 2698374.9849 | 1236725.5753
42 | 2698253.939 | 1236509.5455 | 2698205.6234 | 1236552.1451 | 2698186.5459 | 1236568.9673
43 | 2698181.9073 | 1236573.0576 | 2698186.5459 | 1236568.9673
44 | 2698043.2685 | 1236449.3756 | 2698181.9073 | 1236573.0576
45 | 2698012.9123 | 1236469.4962 | 2698017.6692 | 1236466.5329 | 2698032.9926 | 1236456.5783 | 2698042.0952 | 1236450.2794 | 2698043.2685 | 1236449.3756
46 | 2698400.8597 | 1236169.7683 | 2698401.4694 | 1236171.6397
47 | 2698406.8259 | 1236167.8101 | 2698400.8597 | 1236169.7683
48 | 2698406.8259 | 1236167.8101 | 2698394.6233 | 1236135.5172 | 2698394.2168 | 1236134.0094 | 2698393.8822 | 1236132.2803
49 | 2698377.7637 | 1236110.1969 | 2698381.3494 | 1236117.6174 | 2698387.9874 | 1236114.8586
50 | 2698377.7637 | 1236110.1969 | 2698361.0832 | 1236127.576
51 | 2698387.9874 | 1236114.8586 | 2698385.0765 | 1236108.2833 | 2698374.0329 | 1236086.129
52 | 2698393.8822 | 1236132.2803 | 2698393.4851 | 1236128.8378 | 2698393.2793 | 1236127.5557 | 2698392.9733 | 1236126.3831 | 2698392.5254 | 1236125.0969 | 2698387.9874 | 1236114.8586
53 | 2698351.131 | 1236137.9449 | 2698361.0832 | 1236127.576
54 | 2698393.8822 | 1236132.2803 | 2698398.7601 | 1236128.4027 | 2698402.9345 | 1236124.5022 | 2698407.0666 | 1236119.9562 | 2698415.3609 | 1236109.508 | 2698427.7935 | 1236095.1971
55 | 2698427.7935 | 1236095.1971 | 2698428.7486 | 1236094.0978
56 | 2698353.5489 | 1236045.0364 | 2698374.0329 | 1236086.129
57 | 2698353.5489 | 1236045.0364 | 2698351.4245 | 1236040.7758 | 2698343.4419 | 1236030.5806 | 2698338.0087 | 1236020.3656
58 | 2698331.0382 | 1236016.7872 | 2698335.0228 | 1236014.7516 | 2698338.0087 | 1236020.3656
59 | 2698331.0382 | 1236016.7872 | 2698325.5265 | 1236008.2007 | 2698320.1146 | 1236000.4498 | 2698317.1345 | 1235996.9012
60 | 2698331.0382 | 1236016.7872 | 2698315.0322 | 1236025.5428
61 | 2698255.7903 | 1235945.4114 | 2698300.3371 | 1235980.808 | 2698308.7526 | 1235988.186 | 2698315.0673 | 1235994.4396 | 2698317.1345 | 1235996.9012
62 | 2698315.0322 | 1236025.5428 | 2698313.2418 | 1236026.5222 | 2698311.6204 | 1236027.2495
63 | 2698012.9123 | 1236469.4962 | 2697999.3934 | 1236477.9176 | 2697997.9313 | 1236478.955
64 | 2698051.5442 | 1236180.1538 | 2698057.4595 | 1236184.5902
65 | 2698044.7259 | 1236175.04 | 2698051.5442 | 1236180.1538
66 | 2697958.9432 | 1236529.6557 | 2697960.9148 | 1236528.4985 | 2697962.7148 | 1236526.738 | 2697981.8942 | 1236499.5673 | 2697992.3963 | 1236484.585 | 2697993.6876 | 1236482.9272 | 2697995.2211 | 1236481.2624 | 2697997.1267 | 1236479.5259 | 2697997.9313 | 1236478.955
67 | 2698255.7903 | 1235945.4114 | 2698260.0996 | 1235940.2233 | 2698264.8955 | 1235934.4427
68 | 2698311.6204 | 1236027.2495 | 2698308.9868 | 1236028.431 | 2698306.7008 | 1236032.107 | 2698306.1437 | 1236034.169
69 | 2698044.7259 | 1236175.04 | 2698058.8231 | 1236161.4737 | 2698062.6425 | 1236157.5116 | 2698071.7628 | 1236147.4213 | 2698087.4283 | 1236130.1003 | 2698090.634 | 1236127.5514 | 2698094.5648 | 1236125.5592
70 | 2697899.3424 | 1236168.3988 | 2698044.7259 | 1236175.04
71 | 2697868.2523 | 1236162.4606 | 2697880.4303 | 1236162.5329 | 2697899.3424 | 1236168.3988
72 | 2697846.7082 | 1236162.3328 | 2697868.2523 | 1236162.4606
73 | 2697958.9432 | 1236529.6557 | 2697959.8096 | 1236533.5618 | 2697960.4094 | 1236536.6518 | 2697960.9007 | 1236540.3626 | 2697962.7339 | 1236566.8571 | 2697962.5253 | 1236571.7017
74 | 2698276.3983 | 1236070.8217 | 2698094.5648 | 1236125.5592
75 | 2698276.3983 | 1236070.8217 | 2698293.2763 | 1236056.1917 | 2698300.3385 | 1236049.2923 | 2698303.8385 | 1236042.7009 | 2698306.1437 | 1236034.169
76 | 2698264.8955 | 1235934.4427 | 2698282.2848 | 1235914.1041
77 | 2698294.8041 | 1235903.103 | 2698284.3917 | 1235911.6482 | 2698282.2848 | 1235914.1041
78 | 2698282.2848 | 1235914.1041 | 2698270.2472 | 1235904.6869 | 2698268.0734 | 1235904.636
79 | 2698231.7546 | 1235926.0218 | 2698211.009 | 1235909.511
80 | 2698231.7546 | 1235926.0218 | 2698207.5376 | 1235950.0669
81 | 2698211.009 | 1235909.511 | 2698214.5819 | 1235904.9111 | 2698225.1019 | 1235906.3305 | 2698231.3505 | 1235905.3004
82 | 2698211.009 | 1235909.511 | 2698187.8144 | 1235891.1407
83 | 2698207.5376 | 1235950.0669 | 2698207.1683 | 1235950.4335 | 2698200.5365 | 1235953.2705 | 2698194.4951 | 1235949.7013 | 2698191.4812 | 1235945.7907
84 | 2698307.9407 | 1235892.3123 | 2698294.8041 | 1235903.103
85 | 2698294.8041 | 1235903.103 | 2698313.9195 | 1235924.1882
86 | 2698268.0734 | 1235904.636 | 2698257.9384 | 1235904.3987
87 | 2698247.8636 | 1235904.1629 | 2698239.4462 | 1235903.9659 | 2698231.3505 | 1235905.3004
88 | 2698183.0232 | 1235934.8164 | 2698191.4812 | 1235945.7907
89 | 2698183.0232 | 1235934.8164 | 2698180.9796 | 1235932.1649 | 2698177.5056 | 1235927.0481
90 | 2698177.5056 | 1235927.0481 | 2698174.6299 | 1235922.8125
91 | 2698174.6299 | 1235922.8125 | 2698165.5961 | 1235909.5067
92 | 2698257.9384 | 1235904.3987 | 2698247.8636 | 1235904.1629
93 | 2698157.5969 | 1235897.0038 | 2698163.5639 | 1235906.5136 | 2698165.5961 | 1235909.5067
94 | 2698157.5969 | 1235897.0038 | 2698155.8723 | 1235894.2552 | 2698151.2083 | 1235886.3617
95 | 2698149.3225 | 1235872.4419 | 2698148.4465 | 1235874.1509 | 2698147.7167 | 1235876.1737 | 2698147.4468 | 1235877.8482 | 2698147.5477 | 1235879.5289 | 2698148.156 | 1235881.1958 | 2698151.2083 | 1235886.3617
96 | 2698149.3225 | 1235872.4419 | 2698140.6935 | 1235872.9219 | 2698139.7532 | 1235873.0287 | 2698139.0527 | 1235873.284 | 2698138.2515 | 1235873.671 | 2698085.2108 | 1235912.0237
97 | 2698153.8665 | 1235865.8676 | 2698150.784 | 1235870.1087 | 2698149.3225 | 1235872.4419
98 | 2698140.4117 | 1235855.1707 | 2698148.3207 | 1235861.6173 | 2698153.8665 | 1235865.8676
99 | 2698140.4117 | 1235855.1707 | 2698129.4075 | 1235863.3506
100 | 2698140.4117 | 1235855.1707 | 2698137.0963 | 1235852.4361 | 2698131.4742 | 1235847.762
101 | 2698131.4742 | 1235847.762 | 2698138.9535 | 1235839.446 | 2698141.6296 | 1235836.8995 | 2698143.6729 | 1235835.0874 | 2698144.9472 | 1235834.1731
102 | 2698119.2503 | 1235837.2301 | 2698124.3214 | 1235841.8173 | 2698131.4742 | 1235847.762
103 | 2698144.9472 | 1235834.1731 | 2698146.3691 | 1235833.1527 | 2698150.103 | 1235831.1796 | 2698162.1213 | 1235826.2189 | 2698171.0358 | 1235823.1195 | 2698175.248 | 1235821.7894
104 | 2698119.2503 | 1235837.2301 | 2698114.4486 | 1235832.3694 | 2698110.18 | 1235827.7733 | 2698108.442 | 1235825.6555
105 | 2698119.2503 | 1235837.2301 | 2698116.0552 | 1235839.1232 | 2698113.6016 | 1235840.5726 | 2698111.2436 | 1235841.7346 | 2698108.2861 | 1235842.9867 | 2698094.7459 | 1235848.4449 | 2698092.869 | 1235849.348 | 2698090.4965 | 1235850.4763 | 2698088.2976 | 1235851.6471
106 | 2698073.1116 | 1235860.4968 | 2698072.876 | 1235863.762 | 2698073.0465 | 1235864.899 | 2698073.4675 | 1235865.9845 | 2698074.1178 | 1235866.9404 | 2698074.9676 | 1235867.7328 | 2698075.9722 | 1235868.3165 | 2698077.079 | 1235868.6683
107 | 2698077.3169 | 1235857.9309 | 2698074.0144 | 1235859.9112 | 2698073.1116 | 1235860.4968
108 | 2698077.3169 | 1235857.9309 | 2698079.7096 | 1235856.5027 | 2698085.7163 | 1235853.0215 | 2698088.2976 | 1235851.6471
109 | 2698105.0827 | 1235821.5623 | 2698108.442 | 1235825.6555
110 | 2698105.0827 | 1235821.5623 | 2698111.5324 | 1235816.0091 | 2698110.2919 | 1235811.3852
111 | 2698030.1273 | 1235751.4174 | 2698035.4595 | 1235752.5729 | 2698040.144 | 1235753.9957 | 2698044.9968 | 1235755.766 | 2698049.3934 | 1235757.6622 | 2698053.1098 | 1235759.4916 | 2698058.1719 | 1235762.3439 | 2698063.246 | 1235765.3743 | 2698067.9317 | 1235768.554 | 2698072.0651 | 1235771.7246 | 2698076.5784 | 1235775.7132 | 2698080.2805 | 1235779.3325 | 2698084.6047 | 1235784.2298 | 2698097.4963 | 1235801.0885 | 2698098.0113 | 1235801.9865 | 2698098.4861 | 1235803.0285 | 2698098.6581 | 1235804.0654 | 2698098.8926 | 1235813.6987 | 2698105.0827 | 1235821.5623
112 | 2698110.2919 | 1235811.3852 | 2698118.3442 | 1235805.0356 | 2698119.5073 | 1235804.1765
113 | 2698135.0355 | 1235793.9475 | 2698130.9719 | 1235798.9285 | 2698128.726 | 1235801.5489 | 2698126.1106 | 1235804.0854 | 2698111.5324 | 1235816.0091 | 2698110.2919 | 1235811.3852
114 | 2697938.8404 | 1235765.4224 | 2697957.1662 | 1235762.6002 | 2697995.1511 | 1235756.889 | 2698001.636 | 1235756.0842 | 2698005.592 | 1235755.7826 | 2698011.2167 | 1235755.7309 | 2698016.97 | 1235756.1372 | 2698023.0128 | 1235756.893 | 2698028.8079 | 1235757.9783 | 2698030.1273 | 1235751.4174
115 | 2698135.0355 | 1235793.9475 | 2698145.2171 | 1235801.6547 | 2698149.2903 | 1235806.706
116 | 2698135.0355 | 1235793.9475 | 2698144.1224 | 1235781.6454
117 | 2698149.2903 | 1235806.706 | 2698155.2305 | 1235814.0727
118 | 2698144.1224 | 1235781.6454 | 2698145.121 | 1235780.2934
119 | 2697938.8404 | 1235765.4224 | 2697890.1993 | 1235772.9153 | 2697883.1182 | 1235773.6214 | 2697875.8287 | 1235774.1128 | 2697873.5265 | 1235774.1861
120 | 2697938.8404 | 1235765.4224 | 2697936.1045 | 1235753.702 | 2697935.2 | 1235751.6411 | 2697933.8121 | 1235749.9725 | 2697932.0677 | 1235748.8096
121 | 2697860.3648 | 1235767.7089 | 2697860.0985 | 1235774.2205 | 2697868.5816 | 1235774.3269 | 2697873.5265 | 1235774.1861
122 | 2697919.179 | 1235763.565 | 2697918.2206 | 1235763.6924 | 2697897.5628 | 1235766.7034
123 | 2697860.3648 | 1235767.7089 | 2697861.8428 | 1235768.0446 | 2697863.4204 | 1235768.3041 | 2697864.5839 | 1235768.4345 | 2697866.0504 | 1235768.5476 | 2697870.2265 | 1235768.672 | 2697875.3275 | 1235768.7005 | 2697880.6574 | 1235768.6216 | 2697883.5063 | 1235768.4462 | 2697886.1586 | 1235768.2564 | 2697889.093 | 1235767.9379 | 2697897.5628 | 1235766.7034
124 | 2697846.7082 | 1236162.3328 | 2697838.5315 | 1236156.9914
125 | 2697827.6938 | 1236145.9297 | 2697837.7676 | 1236156.4924 | 2697838.5315 | 1236156.9914
126 | 2697827.6938 | 1236145.9297 | 2697836.4597 | 1236142.6272 | 2697846.245 | 1236134.8714 | 2697861.2075 | 1236118.3723 | 2697891.1223 | 1236081.8824 | 2697900.2894 | 1236069.4019 | 2697910.4036 | 1236054.825
127 | 2697910.5178 | 1236054.6604 | 2697910.4036 | 1236054.825

## bus_geodata
| x | y | coords
0 | 2698595.2253 | 1236403.7072
1 | 2698583.9003 | 1236417.543
2 | 2698609.9276 | 1236347.8229
3 | 2698512.2925 | 1236415.0867
4 | 2698581.8858 | 1236338.3172
5 | 2698498.0853 | 1236390.0992
6 | 2698501.5711 | 1236346.9581
7 | 2698467.0814 | 1236310.0478
8 | 2698569.6322 | 1236351.3894
9 | 2698426.5507 | 1236415.1657
10 | 2698446.007 | 1236397.4676
11 | 2698292.1364 | 1236551.9868
12 | 2698426.7556 | 1236369.0235
13 | 2698444.2428 | 1236803.2263
14 | 2698416.2599 | 1236846.4282
15 | 2698516.3629 | 1236720.204
16 | 2698412.5164 | 1236772.3692
17 | 2698423.5922 | 1236859.2593
18 | 2698408.7084 | 1236858.4826
19 | 2698401.9657 | 1236873.5135
20 | 2698391.6851 | 1236903.773
21 | 2698386.6308 | 1236917.3015
22 | 2698370.5033 | 1236920.8176
23 | 2698431.934 | 1236963.8382
24 | 2698443.1492 | 1236269.0317
25 | 2698412.9449 | 1236185.9344
26 | 2698436.7232 | 1236273.1616
27 | 2698450.6819 | 1236321.6991
28 | 2698440.6719 | 1236279.5802
29 | 2698547.1127 | 1236346.2528
30 | 2698433.409 | 1236364.4081
31 | 2698442.0591 | 1236348.8243
32 | 2698408.882 | 1236768.2704
33 | 2698395.8741 | 1236753.6002
34 | 2698386.1539 | 1236740.9191
35 | 2698385.448 | 1236739.9493
36 | 2698374.9849 | 1236725.5753
37 | 2698372.3844 | 1236722.0029
38 | 2698369.3181 | 1236920.1831
39 | 2698253.939 | 1236509.5455
40 | 2698186.5459 | 1236568.9673
41 | 2698181.9073 | 1236573.0576
42 | 2698043.2685 | 1236449.3756
43 | 2698433.0883 | 1236266.3181
44 | 2698401.4694 | 1236171.6397
45 | 2698400.8597 | 1236169.7683
46 | 2698439.0019 | 1236276.94
47 | 2698406.8259 | 1236167.8101
48 | 2698377.7637 | 1236110.1969
49 | 2698387.9874 | 1236114.8586
50 | 2698361.0832 | 1236127.576
51 | 2698393.8822 | 1236132.2803
52 | 2698427.7935 | 1236095.1971
53 | 2698374.0329 | 1236086.129
54 | 2698351.131 | 1236137.9449
55 | 2698353.5489 | 1236045.0364
56 | 2698338.0087 | 1236020.3656
57 | 2698331.0382 | 1236016.7872
58 | 2698317.1345 | 1235996.9012
59 | 2698315.0322 | 1236025.5428
60 | 2698012.9123 | 1236469.4962
61 | 2698057.4595 | 1236184.5902
62 | 2698051.5442 | 1236180.1538
63 | 2697997.9313 | 1236478.955
64 | 2698428.7486 | 1236094.0978
65 | 2698255.7903 | 1235945.4114
66 | 2698311.6204 | 1236027.2495
67 | 2698044.7259 | 1236175.04
68 | 2697899.3424 | 1236168.3988
69 | 2697868.2523 | 1236162.4606
70 | 2697962.5253 | 1236571.7017
71 | 2697958.9432 | 1236529.6557
72 | 2698094.5648 | 1236125.5592
73 | 2698276.3983 | 1236070.8217
74 | 2698306.1437 | 1236034.169
75 | 2698264.8955 | 1235934.4427
76 | 2698282.2848 | 1235914.1041
77 | 2698231.7546 | 1235926.0218
78 | 2698211.009 | 1235909.511
79 | 2698207.5376 | 1235950.0669
80 | 2698294.8041 | 1235903.103
81 | 2698268.0734 | 1235904.636
82 | 2698313.9195 | 1235924.1882
83 | 2698231.3505 | 1235905.3004
84 | 2698187.8144 | 1235891.1407
85 | 2698191.4812 | 1235945.7907
86 | 2698183.0232 | 1235934.8164
87 | 2698177.5056 | 1235927.0481
88 | 2698174.6299 | 1235922.8125
89 | 2698247.8636 | 1235904.1629
90 | 2698165.5961 | 1235909.5067
91 | 2698157.5969 | 1235897.0038
92 | 2698151.2083 | 1235886.3617
93 | 2698149.3225 | 1235872.4419
94 | 2698085.2108 | 1235912.0237
95 | 2698153.8665 | 1235865.8676
96 | 2698140.4117 | 1235855.1707
97 | 2698129.4075 | 1235863.3506
98 | 2698131.4742 | 1235847.762
99 | 2698144.9472 | 1235834.1731
100 | 2698119.2503 | 1235837.2301
101 | 2698257.9384 | 1235904.3987
102 | 2698307.9407 | 1235892.3123
103 | 2698077.079 | 1235868.6683
104 | 2698073.1116 | 1235860.4968
105 | 2698077.3169 | 1235857.9309
106 | 2698088.2976 | 1235851.6471
107 | 2698108.442 | 1235825.6555
108 | 2698105.0827 | 1235821.5623
109 | 2698110.2919 | 1235811.3852
110 | 2698030.1273 | 1235751.4174
111 | 2698135.0355 | 1235793.9475
112 | 2698149.2903 | 1235806.706
113 | 2698144.1224 | 1235781.6454
114 | 2698119.5073 | 1235804.1765
115 | 2697938.8404 | 1235765.4224
116 | 2698175.248 | 1235821.7894
117 | 2698155.2305 | 1235814.0727
118 | 2698145.121 | 1235780.2934
119 | 2697873.5265 | 1235774.1861
120 | 2697932.0677 | 1235748.8096
121 | 2697919.179 | 1235763.565
122 | 2697897.5628 | 1235766.7034
123 | 2697846.7082 | 1236162.3328
124 | 2697838.5315 | 1236156.9914
125 | 2697827.6938 | 1236145.9297
126 | 2697910.4036 | 1236054.825
127 | 2697910.5178 | 1236054.6604
128 | 2697860.3648 | 1235767.7089
129 | 2698331.0382 | 1236016.7872

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98023 | -0.37786 | 0.010509 | 0.0026338
1 | 0.98081 | -0.36648 | 0 | 0
2 | 0.97653 | -0.44997 | 0 | 0
3 | 0.9829 | -0.32606 | 0 | 0
4 | 0.97296 | -0.52015 | 0 | 0
5 | 0.98286 | -0.32681 | 0.0014396 | 0.0003608
6 | 0.9851 | -0.28358 | 0 | 0
7 | 0.98622 | -0.26196 | 0 | 0
8 | 0.97196 | -0.53995 | 0.036839 | 0.0092327
9 | 0.98343 | -0.31612 | 0 | 0
10 | 0.98342 | -0.31622 | 0.00022255 | 5.5776e-05
11 | 0.97968 | -0.38938 | 0 | 0
12 | 0.98443 | -0.29663 | 0.00083187 | 0.00020849
13 | 0.97619 | -0.45787 | 0 | 0
14 | 0.97601 | -0.46157 | 0 | 0
15 | 0.97611 | -0.45946 | 0.00078691 | 0.00019722
16 | 0.97639 | -0.45404 | 0.0031716 | 0.00079487
17 | 0.976 | -0.46165 | 0.00030707 | 7.696e-05
18 | 0.97596 | -0.46251 | 0.00011127 | 2.7886e-05
19 | 0.9759 | -0.46357 | 0.00030539 | 7.6539e-05
20 | 0.97581 | -0.46544 | 0.00044945 | 0.00011264
21 | 0.97577 | -0.46617 | 0 | 0
22 | 0.97576 | -0.46633 | 0.00026384 | 6.6126e-05
23 | 0.97563 | -0.46897 | 0.0023426 | 0.00058711
24 | 0.98789 | -0.2298 | 0 | 0
25 | 0.99058 | -0.17829 | 0.00059283 | 0.00014858
26 | 0.98766 | -0.23425 | 0 | 0
27 | 0.98574 | -0.27121 | 0.00082906 | 0.00020778
28 | 0.98743 | -0.23862 | 0.00032237 | 8.0793e-05
29 | 0.97129 | -0.55321 | 0.02287 | 0.0057316
30 | 0.9846 | -0.2934 | 0.0018454 | 0.0004625
31 | 0.985 | -0.28565 | 0.00028867 | 7.2349e-05
32 | 0.97643 | -0.45325 | 0.0020255 | 0.00050764
33 | 0.97661 | -0.4497 | 0.0017754 | 0.00044495
34 | 0.97678 | -0.44628 | 0.0014617 | 0.00036635
35 | 0.9768 | -0.44599 | 0.00067946 | 0.00017029
36 | 0.97702 | -0.4415 | 0.00068921 | 0.00017273
37 | 0.97708 | -0.44033 | 0.00035749 | 8.9595e-05
38 | 0.97576 | -0.46633 | 0.00014016 | 3.5127e-05
39 | 0.97932 | -0.39636 | 0 | 0
40 | 0.97881 | -0.40652 | 0.00070045 | 0.00017555
41 | 0.97877 | -0.40714 | 0.00073922 | 0.00018527
42 | 0.97795 | -0.4233 | 0.0012803 | 0.00032086
43 | 0.98766 | -0.23434 | 0.0006114 | 0.00015323
44 | 0.99117 | -0.16718 | 0.00036634 | 9.1813e-05
45 | 0.99117 | -0.16717 | 0 | 0
46 | 0.98753 | -0.23681 | 0.00025965 | 6.5074e-05
47 | 0.99117 | -0.16713 | 0 | 0
48 | 0.99289 | -0.13438 | 0 | 0
49 | 0.99291 | -0.13399 | 0 | 0
50 | 0.99286 | -0.135 | 0.00036554 | 9.1612e-05
51 | 0.99233 | -0.14501 | 0 | 0
52 | 0.99225 | -0.14662 | 0.0012083 | 0.00030282
53 | 0.99392 | -0.11476 | 0.00054222 | 0.00013589
54 | 0.99285 | -0.13527 | 0.0010776 | 0.00027007
55 | 0.99539 | -0.087035 | 0 | 0
56 | 0.99632 | -0.069399 | 0.00071607 | 0.00017946
57 | 0.99667 | -0.062837 | 0 | 0
58 | 0.99488 | -0.096787 | 0.0038204 | 0.00095748
59 | 0.9986 | -0.026407 | 0.001229 | 0.00030801
60 | 0.97784 | -0.42562 | 0.00098185 | 0.00024607
61 | 0.99875 | -0.024075 | 0.00085038 | 0.00021313
62 | 0.99876 | -0.023965 | 0.0010016 | 0.00025102
63 | 0.97779 | -0.42643 | 0.001499 | 0.00037568
64 | 0.99225 | -0.14664 | 0.0006043 | 0.00015145
65 | 0.98908 | -0.20791 | 0 | 0
66 | 0.999 | -0.018774 | 0.0019203 | 0.00048126
67 | 0.99877 | -0.023689 | 0 | 0
68 | 0.99846 | -0.02979 | 0.00042402 | 0.00010627
69 | 0.9984 | -0.030892 | 0.00084843 | 0.00021264
70 | 0.9777 | -0.42838 | 0.001006 | 0.00025213
71 | 0.97773 | -0.42761 | 0 | 0
72 | 0.99904 | -0.018455 | 0 | 0
73 | 0.99977 | -0.0043435 | 0.00087325 | 0.00021886
74 | 1 | 0 | -0.35837 | -0.091876
75 | 0.98805 | -0.22778 | 0 | 0
76 | 0.98612 | -0.26519 | 0 | 0
77 | 0.98223 | -0.34052 | 0 | 0
78 | 0.98292 | -0.32713 | 0 | 0
79 | 0.98134 | -0.35781 | 0.0026677 | 0.00066858
80 | 0.98517 | -0.28361 | 0 | 0
81 | 0.98518 | -0.28327 | 0.040662 | 0.010191
82 | 0.98404 | -0.30559 | 0.042963 | 0.010768
83 | 0.98375 | -0.31112 | 0.0054374 | 0.0013627
84 | 0.98203 | -0.34469 | 0.032868 | 0.0082374
85 | 0.98085 | -0.36749 | 0.0015513 | 0.00038878
86 | 0.9805 | -0.37417 | 0.0015788 | 0.00039568
87 | 0.98027 | -0.37868 | 0.0015148 | 0.00037964
88 | 0.98015 | -0.38106 | 0.0019364 | 0.00048531
89 | 0.98438 | -0.29892 | 0.0034563 | 0.00086623
90 | 0.97978 | -0.38834 | 0.002671 | 0.00066941
91 | 0.97928 | -0.39807 | 0.0033445 | 0.00083821
92 | 0.97849 | -0.4136 | 0.0041159 | 0.0010315
93 | 0.97757 | -0.43155 | 0 | 0
94 | 0.97746 | -0.43361 | 0.0014742 | 0.00036948
95 | 0.9771 | -0.44076 | 0 | 0
96 | 0.97609 | -0.46059 | 0 | 0
97 | 0.97599 | -0.46249 | 0.007595 | 0.0019035
98 | 0.97549 | -0.47238 | 0 | 0
99 | 0.97529 | -0.47626 | 0.0044774 | 0.0011221
100 | 0.97482 | -0.48555 | 0.0043918 | 0.0011007
101 | 0.98477 | -0.29131 | 0.0066519 | 0.0016671
102 | 0.98488 | -0.28927 | 0.01857 | 0.004654
103 | 0.97449 | -0.492 | 0.0048061 | 0.0012045
104 | 0.97454 | -0.4911 | 0 | 0
105 | 0.97456 | -0.49066 | 0 | 0
106 | 0.97462 | -0.48955 | 0.0015656 | 0.00039239
107 | 0.97432 | -0.49538 | 0.0046256 | 0.0011593
108 | 0.97418 | -0.49822 | 0 | 0
109 | 0.97389 | -0.50383 | 0 | 0
110 | 0.97355 | -0.5106 | 0 | 0
111 | 0.97328 | -0.51606 | 0 | 0
112 | 0.9732 | -0.51759 | 0.0015002 | 0.00037598
113 | 0.97308 | -0.51988 | 0.010602 | 0.0026572
114 | 0.97384 | -0.50493 | 0.0050952 | 0.001277
115 | 0.97299 | -0.52169 | 0 | 0
116 | 0.97509 | -0.48021 | 0.0065629 | 0.0016448
117 | 0.97317 | -0.51809 | 0.0028323 | 0.00070984
118 | 0.97308 | -0.51997 | 0.0029606 | 0.00074199
119 | 0.9727 | -0.52737 | 0 | 0
120 | 0.97296 | -0.5222 | 0.0014956 | 0.00037483
121 | 0.97237 | -0.53398 | 0.0041414 | 0.0010379
122 | 0.97245 | -0.53231 | 0.00054008 | 0.00013536
123 | 0.99838 | -0.031314 | 0 | 0
124 | 0.99837 | -0.031506 | 0.00050587 | 0.00012678
125 | 0.99836 | -0.031673 | 0 | 0
126 | 0.99829 | -0.033007 | 0.00022975 | 5.758e-05
127 | 0.99829 | -0.033009 | 0.00038089 | 9.5461e-05
128 | 0.97262 | -0.52909 | 0 | 0
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.070697 | -0.017903 | 0.070736 | 0.017927 | 3.866e-05 | 2.4291e-05 | 0.10739 | 0.10739 | 0.10739 | 0.98023 | -0.37786 | 0.98081 | -0.36648 | 14.7509
1 | 0.060188 | 0.015269 | -0.05998 | -0.015137 | 0.00020793 | 0.00013224 | 0.091434 | 0.091434 | 0.091434 | 0.98023 | -0.37786 | 0.97653 | -0.44997 | 25.1193
2 | -0.070736 | -0.017927 | 0.070873 | 0.018012 | 0.00013766 | 8.4477e-05 | 0.10739 | 0.10739 | 0.10739 | 0.98081 | -0.36648 | 0.9829 | -0.32606 | 9.8339
3 | 0.05998 | 0.015137 | -0.059779 | -0.015009 | 0.00020085 | 0.00012775 | 0.091434 | 0.091434 | 0.091434 | 0.97653 | -0.44997 | 0.97296 | -0.52015 | 25.1194
4 | 0.0014397 | 0.00036047 | -0.0014396 | -0.0003608 | 5.1169e-08 | -3.3132e-07 | 0.0021794 | 0.0021795 | 0.0021795 | 0.9829 | -0.32606 | 0.98286 | -0.32681 | 0.59877
5 | -0.072313 | -0.018372 | 0.072461 | 0.018463 | 0.0001482 | 9.1087e-05 | 0.10956 | 0.10956 | 0.10956 | 0.9829 | -0.32606 | 0.9851 | -0.28358 | 10.0334
6 | 0.059779 | 0.015009 | -0.059723 | -0.014973 | 5.6415e-05 | 3.5883e-05 | 0.091434 | 0.091435 | 0.091435 | 0.97296 | -0.52015 | 0.97196 | -0.53995 | 25.1194
7 | -0.072461 | -0.018463 | 0.072537 | 0.01851 | 7.57e-05 | 4.6519e-05 | 0.10956 | 0.10956 | 0.10956 | 0.9851 | -0.28358 | 0.98622 | -0.26196 | 10.0333
8 | 0.025282 | 0.0063918 | -0.025271 | -0.0063849 | 1.1209e-05 | 6.9122e-06 | 0.038166 | 0.038166 | 0.038166 | 0.98622 | -0.26196 | 0.98574 | -0.27121 | 10.4851
9 | -0.097819 | -0.024902 | 0.097929 | 0.02497 | 0.00011018 | 6.8968e-05 | 0.14773 | 0.14773 | 0.14773 | 0.98622 | -0.26196 | 0.98743 | -0.23862 | 13.5282
10 | 0.022884 | 0.0057405 | -0.02287 | -0.0057316 | 1.4448e-05 | 8.8583e-06 | 0.035036 | 0.035036 | 0.035036 | 0.97196 | -0.53995 | 0.97129 | -0.55321 | 9.6253
11 | 0.00022255 | 5.5443e-05 | -0.00022255 | -5.5776e-05 | 1.118e-09 | -3.33e-07 | 0.00033662 | 0.00033674 | 0.00033674 | 0.98343 | -0.31612 | 0.98342 | -0.31622 | 0.09251
12 | 0.021204 | 0.0053482 | -0.02113 | -0.0053032 | 7.4094e-05 | 4.4996e-05 | 0.032096 | 0.032097 | 0.032097 | 0.98343 | -0.31612 | 0.97968 | -0.38938 | 8.8177
13 | -0.021427 | -0.0054036 | 0.021447 | 0.0054158 | 2.0007e-05 | 1.216e-05 | 0.032432 | 0.032432 | 0.032432 | 0.98343 | -0.31612 | 0.98443 | -0.29663 | 8.91
14 | 0.0062162 | 0.0015553 | -0.0062142 | -0.0015547 | 2.0658e-06 | 5.4417e-07 | 0.0094408 | 0.0094411 | 0.0094411 | 0.97968 | -0.38938 | 0.97932 | -0.39636 | 2.5937
15 | 0.014914 | 0.0037479 | -0.014878 | -0.0037271 | 3.6189e-05 | 2.08e-05 | 0.022656 | 0.022657 | 0.022657 | 0.97968 | -0.38938 | 0.97708 | -0.44033 | 6.2244
16 | -0.022278 | -0.0056243 | 0.022282 | 0.0056264 | 3.4478e-06 | 2.1036e-06 | 0.033689 | 0.033689 | 0.033689 | 0.98443 | -0.29663 | 0.9846 | -0.2934 | 9.2554
17 | 0.0039215 | 0.0009806 | -0.0039208 | -0.00098081 | 6.9e-07 | -2.0222e-07 | 0.0059768 | 0.005977 | 0.005977 | 0.97619 | -0.45787 | 0.97601 | -0.46157 | 1.642
18 | 0.00078697 | 0.00019588 | -0.00078691 | -0.00019722 | 5.9448e-08 | -1.3397e-06 | 0.0011991 | 0.0011996 | 0.0011996 | 0.97619 | -0.45787 | 0.97611 | -0.45946 | 0.32956
19 | -0.0047085 | -0.0011765 | 0.0047093 | 0.0011765 | 8.574e-07 | -6.5088e-09 | 0.0071759 | 0.0071757 | 0.0071759 | 0.97619 | -0.45787 | 0.97639 | -0.45404 | 1.9714
20 | 0.00030707 | 7.6776e-05 | -0.00030707 | -7.696e-05 | 1.2137e-09 | -1.8379e-07 | 0.0004681 | 0.00046817 | 0.00046817 | 0.97601 | -0.46157 | 0.976 | -0.46165 | 0.12862
21 | 0.0036137 | 0.00090403 | -0.0036136 | -0.0009041 | 1.6192e-07 | -7.4169e-08 | 0.0055089 | 0.005509 | 0.005509 | 0.97601 | -0.46157 | 0.97596 | -0.46251 | 1.5134
22 | -0.0078809 | -0.0019713 | 0.0078812 | 0.0019715 | 2.9626e-07 | 1.2109e-07 | 0.012009 | 0.012009 | 0.012009 | 0.97639 | -0.45404 | 0.97643 | -0.45325 | 3.2992
23 | 0.0035023 | 0.00087622 | -0.0035021 | -0.00087631 | 1.7661e-07 | -9.3391e-08 | 0.0053393 | 0.0053394 | 0.0053394 | 0.97596 | -0.46251 | 0.9759 | -0.46357 | 1.4669
24 | 0.0031967 | 0.00079977 | -0.0031964 | -0.00079999 | 2.8469e-07 | -2.1709e-07 | 0.0048737 | 0.0048739 | 0.0048739 | 0.9759 | -0.46357 | 0.97581 | -0.46544 | 1.339
25 | 0.002747 | 0.00068735 | -0.0027469 | -0.00068747 | 9.5094e-08 | -1.197e-07 | 0.0041885 | 0.0041886 | 0.0041886 | 0.97581 | -0.46544 | 0.97577 | -0.46617 | 1.1507
26 | 0.00040401 | 0.00010097 | -0.000404 | -0.00010124 | 3.0069e-09 | -2.62e-07 | 0.000616 | 0.00061609 | 0.00061609 | 0.97577 | -0.46617 | 0.97576 | -0.46633 | 0.16926
27 | 0.0023429 | 0.00058649 | -0.0023426 | -0.00058711 | 3.123e-07 | -6.1499e-07 | 0.0035726 | 0.0035729 | 0.0035729 | 0.97577 | -0.46617 | 0.97563 | -0.46897 | 0.98156
28 | 0.00014016 | 3.5111e-05 | -0.00014016 | -3.5127e-05 | 2.3029e-11 | -1.6777e-08 | 0.00021373 | 0.00021374 | 0.00021374 | 0.97576 | -0.46633 | 0.97576 | -0.46633 | 0.05872
29 | -0.099165 | -0.025296 | 0.099412 | 0.025451 | 0.00024734 | 0.00015489 | 0.14953 | 0.14952 | 0.14953 | 0.98789 | -0.2298 | 0.99058 | -0.17829 | 13.6928
30 | 0.099165 | 0.025296 | -0.099143 | -0.025282 | 2.131e-05 | 1.3345e-05 | 0.14953 | 0.14953 | 0.14953 | 0.98789 | -0.2298 | 0.98766 | -0.23425 | 13.6928
31 | -0.1 | -0.025599 | 0.10006 | 0.025633 | 5.4099e-05 | 3.3884e-05 | 0.15041 | 0.15041 | 0.15041 | 0.99058 | -0.17829 | 0.99117 | -0.16713 | 13.7742
32 | 0.098532 | 0.025129 | -0.09852 | -0.025122 | 1.218e-05 | 7.6256e-06 | 0.1486 | 0.1486 | 0.1486 | 0.98766 | -0.23425 | 0.98753 | -0.23681 | 13.6085
33 | 0.00061141 | 0.00015313 | -0.0006114 | -0.00015323 | 2.4658e-09 | -9.7597e-08 | 0.00092111 | 0.00092115 | 0.00092115 | 0.98766 | -0.23425 | 0.98766 | -0.23434 | 0.25306
34 | 0.024442 | 0.0061771 | -0.024425 | -0.0061667 | 1.6913e-05 | 1.0403e-05 | 0.036914 | 0.036914 | 0.036914 | 0.98574 | -0.27121 | 0.985 | -0.28565 | 10.1413
35 | -0.098251 | -0.025051 | 0.09826 | 0.025057 | 8.5815e-06 | 5.3722e-06 | 0.14821 | 0.14821 | 0.14821 | 0.98743 | -0.23862 | 0.98753 | -0.23681 | 13.5726
36 | -0.024127 | -0.0060889 | 0.024136 | 0.0060944 | 8.9575e-06 | 5.5044e-06 | 0.036478 | 0.036478 | 0.036478 | 0.9846 | -0.2934 | 0.985 | -0.28565 | 10.0215
37 | -0.0099067 | -0.0024791 | 0.0099084 | 0.0024799 | 1.6755e-06 | 8.2704e-07 | 0.015096 | 0.015096 | 0.015096 | 0.97643 | -0.45325 | 0.97661 | -0.4497 | 4.1472
38 | -0.011684 | -0.0029249 | 0.011686 | 0.0029259 | 1.9003e-06 | 1.016e-06 | 0.017801 | 0.017801 | 0.017801 | 0.97661 | -0.4497 | 0.97678 | -0.44628 | 4.8903
39 | -0.013147 | -0.0032923 | 0.013148 | 0.0032924 | 1.8042e-07 | 1.0045e-07 | 0.020028 | 0.020028 | 0.020028 | 0.97678 | -0.44628 | 0.9768 | -0.44599 | 5.5021
40 | -0.013827 | -0.0034626 | 0.01383 | 0.0034643 | 2.9577e-06 | 1.6704e-06 | 0.021063 | 0.021063 | 0.021063 | 0.9768 | -0.44599 | 0.97702 | -0.4415 | 5.7864
41 | -0.014519 | -0.003637 | 0.01452 | 0.0036375 | 8.1019e-07 | 4.6318e-07 | 0.022112 | 0.022112 | 0.022112 | 0.97702 | -0.4415 | 0.97708 | -0.44033 | 6.0748
42 | 0.0062142 | 0.0015547 | -0.0062112 | -0.001554 | 3.0033e-06 | 7.9222e-07 | 0.0094411 | 0.0094415 | 0.0094415 | 0.97932 | -0.39636 | 0.97881 | -0.40652 | 2.5938
43 | 0.0055107 | 0.0013784 | -0.0055105 | -0.0013784 | 1.6273e-07 | 2.6417e-08 | 0.0083766 | 0.0083766 | 0.0083766 | 0.97881 | -0.40652 | 0.97877 | -0.40714 | 2.3013
44 | 0.0047713 | 0.0011931 | -0.0047677 | -0.0011931 | 3.6654e-06 | 1.2723e-08 | 0.0072528 | 0.0072536 | 0.0072536 | 0.97877 | -0.40714 | 0.97795 | -0.4233 | 1.9928
45 | 0.0034874 | 0.00087223 | -0.003487 | -0.00087244 | 3.8455e-07 | -2.109e-07 | 0.0053057 | 0.0053058 | 0.0053058 | 0.97795 | -0.4233 | 0.97784 | -0.42562 | 1.4576
46 | -0.00036634 | -9.1813e-05 | 0.00036634 | 9.1788e-05 | 2.2321e-10 | -2.5226e-08 | 0.00054998 | 0.00054997 | 0.00054998 | 0.99117 | -0.16718 | 0.99117 | -0.16717 | 0.15109
47 | -0.00036634 | -9.1788e-05 | 0.00036634 | 9.1708e-05 | 7.1032e-10 | -8.0267e-08 | 0.00054997 | 0.00054994 | 0.00054997 | 0.99117 | -0.16717 | 0.99117 | -0.16713 | 0.15109
48 | -0.10043 | -0.025725 | 0.10053 | 0.025792 | 0.00010778 | 6.7517e-05 | 0.15096 | 0.15096 | 0.15096 | 0.99117 | -0.16713 | 0.99233 | -0.14501 | 13.8246
49 | -0.0014432 | -0.00036122 | 0.0014432 | 0.00036103 | 2.7062e-08 | -1.8225e-07 | 0.0021627 | 0.0021626 | 0.0021627 | 0.99289 | -0.13438 | 0.99291 | -0.13399 | 0.59414
50 | 0.0014432 | 0.00036122 | -0.0014431 | -0.0003615 | 4.2252e-08 | -2.845e-07 | 0.0021627 | 0.0021628 | 0.0021628 | 0.99289 | -0.13438 | 0.99286 | -0.135 | 0.59417
51 | -0.10384 | -0.026641 | 0.10394 | 0.026702 | 9.6983e-05 | 6.0828e-05 | 0.15584 | 0.15584 | 0.15584 | 0.99291 | -0.13399 | 0.99392 | -0.11476 | 14.2714
52 | 0.1024 | 0.02628 | -0.10235 | -0.026246 | 5.4717e-05 | 3.43e-05 | 0.15368 | 0.15368 | 0.15368 | 0.99291 | -0.13399 | 0.99233 | -0.14501 | 14.0734
53 | 0.0010776 | 0.00026989 | -0.0010776 | -0.00027007 | 1.4057e-08 | -1.7687e-07 | 0.0016149 | 0.001615 | 0.001615 | 0.99286 | -0.135 | 0.99285 | -0.13527 | 0.44368
54 | 0.0018127 | 0.00045369 | -0.0018126 | -0.00045426 | 1.3959e-07 | -5.6152e-07 | 0.002718 | 0.0027182 | 0.0027182 | 0.99233 | -0.14501 | 0.99225 | -0.14662 | 0.74676
55 | 0.0006043 | 0.00015143 | -0.0006043 | -0.00015145 | 4.485e-10 | -1.8523e-08 | 0.00090622 | 0.00090623 | 0.00090623 | 0.99225 | -0.14662 | 0.99225 | -0.14664 | 0.24896
56 | -0.10448 | -0.026838 | 0.10462 | 0.026926 | 0.00014085 | 8.8356e-05 | 0.15666 | 0.15665 | 0.15666 | 0.99392 | -0.11476 | 0.99539 | -0.087035 | 14.3457
57 | -0.10462 | -0.026926 | 0.10471 | 0.026983 | 8.9817e-05 | 5.634e-05 | 0.15665 | 0.15665 | 0.15665 | 0.99539 | -0.087035 | 0.99632 | -0.069399 | 14.3457
58 | -0.10543 | -0.027162 | 0.10546 | 0.027183 | 3.3686e-05 | 2.1136e-05 | 0.15772 | 0.15772 | 0.15772 | 0.99632 | -0.069399 | 0.99667 | -0.062837 | 14.4436
59 | 0.24192 | 0.061946 | -0.24152 | -0.061692 | 0.00039712 | 0.00025321 | 0.36165 | 0.36165 | 0.36165 | 0.99667 | -0.062837 | 0.99488 | -0.096787 | 33.1179
60 | -0.34738 | -0.089129 | 0.348 | 0.089522 | 0.00061516 | 0.00039299 | 0.51937 | 0.51937 | 0.51937 | 0.99667 | -0.062837 | 0.9986 | -0.026407 | 47.5614
61 | 0.2377 | 0.060735 | -0.23643 | -0.059925 | 0.0012699 | 0.00080964 | 0.35593 | 0.35593 | 0.35593 | 0.99488 | -0.096787 | 0.98908 | -0.20791 | 32.5948
62 | -0.34922 | -0.08983 | 0.34935 | 0.089913 | 0.00012964 | 8.2818e-05 | 0.5212 | 0.5212 | 0.5212 | 0.9986 | -0.026407 | 0.999 | -0.018774 | 47.7291
63 | 0.0025052 | 0.00062637 | -0.0025051 | -0.00062653 | 9.6548e-08 | -1.6048e-07 | 0.0038117 | 0.0038118 | 0.0038118 | 0.97784 | -0.42562 | 0.97779 | -0.42643 | 1.0472
64 | -0.00085038 | -0.00021313 | 0.00085039 | 0.00021303 | 4.4507e-09 | -9.3915e-08 | 0.001267 | 0.0012669 | 0.001267 | 0.99875 | -0.024075 | 0.99876 | -0.023965 | 0.34807
65 | -0.001852 | -0.00046405 | 0.001852 | 0.00046396 | 2.4331e-08 | -9.5967e-08 | 0.0027592 | 0.0027591 | 0.0027592 | 0.99876 | -0.023965 | 0.99877 | -0.023689 | 0.75801
66 | 0.0010061 | 0.00025085 | -0.001006 | -0.00025162 | 5.6491e-08 | -7.7017e-07 | 0.0015306 | 0.0015309 | 0.0015309 | 0.97779 | -0.42643 | 0.97773 | -0.42761 | 0.42058
67 | 0.23643 | 0.059925 | -0.2362 | -0.059781 | 0.00022551 | 0.00014378 | 0.35593 | 0.35593 | 0.35593 | 0.98908 | -0.20791 | 0.98805 | -0.22778 | 32.5948
68 | -0.35127 | -0.090394 | 0.3516 | 0.090599 | 0.00032103 | 0.00020509 | 0.52406 | 0.52406 | 0.52406 | 0.999 | -0.018774 | 1 | 0 | 47.991
69 | -0.0042418 | -0.0010587 | 0.0042429 | 0.0010584 | 1.0542e-06 | -2.4726e-07 | 0.0063181 | 0.0063178 | 0.0063181 | 0.99877 | -0.023689 | 0.99904 | -0.018455 | 1.7357
70 | 0.0023898 | 0.00059472 | -0.0023891 | -0.00059618 | 6.9141e-07 | -1.4615e-06 | 0.003559 | 0.0035597 | 0.0035597 | 0.99877 | -0.023689 | 0.99846 | -0.02979 | 0.97793
71 | 0.0019651 | 0.00048991 | -0.001965 | -0.00049027 | 1.028e-07 | -3.5244e-07 | 0.0029277 | 0.0029279 | 0.0029279 | 0.99846 | -0.02979 | 0.9984 | -0.030892 | 0.80436
72 | 0.0011166 | 0.00027763 | -0.0011166 | -0.0002779 | 2.2355e-08 | -2.6743e-07 | 0.0016634 | 0.0016635 | 0.0016635 | 0.9984 | -0.030892 | 0.99838 | -0.031314 | 0.457
73 | -0.001006 | -0.00025213 | 0.001006 | 0.00025162 | 3.718e-08 | -5.0668e-07 | 0.0015311 | 0.0015309 | 0.0015311 | 0.9777 | -0.42838 | 0.97773 | -0.42761 | 0.42063
74 | -0.0042429 | -0.0010584 | 0.0042457 | 0.0010578 | 2.8419e-06 | -6.6949e-07 | 0.0063178 | 0.0063169 | 0.0063178 | 0.99904 | -0.018455 | 0.99977 | -0.0043435 | 1.7357
75 | -0.005119 | -0.0012766 | 0.00512 | 0.0012767 | 1.0553e-06 | 3.9119e-08 | 0.0076166 | 0.0076164 | 0.0076166 | 0.99977 | -0.0043435 | 1 | 0 | 2.0925
76 | 0.2362 | 0.059781 | -0.23578 | -0.059512 | 0.00042329 | 0.00026988 | 0.35593 | 0.35594 | 0.35594 | 0.98805 | -0.22778 | 0.98612 | -0.26519 | 32.5948
77 | 0.061637 | 0.015487 | -0.061583 | -0.015453 | 5.4126e-05 | 3.4428e-05 | 0.093023 | 0.093023 | 0.093023 | 0.98612 | -0.26519 | 0.98517 | -0.28361 | 25.5557
78 | 0.17414 | 0.044024 | -0.17399 | -0.043928 | 0.00015084 | 9.5872e-05 | 0.26291 | 0.26291 | 0.26291 | 0.98612 | -0.26519 | 0.98518 | -0.28327 | 24.0763
79 | -0.084576 | -0.021389 | 0.08463 | 0.021422 | 5.4368e-05 | 3.379e-05 | 0.1282 | 0.12819 | 0.1282 | 0.98223 | -0.34052 | 0.98292 | -0.32713 | 11.7395
80 | 0.084576 | 0.021389 | -0.084505 | -0.021345 | 7.0105e-05 | 4.3572e-05 | 0.1282 | 0.1282 | 0.1282 | 0.98223 | -0.34052 | 0.98134 | -0.35781 | 11.7395
81 | -0.11753 | -0.029677 | 0.11762 | 0.029734 | 9.0188e-05 | 5.6854e-05 | 0.178 | 0.178 | 0.178 | 0.98292 | -0.32713 | 0.98375 | -0.31112 | 16.3001
82 | 0.032895 | 0.0082546 | -0.032868 | -0.0082374 | 2.752e-05 | 1.7238e-05 | 0.049803 | 0.049803 | 0.049803 | 0.98292 | -0.32713 | 0.98203 | -0.34469 | 13.6821
83 | 0.081838 | 0.020677 | -0.0818 | -0.020653 | 3.7932e-05 | 2.3531e-05 | 0.12415 | 0.12415 | 0.12415 | 0.98134 | -0.35781 | 0.98085 | -0.36749 | 11.3691
84 | 0.018575 | 0.004657 | -0.01857 | -0.004654 | 5.0098e-06 | 2.9902e-06 | 0.028056 | 0.028056 | 0.028056 | 0.98517 | -0.28361 | 0.98488 | -0.28927 | 7.7077
85 | 0.043008 | 0.010796 | -0.042963 | -0.010768 | 4.5045e-05 | 2.8467e-05 | 0.064967 | 0.064967 | 0.064967 | 0.98517 | -0.28361 | 0.98404 | -0.30559 | 17.848
86 | 0.13333 | 0.033737 | -0.13328 | -0.033705 | 5.145e-05 | 3.2541e-05 | 0.2015 | 0.2015 | 0.2015 | 0.98518 | -0.28327 | 0.98477 | -0.29131 | 18.4521
87 | -0.12305 | -0.031097 | 0.12312 | 0.031142 | 7.2065e-05 | 4.5488e-05 | 0.18622 | 0.18622 | 0.18622 | 0.98375 | -0.31112 | 0.98438 | -0.29892 | 17.0533
88 | 0.080249 | 0.020264 | -0.080223 | -0.020248 | 2.5692e-05 | 1.5919e-05 | 0.1218 | 0.1218 | 0.1218 | 0.98085 | -0.36749 | 0.9805 | -0.37417 | 11.1536
89 | 0.078644 | 0.019853 | -0.078627 | -0.019842 | 1.6988e-05 | 1.0511e-05 | 0.1194 | 0.1194 | 0.1194 | 0.9805 | -0.37417 | 0.98027 | -0.37868 | 10.9342
90 | 0.077112 | 0.019462 | -0.077104 | -0.019457 | 8.7756e-06 | 5.4228e-06 | 0.1171 | 0.1171 | 0.1171 | 0.98027 | -0.37868 | 0.98015 | -0.38106 | 10.7237
91 | 0.075167 | 0.018972 | -0.075141 | -0.018956 | 2.6201e-05 | 1.6161e-05 | 0.11416 | 0.11416 | 0.11416 | 0.98015 | -0.38106 | 0.97978 | -0.38834 | 10.4545
92 | -0.12658 | -0.032008 | 0.12663 | 0.032038 | 4.617e-05 | 2.9164e-05 | 0.19145 | 0.19145 | 0.19145 | 0.98438 | -0.29892 | 0.98477 | -0.29131 | 17.5317
93 | 0.07247 | 0.018286 | -0.072436 | -0.018265 | 3.3744e-05 | 2.1222e-05 | 0.11011 | 0.11011 | 0.11011 | 0.97978 | -0.38834 | 0.97928 | -0.39807 | 15.1245
94 | 0.069092 | 0.017427 | -0.06904 | -0.017394 | 5.1345e-05 | 3.2705e-05 | 0.10502 | 0.10502 | 0.10502 | 0.97928 | -0.39807 | 0.97849 | -0.4136 | 28.8529
95 | 0.064924 | 0.016362 | -0.064869 | -0.016327 | 5.5694e-05 | 3.5453e-05 | 0.098765 | 0.098766 | 0.098766 | 0.97849 | -0.4136 | 0.97757 | -0.43155 | 27.1334
96 | 0.0014744 | 0.00036861 | -0.0014742 | -0.00036948 | 1.4452e-07 | -8.6685e-07 | 0.0022439 | 0.0022442 | 0.0022442 | 0.97757 | -0.43155 | 0.97746 | -0.43361 | 0.61655
97 | 0.063394 | 0.015958 | -0.063366 | -0.015941 | 2.7911e-05 | 1.7763e-05 | 0.096522 | 0.096522 | 0.096522 | 0.97757 | -0.43155 | 0.9771 | -0.44076 | 26.5169
98 | 0.063366 | 0.015941 | -0.063307 | -0.015902 | 5.9948e-05 | 3.8152e-05 | 0.096522 | 0.096522 | 0.096522 | 0.9771 | -0.44076 | 0.97609 | -0.46059 | 26.517
99 | 0.0075957 | 0.0019038 | -0.007595 | -0.0019035 | 6.882e-07 | 2.6939e-07 | 0.011579 | 0.011579 | 0.011579 | 0.97609 | -0.46059 | 0.97599 | -0.46249 | 3.1812
100 | 0.055711 | 0.013999 | -0.055679 | -0.013979 | 3.1356e-05 | 1.9923e-05 | 0.084942 | 0.084942 | 0.084942 | 0.97609 | -0.46059 | 0.97549 | -0.47238 | 23.3358
101 | 0.011044 | 0.0027684 | -0.011041 | -0.0027673 | 2.041e-06 | 1.0669e-06 | 0.016846 | 0.016846 | 0.016846 | 0.97549 | -0.47238 | 0.97529 | -0.47626 | 4.6281
102 | 0.044636 | 0.01121 | -0.044608 | -0.011193 | 2.8017e-05 | 1.773e-05 | 0.068096 | 0.068096 | 0.068096 | 0.97549 | -0.47238 | 0.97482 | -0.48555 | 18.7078
103 | 0.0065641 | 0.0016452 | -0.0065629 | -0.0016448 | 1.2348e-06 | 3.8069e-07 | 0.010015 | 0.010015 | 0.010015 | 0.97529 | -0.47626 | 0.97509 | -0.48021 | 2.7514
104 | 0.033843 | 0.0084947 | -0.033827 | -0.0084847 | 1.5859e-05 | 9.9525e-06 | 0.051664 | 0.051664 | 0.051664 | 0.97482 | -0.48555 | 0.97432 | -0.49538 | 14.1933
105 | 0.0063735 | 0.0015973 | -0.0063723 | -0.0015969 | 1.2141e-06 | 3.5067e-07 | 0.0097289 | 0.009729 | 0.009729 | 0.97482 | -0.48555 | 0.97462 | -0.48955 | 2.6728
106 | -0.0048061 | -0.0012045 | 0.0048063 | 0.0012045 | 2.0659e-07 | 4.7728e-09 | 0.0073388 | 0.0073387 | 0.0073388 | 0.97449 | -0.492 | 0.97454 | -0.4911 | 2.0161
107 | -0.0048063 | -0.0012045 | 0.0048064 | 0.0012045 | 9.9305e-08 | 2.2894e-09 | 0.0073387 | 0.0073387 | 0.0073387 | 0.97454 | -0.4911 | 0.97456 | -0.49066 | 2.0161
108 | -0.0048064 | -0.0012045 | 0.0048067 | 0.0012045 | 2.5555e-07 | 5.8771e-09 | 0.0073387 | 0.0073387 | 0.0073387 | 0.97456 | -0.49066 | 0.97462 | -0.48955 | 2.0161
109 | 0.029201 | 0.0073255 | -0.029197 | -0.007323 | 3.9498e-06 | 2.4619e-06 | 0.044599 | 0.044599 | 0.044599 | 0.97432 | -0.49538 | 0.97418 | -0.49822 | 12.2526
110 | 0.02301 | 0.0057733 | -0.023004 | -0.0057695 | 6.1613e-06 | 3.7777e-06 | 0.03515 | 0.03515 | 0.03515 | 0.97418 | -0.49822 | 0.97389 | -0.50383 | 9.6565
111 | 0.0061868 | 0.0015497 | -0.0061831 | -0.0015487 | 3.6459e-06 | 9.7874e-07 | 0.0094497 | 0.0094502 | 0.0094502 | 0.97418 | -0.49822 | 0.97355 | -0.5106 | 2.5962
112 | 0.0050955 | 0.001277 | -0.0050952 | -0.001277 | 2.6595e-07 | 2.4623e-08 | 0.0077854 | 0.0077854 | 0.0077854 | 0.97389 | -0.50383 | 0.97384 | -0.50493 | 2.1389
113 | 0.017909 | 0.0044925 | -0.017898 | -0.0044863 | 1.043e-05 | 6.2134e-06 | 0.027364 | 0.027364 | 0.027364 | 0.97389 | -0.50383 | 0.97328 | -0.51606 | 7.5177
114 | 0.0061831 | 0.0015487 | -0.0061798 | -0.0015479 | 3.2663e-06 | 8.7843e-07 | 0.0094502 | 0.0094506 | 0.0094506 | 0.97355 | -0.5106 | 0.97299 | -0.52169 | 2.5963
115 | 0.0043329 | 0.0010857 | -0.0043325 | -0.0010857 | 3.1692e-07 | -3.649e-08 | 0.0066243 | 0.0066244 | 0.0066244 | 0.97328 | -0.51606 | 0.9732 | -0.51759 | 1.8199
116 | 0.013565 | 0.0034006 | -0.013563 | -0.0033992 | 2.4671e-06 | 1.3889e-06 | 0.02074 | 0.02074 | 0.02074 | 0.97328 | -0.51606 | 0.97308 | -0.51988 | 5.6979
117 | 0.0028323 | 0.00070976 | -0.0028323 | -0.00070984 | 6.6555e-08 | -7.4988e-08 | 0.0043306 | 0.0043307 | 0.0043307 | 0.9732 | -0.51759 | 0.97317 | -0.51809 | 1.1897
118 | 0.0029606 | 0.00074198 | -0.0029606 | -0.00074199 | 1.2919e-08 | -1.2612e-08 | 0.0045273 | 0.0045273 | 0.0045273 | 0.97308 | -0.51988 | 0.97308 | -0.51997 | 1.2438
119 | 0.0046842 | 0.0011732 | -0.0046829 | -0.0011732 | 1.2653e-06 | -6.6155e-09 | 0.0071634 | 0.0071637 | 0.0071637 | 0.97299 | -0.52169 | 0.9727 | -0.52737 | 1.968
120 | 0.0014956 | 0.00037463 | -0.0014956 | -0.00037483 | 3.6399e-08 | -2.0713e-07 | 0.0022872 | 0.0022873 | 0.0022873 | 0.97299 | -0.52169 | 0.97296 | -0.5222 | 0.62839
121 | 0.0046829 | 0.0011732 | -0.0046826 | -0.0011732 | 3.8389e-07 | -1.8986e-09 | 0.0071637 | 0.0071638 | 0.0071638 | 0.9727 | -0.52737 | 0.97262 | -0.52909 | 1.9681
122 | -0.0041414 | -0.0010379 | 0.0041418 | 0.0010379 | 3.2899e-07 | -6.0413e-08 | 0.0063376 | 0.0063375 | 0.0063376 | 0.97237 | -0.53398 | 0.97245 | -0.53231 | 1.7411
123 | -0.0046818 | -0.0011732 | 0.0046826 | 0.0011732 | 7.1958e-07 | -3.4229e-09 | 0.0071639 | 0.0071638 | 0.0071639 | 0.97245 | -0.53231 | 0.97262 | -0.52909 | 1.9681
124 | 0.0011166 | 0.0002779 | -0.0011166 | -0.00027802 | 1.0135e-08 | -1.2123e-07 | 0.0016635 | 0.0016635 | 0.0016635 | 0.99838 | -0.031314 | 0.99837 | -0.031506 | 0.45701
125 | 0.00061068 | 0.00015124 | -0.00061068 | -0.00015143 | 4.8117e-09 | -1.9972e-07 | 0.00090956 | 0.00090963 | 0.00090963 | 0.99837 | -0.031506 | 0.99836 | -0.031673 | 0.2499
126 | 0.00061068 | 0.00015143 | -0.00061064 | -0.00015304 | 3.8667e-08 | -1.6037e-06 | 0.00090963 | 0.0009102 | 0.0009102 | 0.99836 | -0.031673 | 0.99829 | -0.033007 | 0.25005
127 | 0.00038089 | 9.5458e-05 | -0.00038089 | -9.5461e-05 | 2.4525e-11 | -2.6039e-09 | 0.00056774 | 0.00056774 | 0.00056774 | 0.99829 | -0.033007 | 0.99829 | -0.033009 | 0.15597

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35874 | 0.09197

## res_load
| p_mw | q_mvar
0 | 0.010509 | 0.0026338
1 | 0.0014396 | 0.0003608
2 | 0.036839 | 0.0092327
3 | 0.00022255 | 5.5776e-05
4 | 0.00083187 | 0.00020849
5 | 0.00078691 | 0.00019722
6 | 0.0031716 | 0.00079487
7 | 0.00030707 | 7.696e-05
8 | 0.00011127 | 2.7886e-05
9 | 0.00030539 | 7.6539e-05
10 | 0.00044945 | 0.00011264
11 | 0.00026384 | 6.6126e-05
12 | 0.0023426 | 0.00058711
13 | 0.00059283 | 0.00014858
14 | 0.00082906 | 0.00020778
15 | 0.00032237 | 8.0793e-05
16 | 0.02287 | 0.0057316
17 | 0.0018454 | 0.0004625
18 | 0.00028867 | 7.2349e-05
19 | 0.0020255 | 0.00050764
20 | 0.0017754 | 0.00044495
21 | 0.0014617 | 0.00036635
22 | 0.00067946 | 0.00017029
23 | 0.00068921 | 0.00017273
24 | 0.00035749 | 8.9595e-05
25 | 0.00014016 | 3.5127e-05
26 | 0.00070045 | 0.00017555
27 | 0.00073922 | 0.00018527
28 | 0.0012803 | 0.00032086
29 | 0.0006114 | 0.00015323
30 | 0.00036634 | 9.1813e-05
31 | 0.00025965 | 6.5074e-05
32 | 0.00036554 | 9.1612e-05
33 | 0.0012083 | 0.00030282
34 | 0.00054222 | 0.00013589
35 | 0.0010776 | 0.00027007
36 | 0.00071607 | 0.00017946
37 | 0.0038204 | 0.00095748
38 | 0.001229 | 0.00030801
39 | 0.00098185 | 0.00024607
40 | 0.00085038 | 0.00021313
41 | 0.0010016 | 0.00025102
42 | 0.001499 | 0.00037568
43 | 0.0006043 | 0.00015145
44 | 0.0019203 | 0.00048126
45 | 0.00042402 | 0.00010627
46 | 0.00084843 | 0.00021264
47 | 0.001006 | 0.00025213
48 | 0.00087325 | 0.00021886
49 | 0.00037573 | 9.4168e-05
50 | 0.0026677 | 0.00066858
51 | 0.040662 | 0.010191
52 | 0.042963 | 0.010768
53 | 0.0054374 | 0.0013627
54 | 0.032868 | 0.0082374
55 | 0.0015513 | 0.00038878
56 | 0.0015788 | 0.00039568
57 | 0.0015148 | 0.00037964
58 | 0.0019364 | 0.00048531
59 | 0.0034563 | 0.00086623
60 | 0.002671 | 0.00066941
61 | 0.0033445 | 0.00083821
62 | 0.0041159 | 0.0010315
63 | 0.0014742 | 0.00036948
64 | 0.007595 | 0.0019035
65 | 0.0044774 | 0.0011221
66 | 0.0043918 | 0.0011007
67 | 0.0066519 | 0.0016671
68 | 0.01857 | 0.004654
69 | 0.0048061 | 0.0012045
70 | 0.0015656 | 0.00039239
71 | 0.0046256 | 0.0011593
72 | 0.0015002 | 0.00037598
73 | 0.010602 | 0.0026572
74 | 0.0050952 | 0.001277
75 | 0.0065629 | 0.0016448
76 | 0.0028323 | 0.00070984
77 | 0.0029606 | 0.00074199
78 | 0.0014956 | 0.00037483
79 | 0.0041414 | 0.0010379
80 | 0.00054008 | 0.00013536
81 | 0.00050587 | 0.00012678
82 | 0.00022975 | 5.758e-05
83 | 0.00038089 | 9.5461e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1