## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1704-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1704-10_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1704-10_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1704-10_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1704-10_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1704-10_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1704-10_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1704-10_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1704-10_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1704-10_0_3_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_1704-10_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1704-10_0_3_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_1704-10_0_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1704-10_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1704-10_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1704-10_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1704-10_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1704-10_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1704-10_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_1704-10_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1704-10_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1704-10_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1704-10_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1704-10_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1704-10_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1704-10_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1704-10_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1704-10_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1704-10_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1704-10_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1704-10_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1704-10_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1704-10_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1704-10_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_MV_25_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1704-10_0_3_load_0 | 0 | 0.0072904 | 0.0018271 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1704-10_0_3_load_1 | 1 | 0.0058232 | 0.0014594 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1704-10_0_3_load_13 | 5 | 0.0029407 | 0.000737 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1704-10_0_3_load_12 | 6 | 0.0096402 | 0.0024161 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1704-10_0_3_load_5 | 8 | 0.004814 | 0.0012065 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1704-10_0_3_load_14 | 9 | 0.0045129 | 0.001131 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1704-10_0_3_load_11 | 10 | 0.012264 | 0.0030738 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1704-10_0_3_load_28 | 12 | 0.021967 | 0.0055054 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1704-10_0_3_load_6 | 13 | 0.031462 | 0.007885 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1704-10_0_3_load_9 | 15 | 0.0018965 | 0.0004753 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1704-10_0_3_load_10 | 16 | 0.015042 | 0.00377 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1704-10_0_3_load_24 | 17 | 0.014856 | 0.0037234 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1704-10_0_3_load_27 | 19 | 0.0109 | 0.0027318 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1704-10_0_3_load_15 | 21 | 0.003966 | 0.00099397 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1704-10_0_3_load_16 | 22 | 0.0046761 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1704-10_0_3_load_18 | 24 | 0.0048327 | 0.0012112 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1704-10_0_3_load_19 | 25 | 0.0034431 | 0.00086291 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1704-10_0_3_load_21 | 26 | 0.0063857 | 0.0016004 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1704-10_0_3_load_22 | 27 | 0.0023133 | 0.00057977 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1704-10_0_3_load_25 | 28 | 0.0082541 | 0.0020687 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1704-10_0_3_load_26 | 29 | 0.0089108 | 0.0022333 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1704-10_0_3_load_34 | 30 | 0.056747 | 0.014222 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1704-10_0_3_load_32 | 31 | 0.021544 | 0.0053994 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1704-10_0_3_load_30 | 32 | 0.019792 | 0.0049604 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1704-10_0_3_load_31 | 33 | 0.0099552 | 0.002495 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1704-10_0_3_line_0 |  | 0 | 1 | 0.0081705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1704-10_0_3_line_1 |  | 0 | 2 | 0.026901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1704-10_0_3_line_2 |  | 2 | 3 | 0.016883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1704-10_0_3_line_3 |  | 3 | 7 | 0.038205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1704-10_0_3_line_4 |  | 3 | 8 | 0.015484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1704-10_0_3_line_5 |  | 4 | 5 | 0.0025421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1704-10_0_3_line_6 |  | 4 | 6 | 0.014333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1704-10_0_3_line_7 |  | 5 | 9 | 0.022635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1704-10_0_3_line_8 |  | 6 | 10 | 0.0065912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1704-10_0_3_line_9 |  | 7 | 11 | 0.040033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1704-10_0_3_line_10 |  | 7 | 12 | 0.029182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1704-10_0_3_line_11 |  | 8 | 13 | 0.01528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1704-10_0_3_line_12 |  | 9 | 21 | 0.0068859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1704-10_0_3_line_13 |  | 10 | 15 | 0.01782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1704-10_0_3_line_14 |  | 11 | 18 | 0.011101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1704-10_0_3_line_15 |  | 12 | 19 | 0.018818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1704-10_0_3_line_16 |  | 13 | 14 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1704-10_0_3_line_17 |  | 14 | 15 | 0.012338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1704-10_0_3_line_18 |  | 16 | 17 | 0.032272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1704-10_0_3_line_19 |  | 17 | 20 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1704-10_0_3_line_20 |  | 18 | 30 | 0.0064632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1704-10_0_3_line_21 |  | 18 | 31 | 0.030961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1704-10_0_3_line_22 |  | 19 | 29 | 0.012921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1704-10_0_3_line_23 |  | 20 | 27 | 0.038081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1704-10_0_3_line_24 |  | 21 | 22 | 0.012278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1704-10_0_3_line_25 |  | 22 | 23 | 0.015872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1704-10_0_3_line_26 |  | 23 | 24 | 0.0091564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1704-10_0_3_line_27 |  | 23 | 25 | 0.0099163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1704-10_0_3_line_28 |  | 25 | 26 | 0.030242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1704-10_0_3_line_29 |  | 26 | 27 | 0.004139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1704-10_0_3_line_30 |  | 28 | 29 | 0.00031743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1704-10_0_3_line_31 |  | 31 | 33 | 0.038599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1704-10_0_3_line_32 |  | 32 | 33 | 0.013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1704-10_0_3_trafo_27 | 0.63 MVA 20/0.4 kV | 34 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2687330.85 | 1225816.4684 | 2687332.0727 | 1225809.9567 | 2687332.5327 | 1225808.4817
1 | 2687331.9029 | 1225842.1765 | 2687328.4283 | 1225836.655 | 2687328.9392 | 1225826.6445 | 2687330.85 | 1225816.4684
2 | 2687343.3962 | 1225829.781 | 2687331.9029 | 1225842.1765
3 | 2687369.264 | 1225853.4882 | 2687355.7852 | 1225832.7982 | 2687350.2449 | 1225829.0699 | 2687343.3962 | 1225829.781
4 | 2687343.3962 | 1225829.781 | 2687347.1684 | 1225823.81 | 2687355.2787 | 1225821.5431
5 | 2687343.203 | 1225775.3072 | 2687344.0228 | 1225772.9009
6 | 2687343.203 | 1225775.3072 | 2687354.7217 | 1225783.8371
7 | 2687344.0228 | 1225772.9009 | 2687347.2436 | 1225763.4471 | 2687349.7785 | 1225751.0563
8 | 2687360.252 | 1225787.4139 | 2687356.1776 | 1225784.9153 | 2687354.7217 | 1225783.8371
9 | 2687369.264 | 1225853.4882 | 2687375.8974 | 1225861.758 | 2687380.3261 | 1225867.3491 | 2687388.2444 | 1225865.5641 | 2687394.3989 | 1225865.1542 | 2687402.236 | 1225866.826
10 | 2687369.264 | 1225853.4882 | 2687381.7842 | 1225842.9313 | 2687392.1892 | 1225835.4678
11 | 2687355.2787 | 1225821.5431 | 2687368.5596 | 1225817.831 | 2687369.714 | 1225816.8891
12 | 2687350.4244 | 1225744.2446 | 2687350.5025 | 1225747.5173 | 2687349.7785 | 1225751.0563
13 | 2687360.252 | 1225787.4139 | 2687367.2678 | 1225791.7161 | 2687375.1602 | 1225797.1647
14 | 2687413.143 | 1225869.0544 | 2687402.236 | 1225866.826
15 | 2687392.1892 | 1225835.4678 | 2687392.1892 | 1225835.4678 | 2687407.0398 | 1225823.9102
16 | 2687385.3334 | 1225804.1455 | 2687369.714 | 1225816.8891
17 | 2687385.3334 | 1225804.1455 | 2687380.2518 | 1225800.6796 | 2687375.1602 | 1225797.1647
18 | 2687434.1115 | 1225743.4048 | 2687435.505 | 1225752.1686 | 2687435.6658 | 1225758.7644 | 2687433.4336 | 1225764.1464 | 2687424.6945 | 1225770.7832
19 | 2687431.8616 | 1225729.2548 | 2687434.1115 | 1225743.4048
20 | 2687413.143 | 1225869.0544 | 2687419.4719 | 1225870.3652
21 | 2687413.143 | 1225869.0544 | 2687433.4281 | 1225866.1169 | 2687442.3984 | 1225860.729
22 | 2687407.0398 | 1225823.9102 | 2687417.2364 | 1225815.9747
23 | 2687431.8616 | 1225729.2548 | 2687423.733 | 1225726.767 | 2687412.4913 | 1225718.4072 | 2687401.2213 | 1225715.5842 | 2687397.28 | 1225715.2822
24 | 2687350.4244 | 1225744.2446 | 2687350.1314 | 1225731.9699
25 | 2687353.8267 | 1225716.8226 | 2687351.0725 | 1225722.1303 | 2687350.1083 | 1225731.0001 | 2687350.1314 | 1225731.9699
26 | 2687353.8267 | 1225716.8226 | 2687347.6374 | 1225711.8506 | 2687347.1959 | 1225710.7161
27 | 2687353.8267 | 1225716.8226 | 2687357.2593 | 1225714.3602 | 2687362.9504 | 1225714.2687
28 | 2687362.9504 | 1225714.2687 | 2687380.3958 | 1225713.9884 | 2687393.1532 | 1225714.966
29 | 2687393.1532 | 1225714.966 | 2687397.28 | 1225715.2822
30 | 2687417.4869 | 1225815.7797 | 2687417.2364 | 1225815.9747
31 | 2687442.3984 | 1225860.729 | 2687443.9987 | 1225859.7678 | 2687454.6249 | 1225850.1618 | 2687452.6489 | 1225844.3065 | 2687442.7012 | 1225831.4848 | 2687442.7012 | 1225831.4848
32 | 2687432.7824 | 1225840.1476 | 2687442.7012 | 1225831.4848

## bus_geodata
| x | y | coords
0 | 2687330.85 | 1225816.4684
1 | 2687332.5327 | 1225808.4817
2 | 2687331.9029 | 1225842.1765
3 | 2687343.3962 | 1225829.781
4 | 2687343.203 | 1225775.3072
5 | 2687344.0228 | 1225772.9009
6 | 2687354.7217 | 1225783.8371
7 | 2687369.264 | 1225853.4882
8 | 2687355.2787 | 1225821.5431
9 | 2687349.7785 | 1225751.0563
10 | 2687360.252 | 1225787.4139
11 | 2687402.236 | 1225866.826
12 | 2687392.1892 | 1225835.4678
13 | 2687369.714 | 1225816.8891
14 | 2687385.3334 | 1225804.1455
15 | 2687375.1602 | 1225797.1647
16 | 2687424.6945 | 1225770.7832
17 | 2687434.1115 | 1225743.4048
18 | 2687413.143 | 1225869.0544
19 | 2687407.0398 | 1225823.9102
20 | 2687431.8616 | 1225729.2548
21 | 2687350.4244 | 1225744.2446
22 | 2687350.1314 | 1225731.9699
23 | 2687353.8267 | 1225716.8226
24 | 2687347.1959 | 1225710.7161
25 | 2687362.9504 | 1225714.2687
26 | 2687393.1532 | 1225714.966
27 | 2687397.28 | 1225715.2822
28 | 2687417.4869 | 1225815.7797
29 | 2687417.2364 | 1225815.9747
30 | 2687419.4719 | 1225870.3652
31 | 2687442.3984 | 1225860.729
32 | 2687432.7824 | 1225840.1476
33 | 2687442.7012 | 1225831.4848
34 | 2687369.264 | 1225853.4882

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98907 | -0.20872 | 0.0072904 | 0.0018271
1 | 0.98902 | -0.20957 | 0.0058232 | 0.0014594
2 | 0.98939 | -0.20244 | 0 | 0
3 | 0.98959 | -0.1985 | 0 | 0
4 | 0.98086 | -0.36775 | 0 | 0
5 | 0.98071 | -0.37065 | 0.0029407 | 0.000737
6 | 0.9817 | -0.35141 | 0.0096402 | 0.0024161
7 | 0.99441 | -0.10635 | 0 | 0
8 | 0.98783 | -0.23247 | 0.004814 | 0.0012065
9 | 0.97945 | -0.39531 | 0.0045129 | 0.001131
10 | 0.98214 | -0.34276 | 0.012264 | 0.0030738
11 | 0.99044 | -0.1829 | 0 | 0
12 | 0.99769 | -0.043754 | 0.021967 | 0.0055054
13 | 0.98616 | -0.2648 | 0.031462 | 0.007885
14 | 0.98454 | -0.2962 | 0 | 0
15 | 0.98354 | -0.31547 | 0.0018965 | 0.0004753
16 | 0.9743 | -0.49631 | 0.015042 | 0.00377
17 | 0.97476 | -0.4874 | 0.014856 | 0.0037234
18 | 0.98934 | -0.20423 | 0 | 0
19 | 1 | 0 | -0.2886 | -0.073317
20 | 0.97515 | -0.47954 | 0 | 0
21 | 0.97909 | -0.40226 | 0.003966 | 0.00099397
22 | 0.9785 | -0.41378 | 0.0046761 | 0.0011719
23 | 0.97781 | -0.42733 | 0 | 0
24 | 0.97777 | -0.42814 | 0.0048327 | 0.0012112
25 | 0.97742 | -0.43493 | 0.0034431 | 0.00086291
26 | 0.97634 | -0.45625 | 0.0063857 | 0.0016004
27 | 0.97621 | -0.45869 | 0.0023133 | 0.00057977
28 | 0.9998 | -0.003912 | 0.0082541 | 0.0020687
29 | 0.9998 | -0.0038664 | 0.0089108 | 0.0022333
30 | 0.989 | -0.21076 | 0.056747 | 0.014222
31 | 0.98788 | -0.23255 | 0.021544 | 0.0053994
32 | 0.98658 | -0.25775 | 0.019792 | 0.0049604
33 | 0.98682 | -0.25308 | 0.0099552 | 0.002495
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0058235 | 0.0014595 | -0.0058232 | -0.0014594 | 2.3518e-07 | 4.5661e-08 | 0.0087612 | 0.0087612 | 0.0087612 | 0.98907 | -0.20872 | 0.98902 | -0.20957 | 2.4069
1 | -0.013114 | -0.0032866 | 0.013118 | 0.0032888 | 3.9267e-06 | 2.1677e-06 | 0.019729 | 0.019729 | 0.019729 | 0.98907 | -0.20872 | 0.98939 | -0.20244 | 5.4201
2 | -0.013118 | -0.0032888 | 0.01312 | 0.0032902 | 2.4643e-06 | 1.3603e-06 | 0.019729 | 0.019729 | 0.019729 | 0.98939 | -0.20244 | 0.98959 | -0.1985 | 5.4201
3 | -0.13722 | -0.034799 | 0.13783 | 0.035189 | 0.0006108 | 0.00039042 | 0.20648 | 0.20648 | 0.20648 | 0.98959 | -0.1985 | 0.99441 | -0.10635 | 56.7248
4 | 0.1241 | 0.031509 | -0.1239 | -0.03138 | 0.0002025 | 0.0001294 | 0.18675 | 0.18675 | 0.18675 | 0.98959 | -0.1985 | 0.98783 | -0.23247 | 51.3047
5 | 0.063232 | 0.015948 | -0.063224 | -0.015942 | 8.7787e-06 | 5.5863e-06 | 0.095963 | 0.095963 | 0.095963 | 0.98086 | -0.36775 | 0.98071 | -0.37065 | 26.3635
6 | -0.063232 | -0.015948 | 0.063282 | 0.015979 | 4.9497e-05 | 3.1497e-05 | 0.095963 | 0.095963 | 0.095963 | 0.98086 | -0.36775 | 0.9817 | -0.35141 | 26.3635
7 | 0.060283 | 0.015205 | -0.060212 | -0.01516 | 7.1066e-05 | 4.5197e-05 | 0.091501 | 0.091501 | 0.091501 | 0.98071 | -0.37065 | 0.97945 | -0.39531 | 25.1377
8 | -0.072922 | -0.018395 | 0.072952 | 0.018414 | 3.0221e-05 | 1.9258e-05 | 0.11058 | 0.11058 | 0.11058 | 0.9817 | -0.35141 | 0.98214 | -0.34276 | 30.3778
9 | 0.10867 | 0.027477 | -0.10827 | -0.027223 | 0.00039736 | 0.00025379 | 0.16269 | 0.16269 | 0.16269 | 0.99441 | -0.10635 | 0.99044 | -0.1829 | 44.6959
10 | -0.2465 | -0.062667 | 0.24724 | 0.063143 | 0.00074571 | 0.00047649 | 0.36917 | 0.36917 | 0.36917 | 0.99441 | -0.10635 | 0.99769 | -0.043754 | 50.7103
11 | 0.11908 | 0.030173 | -0.1189 | -0.030055 | 0.00018462 | 0.00011796 | 0.1795 | 0.1795 | 0.1795 | 0.98783 | -0.23247 | 0.98616 | -0.2648 | 49.3126
12 | 0.055699 | 0.014029 | -0.055681 | -0.014017 | 1.8501e-05 | 1.1754e-05 | 0.084645 | 0.084645 | 0.084645 | 0.97945 | -0.39531 | 0.97909 | -0.40226 | 23.2542
13 | -0.085217 | -0.021488 | 0.085328 | 0.021559 | 0.00011148 | 7.1118e-05 | 0.12916 | 0.12916 | 0.12916 | 0.98214 | -0.34276 | 0.98354 | -0.31547 | 35.4826
14 | 0.10827 | 0.027223 | -0.10816 | -0.027153 | 0.00011019 | 7.0377e-05 | 0.16269 | 0.16269 | 0.16269 | 0.99044 | -0.1829 | 0.98934 | -0.20423 | 44.6959
15 | -0.26921 | -0.068649 | 0.26978 | 0.069013 | 0.00057001 | 0.00036431 | 0.40193 | 0.40193 | 0.40193 | 0.99769 | -0.043754 | 1 | 0 | 55.2106
16 | 0.087437 | 0.02217 | -0.087305 | -0.022086 | 0.00013177 | 8.4074e-05 | 0.13203 | 0.13203 | 0.13203 | 0.98616 | -0.2648 | 0.98454 | -0.2962 | 36.2708
17 | 0.087305 | 0.022086 | -0.087225 | -0.022035 | 8.0648e-05 | 5.1458e-05 | 0.13203 | 0.13203 | 0.13203 | 0.98454 | -0.2962 | 0.98354 | -0.31547 | 36.2708
18 | -0.015042 | -0.00377 | 0.015049 | 0.0037737 | 6.3873e-06 | 3.6858e-06 | 0.022974 | 0.022974 | 0.022974 | 0.9743 | -0.49631 | 0.97476 | -0.4874 | 6.3115
19 | -0.029905 | -0.007497 | 0.029916 | 0.007504 | 1.1198e-05 | 6.9881e-06 | 0.045653 | 0.045653 | 0.045653 | 0.97476 | -0.4874 | 0.97515 | -0.47954 | 12.5419
20 | 0.056765 | 0.014233 | -0.056747 | -0.014222 | 1.7668e-05 | 1.1224e-05 | 0.08538 | 0.08538 | 0.08538 | 0.98934 | -0.20423 | 0.989 | -0.21076 | 23.456
21 | 0.051394 | 0.01292 | -0.051325 | -0.012876 | 6.9399e-05 | 4.4019e-05 | 0.077314 | 0.077314 | 0.077314 | 0.98934 | -0.20423 | 0.98788 | -0.23255 | 21.24
22 | 0.017168 | 0.0043038 | -0.017165 | -0.0043019 | 3.1622e-06 | 1.8543e-06 | 0.025547 | 0.025547 | 0.025547 | 1 | 0 | 0.9998 | -0.0038664 | 7.0184
23 | -0.029916 | -0.007504 | 0.029946 | 0.0075226 | 2.9763e-05 | 1.8572e-05 | 0.045653 | 0.045652 | 0.045653 | 0.97515 | -0.47954 | 0.97621 | -0.45869 | 12.5419
24 | 0.051715 | 0.013023 | -0.051686 | -0.013005 | 2.8458e-05 | 1.8059e-05 | 0.078618 | 0.078618 | 0.078618 | 0.97909 | -0.40226 | 0.9785 | -0.41378 | 21.5983
25 | 0.04701 | 0.011833 | -0.04698 | -0.011814 | 3.0434e-05 | 1.9278e-05 | 0.071507 | 0.071507 | 0.071507 | 0.9785 | -0.41378 | 0.97781 | -0.42733 | 19.6448
26 | 0.0048329 | 0.0012112 | -0.0048327 | -0.0012112 | 1.8573e-07 | 4.0169e-09 | 0.0073546 | 0.0073546 | 0.0073546 | 0.97781 | -0.42733 | 0.97777 | -0.42814 | 2.0205
27 | 0.042147 | 0.010603 | -0.042131 | -0.010593 | 1.5304e-05 | 9.6703e-06 | 0.064152 | 0.064152 | 0.064152 | 0.97781 | -0.42733 | 0.97742 | -0.43493 | 17.6243
28 | 0.038688 | 0.0097299 | -0.038649 | -0.0097051 | 3.9358e-05 | 2.4811e-05 | 0.058911 | 0.058911 | 0.058911 | 0.97742 | -0.43493 | 0.97634 | -0.45625 | 16.1843
29 | 0.032263 | 0.0081047 | -0.03226 | -0.0081024 | 3.7538e-06 | 2.3507e-06 | 0.049179 | 0.049179 | 0.049179 | 0.97634 | -0.45625 | 0.97621 | -0.45869 | 13.5106
30 | -0.0082541 | -0.0020687 | 0.0082541 | 0.0020687 | 1.7964e-08 | 7.3342e-09 | 0.012285 | 0.012285 | 0.012285 | 0.9998 | -0.003912 | 0.9998 | -0.0038664 | 3.3749
31 | 0.029781 | 0.0074762 | -0.029752 | -0.0074581 | 2.9133e-05 | 1.8152e-05 | 0.044863 | 0.044863 | 0.044863 | 0.98788 | -0.23255 | 0.98682 | -0.25308 | 12.325
32 | -0.019792 | -0.0049604 | 0.019797 | 0.0049631 | 4.4008e-06 | 2.6483e-06 | 0.029852 | 0.029852 | 0.029852 | 0.98658 | -0.25775 | 0.98682 | -0.25308 | 8.2011

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2995 | 0.076049

## res_load
| p_mw | q_mvar
0 | 0.0072904 | 0.0018271
1 | 0.0058232 | 0.0014594
2 | 0.0029407 | 0.000737
3 | 0.0096402 | 0.0024161
4 | 0.004814 | 0.0012065
5 | 0.0045129 | 0.001131
6 | 0.012264 | 0.0030738
7 | 0.021967 | 0.0055054
8 | 0.031462 | 0.007885
9 | 0.0018965 | 0.0004753
10 | 0.015042 | 0.00377
11 | 0.014856 | 0.0037234
12 | 0.0109 | 0.0027318
13 | 0.003966 | 0.00099397
14 | 0.0046761 | 0.0011719
15 | 0.0048327 | 0.0012112
16 | 0.0034431 | 0.00086291
17 | 0.0063857 | 0.0016004
18 | 0.0023133 | 0.00057977
19 | 0.0082541 | 0.0020687
20 | 0.0089108 | 0.0022333
21 | 0.056747 | 0.014222
22 | 0.021544 | 0.0053994
23 | 0.019792 | 0.0049604
24 | 0.0099552 | 0.002495

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1