## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_173-1_2_2_node_76 | 0.4 | n |  | TRUE
1 | bus_LV_173-1_2_2_node_231 | 0.4 | n |  | TRUE
2 | bus_LV_173-1_2_2_node_228 | 0.4 | n |  | TRUE
3 | bus_LV_173-1_2_2_node_94 | 0.4 | n |  | TRUE
4 | bus_LV_173-1_2_2_node_203 | 0.4 | n |  | TRUE
5 | bus_LV_173-1_2_2_node_215 | 0.4 | n |  | TRUE
6 | bus_LV_173-1_2_2_node_96 | 0.4 | n |  | TRUE
7 | bus_LV_173-1_2_2_node_217 | 0.4 | n |  | TRUE
8 | bus_LV_173-1_2_2_node_98 | 0.4 | n |  | TRUE
9 | bus_LV_173-1_2_2_node_209 | 0.4 | n |  | TRUE
10 | bus_LV_173-1_2_2_node_97 | 0.4 | n |  | TRUE
11 | bus_LV_173-1_2_2_node_278 | 0.4 | n |  | TRUE
12 | bus_LV_173-1_2_2_node_275 | 0.4 | n |  | TRUE
13 | bus_LV_173-1_2_2_node_216 | 0.4 | n |  | TRUE
14 | bus_LV_173-1_2_2_node_139 | 0.4 | n |  | TRUE
15 | bus_LV_173-1_2_2_node_140 | 0.4 | n |  | TRUE
16 | bus_LV_173-1_2_2_node_141 | 0.4 | n |  | TRUE
17 | bus_LV_173-1_2_2_node_142 | 0.4 | n |  | TRUE
18 | bus_LV_173-1_2_2_node_143 | 0.4 | n |  | TRUE
19 | bus_LV_173-1_2_2_node_153 | 0.4 | n |  | TRUE
20 | bus_LV_173-1_2_2_node_147 | 0.4 | n |  | TRUE
21 | bus_LV_173-1_2_2_node_152 | 0.4 | n |  | TRUE
22 | bus_LV_173-1_2_2_node_144 | 0.4 | n |  | TRUE
23 | bus_LV_173-1_2_2_node_145 | 0.4 | n |  | TRUE
24 | bus_LV_173-1_2_2_node_324 | 0.4 | n |  | TRUE
25 | bus_LV_173-1_2_2_node_173 | 0.4 | n |  | TRUE
26 | bus_LV_173-1_2_2_node_150 | 0.4 | n |  | TRUE
27 | bus_LV_173-1_2_2_node_151 | 0.4 | n |  | TRUE
28 | bus_LV_173-1_2_2_node_156 | 0.4 | n |  | TRUE
29 | bus_LV_173-1_2_2_node_227 | 0.4 | n |  | TRUE
30 | bus_LV_173-1_2_2_node_226 | 0.4 | n |  | TRUE
31 | bus_LV_173-1_2_2_node_154 | 0.4 | n |  | TRUE
32 | bus_LV_173-1_2_2_node_155 | 0.4 | n |  | TRUE
33 | bus_LV_173-1_2_2_node_157 | 0.4 | n |  | TRUE
34 | bus_LV_173-1_2_2_node_159 | 0.4 | n |  | TRUE
35 | bus_LV_173-1_2_2_node_158 | 0.4 | n |  | TRUE
36 | bus_LV_173-1_2_2_node_160 | 0.4 | n |  | TRUE
37 | bus_LV_173-1_2_2_node_161 | 0.4 | n |  | TRUE
38 | bus_LV_173-1_2_2_node_162 | 0.4 | n |  | TRUE
39 | bus_LV_173-1_2_2_node_163 | 0.4 | n |  | TRUE
40 | bus_LV_173-1_2_2_node_165 | 0.4 | n |  | TRUE
41 | bus_LV_173-1_2_2_node_164 | 0.4 | n |  | TRUE
42 | bus_LV_173-1_2_2_node_175 | 0.4 | n |  | TRUE
43 | bus_LV_173-1_2_2_node_166 | 0.4 | n |  | TRUE
44 | bus_LV_173-1_2_2_node_167 | 0.4 | n |  | TRUE
45 | bus_LV_173-1_2_2_node_172 | 0.4 | n |  | TRUE
46 | bus_LV_173-1_2_2_node_169 | 0.4 | n |  | TRUE
47 | bus_LV_173-1_2_2_node_168 | 0.4 | n |  | TRUE
48 | bus_LV_173-1_2_2_node_174 | 0.4 | n |  | TRUE
49 | bus_LV_173-1_2_2_node_176 | 0.4 | n |  | TRUE
50 | bus_LV_173-1_2_2_node_179 | 0.4 | n |  | TRUE
51 | bus_LV_173-1_2_2_node_186 | 0.4 | n |  | TRUE
52 | bus_LV_173-1_2_2_node_177 | 0.4 | n |  | TRUE
53 | bus_LV_173-1_2_2_node_178 | 0.4 | n |  | TRUE
54 | bus_LV_173-1_2_2_node_180 | 0.4 | n |  | TRUE
55 | bus_LV_173-1_2_2_node_183 | 0.4 | n |  | TRUE
56 | bus_LV_173-1_2_2_node_188 | 0.4 | n |  | TRUE
57 | bus_LV_173-1_2_2_node_181 | 0.4 | n |  | TRUE
58 | bus_LV_173-1_2_2_node_279 | 0.4 | n |  | TRUE
59 | bus_LV_173-1_2_2_node_187 | 0.4 | n |  | TRUE
60 | bus_LV_173-1_2_2_node_230 | 0.4 | n |  | TRUE
61 | bus_LV_173-1_2_2_node_182 | 0.4 | n |  | TRUE
62 | bus_LV_173-1_2_2_node_281 | 0.4 | n |  | TRUE
63 | bus_LV_173-1_2_2_node_280 | 0.4 | n |  | TRUE
64 | bus_LV_173-1_2_2_node_184 | 0.4 | n |  | TRUE
65 | bus_LV_173-1_2_2_node_185 | 0.4 | n |  | TRUE
66 | bus_LV_173-1_2_2_node_189 | 0.4 | n |  | TRUE
67 | bus_LV_173-1_2_2_node_190 | 0.4 | n |  | TRUE
68 | bus_LV_173-1_2_2_node_198 | 0.4 | n |  | TRUE
69 | bus_LV_173-1_2_2_node_200 | 0.4 | n |  | TRUE
70 | bus_LV_173-1_2_2_node_191 | 0.4 | n |  | TRUE
71 | bus_LV_173-1_2_2_node_192 | 0.4 | n |  | TRUE
72 | bus_LV_173-1_2_2_node_193 | 0.4 | n |  | TRUE
73 | bus_LV_173-1_2_2_node_194 | 0.4 | n |  | TRUE
74 | bus_LV_173-1_2_2_node_196 | 0.4 | n |  | TRUE
75 | bus_LV_173-1_2_2_node_195 | 0.4 | n |  | TRUE
76 | bus_LV_173-1_2_2_node_197 | 0.4 | n |  | TRUE
77 | bus_LV_173-1_2_2_node_199 | 0.4 | n |  | TRUE
78 | bus_LV_173-1_2_2_node_201 | 0.4 | n |  | TRUE
79 | bus_LV_173-1_2_2_node_224 | 0.4 | n |  | TRUE
80 | bus_LV_173-1_2_2_node_202 | 0.4 | n |  | TRUE
81 | bus_LV_173-1_2_2_node_204 | 0.4 | n |  | TRUE
82 | bus_LV_173-1_2_2_node_210 | 0.4 | n |  | TRUE
83 | bus_LV_173-1_2_2_node_206 | 0.4 | n |  | TRUE
84 | bus_LV_173-1_2_2_node_207 | 0.4 | n |  | TRUE
85 | bus_LV_173-1_2_2_node_208 | 0.4 | n |  | TRUE
86 | bus_LV_173-1_2_2_node_211 | 0.4 | n |  | TRUE
87 | bus_LV_173-1_2_2_node_213 | 0.4 | n |  | TRUE
88 | bus_LV_173-1_2_2_node_214 | 0.4 | n |  | TRUE
89 | bus_LV_173-1_2_2_node_293 | 0.4 | n |  | TRUE
90 | bus_LV_173-1_2_2_node_283 | 0.4 | n |  | TRUE
91 | bus_LV_173-1_2_2_node_218 | 0.4 | n |  | TRUE
92 | bus_LV_173-1_2_2_node_219 | 0.4 | n |  | TRUE
93 | bus_LV_173-1_2_2_node_220 | 0.4 | n |  | TRUE
94 | bus_LV_173-1_2_2_node_221 | 0.4 | n |  | TRUE
95 | bus_LV_173-1_2_2_node_284 | 0.4 | n |  | TRUE
96 | bus_LV_173-1_2_2_node_285 | 0.4 | n |  | TRUE
97 | bus_LV_173-1_2_2_node_282 | 0.4 | n |  | TRUE
98 | bus_LV_173-1_2_2_node_222 | 0.4 | n |  | TRUE
99 | bus_LV_173-1_2_2_node_223 | 0.4 | n |  | TRUE
100 | bus_LV_173-1_2_2_node_225 | 0.4 | n |  | TRUE
101 | bus_LV_173-1_2_2_node_229 | 0.4 | n |  | TRUE
102 | bus_LV_173-1_2_2_node_291 | 0.4 | n |  | TRUE
103 | bus_LV_173-1_2_2_node_276 | 0.4 | n |  | TRUE
104 | bus_LV_173-1_2_2_node_277 | 0.4 | n |  | TRUE
105 | bus_LV_173-1_2_2_node_292 | 0.4 | n |  | TRUE
106 | bus_LV_173-1_2_2_node_289 | 0.4 | n |  | TRUE
107 | bus_LV_173-1_2_2_node_290 | 0.4 | n |  | TRUE
108 | bus_LV_173-1_2_2_node_295 | 0.4 | n |  | TRUE
109 | bus_LV_173-1_2_2_node_286 | 0.4 | n |  | TRUE
110 | bus_LV_173-1_2_2_node_288 | 0.4 | n |  | TRUE
111 | bus_LV_173-1_2_2_node_287 | 0.4 | n |  | TRUE
112 | bus_LV_173-1_2_2_node_294 | 0.4 | n |  | TRUE
113 | bus_MV_7_1_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_173-1_2_2_load_231 | 1 | 0.0001793 | 4.4936e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_173-1_2_2_load_228 | 2 | 0.00050743 | 0.00012717 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_173-1_2_2_load_215 | 5 | 0.00055315 | 0.00013863 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_173-1_2_2_load_209 | 9 | 0.00025582 | 6.4114e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_173-1_2_2_load_278 | 11 | 0.00087667 | 0.00021971 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_173-1_2_2_load_275 | 12 | 0.00031798 | 7.9694e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_173-1_2_2_load_216 | 13 | 0.00023113 | 5.7928e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_173-1_2_2_load_139 | 14 | 0.0040196 | 0.0010074 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_173-1_2_2_load_141 | 16 | 0.0032308 | 0.00080972 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_173-1_2_2_load_142 | 17 | 0.0019746 | 0.00049489 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_173-1_2_2_load_153 | 19 | 0.0021159 | 0.00053029 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_173-1_2_2_load_152 | 21 | 0.002561 | 0.00064185 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_173-1_2_2_load_324 | 24 | 0.013955 | 0.0034975 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_173-1_2_2_load_173 | 25 | 0.0017745 | 0.00044474 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_173-1_2_2_load_156 | 28 | 0.00067205 | 0.00016843 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_173-1_2_2_load_227 | 29 | 0.0012548 | 0.00031448 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_173-1_2_2_load_226 | 30 | 0.002475 | 0.0006203 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_173-1_2_2_load_154 | 31 | 0.003139 | 0.0007867 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_173-1_2_2_load_155 | 32 | 0.0030088 | 0.00075408 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_173-1_2_2_load_157 | 33 | 0.0010919 | 0.00027365 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_173-1_2_2_load_159 | 34 | 0.00055357 | 0.00013874 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_173-1_2_2_load_158 | 35 | 0.0020883 | 0.00052338 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_173-1_2_2_load_161 | 37 | 0.0016925 | 0.00042419 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_173-1_2_2_load_162 | 38 | 0.0018663 | 0.00046773 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_173-1_2_2_load_163 | 39 | 0.0023288 | 0.00058364 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_173-1_2_2_load_164 | 41 | 0.001783 | 0.00044685 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_173-1_2_2_load_175 | 42 | 0.00067461 | 0.00016907 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_173-1_2_2_load_167 | 44 | 0.0010382 | 0.0002602 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_173-1_2_2_load_172 | 45 | 0.0025527 | 0.00063976 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_173-1_2_2_load_169 | 46 | 0.0011873 | 0.00029757 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_173-1_2_2_load_168 | 47 | 0.0011872 | 0.00029754 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_173-1_2_2_load_174 | 48 | 0.0012322 | 0.00030881 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_173-1_2_2_load_186 | 51 | 0.00095787 | 0.00024006 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_173-1_2_2_load_177 | 52 | 0.0067362 | 0.0016882 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_173-1_2_2_load_180 | 54 | 0.0041891 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_173-1_2_2_load_183 | 55 | 0.0014785 | 0.00037055 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_173-1_2_2_load_188 | 56 | 0.0032755 | 0.00082091 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_173-1_2_2_load_279 | 58 | 0.0032991 | 0.00082682 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_173-1_2_2_load_187 | 59 | 0.0006559 | 0.00016438 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_173-1_2_2_load_230 | 60 | 0.001212 | 0.00030375 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_173-1_2_2_load_280 | 63 | 0.0050375 | 0.0012625 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_173-1_2_2_load_184 | 64 | 0.00059607 | 0.00014939 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_173-1_2_2_load_185 | 65 | 0.0074715 | 0.0018725 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_173-1_2_2_load_189 | 66 | 0.0036095 | 0.00090463 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_173-1_2_2_load_198 | 68 | 0.00069612 | 0.00017446 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_173-1_2_2_load_191 | 70 | 0.0027385 | 0.00068634 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_173-1_2_2_load_194 | 73 | 0.0022993 | 0.00057625 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_173-1_2_2_load_196 | 74 | 0.0014366 | 0.00036004 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_173-1_2_2_load_195 | 75 | 0.00028509 | 7.145e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_173-1_2_2_load_197 | 76 | 0.0013046 | 0.00032696 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_173-1_2_2_load_199 | 77 | 0.0051316 | 0.0012861 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_173-1_2_2_load_224 | 79 | 0.0040881 | 0.0010246 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_173-1_2_2_load_202 | 80 | 0.0042771 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_173-1_2_2_load_204 | 81 | 0.00017888 | 4.4831e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_173-1_2_2_load_210 | 82 | 0.0033023 | 0.00082764 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_173-1_2_2_load_206 | 83 | 0.0011659 | 0.00029221 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_173-1_2_2_load_207 | 84 | 0.00075355 | 0.00018886 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_173-1_2_2_load_208 | 85 | 0.00051461 | 0.00012897 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_173-1_2_2_load_211 | 86 | 0.0041042 | 0.0010286 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_173-1_2_2_load_293 | 89 | 0.00063632 | 0.00015948 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_173-1_2_2_load_283 | 90 | 0.00023595 | 5.9135e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_173-1_2_2_load_218 | 91 | 0.0014445 | 0.00036203 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_173-1_2_2_load_220 | 93 | 0.0013262 | 0.00033238 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_173-1_2_2_load_284 | 95 | 0.00098229 | 0.00024619 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_173-1_2_2_load_285 | 96 | 0.00062109 | 0.00015566 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_173-1_2_2_load_282 | 97 | 0.00084778 | 0.00021247 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_173-1_2_2_load_222 | 98 | 0.0057029 | 0.0014293 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_173-1_2_2_load_223 | 99 | 0.00028044 | 7.0285e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_173-1_2_2_load_225 | 100 | 0.0010097 | 0.00025306 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_173-1_2_2_load_229 | 101 | 0.00098932 | 0.00024795 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_173-1_2_2_load_291 | 102 | 0.00024065 | 6.0313e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_173-1_2_2_load_276 | 103 | 0.0010879 | 0.00027264 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_173-1_2_2_load_292 | 105 | 0.0011842 | 0.00029678 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_173-1_2_2_load_289 | 106 | 0.00082515 | 0.0002068 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_173-1_2_2_load_290 | 107 | 0.00060926 | 0.00015269 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_173-1_2_2_load_286 | 109 | 0.00027875 | 6.9861e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_173-1_2_2_load_287 | 111 | 0.00040323 | 0.00010106 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_173-1_2_2_load_294 | 112 | 0.00050508 | 0.00012659 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_173-1_2_2_line_0 |  | 0 | 1 | 0.025815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_173-1_2_2_line_1 |  | 0 | 2 | 0.0050426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_173-1_2_2_line_2 |  | 1 | 102 | 0.0031825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_173-1_2_2_line_3 |  | 2 | 101 | 0.017979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_173-1_2_2_line_4 |  | 3 | 4 | 0.029404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_173-1_2_2_line_5 |  | 3 | 5 | 0.025978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_173-1_2_2_line_6 |  | 4 | 81 | 0.036636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_173-1_2_2_line_7 |  | 4 | 80 | 0.024714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_173-1_2_2_line_8 |  | 5 | 13 | 0.019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_173-1_2_2_line_9 |  | 6 | 7 | 0.11492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_173-1_2_2_line_10 |  | 6 | 8 | 0.66067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_173-1_2_2_line_11 |  | 6 | 9 | 0.33017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_173-1_2_2_line_12 |  | 7 | 90 | 0.018133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_173-1_2_2_line_13 |  | 8 | 13 | 0.040358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_173-1_2_2_line_14 |  | 9 | 84 | 0.026426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_173-1_2_2_line_15 |  | 10 | 11 | 0.015452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_173-1_2_2_line_16 |  | 10 | 12 | 0.0029559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_173-1_2_2_line_17 |  | 11 | 107 | 0.00098081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_173-1_2_2_line_18 |  | 12 | 103 | 0.0080879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_173-1_2_2_line_19 |  | 14 | 15 | 0.010551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_173-1_2_2_line_20 |  | 14 | 16 | 0.0063467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_173-1_2_2_line_21 |  | 15 | 17 | 0.0082896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_173-1_2_2_line_22 |  | 15 | 18 | 0.21812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_173-1_2_2_line_23 |  | 18 | 19 | 0.023592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_173-1_2_2_line_24 |  | 18 | 20 | 0.41655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_173-1_2_2_line_25 |  | 18 | 21 | 0.24534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_173-1_2_2_line_26 |  | 19 | 22 | 0.0020448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_173-1_2_2_line_27 |  | 20 | 25 | 0.066188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_173-1_2_2_line_28 |  | 22 | 23 | 0.099214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_173-1_2_2_line_29 |  | 23 | 24 | 0.043905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_173-1_2_2_line_30 |  | 25 | 44 | 0.02833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_173-1_2_2_line_31 |  | 26 | 27 | 0.020739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_173-1_2_2_line_32 |  | 26 | 28 | 0.038607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_173-1_2_2_line_33 |  | 27 | 29 | 0.007816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_173-1_2_2_line_34 |  | 27 | 30 | 0.011013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_173-1_2_2_line_35 |  | 28 | 31 | 0.044715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_173-1_2_2_line_36 |  | 31 | 32 | 0.033239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_173-1_2_2_line_37 |  | 32 | 33 | 0.0051551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_173-1_2_2_line_38 |  | 33 | 34 | 0.014235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_173-1_2_2_line_39 |  | 34 | 35 | 0.0018022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_173-1_2_2_line_40 |  | 35 | 36 | 0.014253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_173-1_2_2_line_41 |  | 36 | 37 | 0.0070341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_173-1_2_2_line_42 |  | 36 | 38 | 0.010586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_173-1_2_2_line_43 |  | 37 | 39 | 0.012213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_173-1_2_2_line_44 |  | 38 | 40 | 0.013396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_173-1_2_2_line_45 |  | 39 | 41 | 0.015811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_173-1_2_2_line_46 |  | 40 | 43 | 0.013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_173-1_2_2_line_47 |  | 40 | 44 | 0.013513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_173-1_2_2_line_48 |  | 41 | 42 | 0.011142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_173-1_2_2_line_49 |  | 42 | 49 | 0.035865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_173-1_2_2_line_50 |  | 43 | 45 | 0.026178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_173-1_2_2_line_51 |  | 43 | 46 | 0.031051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_173-1_2_2_line_52 |  | 45 | 48 | 0.027347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_173-1_2_2_line_53 |  | 46 | 47 | 0.032076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_173-1_2_2_line_54 |  | 49 | 50 | 0.024098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_173-1_2_2_line_55 |  | 49 | 51 | 0.011418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_173-1_2_2_line_56 |  | 50 | 55 | 0.033449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_173-1_2_2_line_57 |  | 50 | 53 | 0.02342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_173-1_2_2_line_58 |  | 51 | 65 | 0.014614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_173-1_2_2_line_59 |  | 52 | 53 | 0.032379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_173-1_2_2_line_60 |  | 53 | 54 | 0.033165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_173-1_2_2_line_61 |  | 54 | 56 | 0.017221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_173-1_2_2_line_62 |  | 55 | 64 | 0.0043715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_173-1_2_2_line_63 |  | 56 | 66 | 0.003445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_173-1_2_2_line_64 |  | 57 | 58 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_173-1_2_2_line_65 |  | 57 | 59 | 0.023171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_173-1_2_2_line_66 |  | 57 | 60 | 0.012562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_173-1_2_2_line_67 |  | 58 | 108 | 0.015156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_173-1_2_2_line_68 |  | 59 | 65 | 0.0064465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_173-1_2_2_line_69 |  | 60 | 101 | 0.0073769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_173-1_2_2_line_70 |  | 61 | 62 | 0.007286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_173-1_2_2_line_71 |  | 61 | 63 | 0.0021401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_173-1_2_2_line_72 |  | 62 | 98 | 0.014946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_173-1_2_2_line_73 |  | 63 | 78 | 0.025392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_173-1_2_2_line_74 |  | 66 | 67 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_173-1_2_2_line_75 |  | 67 | 68 | 0.017084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_173-1_2_2_line_76 |  | 67 | 69 | 0.005218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_173-1_2_2_line_77 |  | 68 | 72 | 0.021727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_173-1_2_2_line_78 |  | 69 | 78 | 0.009649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_173-1_2_2_line_79 |  | 69 | 77 | 0.017668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_173-1_2_2_line_80 |  | 70 | 71 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_173-1_2_2_line_81 |  | 71 | 72 | 0.012032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_173-1_2_2_line_82 |  | 71 | 73 | 0.045885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_173-1_2_2_line_83 |  | 72 | 74 | 0.017462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_173-1_2_2_line_84 |  | 74 | 75 | 0.0098276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_173-1_2_2_line_85 |  | 75 | 76 | 0.022804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_173-1_2_2_line_86 |  | 78 | 79 | 0.015846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_173-1_2_2_line_87 |  | 79 | 99 | 0.028492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_173-1_2_2_line_88 |  | 81 | 82 | 0.004417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_173-1_2_2_line_89 |  | 83 | 84 | 0.047883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_173-1_2_2_line_90 |  | 83 | 85 | 0.013031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_173-1_2_2_line_91 |  | 86 | 87 | 0.023575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_173-1_2_2_line_92 |  | 87 | 88 | 0.26155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_173-1_2_2_line_93 |  | 88 | 89 | 0.063072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_173-1_2_2_line_94 |  | 89 | 111 | 0.0018421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_173-1_2_2_line_95 |  | 90 | 97 | 0.042329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_173-1_2_2_line_96 |  | 91 | 92 | 0.015806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_173-1_2_2_line_97 |  | 91 | 93 | 0.026877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_173-1_2_2_line_98 |  | 92 | 94 | 0.041772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_173-1_2_2_line_99 |  | 94 | 95 | 0.0064681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_173-1_2_2_line_100 |  | 94 | 96 | 0.023013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_173-1_2_2_line_101 |  | 94 | 97 | 0.0065147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_173-1_2_2_line_102 |  | 95 | 109 | 0.01633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_173-1_2_2_line_103 |  | 96 | 110 | 0.011363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_173-1_2_2_line_104 |  | 99 | 100 | 0.025614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_173-1_2_2_line_105 |  | 104 | 105 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_173-1_2_2_line_106 |  | 104 | 106 | 0.0081353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_173-1_2_2_line_107 |  | 105 | 112 | 0.0093032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_173-1_2_2_line_108 |  | 106 | 110 | 0.016092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_173-1_2_2_line_109 |  | 107 | 110 | 0.012641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_173-1_2_2_line_110 |  | 108 | 112 | 0.0048747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_173-1_2_2_line_111 |  | 109 | 111 | 0.0084435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_173-1_2_2_trafo_175 | 0.63 MVA 20/0.4 kV | 113 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38
0 | 2706049.145 | 1247162.078 | 2706053.0319 | 1247136.5572
1 | 2706049.145 | 1247162.078 | 2706054.152 | 1247162.6762
2 | 2706053.511 | 1247133.411 | 2706053.0319 | 1247136.5572
3 | 2706054.152 | 1247162.6762 | 2706063.8154 | 1247163.8307 | 2706072.0621 | 1247163.8257
4 | 2705710.9539 | 1247465.1477 | 2705711.7018 | 1247474.0348 | 2705711.4946 | 1247480.1471 | 2705710.9967 | 1247494.5052
5 | 2705710.9539 | 1247465.1477 | 2705722.6929 | 1247465.1792 | 2705736.9316 | 1247465.2242
6 | 2705710.9967 | 1247494.5052 | 2705721.0506 | 1247495.4073 | 2705723.9978 | 1247502.977 | 2705722.6444 | 1247521.346
7 | 2705710.9967 | 1247494.5052 | 2705704.8545 | 1247495.3741 | 2705695.799 | 1247499.4827 | 2705690.9699 | 1247503.3997 | 2705689.6558 | 1247505.3469
8 | 2705736.9316 | 1247465.2242 | 2705746.1633 | 1247465.2533 | 2705756.4555 | 1247465.2857
9 | 2706097.4659 | 1247342.664 | 2706093.5009 | 1247351.8782 | 2706088.9531 | 1247374.2368 | 2706088.6664 | 1247402.065 | 2706086.985 | 1247420.8721 | 2706080.554 | 1247434.0676 | 2706067.8641 | 1247450.4314
10 | 2705796.8132 | 1247465.4124 | 2705798.1832 | 1247450.8809 | 2705794.757 | 1247427.8347 | 2705771.1095 | 1247331.4473 | 2705771.3965 | 1247318.3308 | 2705779.6402 | 1247326.2842 | 2705790.2937 | 1247335.9375 | 2705803.0081 | 1247345.2495 | 2705812.7668 | 1247350.4278 | 2705824.4919 | 1247354.6403 | 2705835.9333 | 1247356.546 | 2705855.5977 | 1247359.5216 | 2705864.8187 | 1247361.3877 | 2705869.8571 | 1247363.9575 | 2705873.7052 | 1247366.7618 | 2705878.4194 | 1247372.2503 | 2705881.1781 | 1247377.248 | 2705882.7711 | 1247382.8031 | 2705885.0935 | 1247399.5356 | 2705889.5659 | 1247410.9468 | 2705895.5689 | 1247419.9834 | 2705901.9008 | 1247427.1022 | 2705929.1534 | 1247454.7999 | 2705933.5185 | 1247457.4133 | 2705938.4911 | 1247457.7357 | 2705942.1793 | 1247455.5332 | 2705944.2198 | 1247452.5339 | 2705945.1006 | 1247448.0572 | 2705939.6196 | 1247424.6184 | 2705939.941 | 1247408.7559 | 2705954.2185 | 1247351.7545 | 2705957.1627 | 1247346.3806 | 2705961.3995 | 1247343.0759 | 2705966.0994 | 1247342.6039 | 2705970.6631 | 1247344.2535 | 2705974.4278 | 1247347.49 | 2706032.8444 | 1247418.602 | 2706055.6349 | 1247442.3285 | 2706067.8641 | 1247450.4314
11 | 2706067.8641 | 1247450.4314 | 2706011.3882 | 1247526.3487 | 2706002.2843 | 1247534.4146 | 2705992.0263 | 1247539.0127 | 2705972.2137 | 1247541.4049 | 2705957.3099 | 1247545.5753 | 2705948.7306 | 1247547.9683 | 2705934.1399 | 1247553.223 | 2705907.6484 | 1247567.4945 | 2705857.1636 | 1247602.9657 | 2705817.0009 | 1247634.9188 | 2705810.1192 | 1247641.0041
12 | 2706097.4659 | 1247342.664 | 2706104.6348 | 1247326.0084
13 | 2705796.8132 | 1247465.4124 | 2705756.4555 | 1247465.2857
14 | 2705810.1192 | 1247641.0041 | 2705807.0535 | 1247643.715 | 2705798.3721 | 1247645.9174 | 2705789.8737 | 1247645.9102 | 2705786.648 | 1247649.571
15 | 2706086.1443 | 1247256.8486 | 2706088.5326 | 1247257.6364 | 2706092.4056 | 1247256.9385 | 2706100.7678 | 1247253.606
16 | 2706086.1443 | 1247256.8486 | 2706084.3874 | 1247254.5487 | 2706084.374 | 1247254.4884
17 | 2706100.7678 | 1247253.606 | 2706101.679 | 1247253.243
18 | 2706084.374 | 1247254.4884 | 2706082.8352 | 1247247.5709 | 2706083.2641 | 1247246.6661
19 | 2706057.4646 | 1246503.8588 | 2706047.1539 | 1246506.0975
20 | 2706040.9517 | 1246507.4442 | 2706047.1539 | 1246506.0975
21 | 2706057.4646 | 1246503.8588 | 2706059.307 | 1246503.5026 | 2706059.7615 | 1246497.1056
22 | 2706057.4646 | 1246503.8588 | 2706058.0303 | 1246517.0016 | 2706053.204 | 1246541.3902 | 2706047.5542 | 1246563.6624 | 2706047.0902 | 1246572.2832 | 2706049.3334 | 1246578.2392 | 2706055.7854 | 1246582.4912 | 2706083.9368 | 1246596.0388 | 2706104.7451 | 1246610.8006 | 2706120.7138 | 1246597.509 | 2706140.7565 | 1246585.4025 | 2706161.4526 | 1246575.2093 | 2706164.7518 | 1246585.0539
23 | 2706164.7518 | 1246585.0539 | 2706173.1374 | 1246581.3233 | 2706173.3321 | 1246578.0464 | 2706176.4018 | 1246574.5542 | 2706182.2417 | 1246571.7425
24 | 2706004.8448 | 1246926.3317 | 2706013.4553 | 1246896.4841 | 2706015.4756 | 1246885.3335 | 2706015.8285 | 1246870.6726 | 2706016.2163 | 1246848.9957 | 2706016.541 | 1246841.8291 | 2706017.5343 | 1246817.5609 | 2706021.5121 | 1246775.543 | 2706027.0138 | 1246748.4421 | 2706040.0038 | 1246715.8039 | 2706059.5787 | 1246676.6117 | 2706080.4076 | 1246642.9352 | 2706104.7451 | 1246610.8006 | 2706120.7138 | 1246597.509 | 2706140.7565 | 1246585.4025 | 2706161.4526 | 1246575.2093 | 2706164.7518 | 1246585.0539
25 | 2706164.7518 | 1246585.0539 | 2706175.9061 | 1246611.0743 | 2706176.5438 | 1246616.39 | 2706174.9986 | 1246621.2439 | 2706165.2424 | 1246636.537 | 2706135.066 | 1246698.524 | 2706130.5927 | 1246709.5193 | 2706127.6334 | 1246727.9477 | 2706125.388 | 1246734.7796 | 2706108.6596 | 1246767.3062 | 2706107.4183 | 1246770.809 | 2706106.7996 | 1246774.979 | 2706107.1557 | 1246779.5668 | 2706111.3684 | 1246787.7598 | 2706118.2722 | 1246795.4561 | 2706124.3812 | 1246807.0634
26 | 2706184.0841 | 1246570.8554 | 2706182.2417 | 1246571.7425
27 | 2706004.8448 | 1246926.3317 | 2706005.0966 | 1246935.0654 | 2706007.2808 | 1246945.1569 | 2706010.8365 | 1246953.338 | 2706026.659 | 1246972.6474 | 2706033.1386 | 1246984.1946
28 | 2706153.4522 | 1246487.8411 | 2706152.8931 | 1246498.3839 | 2706153.041 | 1246504.8917 | 2706157.6462 | 1246507.2093 | 2706175.4801 | 1246519.3048 | 2706182.3005 | 1246534.1943 | 2706178.3249 | 1246539.7498 | 2706177.3002 | 1246543.3899 | 2706178.1353 | 1246550.3326 | 2706181.2096 | 1246564.2987 | 2706184.0841 | 1246570.8554
29 | 2706156.0183 | 1246444.5526 | 2706155.9477 | 1246483.082 | 2706153.4522 | 1246487.8411
30 | 2706038.5012 | 1247011.9526 | 2706036.8748 | 1246998.7508 | 2706033.1386 | 1246984.1946 | 2706033.1386 | 1246984.1946
31 | 2705914.3438 | 1246968.0479 | 2705913.2469 | 1246963.9028 | 2705907.8554 | 1246954.866 | 2705907.0766 | 1246948.9807
32 | 2705914.3438 | 1246968.0479 | 2705918.1287 | 1246970.1727 | 2705927.1568 | 1246975.2602 | 2705944.5867 | 1246991.6184
33 | 2705913.9802 | 1246945.2788 | 2705907.0766 | 1246948.9807
34 | 2705907.0766 | 1246948.9807 | 2705908.6203 | 1246942.9257 | 2705912.4639 | 1246940.1113
35 | 2705980.1803 | 1247018.65 | 2705965.6796 | 1247008.2525 | 2705946.253 | 1246993.1823 | 2705944.5867 | 1246991.6184
36 | 2705980.1803 | 1247018.65 | 2705997.4417 | 1247031.0271 | 2706008.3555 | 1247036.0121
37 | 2706013.1843 | 1247037.8074 | 2706009.2744 | 1247036.4318 | 2706008.3555 | 1247036.0121
38 | 2706026.5386 | 1247042.718 | 2706024.2599 | 1247041.7039 | 2706013.1843 | 1247037.8074
39 | 2706026.5386 | 1247042.718 | 2706028.1851 | 1247043.4508
40 | 2706041.2068 | 1247049.2462 | 2706028.1851 | 1247043.4508
41 | 2706041.2068 | 1247049.2462 | 2706044.7312 | 1247055.3336
42 | 2706041.2068 | 1247049.2462 | 2706040.0003 | 1247041.9411 | 2706040.0297 | 1247038.759
43 | 2706044.7312 | 1247055.3336 | 2706046.0729 | 1247057.651 | 2706053.5181 | 1247063.608
44 | 2706040.1534 | 1247025.3639 | 2706040.0297 | 1247038.759
45 | 2706065.8641 | 1247073.4861 | 2706053.5181 | 1247063.608
46 | 2706040.1534 | 1247025.3639 | 2706047.8999 | 1247020.999 | 2706049.4383 | 1247016.5118
47 | 2706040.1534 | 1247025.3639 | 2706038.5012 | 1247011.9526
48 | 2706074.564 | 1247080.447 | 2706065.8641 | 1247073.4861
49 | 2706098.557 | 1247107.0513 | 2706076.7228 | 1247082.1743 | 2706074.564 | 1247080.447
50 | 2706049.4383 | 1247016.5118 | 2706065.0388 | 1247020.772 | 2706072.9437 | 1247018.1112 | 2706074.601 | 1247017.9431
51 | 2706049.4383 | 1247016.5118 | 2706049.7716 | 1247008.0221 | 2706053.232 | 1246999.5662 | 2706058.9739 | 1246994.9207 | 2706064.7477 | 1246993.1749
52 | 2706094.6208 | 1247031.9434 | 2706085.7368 | 1247018.8184 | 2706081.89 | 1247017.2039 | 2706074.601 | 1247017.9431
53 | 2706096.0369 | 1246997.0376 | 2706082.7376 | 1246993.0665 | 2706068.5224 | 1246992.0336 | 2706064.7477 | 1246993.1749
54 | 2706118.2235 | 1247120.9143 | 2706104.5348 | 1247112.4293 | 2706098.557 | 1247107.0513
55 | 2706098.557 | 1247107.0513 | 2706095.13 | 1247117.9431
56 | 2706118.2235 | 1247120.9143 | 2706117.4448 | 1247115.0401 | 2706111.5954 | 1247092.3618 | 2706114.8408 | 1247089.8519
57 | 2706118.2235 | 1247120.9143 | 2706131.5345 | 1247129.8151 | 2706136.7734 | 1247135.1131
58 | 2706095.13 | 1247117.9431 | 2706095.0082 | 1247118.3302 | 2706092.142 | 1247132.2468
59 | 2706136.7734 | 1247135.1131 | 2706142.1063 | 1247132.6288 | 2706152.3496 | 1247117.5112 | 2706154.6505 | 1247113.06 | 2706157.0303 | 1247110.8849
60 | 2706136.7734 | 1247135.1131 | 2706164.6213 | 1247143.9408 | 2706168.1543 | 1247145.7108
61 | 2706168.1543 | 1247145.7108 | 2706177.0059 | 1247150.1453 | 2706182.5872 | 1247154.8823 | 2706182.5872 | 1247154.8823
62 | 2706118.2988 | 1247087.1776 | 2706114.8408 | 1247089.8519
63 | 2706183.7762 | 1247158.1156 | 2706182.5872 | 1247154.8823
64 | 2706091.8352 | 1247161.7858 | 2706095.0086 | 1247175.1876
65 | 2706091.8352 | 1247161.7858 | 2706091.3538 | 1247149.434 | 2706091.4416 | 1247138.6244
66 | 2706091.8352 | 1247161.7858 | 2706079.439 | 1247163.8212
67 | 2706102.046 | 1247188.1339 | 2706096.5552 | 1247181.7194 | 2706095.0086 | 1247175.1876
68 | 2706091.4416 | 1247138.6244 | 2706091.4668 | 1247135.525 | 2706092.142 | 1247132.2468
69 | 2706079.439 | 1247163.8212 | 2706072.0621 | 1247163.8257
70 | 2706144.112 | 1247177.9786 | 2706145.6448 | 1247170.8559
71 | 2706145.6448 | 1247170.8559 | 2706147.7454 | 1247171.2651
72 | 2706144.112 | 1247177.9786 | 2706147.1317 | 1247192.6163
73 | 2706172.8185 | 1247175.1347 | 2706161.0483 | 1247173.8563 | 2706147.7454 | 1247171.2651
74 | 2706187.6427 | 1247176.7347 | 2706185.901 | 1247163.8933 | 2706183.7762 | 1247158.1156
75 | 2706187.6427 | 1247176.7347 | 2706200.8332 | 1247177.5938 | 2706204.6869 | 1247177.2947
76 | 2706182.4399 | 1247176.1744 | 2706187.6427 | 1247176.7347
77 | 2706226.0742 | 1247173.7873 | 2706213.5203 | 1247176.6091 | 2706204.6869 | 1247177.2947
78 | 2706172.8185 | 1247175.1347 | 2706182.4399 | 1247176.1744
79 | 2706182.4399 | 1247176.1744 | 2706182.0176 | 1247184.985 | 2706181.8704 | 1247188.1404 | 2706181.7083 | 1247193.8262
80 | 2706237.727 | 1247170.6602 | 2706250.4293 | 1247167.6447
81 | 2706237.727 | 1247170.6602 | 2706226.0742 | 1247173.7873
82 | 2706221.0685 | 1247128.0946 | 2706228.2256 | 1247141.0108 | 2706237.727 | 1247170.6602
83 | 2706226.0742 | 1247173.7873 | 2706226.1941 | 1247191.2489
84 | 2706226.2616 | 1247201.0763 | 2706226.1941 | 1247191.2489
85 | 2706238.8984 | 1247217.4073 | 2706229.2314 | 1247211.7519 | 2706226.3065 | 1247207.6073 | 2706226.2616 | 1247201.0763
86 | 2706172.8185 | 1247175.1347 | 2706172.1945 | 1247190.9687
87 | 2706174.1154 | 1247219.1016 | 2706172.9421 | 1247216.303 | 2706171.5438 | 1247207.4821 | 2706172.1945 | 1247190.9687
88 | 2705722.3198 | 1247525.7511 | 2705722.6444 | 1247521.346
89 | 2705784.4452 | 1247693.5421 | 2705783.2547 | 1247678.1511 | 2705786.4677 | 1247668.2784 | 2705783.2758 | 1247663.8512 | 2705781.1917 | 1247655.7632 | 2705786.648 | 1247649.571
90 | 2705782.6725 | 1247706.2713 | 2705784.8198 | 1247698.3841 | 2705784.4452 | 1247693.5421
91 | 2706102.087 | 1247619.1226 | 2706079.3325 | 1247625.288
92 | 2706102.087 | 1247619.1226 | 2706091.8658 | 1247579.4748 | 2706104.8762 | 1247573.0469 | 2706114.1095 | 1247564.0828 | 2706127.199 | 1247546.4919 | 2706130.9868 | 1247514.6898 | 2706139.1706 | 1247475.7608 | 2706139.8598 | 1247449.0963 | 2706132.9771 | 1247393.0285 | 2706132.4234 | 1247376.7055
93 | 2706132.4234 | 1247376.7055 | 2706132.7053 | 1247355.06 | 2706132.2324 | 1247330.0093 | 2706131.0908 | 1247323.7283 | 2706129.4772 | 1247313.8741
94 | 2706129.4772 | 1247313.8741 | 2706129.1795 | 1247312.0562
95 | 2706121.4987 | 1247287.1846 | 2706115.1391 | 1247301.5808 | 2706108.2572 | 1247317.5926 | 2706104.6348 | 1247326.0084
96 | 2706142.0698 | 1247243.4831 | 2706145.3996 | 1247254.129 | 2706147.8418 | 1247258.0877
97 | 2706159.3422 | 1247282.1565 | 2706155.8466 | 1247271.0628 | 2706147.8418 | 1247258.0877
98 | 2706124.1312 | 1247281.2255 | 2706142.0698 | 1247243.4831
99 | 2706124.1312 | 1247281.2255 | 2706125.1764 | 1247287.6086
100 | 2706124.1312 | 1247281.2255 | 2706119.5023 | 1247266.3419 | 2706117.0989 | 1247259.3149
101 | 2706124.1312 | 1247281.2255 | 2706121.4987 | 1247287.1846
102 | 2706125.1764 | 1247287.6086 | 2706127.8151 | 1247303.7237
103 | 2706113.4218 | 1247248.5634 | 2706117.0989 | 1247259.3149
104 | 2706174.1154 | 1247219.1016 | 2706176.1879 | 1247224.0451 | 2706186.7907 | 1247241.3017
105 | 2706107.1774 | 1247225.1663 | 2706106.6248 | 1247221.0087 | 2706103.7378 | 1247202.0842
106 | 2706107.1774 | 1247225.1663 | 2706108.9874 | 1247233.0977
107 | 2706101.7398 | 1247192.999 | 2706103.6837 | 1247201.7296 | 2706103.7378 | 1247202.0842
108 | 2706113.4218 | 1247248.5634 | 2706109.4401 | 1247235.0814 | 2706108.9874 | 1247233.0977
109 | 2706113.4218 | 1247248.5634 | 2706101.679 | 1247253.243
110 | 2706102.046 | 1247188.1339 | 2706101.7398 | 1247192.999 | 2706101.7398 | 1247192.999
111 | 2706127.8151 | 1247303.7237 | 2706129.1795 | 1247312.0562

## bus_geodata
| x | y | coords
0 | 2706049.145 | 1247162.078
1 | 2706053.0319 | 1247136.5572
2 | 2706054.152 | 1247162.6762
3 | 2705710.9539 | 1247465.1477
4 | 2705710.9967 | 1247494.5052
5 | 2705736.9316 | 1247465.2242
6 | 2706067.8641 | 1247450.4314
7 | 2706097.4659 | 1247342.664
8 | 2705796.8132 | 1247465.4124
9 | 2705810.1192 | 1247641.0041
10 | 2706086.1443 | 1247256.8486
11 | 2706100.7678 | 1247253.606
12 | 2706084.374 | 1247254.4884
13 | 2705756.4555 | 1247465.2857
14 | 2706047.1539 | 1246506.0975
15 | 2706057.4646 | 1246503.8588
16 | 2706040.9517 | 1246507.4442
17 | 2706059.7615 | 1246497.1056
18 | 2706164.7518 | 1246585.0539
19 | 2706182.2417 | 1246571.7425
20 | 2706004.8448 | 1246926.3317
21 | 2706124.3812 | 1246807.0634
22 | 2706184.0841 | 1246570.8554
23 | 2706153.4522 | 1246487.8411
24 | 2706156.0183 | 1246444.5526
25 | 2706033.1386 | 1246984.1946
26 | 2705914.3438 | 1246968.0479
27 | 2705907.0766 | 1246948.9807
28 | 2705944.5867 | 1246991.6184
29 | 2705913.9802 | 1246945.2788
30 | 2705912.4639 | 1246940.1113
31 | 2705980.1803 | 1247018.65
32 | 2706008.3555 | 1247036.0121
33 | 2706013.1843 | 1247037.8074
34 | 2706026.5386 | 1247042.718
35 | 2706028.1851 | 1247043.4508
36 | 2706041.2068 | 1247049.2462
37 | 2706044.7312 | 1247055.3336
38 | 2706040.0297 | 1247038.759
39 | 2706053.5181 | 1247063.608
40 | 2706040.1534 | 1247025.3639
41 | 2706065.8641 | 1247073.4861
42 | 2706074.564 | 1247080.447
43 | 2706049.4383 | 1247016.5118
44 | 2706038.5012 | 1247011.9526
45 | 2706074.601 | 1247017.9431
46 | 2706064.7477 | 1246993.1749
47 | 2706096.0369 | 1246997.0376
48 | 2706094.6208 | 1247031.9434
49 | 2706098.557 | 1247107.0513
50 | 2706118.2235 | 1247120.9143
51 | 2706095.13 | 1247117.9431
52 | 2706157.0303 | 1247110.8849
53 | 2706136.7734 | 1247135.1131
54 | 2706168.1543 | 1247145.7108
55 | 2706114.8408 | 1247089.8519
56 | 2706182.5872 | 1247154.8823
57 | 2706091.8352 | 1247161.7858
58 | 2706095.0086 | 1247175.1876
59 | 2706091.4416 | 1247138.6244
60 | 2706079.439 | 1247163.8212
61 | 2706145.6448 | 1247170.8559
62 | 2706144.112 | 1247177.9786
63 | 2706147.7454 | 1247171.2651
64 | 2706118.2988 | 1247087.1776
65 | 2706092.142 | 1247132.2468
66 | 2706183.7762 | 1247158.1156
67 | 2706187.6427 | 1247176.7347
68 | 2706204.6869 | 1247177.2947
69 | 2706182.4399 | 1247176.1744
70 | 2706250.4293 | 1247167.6447
71 | 2706237.727 | 1247170.6602
72 | 2706226.0742 | 1247173.7873
73 | 2706221.0685 | 1247128.0946
74 | 2706226.1941 | 1247191.2489
75 | 2706226.2616 | 1247201.0763
76 | 2706238.8984 | 1247217.4073
77 | 2706181.7083 | 1247193.8262
78 | 2706172.8185 | 1247175.1347
79 | 2706172.1945 | 1247190.9687
80 | 2705689.6558 | 1247505.3469
81 | 2705722.6444 | 1247521.346
82 | 2705722.3198 | 1247525.7511
83 | 2705784.4452 | 1247693.5421
84 | 2705786.648 | 1247649.571
85 | 2705782.6725 | 1247706.2713
86 | 2706079.3325 | 1247625.288
87 | 2706102.087 | 1247619.1226
88 | 2706132.4234 | 1247376.7055
89 | 2706129.4772 | 1247313.8741
90 | 2706104.6348 | 1247326.0084
91 | 2706147.8418 | 1247258.0877
92 | 2706142.0698 | 1247243.4831
93 | 2706159.3422 | 1247282.1565
94 | 2706124.1312 | 1247281.2255
95 | 2706125.1764 | 1247287.6086
96 | 2706117.0989 | 1247259.3149
97 | 2706121.4987 | 1247287.1846
98 | 2706147.1317 | 1247192.6163
99 | 2706174.1154 | 1247219.1016
100 | 2706186.7907 | 1247241.3017
101 | 2706072.0621 | 1247163.8257
102 | 2706053.511 | 1247133.411
103 | 2706083.2641 | 1247246.6661
104 | 2706107.1774 | 1247225.1663
105 | 2706103.7378 | 1247202.0842
106 | 2706108.9874 | 1247233.0977
107 | 2706101.679 | 1247253.243
108 | 2706102.046 | 1247188.1339
109 | 2706127.8151 | 1247303.7237
110 | 2706113.4218 | 1247248.5634
111 | 2706129.1795 | 1247312.0562
112 | 2706101.7398 | 1247192.999
113 | 2706098.557 | 1247107.0513

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99495 | -0.096842 | 0 | 0
1 | 0.99494 | -0.097033 | 0.0001793 | 4.4936e-05
2 | 0.99495 | -0.096805 | 0.00050743 | 0.00012717
3 | 0.98435 | -0.3025 | 0 | 0
4 | 0.98414 | -0.3066 | 0 | 0
5 | 0.98453 | -0.29887 | 0.00055315 | 0.00013863
6 | 0.9902 | -0.1887 | 0 | 0
7 | 0.99139 | -0.16569 | 0 | 0
8 | 0.985 | -0.28975 | 0 | 0
9 | 0.98939 | -0.20455 | 0.00025582 | 6.4114e-05
10 | 0.99272 | -0.13984 | 0 | 0
11 | 0.99274 | -0.13945 | 0.00087667 | 0.00021971
12 | 0.99272 | -0.13991 | 0.00031798 | 7.9694e-05
13 | 0.98468 | -0.29595 | 0.00023113 | 5.7928e-05
14 | 0.98127 | -0.36074 | 0.0040196 | 0.0010074
15 | 0.98134 | -0.35936 | 0 | 0
16 | 0.98125 | -0.36111 | 0.0032308 | 0.00080972
17 | 0.98132 | -0.35965 | 0.0019746 | 0.00049489
18 | 0.9832 | -0.32299 | 0 | 0
19 | 0.98285 | -0.32983 | 0.0021159 | 0.00053029
20 | 0.99392 | -0.11582 | 0 | 0
21 | 0.98262 | -0.33434 | 0.002561 | 0.00064185
22 | 0.98282 | -0.33035 | 0 | 0
23 | 0.98154 | -0.35537 | 0 | 0
24 | 0.98097 | -0.36646 | 0.013955 | 0.0034975
25 | 0.99563 | -0.0833 | 0.0017745 | 0.00044474
26 | 0.99668 | -0.063596 | 0 | 0
27 | 0.9966 | -0.064954 | 0 | 0
28 | 0.99681 | -0.061068 | 0.00067205 | 0.00016843
29 | 0.9966 | -0.065126 | 0.0012548 | 0.00031448
30 | 0.99658 | -0.065432 | 0.002475 | 0.0006203
31 | 0.99699 | -0.057614 | 0.003139 | 0.0007867
32 | 0.99721 | -0.053217 | 0.0030088 | 0.00075408
33 | 0.99726 | -0.052263 | 0.0010919 | 0.00027365
34 | 0.99741 | -0.049358 | 0.00055357 | 0.00013874
35 | 0.99743 | -0.048973 | 0.0020883 | 0.00052338
36 | 0.99762 | -0.045405 | 0 | 0
37 | 0.99796 | -0.038875 | 0.0016925 | 0.00042419
38 | 0.99724 | -0.05259 | 0.0018663 | 0.00046773
39 | 0.99857 | -0.027187 | 0.0023288 | 0.00058364
40 | 0.99679 | -0.061251 | 0 | 0
41 | 0.9994 | -0.011432 | 0.001783 | 0.00044685
42 | 1 | 0 | -0.15459 | -0.038757
43 | 0.99671 | -0.062723 | 0 | 0
44 | 0.9964 | -0.068533 | 0.0010382 | 0.0002602
45 | 0.99662 | -0.064462 | 0.0025527 | 0.00063976
46 | 0.99664 | -0.064017 | 0.0011873 | 0.00029757
47 | 0.99661 | -0.064686 | 0.0011872 | 0.00029754
48 | 0.99659 | -0.065053 | 0.0012322 | 0.00030881
49 | 0.99695 | -0.058323 | 0 | 0
50 | 0.99585 | -0.079438 | 0 | 0
51 | 0.9965 | -0.066957 | 0.00095787 | 0.00024006
52 | 0.99463 | -0.10299 | 0.0067362 | 0.0016882
53 | 0.99483 | -0.099147 | 0 | 0
54 | 0.99359 | -0.12318 | 0.0041891 | 0.0010499
55 | 0.99579 | -0.080658 | 0.0014785 | 0.00037055
56 | 0.99301 | -0.13441 | 0.0032755 | 0.00082091
57 | 0.99502 | -0.095569 | 0 | 0
58 | 0.99463 | -0.10306 | 0.0032991 | 0.00082682
59 | 0.99574 | -0.081703 | 0.0006559 | 0.00016438
60 | 0.99498 | -0.096262 | 0.001212 | 0.00030375
61 | 0.99187 | -0.15637 | 0 | 0
62 | 0.99183 | -0.15711 | 0 | 0
63 | 0.99188 | -0.15616 | 0.0050375 | 0.0012625
64 | 0.99579 | -0.080704 | 0.00059607 | 0.00014939
65 | 0.99594 | -0.077774 | 0.0074715 | 0.0018725
66 | 0.9929 | -0.13646 | 0.0036095 | 0.00090463
67 | 0.99238 | -0.14661 | 0 | 0
68 | 0.99224 | -0.14926 | 0.00069612 | 0.00017446
69 | 0.99227 | -0.14857 | 0 | 0
70 | 0.99199 | -0.15407 | 0.0027385 | 0.00068634
71 | 0.99202 | -0.15344 | 0 | 0
72 | 0.99208 | -0.15236 | 0 | 0
73 | 0.99193 | -0.1553 | 0.0022993 | 0.00057625
74 | 0.99203 | -0.1533 | 0.0014366 | 0.00036004
75 | 0.99202 | -0.15357 | 0.00028509 | 7.145e-05
76 | 0.99199 | -0.1541 | 0.0013046 | 0.00032696
77 | 0.99219 | -0.15018 | 0.0051316 | 0.0012861
78 | 0.99213 | -0.15132 | 0 | 0
79 | 0.99205 | -0.15283 | 0.0040881 | 0.0010246
80 | 0.98404 | -0.30851 | 0.0042771 | 0.0010719
81 | 0.98402 | -0.3089 | 0.00017888 | 4.4831e-05
82 | 0.98401 | -0.30916 | 0.0033023 | 0.00082764
83 | 0.98925 | -0.20713 | 0.0011659 | 0.00029221
84 | 0.98933 | -0.2057 | 0.00075355 | 0.00018886
85 | 0.98925 | -0.20725 | 0.00051461 | 0.00012897
86 | 0.99062 | -0.18062 | 0.0041042 | 0.0010286
87 | 0.99071 | -0.1789 | 0 | 0
88 | 0.99169 | -0.15984 | 0 | 0
89 | 0.99193 | -0.15524 | 0.00063632 | 0.00015948
90 | 0.99157 | -0.16207 | 0.00023595 | 5.9135e-05
91 | 0.99195 | -0.15483 | 0.0014445 | 0.00036203
92 | 0.99199 | -0.15406 | 0 | 0
93 | 0.99192 | -0.15546 | 0.0013262 | 0.00033238
94 | 0.99209 | -0.15201 | 0 | 0
95 | 0.99206 | -0.15274 | 0.00098229 | 0.00024619
96 | 0.99255 | -0.14323 | 0.00062109 | 0.00015566
97 | 0.99202 | -0.15343 | 0.00084778 | 0.00021247
98 | 0.99176 | -0.15862 | 0.0057029 | 0.0014293
99 | 0.99202 | -0.15349 | 0.00028044 | 7.0285e-05
100 | 0.992 | -0.15394 | 0.0010097 | 0.00025306
101 | 0.99497 | -0.096511 | 0.00098932 | 0.00024795
102 | 0.99494 | -0.097047 | 0.00024065 | 6.0313e-05
103 | 0.99271 | -0.14007 | 0.0010879 | 0.00027264
104 | 0.99334 | -0.12791 | 0 | 0
105 | 0.99389 | -0.11725 | 0.0011842 | 0.00029678
106 | 0.99315 | -0.13164 | 0.00082515 | 0.0002068
107 | 0.99275 | -0.13941 | 0.00060926 | 0.00015269
108 | 0.99425 | -0.11043 | 0 | 0
109 | 0.99198 | -0.15431 | 0.00027875 | 6.9861e-05
110 | 0.99278 | -0.13877 | 0 | 0
111 | 0.99194 | -0.15508 | 0.00040323 | 0.00010106
112 | 0.99412 | -0.1128 | 0.00050508 | 0.00012659
113 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00041995 | 0.00010487 | -0.00041995 | -0.00010521 | 3.8178e-09 | -3.3282e-07 | 0.00062793 | 0.00062805 | 0.00062805 | 0.99495 | -0.096842 | 0.99494 | -0.097033 | 0.17254
1 | -0.00041995 | -0.00010487 | 0.00041995 | 0.00010481 | 7.4559e-10 | -6.5012e-08 | 0.00062793 | 0.00062791 | 0.00062793 | 0.99495 | -0.096842 | 0.99495 | -0.096805 | 0.17251
2 | 0.00024065 | 6.0272e-05 | -0.00024065 | -6.0313e-05 | 1.5455e-10 | -4.1231e-08 | 0.0003599 | 0.00035991 | 0.00035991 | 0.99494 | -0.097033 | 0.99494 | -0.097047 | 0.098877
3 | -0.00092738 | -0.00023198 | 0.00092739 | 0.00023176 | 1.2966e-08 | -2.252e-07 | 0.0013868 | 0.0013867 | 0.0013868 | 0.99495 | -0.096805 | 0.99497 | -0.096511 | 0.38099
4 | 0.0077606 | 0.0019447 | -0.0077591 | -0.0019441 | 1.5176e-06 | 5.9754e-07 | 0.011731 | 0.011732 | 0.011732 | 0.98435 | -0.3025 | 0.98414 | -0.3066 | 3.223
5 | -0.0077606 | -0.0019447 | 0.007762 | 0.0019452 | 1.3407e-06 | 5.2776e-07 | 0.011731 | 0.011731 | 0.011731 | 0.98435 | -0.3025 | 0.98453 | -0.29887 | 3.2229
6 | 0.0034816 | 0.00087222 | -0.0034812 | -0.00087244 | 3.8072e-07 | -2.218e-07 | 0.0052641 | 0.0052643 | 0.0052643 | 0.98414 | -0.3066 | 0.98402 | -0.3089 | 1.4462
7 | 0.0042775 | 0.0010719 | -0.0042771 | -0.0010719 | 3.8767e-07 | -6.5894e-08 | 0.0064675 | 0.0064676 | 0.0064676 | 0.98414 | -0.3066 | 0.98404 | -0.30851 | 1.7768
8 | -0.0083151 | -0.0020838 | 0.0083163 | 0.0020843 | 1.1563e-06 | 4.9174e-07 | 0.012567 | 0.012567 | 0.012567 | 0.98453 | -0.29887 | 0.98468 | -0.29595 | 3.4526
9 | -0.011283 | -0.0028316 | 0.011296 | 0.0028381 | 1.2392e-05 | 6.4508e-06 | 0.016957 | 0.016957 | 0.016957 | 0.9902 | -0.1887 | 0.99139 | -0.16569 | 4.6586
10 | 0.0085912 | 0.0021614 | -0.0085499 | -0.0021434 | 4.1323e-05 | 1.7993e-05 | 0.012913 | 0.012916 | 0.012916 | 0.9902 | -0.1887 | 0.985 | -0.28975 | 3.5484
11 | 0.0026922 | 0.00067025 | -0.0026902 | -0.0006732 | 2.0257e-06 | -2.9472e-06 | 0.0040441 | 0.0040456 | 0.0040456 | 0.9902 | -0.1887 | 0.98939 | -0.20455 | 1.1114
12 | -0.011296 | -0.0028381 | 0.011298 | 0.0028391 | 1.9552e-06 | 1.0175e-06 | 0.016957 | 0.016957 | 0.016957 | 0.99139 | -0.16569 | 0.99157 | -0.16207 | 4.6585
13 | 0.0085499 | 0.0021434 | -0.0085474 | -0.0021423 | 2.5249e-06 | 1.1024e-06 | 0.012916 | 0.012917 | 0.012917 | 0.985 | -0.28975 | 0.98468 | -0.29595 | 3.5485
14 | 0.0024344 | 0.00060908 | -0.0024342 | -0.00060934 | 1.3282e-07 | -2.5435e-07 | 0.0036609 | 0.003661 | 0.003661 | 0.98939 | -0.20455 | 0.98933 | -0.2057 | 1.0058
15 | -0.0014059 | -0.0003522 | 0.0014059 | 0.00035202 | 2.5729e-08 | -1.8332e-07 | 0.0021072 | 0.0021071 | 0.0021072 | 0.99272 | -0.13984 | 0.99274 | -0.13945 | 0.57891
16 | 0.0014059 | 0.0003522 | -0.0014058 | -0.00035224 | 4.9221e-09 | -3.5067e-08 | 0.0021072 | 0.0021072 | 0.0021072 | 0.99272 | -0.13984 | 0.99272 | -0.13991 | 0.57891
17 | -0.0022826 | -0.00057173 | 0.0022826 | 0.00057172 | 4.3048e-09 | -9.9263e-09 | 0.0034212 | 0.0034212 | 0.0034212 | 0.99274 | -0.13945 | 0.99275 | -0.13941 | 0.93989
18 | 0.0010879 | 0.00027254 | -0.0010879 | -0.00027264 | 8.0643e-09 | -9.9406e-08 | 0.0016306 | 0.0016306 | 0.0016306 | 0.99272 | -0.13991 | 0.99271 | -0.14007 | 0.44798
19 | -0.0072505 | -0.0018171 | 0.0072509 | 0.0018173 | 4.7829e-07 | 1.7281e-07 | 0.010995 | 0.010995 | 0.010995 | 0.98127 | -0.36074 | 0.98134 | -0.35936 | 3.0205
20 | 0.0032309 | 0.00080968 | -0.0032308 | -0.00080972 | 5.713e-08 | -4.361e-08 | 0.0048994 | 0.0048994 | 0.0048994 | 0.98127 | -0.36074 | 0.98125 | -0.36111 | 1.346
21 | 0.0019747 | 0.0004948 | -0.0019746 | -0.00049489 | 2.7869e-08 | -8.6895e-08 | 0.0029942 | 0.0029942 | 0.0029942 | 0.98134 | -0.35936 | 0.98132 | -0.35965 | 0.82259
22 | -0.0092256 | -0.0023121 | 0.0092416 | 0.0023195 | 1.6005e-05 | 7.4823e-06 | 0.013989 | 0.013988 | 0.013989 | 0.98134 | -0.35936 | 0.9832 | -0.32299 | 3.8431
23 | 0.016101 | 0.0040446 | -0.016095 | -0.0040415 | 5.2545e-06 | 3.0638e-06 | 0.024371 | 0.024371 | 0.024371 | 0.9832 | -0.32299 | 0.98285 | -0.32983 | 6.6953
24 | -0.027905 | -0.0070038 | 0.028183 | 0.0071767 | 0.00027864 | 0.00017299 | 0.042236 | 0.042234 | 0.042236 | 0.9832 | -0.32299 | 0.99392 | -0.11582 | 11.6032
25 | 0.0025624 | 0.00063962 | -0.002561 | -0.00064185 | 1.3834e-06 | -2.2243e-06 | 0.0038771 | 0.0038782 | 0.0038782 | 0.9832 | -0.32299 | 0.98262 | -0.33434 | 1.0654
26 | 0.013979 | 0.0035112 | -0.013979 | -0.003511 | 3.4358e-07 | 1.9398e-07 | 0.021167 | 0.021167 | 0.021167 | 0.98285 | -0.32983 | 0.98282 | -0.33035 | 5.8152
27 | -0.028183 | -0.0071767 | 0.028227 | 0.0072042 | 4.4272e-05 | 2.7475e-05 | 0.042234 | 0.042234 | 0.042234 | 0.99392 | -0.11582 | 0.99563 | -0.0833 | 11.6027
28 | 0.013979 | 0.003511 | -0.013962 | -0.0035016 | 1.6671e-05 | 9.4135e-06 | 0.021167 | 0.021168 | 0.021168 | 0.98282 | -0.33035 | 0.98154 | -0.35537 | 5.8153
29 | 0.013962 | 0.0035016 | -0.013955 | -0.0034975 | 7.3774e-06 | 4.1669e-06 | 0.021168 | 0.021168 | 0.021168 | 0.98154 | -0.35537 | 0.98097 | -0.36646 | 5.8154
30 | -0.030002 | -0.007649 | 0.030023 | 0.0076623 | 2.1403e-05 | 1.333e-05 | 0.044886 | 0.044885 | 0.044886 | 0.99563 | -0.0833 | 0.9964 | -0.068533 | 12.3312
31 | 0.0037301 | 0.00093445 | -0.0037299 | -0.00093457 | 2.4119e-07 | -1.159e-07 | 0.0055688 | 0.0055689 | 0.0055689 | 0.99668 | -0.063596 | 0.9966 | -0.064954 | 1.5299
32 | -0.0037301 | -0.00093445 | 0.0037305 | 0.00093424 | 4.4896e-07 | -2.1587e-07 | 0.0055688 | 0.0055686 | 0.0055688 | 0.99668 | -0.063596 | 0.99681 | -0.061068 | 1.5299
33 | 0.0012548 | 0.00031438 | -0.0012548 | -0.00031448 | 1.0288e-08 | -9.526e-08 | 0.0018735 | 0.0018735 | 0.0018735 | 0.9966 | -0.064954 | 0.9966 | -0.065126 | 0.5147
34 | 0.0024751 | 0.00062019 | -0.002475 | -0.0006203 | 5.6397e-08 | -1.074e-07 | 0.0036954 | 0.0036955 | 0.0036955 | 0.9966 | -0.064954 | 0.99658 | -0.065432 | 1.0152
35 | -0.0044026 | -0.0011027 | 0.0044033 | 0.0011026 | 7.2418e-07 | -1.1952e-07 | 0.0065719 | 0.0065717 | 0.0065719 | 0.99681 | -0.061068 | 0.99699 | -0.057614 | 1.8055
36 | -0.0075423 | -0.0018893 | 0.0075439 | 0.0018898 | 1.5794e-06 | 5.7726e-07 | 0.011257 | 0.011256 | 0.011257 | 0.99699 | -0.057614 | 0.99721 | -0.053217 | 3.0925
37 | -0.010553 | -0.0026439 | 0.010553 | 0.0026441 | 4.793e-07 | 2.395e-07 | 0.015746 | 0.015746 | 0.015746 | 0.99721 | -0.053217 | 0.99726 | -0.052263 | 4.3259
38 | -0.011645 | -0.0029178 | 0.011647 | 0.0029186 | 1.6116e-06 | 8.4566e-07 | 0.017375 | 0.017375 | 0.017375 | 0.99726 | -0.052263 | 0.99741 | -0.049358 | 4.7734
39 | -0.0122 | -0.0030574 | 0.0122 | 0.0030575 | 2.2389e-07 | 1.1977e-07 | 0.018201 | 0.018201 | 0.018201 | 0.99741 | -0.049358 | 0.99743 | -0.048973 | 5.0003
40 | -0.014289 | -0.0035809 | 0.014291 | 0.0035822 | 2.4287e-06 | 1.3683e-06 | 0.021316 | 0.021316 | 0.021316 | 0.99743 | -0.048973 | 0.99762 | -0.045405 | 5.8562
41 | -0.053419 | -0.01354 | 0.053436 | 0.013551 | 1.6769e-05 | 1.064e-05 | 0.079732 | 0.079732 | 0.079732 | 0.99762 | -0.045405 | 0.99796 | -0.038875 | 21.9045
42 | 0.039128 | 0.0099579 | -0.039115 | -0.0099494 | 1.3547e-05 | 8.5319e-06 | 0.058416 | 0.058416 | 0.058416 | 0.99762 | -0.045405 | 0.99724 | -0.05259 | 16.0484
43 | -0.055129 | -0.013975 | 0.05516 | 0.013995 | 3.0987e-05 | 1.9672e-05 | 0.082256 | 0.082256 | 0.082256 | 0.99796 | -0.038875 | 0.99857 | -0.027187 | 22.5978
44 | 0.037248 | 0.0094817 | -0.037233 | -0.0094719 | 1.5547e-05 | 9.7751e-06 | 0.055631 | 0.055631 | 0.055631 | 0.99724 | -0.05259 | 0.99679 | -0.061251 | 15.2834
45 | -0.057488 | -0.014578 | 0.057532 | 0.014606 | 4.3574e-05 | 2.768e-05 | 0.085726 | 0.085726 | 0.085726 | 0.99857 | -0.027187 | 0.9994 | -0.011432 | 23.5511
46 | 0.0061603 | 0.0015426 | -0.0061599 | -0.0015425 | 4.3174e-07 | 9.8853e-08 | 0.0091957 | 0.0091957 | 0.0091957 | 0.99679 | -0.061251 | 0.99671 | -0.062723 | 2.5263
47 | 0.031073 | 0.0079293 | -0.031062 | -0.0079225 | 1.0927e-05 | 6.8169e-06 | 0.046436 | 0.046436 | 0.046436 | 0.99679 | -0.061251 | 0.9964 | -0.068533 | 12.7571
48 | -0.059315 | -0.015053 | 0.059348 | 0.015074 | 3.2637e-05 | 2.0741e-05 | 0.088381 | 0.088381 | 0.088381 | 0.9994 | -0.011432 | 1 | 0 | 24.2804
49 | 0.093597 | 0.023683 | -0.093336 | -0.023517 | 0.00026118 | 0.00016668 | 0.13935 | 0.13935 | 0.13935 | 1 | 0 | 0.99695 | -0.058323 | 38.2841
50 | 0.0037852 | 0.00094809 | -0.0037849 | -0.00094823 | 3.1347e-07 | -1.4053e-07 | 0.0056508 | 0.0056509 | 0.0056509 | 0.99671 | -0.062723 | 0.99662 | -0.064462 | 1.5525
51 | 0.0023747 | 0.0005944 | -0.0023745 | -0.00059471 | 1.4633e-07 | -3.1101e-07 | 0.0035449 | 0.0035451 | 0.0035451 | 0.99671 | -0.062723 | 0.99664 | -0.064017 | 0.97393
52 | 0.0012322 | 0.00030848 | -0.0012322 | -0.00030881 | 3.4708e-08 | -3.3413e-07 | 0.0018396 | 0.0018398 | 0.0018398 | 0.99662 | -0.064462 | 0.99659 | -0.065053 | 0.50543
53 | 0.0011872 | 0.00029714 | -0.0011872 | -0.00029754 | 3.779e-08 | -3.9379e-07 | 0.0017724 | 0.0017726 | 0.0017726 | 0.99664 | -0.064017 | 0.99661 | -0.064686 | 0.48697
54 | 0.050088 | 0.012622 | -0.050038 | -0.01259 | 5.054e-05 | 3.2031e-05 | 0.074784 | 0.074784 | 0.074784 | 0.99695 | -0.058323 | 0.99585 | -0.079438 | 20.5451
55 | 0.043248 | 0.010895 | -0.04323 | -0.010884 | 1.7852e-05 | 1.1277e-05 | 0.06457 | 0.06457 | 0.06457 | 0.99695 | -0.058323 | 0.9965 | -0.066957 | 17.7391
56 | 0.0020747 | 0.00051952 | -0.0020746 | -0.00051988 | 1.2054e-07 | -3.5802e-07 | 0.0030999 | 0.0031 | 0.0031 | 0.99585 | -0.079438 | 0.99579 | -0.080658 | 0.85166
57 | 0.047963 | 0.01207 | -0.047918 | -0.012042 | 4.513e-05 | 2.8579e-05 | 0.071684 | 0.071684 | 0.071684 | 0.99585 | -0.079438 | 0.99483 | -0.099147 | 19.6935
58 | 0.042272 | 0.010643 | -0.04225 | -0.01063 | 2.1848e-05 | 1.3793e-05 | 0.06314 | 0.06314 | 0.06314 | 0.9965 | -0.066957 | 0.99594 | -0.077774 | 17.3461
59 | -0.0067362 | -0.0016882 | 0.0067374 | 0.0016886 | 1.2331e-06 | 3.6887e-07 | 0.010078 | 0.010078 | 0.010078 | 0.99463 | -0.10299 | 0.99483 | -0.099147 | 2.7686
60 | 0.04118 | 0.010353 | -0.041133 | -0.010323 | 4.7204e-05 | 2.978e-05 | 0.061607 | 0.061607 | 0.061607 | 0.99483 | -0.099147 | 0.99359 | -0.12318 | 16.925
61 | 0.036944 | 0.0092735 | -0.036924 | -0.0092611 | 1.9772e-05 | 1.2431e-05 | 0.055333 | 0.055333 | 0.055333 | 0.99359 | -0.12318 | 0.99301 | -0.13441 | 15.2015
62 | 0.00059607 | 0.00014933 | -0.00059607 | -0.00014939 | 1.3005e-09 | -5.6036e-08 | 0.00089069 | 0.00089071 | 0.00089071 | 0.99579 | -0.080658 | 0.99579 | -0.080704 | 0.2447
63 | 0.033649 | 0.0084401 | -0.033646 | -0.0084381 | 3.2848e-06 | 2.0577e-06 | 0.050425 | 0.050425 | 0.050425 | 0.99301 | -0.13441 | 0.9929 | -0.13646 | 13.8531
64 | 0.030965 | 0.0077912 | -0.030954 | -0.0077843 | 1.108e-05 | 6.9125e-06 | 0.046318 | 0.046318 | 0.046318 | 0.99502 | -0.095569 | 0.99463 | -0.10306 | 12.7248
65 | -0.034094 | -0.0085745 | 0.034117 | 0.0085887 | 2.2598e-05 | 1.4161e-05 | 0.050997 | 0.050997 | 0.050997 | 0.99502 | -0.095569 | 0.99574 | -0.081703 | 14.0101
66 | 0.0031288 | 0.00078327 | -0.0031287 | -0.00078337 | 1.0312e-07 | -9.7165e-08 | 0.0046787 | 0.0046788 | 0.0046788 | 0.99502 | -0.095569 | 0.99498 | -0.096262 | 1.2854
67 | 0.027655 | 0.0069575 | -0.027645 | -0.0069515 | 9.7332e-06 | 6.0326e-06 | 0.041383 | 0.041383 | 0.041383 | 0.99463 | -0.10306 | 0.99425 | -0.11043 | 11.3689
68 | -0.034772 | -0.0087531 | 0.034779 | 0.0087572 | 6.531e-06 | 4.096e-06 | 0.051977 | 0.051977 | 0.051977 | 0.99574 | -0.081703 | 0.99594 | -0.077774 | 14.2794
69 | 0.0019167 | 0.00047962 | -0.0019167 | -0.0004797 | 2.2727e-08 | -8.1264e-08 | 0.0028663 | 0.0028663 | 0.0028663 | 0.99498 | -0.096262 | 0.99497 | -0.096511 | 0.78744
70 | 0.0057035 | 0.0014294 | -0.0057033 | -0.0014293 | 2.0003e-07 | 3.3986e-08 | 0.0085564 | 0.0085564 | 0.0085564 | 0.99187 | -0.15637 | 0.99183 | -0.15711 | 2.3507
71 | -0.0057035 | -0.0014294 | 0.0057036 | 0.0014294 | 5.8756e-08 | 9.9812e-09 | 0.0085564 | 0.0085564 | 0.0085564 | 0.99187 | -0.15637 | 0.99188 | -0.15616 | 2.3507
72 | 0.0057033 | 0.0014293 | -0.0057029 | -0.0014293 | 4.1034e-07 | 6.9743e-08 | 0.0085564 | 0.0085565 | 0.0085565 | 0.99183 | -0.15711 | 0.99176 | -0.15862 | 2.3507
73 | -0.010741 | -0.0026919 | 0.010744 | 0.0026932 | 2.4724e-06 | 1.2545e-06 | 0.016114 | 0.016114 | 0.016114 | 0.99188 | -0.15616 | 0.99213 | -0.15132 | 4.4268
74 | 0.030036 | 0.0075335 | -0.030022 | -0.0075244 | 1.4526e-05 | 9.0493e-06 | 0.045016 | 0.045016 | 0.045016 | 0.9929 | -0.13646 | 0.99238 | -0.14661 | 12.367
75 | 0.0087632 | 0.0021954 | -0.0087621 | -0.0021949 | 1.1061e-06 | 4.872e-07 | 0.01314 | 0.01314 | 0.01314 | 0.99238 | -0.14661 | 0.99224 | -0.14926 | 3.6098
76 | 0.021258 | 0.005329 | -0.021256 | -0.0053278 | 1.9882e-06 | 1.2051e-06 | 0.031876 | 0.031876 | 0.031876 | 0.99238 | -0.14661 | 0.99227 | -0.14857 | 8.7572
77 | 0.008066 | 0.0020204 | -0.0080648 | -0.0020199 | 1.1921e-06 | 4.8234e-07 | 0.012096 | 0.012096 | 0.012096 | 0.99224 | -0.14926 | 0.99208 | -0.15236 | 3.323
78 | 0.016124 | 0.0040417 | -0.016122 | -0.0040405 | 2.1156e-06 | 1.2294e-06 | 0.02418 | 0.02418 | 0.02418 | 0.99227 | -0.14857 | 0.99213 | -0.15132 | 6.643
79 | 0.005132 | 0.0012861 | -0.0051316 | -0.0012861 | 3.924e-07 | 2.2935e-08 | 0.0076959 | 0.0076959 | 0.0076959 | 0.99227 | -0.14857 | 0.99219 | -0.15018 | 2.1143
80 | -0.0027385 | -0.00068634 | 0.0027386 | 0.00068623 | 8.2614e-08 | -1.1568e-07 | 0.0041079 | 0.0041078 | 0.0041079 | 0.99199 | -0.15407 | 0.99202 | -0.15344 | 1.1285
81 | -0.0050381 | -0.001262 | 0.0050383 | 0.001262 | 2.5766e-07 | 9.5486e-09 | 0.0075568 | 0.0075567 | 0.0075568 | 0.99202 | -0.15344 | 0.99208 | -0.15236 | 2.076
82 | 0.0022995 | 0.00057579 | -0.0022993 | -0.00057625 | 2.047e-07 | -4.6135e-07 | 0.003449 | 0.0034492 | 0.0034492 | 0.99202 | -0.15344 | 0.99193 | -0.1553 | 0.94758
83 | 0.0030264 | 0.00075792 | -0.0030263 | -0.00075806 | 1.3492e-07 | -1.3911e-07 | 0.0045391 | 0.0045392 | 0.0045392 | 0.99208 | -0.15236 | 0.99203 | -0.1533 | 1.247
84 | 0.0015897 | 0.00039802 | -0.0015897 | -0.00039814 | 2.0953e-08 | -1.1347e-07 | 0.0023844 | 0.0023845 | 0.0023845 | 0.99203 | -0.1533 | 0.99202 | -0.15357 | 0.65507
85 | 0.0013046 | 0.00032669 | -0.0013046 | -0.00032696 | 3.2746e-08 | -2.7344e-07 | 0.0019568 | 0.0019569 | 0.0019569 | 0.99202 | -0.15357 | 0.99199 | -0.1541 | 0.53762
86 | 0.0053787 | 0.0013473 | -0.0053784 | -0.0013473 | 3.867e-07 | 4.287e-08 | 0.0080669 | 0.0080669 | 0.0080669 | 0.99213 | -0.15132 | 0.99205 | -0.15283 | 2.2162
87 | 0.0012902 | 0.00032269 | -0.0012902 | -0.00032303 | 4.0009e-08 | -3.4226e-07 | 0.001935 | 0.0019352 | 0.0019352 | 0.99205 | -0.15283 | 0.99202 | -0.15349 | 0.53164
88 | 0.0033024 | 0.00082761 | -0.0033023 | -0.00082764 | 4.1307e-08 | -2.9674e-08 | 0.0049938 | 0.0049938 | 0.0049938 | 0.98402 | -0.3089 | 0.98401 | -0.30916 | 1.3719
89 | -0.0016806 | -0.00042102 | 0.0016807 | 0.00042048 | 1.1473e-07 | -5.4138e-07 | 0.0025278 | 0.0025276 | 0.0025278 | 0.98925 | -0.20713 | 0.98933 | -0.2057 | 0.69445
90 | 0.00051461 | 0.00012881 | -0.00051461 | -0.00012897 | 2.9277e-09 | -1.6542e-07 | 0.00077401 | 0.00077407 | 0.00077407 | 0.98925 | -0.20713 | 0.98925 | -0.20725 | 0.21266
91 | -0.0041042 | -0.0010286 | 0.0041045 | 0.0010285 | 3.3599e-07 | -8.8506e-08 | 0.0061649 | 0.0061648 | 0.0061649 | 0.99062 | -0.18062 | 0.99071 | -0.1789 | 1.6937
92 | -0.0041045 | -0.0010285 | 0.0041082 | 0.0010275 | 3.7269e-06 | -9.8608e-07 | 0.0061648 | 0.0061636 | 0.0061648 | 0.99071 | -0.1789 | 0.99169 | -0.15984 | 1.6936
93 | -0.0041082 | -0.0010275 | 0.0041091 | 0.0010273 | 8.9849e-07 | -2.3892e-07 | 0.0061636 | 0.0061633 | 0.0061636 | 0.99169 | -0.15984 | 0.99193 | -0.15524 | 1.6933
94 | -0.0047454 | -0.0011868 | 0.0047455 | 0.0011868 | 3.4999e-08 | -1.38e-09 | 0.0071179 | 0.0071179 | 0.0071179 | 0.99193 | -0.15524 | 0.99194 | -0.15508 | 1.9555
95 | -0.011534 | -0.0028982 | 0.011538 | 0.0029007 | 4.7566e-06 | 2.498e-06 | 0.017311 | 0.017311 | 0.017311 | 0.99157 | -0.16207 | 0.99202 | -0.15343 | 4.7557
96 | -0.0027708 | -0.00069409 | 0.0027709 | 0.00069395 | 1.0239e-07 | -1.3852e-07 | 0.0041563 | 0.0041562 | 0.0041563 | 0.99195 | -0.15483 | 0.99199 | -0.15406 | 1.1418
97 | 0.0013263 | 0.00033206 | -0.0013262 | -0.00033238 | 3.9892e-08 | -3.2141e-07 | 0.0019894 | 0.0019895 | 0.0019895 | 0.99195 | -0.15483 | 0.99192 | -0.15546 | 0.54657
98 | -0.0027709 | -0.00069395 | 0.0027712 | 0.00069359 | 2.7058e-07 | -3.6616e-07 | 0.0041562 | 0.0041561 | 0.0041562 | 0.99199 | -0.15406 | 0.99209 | -0.15201 | 1.1418
99 | 0.0064106 | 0.001604 | -0.0064104 | -0.0016039 | 2.242e-07 | 5.9968e-08 | 0.0096141 | 0.0096141 | 0.0096141 | 0.99209 | -0.15201 | 0.99206 | -0.15274 | 2.6412
100 | -0.021569 | -0.0054112 | 0.021578 | 0.0054167 | 9.0329e-06 | 5.4838e-06 | 0.032353 | 0.032352 | 0.032353 | 0.99209 | -0.15201 | 0.99255 | -0.14323 | 8.8881
101 | 0.012387 | 0.0031136 | -0.012386 | -0.0031132 | 8.4358e-07 | 4.5577e-07 | 0.018582 | 0.018582 | 0.018582 | 0.99209 | -0.15201 | 0.99202 | -0.15343 | 5.105
102 | 0.0054281 | 0.0013577 | -0.0054277 | -0.0013577 | 4.0583e-07 | 4.8904e-08 | 0.0081408 | 0.0081408 | 0.0081408 | 0.99206 | -0.15274 | 0.99198 | -0.15431 | 2.2365
103 | -0.022199 | -0.0055724 | 0.022204 | 0.0055752 | 4.7204e-06 | 2.8742e-06 | 0.033284 | 0.033283 | 0.033284 | 0.99255 | -0.14323 | 0.99278 | -0.13877 | 9.1438
104 | 0.0010098 | 0.00025275 | -0.0010097 | -0.00025306 | 2.2033e-08 | -3.1659e-07 | 0.0015145 | 0.0015146 | 0.0015146 | 0.99202 | -0.15349 | 0.992 | -0.15394 | 0.4161
105 | -0.025934 | -0.0065145 | 0.025947 | 0.0065226 | 1.3212e-05 | 8.1532e-06 | 0.038854 | 0.038854 | 0.038854 | 0.99334 | -0.12791 | 0.99389 | -0.11725 | 10.6742
106 | 0.025934 | 0.0065145 | -0.025929 | -0.0065116 | 4.6055e-06 | 2.8422e-06 | 0.038854 | 0.038854 | 0.038854 | 0.99334 | -0.12791 | 0.99315 | -0.13164 | 10.6742
107 | -0.027131 | -0.0068194 | 0.027137 | 0.006823 | 5.7582e-06 | 3.5647e-06 | 0.040627 | 0.040627 | 0.040627 | 0.99389 | -0.11725 | 0.99412 | -0.1128 | 11.1612
108 | 0.025104 | 0.0063048 | -0.025096 | -0.0062996 | 8.5396e-06 | 5.2572e-06 | 0.037618 | 0.037618 | 0.037618 | 0.99315 | -0.13164 | 0.99278 | -0.13877 | 10.3346
109 | -0.0028918 | -0.00072442 | 0.0028919 | 0.00072431 | 8.9055e-08 | -1.0645e-07 | 0.0043344 | 0.0043343 | 0.0043344 | 0.99275 | -0.13941 | 0.99278 | -0.13877 | 1.1908
110 | 0.027645 | 0.0069515 | -0.027642 | -0.0069495 | 3.1305e-06 | 1.9403e-06 | 0.041383 | 0.041383 | 0.041383 | 0.99425 | -0.11043 | 0.99412 | -0.1128 | 11.3689
111 | 0.0051489 | 0.0012878 | -0.0051487 | -0.0012878 | 1.8884e-07 | 1.186e-08 | 0.0077227 | 0.0077227 | 0.0077227 | 0.99198 | -0.15431 | 0.99194 | -0.15508 | 2.1216

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.15527 | 0.038926

## res_load
| p_mw | q_mvar
0 | 0.0001793 | 4.4936e-05
1 | 0.00050743 | 0.00012717
2 | 0.00055315 | 0.00013863
3 | 0.00025582 | 6.4114e-05
4 | 0.00087667 | 0.00021971
5 | 0.00031798 | 7.9694e-05
6 | 0.00023113 | 5.7928e-05
7 | 0.0040196 | 0.0010074
8 | 0.0032308 | 0.00080972
9 | 0.0019746 | 0.00049489
10 | 0.0021159 | 0.00053029
11 | 0.002561 | 0.00064185
12 | 0.013955 | 0.0034975
13 | 0.0017745 | 0.00044474
14 | 0.00067205 | 0.00016843
15 | 0.0012548 | 0.00031448
16 | 0.002475 | 0.0006203
17 | 0.003139 | 0.0007867
18 | 0.0030088 | 0.00075408
19 | 0.0010919 | 0.00027365
20 | 0.00055357 | 0.00013874
21 | 0.0020883 | 0.00052338
22 | 0.0016925 | 0.00042419
23 | 0.0018663 | 0.00046773
24 | 0.0023288 | 0.00058364
25 | 0.001783 | 0.00044685
26 | 0.00067461 | 0.00016907
27 | 0.0010382 | 0.0002602
28 | 0.0025527 | 0.00063976
29 | 0.0011873 | 0.00029757
30 | 0.0011872 | 0.00029754
31 | 0.0012322 | 0.00030881
32 | 0.00095787 | 0.00024006
33 | 0.0067362 | 0.0016882
34 | 0.0041891 | 0.0010499
35 | 0.0014785 | 0.00037055
36 | 0.0032755 | 0.00082091
37 | 0.0032991 | 0.00082682
38 | 0.0006559 | 0.00016438
39 | 0.001212 | 0.00030375
40 | 0.0050375 | 0.0012625
41 | 0.00059607 | 0.00014939
42 | 0.0074715 | 0.0018725
43 | 0.0036095 | 0.00090463
44 | 0.00069612 | 0.00017446
45 | 0.0027385 | 0.00068634
46 | 0.0022993 | 0.00057625
47 | 0.0014366 | 0.00036004
48 | 0.00028509 | 7.145e-05
49 | 0.0013046 | 0.00032696
50 | 0.0051316 | 0.0012861
51 | 0.0040881 | 0.0010246
52 | 0.0042771 | 0.0010719
53 | 0.00017888 | 4.4831e-05
54 | 0.0033023 | 0.00082764
55 | 0.0011659 | 0.00029221
56 | 0.00075355 | 0.00018886
57 | 0.00051461 | 0.00012897
58 | 0.0041042 | 0.0010286
59 | 0.00063632 | 0.00015948
60 | 0.00023595 | 5.9135e-05
61 | 0.0014445 | 0.00036203
62 | 0.0013262 | 0.00033238
63 | 0.00098229 | 0.00024619
64 | 0.00062109 | 0.00015566
65 | 0.00084778 | 0.00021247
66 | 0.0057029 | 0.0014293
67 | 0.00028044 | 7.0285e-05
68 | 0.0010097 | 0.00025306
69 | 0.00098932 | 0.00024795
70 | 0.00024065 | 6.0313e-05
71 | 0.0010879 | 0.00027264
72 | 0.0011842 | 0.00029678
73 | 0.00082515 | 0.0002068
74 | 0.00060926 | 0.00015269
75 | 0.00027875 | 6.9861e-05
76 | 0.00040323 | 0.00010106
77 | 0.00050508 | 0.00012659

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1