## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_173-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_173-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_173-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_173-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_173-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_173-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_173-3_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_173-3_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_173-3_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_173-3_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_173-3_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_173-3_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_173-3_0_4_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_173-3_0_4_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_173-3_0_4_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_173-3_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_173-3_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_173-3_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_173-3_0_4_node_95 | 0.4 | n |  | TRUE
19 | bus_LV_173-3_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_173-3_0_4_node_96 | 0.4 | n |  | TRUE
21 | bus_LV_173-3_0_4_node_93 | 0.4 | n |  | TRUE
22 | bus_LV_173-3_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_173-3_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_173-3_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_173-3_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_173-3_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_173-3_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_173-3_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_173-3_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_173-3_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_173-3_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_173-3_0_4_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_173-3_0_4_node_109 | 0.4 | n |  | TRUE
34 | bus_LV_173-3_0_4_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_173-3_0_4_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_173-3_0_4_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_173-3_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_173-3_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_173-3_0_4_node_111 | 0.4 | n |  | TRUE
40 | bus_LV_173-3_0_4_node_137 | 0.4 | n |  | TRUE
41 | bus_LV_173-3_0_4_node_91 | 0.4 | n |  | TRUE
42 | bus_LV_173-3_0_4_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_173-3_0_4_node_138 | 0.4 | n |  | TRUE
44 | bus_LV_173-3_0_4_node_129 | 0.4 | n |  | TRUE
45 | bus_LV_173-3_0_4_node_94 | 0.4 | n |  | TRUE
46 | bus_LV_173-3_0_4_node_117 | 0.4 | n |  | TRUE
47 | bus_LV_173-3_0_4_node_127 | 0.4 | n |  | TRUE
48 | bus_LV_173-3_0_4_node_92 | 0.4 | n |  | TRUE
49 | bus_LV_173-3_0_4_node_118 | 0.4 | n |  | TRUE
50 | bus_LV_173-3_0_4_node_128 | 0.4 | n |  | TRUE
51 | bus_LV_173-3_0_4_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_173-3_0_4_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_173-3_0_4_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_173-3_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_173-3_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_173-3_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_173-3_0_4_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_173-3_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_173-3_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_173-3_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_173-3_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_173-3_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_173-3_0_4_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_173-3_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_173-3_0_4_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_173-3_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_173-3_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_173-3_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_173-3_0_4_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_173-3_0_4_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_173-3_0_4_node_124 | 0.4 | n |  | TRUE
72 | bus_LV_173-3_0_4_node_131 | 0.4 | n |  | TRUE
73 | bus_LV_173-3_0_4_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_173-3_0_4_node_106 | 0.4 | n |  | TRUE
75 | bus_LV_173-3_0_4_node_122 | 0.4 | n |  | TRUE
76 | bus_LV_173-3_0_4_node_132 | 0.4 | n |  | TRUE
77 | bus_LV_173-3_0_4_node_130 | 0.4 | n |  | TRUE
78 | bus_LV_173-3_0_4_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_173-3_0_4_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_173-3_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_173-3_0_4_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_173-3_0_4_node_107 | 0.4 | n |  | TRUE
83 | bus_LV_173-3_0_4_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_173-3_0_4_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_173-3_0_4_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_173-3_0_4_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_173-3_0_4_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_173-3_0_4_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_173-3_0_4_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_173-3_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_173-3_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_173-3_0_4_node_114 | 0.4 | n |  | TRUE
93 | bus_LV_173-3_0_4_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_173-3_0_4_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_173-3_0_4_node_113 | 0.4 | n |  | TRUE
96 | bus_LV_173-3_0_4_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_173-3_0_4_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_173-3_0_4_node_72 | 0.4 | n |  | TRUE
99 | bus_LV_173-3_0_4_node_76 | 0.4 | n |  | TRUE
100 | bus_LV_173-3_0_4_node_77 | 0.4 | n |  | TRUE
101 | bus_LV_173-3_0_4_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_173-3_0_4_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_173-3_0_4_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_173-3_0_4_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_173-3_0_4_node_139 | 0.4 | n |  | TRUE
106 | bus_LV_173-3_0_4_node_112 | 0.4 | n |  | TRUE
107 | bus_LV_173-3_0_4_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_173-3_0_4_node_83 | 0.4 | n |  | TRUE
109 | bus_LV_173-3_0_4_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_173-3_0_4_node_85 | 0.4 | n |  | TRUE
111 | bus_LV_173-3_0_4_node_86 | 0.4 | n |  | TRUE
112 | bus_LV_173-3_0_4_node_87 | 0.4 | n |  | TRUE
113 | bus_LV_173-3_0_4_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_173-3_0_4_node_120 | 0.4 | n |  | TRUE
115 | bus_LV_173-3_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_173-3_0_4_node_126 | 0.4 | n |  | TRUE
117 | bus_LV_173-3_0_4_node_90 | 0.4 | n |  | TRUE
118 | bus_LV_173-3_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_173-3_0_4_node_135 | 0.4 | n |  | TRUE
120 | bus_LV_173-3_0_4_node_97 | 0.4 | n |  | TRUE
121 | bus_LV_173-3_0_4_node_98 | 0.4 | n |  | TRUE
122 | bus_LV_173-3_0_4_node_99 | 0.4 | n |  | TRUE
123 | bus_LV_173-3_0_4_node_100 | 0.4 | n |  | TRUE
124 | bus_LV_173-3_0_4_node_101 | 0.4 | n |  | TRUE
125 | bus_LV_173-3_0_4_node_102 | 0.4 | n |  | TRUE
126 | bus_LV_173-3_0_4_node_143 | 0.4 | n |  | TRUE
127 | bus_LV_173-3_0_4_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_173-3_0_4_node_141 | 0.4 | n |  | TRUE
129 | bus_LV_173-3_0_4_node_123 | 0.4 | n |  | TRUE
130 | bus_LV_173-3_0_4_node_103 | 0.4 | n |  | TRUE
131 | bus_LV_173-3_0_4_node_108 | 0.4 | n |  | TRUE
132 | bus_LV_173-3_0_4_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_173-3_0_4_node_121 | 0.4 | n |  | TRUE
134 | bus_LV_173-3_0_4_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_173-3_0_4_node_134 | 0.4 | n |  | TRUE
136 | bus_LV_173-3_0_4_node_140 | 0.4 | n |  | TRUE
137 | bus_LV_173-3_0_4_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_173-3_0_4_node_142 | 0.4 | n |  | TRUE
139 | bus_LV_173-3_0_4_node_144 | 0.4 | n |  | TRUE
140 | bus_LV_173-3_0_4_node_145 | 0.4 | n |  | TRUE
141 | bus_MV_7_1_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_173-3_0_4_load_0 | 0 | 0.0096564 | 0.0024201 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_173-3_0_4_load_1 | 1 | 0.0056803 | 0.0014236 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_173-3_0_4_load_4 | 4 | 0.0096594 | 0.0024209 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_173-3_0_4_load_8 | 7 | 0.0066781 | 0.0016737 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_173-3_0_4_load_9 | 8 | 0.0052342 | 0.0013118 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_173-3_0_4_load_30 | 10 | 0.0036118 | 0.00090519 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_173-3_0_4_load_35 | 12 | 0.0043436 | 0.0010886 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_173-3_0_4_load_32 | 13 | 0.0026108 | 0.00065432 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_173-3_0_4_load_37 | 14 | 0.0031115 | 0.00077982 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_173-3_0_4_load_95 | 18 | 0.0072209 | 0.0018097 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_173-3_0_4_load_93 | 21 | 0.0015305 | 0.00038358 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_173-3_0_4_load_13 | 23 | 0.010813 | 0.0027099 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_173-3_0_4_load_10 | 24 | 0.0046072 | 0.0011547 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_173-3_0_4_load_28 | 27 | 0.0016713 | 0.00041886 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_173-3_0_4_load_33 | 28 | 0.0061882 | 0.0015509 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_173-3_0_4_load_22 | 29 | 0.0092541 | 0.0023193 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_173-3_0_4_load_23 | 30 | 0.0086853 | 0.0021767 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_173-3_0_4_load_24 | 31 | 0.0049001 | 0.0012281 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_173-3_0_4_load_52 | 34 | 0.0041678 | 0.0010446 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_173-3_0_4_load_53 | 35 | 0.0083718 | 0.0020982 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_173-3_0_4_load_51 | 36 | 0.0040145 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_173-3_0_4_load_26 | 37 | 0.0019575 | 0.00049058 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_173-3_0_4_load_25 | 38 | 0.0060072 | 0.0015056 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_173-3_0_4_load_137 | 40 | 0.0017638 | 0.00044205 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_173-3_0_4_load_91 | 41 | 0.0066847 | 0.0016753 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_173-3_0_4_load_138 | 43 | 0.0046963 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_173-3_0_4_load_129 | 44 | 0.0064301 | 0.0016115 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_173-3_0_4_load_94 | 45 | 0.0031091 | 0.0007792 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_173-3_0_4_load_117 | 46 | 0.0042886 | 0.0010748 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_173-3_0_4_load_127 | 47 | 0.0047068 | 0.0011796 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_173-3_0_4_load_92 | 48 | 0.0032957 | 0.00082599 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_173-3_0_4_load_118 | 49 | 0.0048483 | 0.0012151 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_173-3_0_4_load_128 | 50 | 0.0045111 | 0.0011306 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_173-3_0_4_load_29 | 52 | 0.0048672 | 0.0012198 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_173-3_0_4_load_31 | 53 | 0.0023181 | 0.00058096 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_173-3_0_4_load_34 | 54 | 0.0044249 | 0.001109 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_173-3_0_4_load_36 | 55 | 0.006924 | 0.0017353 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_173-3_0_4_load_59 | 56 | 0.002061 | 0.00051654 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_173-3_0_4_load_60 | 57 | 0.0098563 | 0.0024702 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_173-3_0_4_load_38 | 58 | 0.010447 | 0.0026183 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_173-3_0_4_load_43 | 62 | 0.0052326 | 0.0013114 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_173-3_0_4_load_44 | 63 | 0.00038189 | 9.5709e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_173-3_0_4_load_41 | 64 | 0.0031759 | 0.00079596 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_173-3_0_4_load_47 | 67 | 0.0014338 | 0.00035934 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_173-3_0_4_load_49 | 69 | 0.005015 | 0.0012569 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_173-3_0_4_load_124 | 71 | 0.0019368 | 0.00048541 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_173-3_0_4_load_56 | 73 | 0.0008976 | 0.00022496 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_173-3_0_4_load_122 | 75 | 0.0023712 | 0.00059429 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_173-3_0_4_load_130 | 77 | 0.0014104 | 0.00035348 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_173-3_0_4_load_55 | 78 | 0.00093277 | 0.00023377 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_173-3_0_4_load_58 | 80 | 0.0035292 | 0.00088449 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_173-3_0_4_load_104 | 81 | 0.0018192 | 0.00045593 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_173-3_0_4_load_107 | 82 | 0.00058745 | 0.00014723 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_173-3_0_4_load_61 | 83 | 0.0019111 | 0.00047896 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_173-3_0_4_load_62 | 84 | 0.0017468 | 0.00043779 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_173-3_0_4_load_63 | 85 | 0.002211 | 0.00055413 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_173-3_0_4_load_64 | 86 | 0.0045957 | 0.0011518 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_173-3_0_4_load_65 | 87 | 0.00062735 | 0.00015723 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_173-3_0_4_load_66 | 88 | 0.0034479 | 0.00086412 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_173-3_0_4_load_67 | 89 | 0.00070164 | 0.00017585 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_173-3_0_4_load_68 | 90 | 0.0028712 | 0.0007196 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_173-3_0_4_load_69 | 91 | 0.00083994 | 0.00021051 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_173-3_0_4_load_74 | 93 | 0.00096046 | 0.00024071 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_173-3_0_4_load_116 | 94 | 0.0021737 | 0.00054478 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_173-3_0_4_load_73 | 96 | 0.00077801 | 0.00019499 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_173-3_0_4_load_70 | 97 | 0.0023252 | 0.00058275 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_173-3_0_4_load_72 | 98 | 0.00072807 | 0.00018247 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_173-3_0_4_load_76 | 99 | 0.0066593 | 0.001669 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_173-3_0_4_load_77 | 100 | 0.0027359 | 0.00068569 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_173-3_0_4_load_78 | 101 | 0.017218 | 0.0043154 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_173-3_0_4_load_80 | 103 | 0.0041847 | 0.0010488 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_173-3_0_4_load_81 | 104 | 0.0033687 | 0.00084428 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_173-3_0_4_load_139 | 105 | 0.011232 | 0.0028151 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_173-3_0_4_load_112 | 106 | 0.002067 | 0.00051805 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_173-3_0_4_load_82 | 107 | 0.01984 | 0.0049724 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_173-3_0_4_load_83 | 108 | 0.0021933 | 0.00054969 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_173-3_0_4_load_85 | 110 | 0.0023252 | 0.00058276 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_173-3_0_4_load_88 | 113 | 0.0045753 | 0.0011467 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_173-3_0_4_load_120 | 114 | 0.006491 | 0.0016268 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_173-3_0_4_load_115 | 115 | 0.0032639 | 0.00081801 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_173-3_0_4_load_126 | 116 | 0.0014824 | 0.00037154 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_173-3_0_4_load_90 | 117 | 0.002657 | 0.0006659 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_173-3_0_4_load_110 | 118 | 0.0018923 | 0.00047424 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_173-3_0_4_load_135 | 119 | 0.0013305 | 0.00033345 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_173-3_0_4_load_97 | 120 | 0.0022168 | 0.00055558 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_173-3_0_4_load_98 | 121 | 0.002213 | 0.00055464 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_173-3_0_4_load_101 | 124 | 0.0051377 | 0.0012876 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_173-3_0_4_load_102 | 125 | 0.0084456 | 0.0021167 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_173-3_0_4_load_143 | 126 | 0.0076049 | 0.001906 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_173-3_0_4_load_125 | 127 | 0.014838 | 0.0037187 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_173-3_0_4_load_141 | 128 | 0.005531 | 0.0013862 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_173-3_0_4_load_123 | 129 | 0.015833 | 0.003968 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_173-3_0_4_load_103 | 130 | 0.0016768 | 0.00042024 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_173-3_0_4_load_108 | 131 | 0.0010693 | 0.000268 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_173-3_0_4_load_119 | 132 | 0.00096944 | 0.00024297 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_173-3_0_4_load_121 | 133 | 0.0015353 | 0.00038479 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_173-3_0_4_load_133 | 134 | 0.00058082 | 0.00014557 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_173-3_0_4_load_134 | 135 | 0.00031134 | 7.8028e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_173-3_0_4_load_140 | 136 | 0.00025558 | 6.4054e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_173-3_0_4_load_136 | 137 | 0.001127 | 0.00028245 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_173-3_0_4_load_142 | 138 | 0.006271 | 0.0015717 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_173-3_0_4_load_144 | 139 | 0.012916 | 0.0032372 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_173-3_0_4_load_145 | 140 | 0.012718 | 0.0031873 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 131 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_173-3_0_4_line_0 |  | 0 | 1 | 0.014576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_173-3_0_4_line_1 |  | 0 | 2 | 0.023064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_173-3_0_4_line_2 |  | 1 | 3 | 0.021195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_173-3_0_4_line_3 |  | 2 | 4 | 0.02298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_173-3_0_4_line_4 |  | 2 | 5 | 0.011396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_173-3_0_4_line_5 |  | 3 | 6 | 0.00755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_173-3_0_4_line_6 |  | 4 | 7 | 0.034577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_173-3_0_4_line_7 |  | 5 | 8 | 0.018582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_173-3_0_4_line_8 |  | 6 | 9 | 0.036164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_173-3_0_4_line_9 |  | 6 | 10 | 0.014733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_173-3_0_4_line_10 |  | 7 | 14 | 0.012408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_173-3_0_4_line_11 |  | 9 | 15 | 0.015509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_173-3_0_4_line_12 |  | 10 | 27 | 0.026124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_173-3_0_4_line_13 |  | 11 | 12 | 0.047465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_173-3_0_4_line_14 |  | 11 | 13 | 0.024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_173-3_0_4_line_15 |  | 13 | 28 | 0.026071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_173-3_0_4_line_16 |  | 15 | 18 | 0.011204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_173-3_0_4_line_17 |  | 16 | 17 | 0.011154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_173-3_0_4_line_18 |  | 16 | 18 | 0.033633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_173-3_0_4_line_19 |  | 17 | 29 | 0.024491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_173-3_0_4_line_20 |  | 17 | 25 | 0.021902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_173-3_0_4_line_21 |  | 19 | 20 | 0.01073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_173-3_0_4_line_22 |  | 19 | 21 | 0.030175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_173-3_0_4_line_23 |  | 20 | 39 | 0.058869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_173-3_0_4_line_24 |  | 20 | 40 | 0.040266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_173-3_0_4_line_25 |  | 21 | 41 | 0.010088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_173-3_0_4_line_26 |  | 22 | 23 | 0.030188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_173-3_0_4_line_27 |  | 22 | 24 | 0.01503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_173-3_0_4_line_28 |  | 24 | 25 | 0.0090865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_173-3_0_4_line_29 |  | 25 | 26 | 0.063527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_173-3_0_4_line_30 |  | 26 | 30 | 0.037311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_173-3_0_4_line_31 |  | 26 | 31 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_173-3_0_4_line_32 |  | 27 | 51 | 0.014339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_173-3_0_4_line_33 |  | 28 | 54 | 0.012846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_173-3_0_4_line_34 |  | 29 | 45 | 0.03889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_173-3_0_4_line_35 |  | 30 | 46 | 0.016382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_173-3_0_4_line_36 |  | 31 | 47 | 0.0033559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_173-3_0_4_line_37 |  | 32 | 33 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_173-3_0_4_line_38 |  | 32 | 34 | 0.0312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_173-3_0_4_line_39 |  | 33 | 39 | 0.025308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_173-3_0_4_line_40 |  | 33 | 82 | 0.0082623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_173-3_0_4_line_41 |  | 34 | 70 | 0.016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_173-3_0_4_line_42 |  | 35 | 36 | 0.056036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_173-3_0_4_line_43 |  | 36 | 65 | 0.019454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_173-3_0_4_line_44 |  | 37 | 38 | 0.0031794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_173-3_0_4_line_45 |  | 38 | 51 | 0.015285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_173-3_0_4_line_46 |  | 39 | 118 | 0.012162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_173-3_0_4_line_47 |  | 40 | 119 | 0.018615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_173-3_0_4_line_48 |  | 41 | 117 | 0.015618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_173-3_0_4_line_49 |  | 42 | 43 | 0.048435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_173-3_0_4_line_50 |  | 42 | 44 | 0.030365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_173-3_0_4_line_51 |  | 44 | 50 | 0.0093914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_173-3_0_4_line_52 |  | 45 | 48 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_173-3_0_4_line_53 |  | 46 | 49 | 0.036228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_173-3_0_4_line_54 |  | 47 | 50 | 0.018137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_173-3_0_4_line_55 |  | 48 | 117 | 0.013639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_173-3_0_4_line_56 |  | 49 | 132 | 0.0077493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_173-3_0_4_line_57 |  | 51 | 52 | 0.00082577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_173-3_0_4_line_58 |  | 52 | 53 | 0.024459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_173-3_0_4_line_59 |  | 54 | 55 | 0.022443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_173-3_0_4_line_60 |  | 55 | 56 | 0.00163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_173-3_0_4_line_61 |  | 56 | 57 | 0.035307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_173-3_0_4_line_62 |  | 57 | 84 | 0.0018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_173-3_0_4_line_63 |  | 58 | 59 | 0.040385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_173-3_0_4_line_64 |  | 58 | 60 | 0.066469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_173-3_0_4_line_65 |  | 59 | 61 | 0.008236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_173-3_0_4_line_66 |  | 60 | 62 | 0.033966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_173-3_0_4_line_67 |  | 60 | 63 | 0.023126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_173-3_0_4_line_68 |  | 61 | 66 | 0.005149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_173-3_0_4_line_69 |  | 61 | 67 | 0.041957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_173-3_0_4_line_70 |  | 62 | 68 | 0.030226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_173-3_0_4_line_71 |  | 63 | 69 | 0.010083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_173-3_0_4_line_72 |  | 64 | 65 | 0.001651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_173-3_0_4_line_73 |  | 65 | 70 | 0.009767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_173-3_0_4_line_74 |  | 66 | 70 | 0.030908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_173-3_0_4_line_75 |  | 66 | 71 | 0.013675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_173-3_0_4_line_76 |  | 67 | 72 | 0.10347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_173-3_0_4_line_77 |  | 68 | 73 | 0.019965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_173-3_0_4_line_78 |  | 69 | 74 | 0.0075064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_173-3_0_4_line_79 |  | 71 | 75 | 0.0047444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_173-3_0_4_line_80 |  | 72 | 76 | 0.028794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_173-3_0_4_line_81 |  | 72 | 77 | 0.094347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_173-3_0_4_line_82 |  | 73 | 80 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_173-3_0_4_line_83 |  | 74 | 81 | 0.040432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_173-3_0_4_line_84 |  | 75 | 133 | 0.0086436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_173-3_0_4_line_85 |  | 76 | 134 | 0.019702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_173-3_0_4_line_86 |  | 76 | 135 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_173-3_0_4_line_87 |  | 77 | 97 | 0.25331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_173-3_0_4_line_88 |  | 78 | 79 | 0.01641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_173-3_0_4_line_89 |  | 79 | 80 | 0.0099567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_173-3_0_4_line_90 |  | 79 | 83 | 0.025993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_173-3_0_4_line_91 |  | 81 | 130 | 0.02656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_173-3_0_4_line_92 |  | 82 | 131 | 0.013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_173-3_0_4_line_93 |  | 83 | 84 | 0.00049395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_173-3_0_4_line_94 |  | 85 | 86 | 0.015068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_173-3_0_4_line_95 |  | 85 | 87 | 0.028979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_173-3_0_4_line_96 |  | 86 | 88 | 0.018601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_173-3_0_4_line_97 |  | 87 | 89 | 0.0037926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_173-3_0_4_line_98 |  | 88 | 90 | 0.0040115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_173-3_0_4_line_99 |  | 89 | 91 | 0.022983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_173-3_0_4_line_100 |  | 90 | 92 | 0.032612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_173-3_0_4_line_101 |  | 91 | 93 | 0.0072048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_173-3_0_4_line_102 |  | 92 | 94 | 0.013785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_173-3_0_4_line_103 |  | 92 | 95 | 0.015352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_173-3_0_4_line_104 |  | 93 | 96 | 0.0058592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_173-3_0_4_line_105 |  | 94 | 132 | 0.00065327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_173-3_0_4_line_106 |  | 95 | 106 | 0.017276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_173-3_0_4_line_107 |  | 95 | 115 | 0.029063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_173-3_0_4_line_108 |  | 97 | 98 | 0.0021826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_173-3_0_4_line_109 |  | 99 | 100 | 0.010507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_173-3_0_4_line_110 |  | 99 | 101 | 0.021682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_173-3_0_4_line_111 |  | 100 | 102 | 0.0095181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_173-3_0_4_line_112 |  | 102 | 103 | 0.037071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_173-3_0_4_line_113 |  | 102 | 104 | 0.034024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_173-3_0_4_line_114 |  | 103 | 105 | 0.017177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_173-3_0_4_line_115 |  | 104 | 106 | 0.0054736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_173-3_0_4_line_116 |  | 107 | 108 | 0.027778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_173-3_0_4_line_117 |  | 107 | 109 | 0.088962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_173-3_0_4_line_118 |  | 108 | 110 | 0.07755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_173-3_0_4_line_119 |  | 109 | 111 | 0.11154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_173-3_0_4_line_120 |  | 110 | 112 | 0.0089347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_173-3_0_4_line_121 |  | 111 | 113 | 0.03116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_173-3_0_4_line_122 |  | 112 | 114 | 0.028368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_173-3_0_4_line_123 |  | 112 | 115 | 0.0034949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_173-3_0_4_line_124 |  | 114 | 116 | 0.0094713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_173-3_0_4_line_125 |  | 119 | 137 | 0.0068652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_173-3_0_4_line_126 |  | 120 | 121 | 0.015299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_173-3_0_4_line_127 |  | 120 | 122 | 0.014976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_173-3_0_4_line_128 |  | 122 | 123 | 0.021068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_173-3_0_4_line_129 |  | 123 | 124 | 0.012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_173-3_0_4_line_130 |  | 123 | 125 | 0.010613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_173-3_0_4_line_131 |  | 124 | 126 | 0.02847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_173-3_0_4_line_132 |  | 125 | 127 | 0.039548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_173-3_0_4_line_133 |  | 126 | 128 | 0.00024435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_173-3_0_4_line_134 |  | 127 | 129 | 0.033217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_173-3_0_4_line_135 |  | 128 | 138 | 0.036021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_173-3_0_4_line_136 |  | 129 | 133 | 0.025344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_173-3_0_4_line_137 |  | 135 | 136 | 0.01589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_173-3_0_4_line_138 |  | 138 | 139 | 0.0035384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_173-3_0_4_line_139 |  | 139 | 140 | 0.015691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_173-3_0_4_trafo_108 | 0.63 MVA 20/0.4 kV | 141 | 131 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2704389.0013 | 1247244.1337 | 2704403.5729 | 1247244.4758
1 | 2704365.9434 | 1247243.5923 | 2704389.0013 | 1247244.1337
2 | 2704424.7625 | 1247244.9733 | 2704403.5729 | 1247244.4758
3 | 2704365.9434 | 1247243.5923 | 2704365.7104 | 1247220.6134
4 | 2704363.9402 | 1247254.8104 | 2704365.9434 | 1247243.5923
5 | 2704424.7625 | 1247244.9733 | 2704425.0376 | 1247252.5174
6 | 2704365.7104 | 1247220.6134 | 2704365.6177 | 1247211.4723 | 2704340.1836 | 1247211.1739
7 | 2704363.9402 | 1247254.8104 | 2704345.3618 | 1247254.4309
8 | 2704406.8796 | 1247275.4715 | 2704415.8459 | 1247270.8145 | 2704424.3128 | 1247270.063 | 2704425.0376 | 1247252.5174
9 | 2704425.0376 | 1247252.5174 | 2704439.7696 | 1247252.3319
10 | 2704327.7763 | 1247211.0283 | 2704340.1836 | 1247211.1739
11 | 2704406.8796 | 1247275.4715 | 2704407.4059 | 1247284.6213 | 2704407.7626 | 1247290.9548
12 | 2704439.7696 | 1247252.3319 | 2704465.8917 | 1247252.0029
13 | 2704411.2392 | 1247174.257 | 2704409.6316 | 1247160.8736 | 2704403.9366 | 1247132.929 | 2704403.7629 | 1247127.4652
14 | 2704411.2392 | 1247174.257 | 2704404.8627 | 1247169.9858 | 2704395.023 | 1247168.0332 | 2704387.9624 | 1247167.6737
15 | 2704361.9248 | 1247166.3477 | 2704387.9624 | 1247167.6737
16 | 2704407.7626 | 1247290.9548 | 2704414.8133 | 1247291.257 | 2704418.8853 | 1247292.0412
17 | 2704461.7565 | 1247304.6165 | 2704450.9918 | 1247301.5801
18 | 2704450.9918 | 1247301.5801 | 2704434.1329 | 1247294.9779 | 2704418.8853 | 1247292.0412
19 | 2704461.7565 | 1247304.6165 | 2704458.1241 | 1247314.3936 | 2704452.2674 | 1247327.1769
20 | 2704481.3797 | 1247313.8251 | 2704472.0251 | 1247307.5108 | 2704461.7565 | 1247304.6165
21 | 2704352.429 | 1247297.1636 | 2704361.9191 | 1247302.2235
22 | 2704361.9191 | 1247302.2235 | 2704354.95 | 1247317.8799 | 2704359.9466 | 1247327.1418 | 2704362.2056 | 1247328.2457
23 | 2704352.429 | 1247297.1636 | 2704342.1417 | 1247292.3231 | 2704318.5834 | 1247290.7741 | 2704303.7438 | 1247294.7718 | 2704296.5494 | 1247299.6269
24 | 2704352.429 | 1247297.1636 | 2704350.8662 | 1247303.1074 | 2704346.8047 | 1247309.8079 | 2704342.5082 | 1247313.1238 | 2704337.5122 | 1247315.8381 | 2704335.2858 | 1247316.9998 | 2704324.7455 | 1247324.0131
25 | 2704371.2693 | 1247332.6749 | 2704362.2056 | 1247328.2457
26 | 2704501.4696 | 1247313.2675 | 2704508.9113 | 1247320.5266 | 2704515.683 | 1247329.3641 | 2704519.0859 | 1247334.3169 | 2704520.478 | 1247336.5713
27 | 2704501.4696 | 1247313.2675 | 2704497.0079 | 1247318.2373 | 2704494.5564 | 1247317.5936 | 2704491.5496 | 1247318.0298 | 2704488.9127 | 1247318.9063
28 | 2704481.3797 | 1247313.8251 | 2704488.9127 | 1247318.9063
29 | 2704481.3797 | 1247313.8251 | 2704469.5339 | 1247338.2579 | 2704455.3868 | 1247354.8219 | 2704444.6054 | 1247364.7398
30 | 2704444.6054 | 1247364.7398 | 2704426.3353 | 1247377.7839 | 2704413.7698 | 1247385.7217
31 | 2704444.6054 | 1247364.7398 | 2704452.1936 | 1247373.9697 | 2704456.3879 | 1247377.9777
32 | 2704480.2292 | 1247251.8224 | 2704465.8917 | 1247252.0029
33 | 2704349.0958 | 1247165.6944 | 2704361.9248 | 1247166.3477
34 | 2704423.3344 | 1247351.1543 | 2704427.0052 | 1247350.4852 | 2704433.7995 | 1247347.7583 | 2704442.0252 | 1247340.5419 | 2704451.4379 | 1247328.9874 | 2704452.2674 | 1247327.1769
35 | 2704399.9755 | 1247394.5577 | 2704407.4121 | 1247389.738 | 2704413.7698 | 1247385.7217
36 | 2704458.8141 | 1247380.2962 | 2704456.3879 | 1247377.9777
37 | 2704257.443 | 1247280.0904 | 2704269.8061 | 1247295.331 | 2704271.3273 | 1247302.4745
38 | 2704257.443 | 1247280.0904 | 2704251.3429 | 1247279.8608 | 2704226.4015 | 1247277.0815
39 | 2704296.5494 | 1247299.6269 | 2704271.3273 | 1247302.4745
40 | 2704271.3273 | 1247302.4745 | 2704272.2982 | 1247310.6795
41 | 2704209.6323 | 1247275.2129 | 2704226.4015 | 1247277.0815
42 | 2704284.7885 | 1247276.0126 | 2704251.3787 | 1247274.3904 | 2704238.7243 | 1247272.6889 | 2704229.2091 | 1247270.2688
43 | 2704210.3551 | 1247265.4734 | 2704229.2091 | 1247270.2688
44 | 2704481.2036 | 1247270.2613 | 2704481.0358 | 1247267.0863
45 | 2704480.2292 | 1247251.8224 | 2704481.0358 | 1247267.0863
46 | 2704296.5494 | 1247299.6269 | 2704298.124 | 1247311.6864
47 | 2704309.1418 | 1247334.1446 | 2704310.8475 | 1247333.2606 | 2704324.7455 | 1247324.0131
48 | 2704385.3019 | 1247339.5322 | 2704371.2693 | 1247332.6749
49 | 2704474.2678 | 1247457.9584 | 2704477.782 | 1247451.8822 | 2704476.9862 | 1247443.884 | 2704500.67 | 1247420.2938
50 | 2704500.67 | 1247420.2938 | 2704478.7167 | 1247399.3152
51 | 2704478.7167 | 1247399.3152 | 2704471.927 | 1247392.8269
52 | 2704423.3344 | 1247351.1543 | 2704418.3274 | 1247352.067 | 2704412.9317 | 1247351.7384 | 2704408.5049 | 1247350.8709 | 2704397.5562 | 1247345.5205
53 | 2704399.9755 | 1247394.5577 | 2704369.5742 | 1247414.2614
54 | 2704458.8141 | 1247380.2962 | 2704471.927 | 1247392.8269
55 | 2704385.3019 | 1247339.5322 | 2704397.5562 | 1247345.5205
56 | 2704363.0713 | 1247418.476 | 2704369.5742 | 1247414.2614
57 | 2704481.0542 | 1247251.7866 | 2704480.2292 | 1247251.8224
58 | 2704505.4738 | 1247250.5147 | 2704502.2982 | 1247250.866 | 2704481.0542 | 1247251.7866
59 | 2704349.0958 | 1247165.6944 | 2704326.6822 | 1247164.5529
60 | 2704325.0543 | 1247164.47 | 2704326.6822 | 1247164.5529
61 | 2704289.7935 | 1247162.6743 | 2704325.0543 | 1247164.47
62 | 2704289.7935 | 1247162.6743 | 2704287.9809 | 1247162.582
63 | 2704174.0871 | 1247264.0796 | 2704166.5542 | 1247224.4037
64 | 2704160.7 | 1247158.7945 | 2704158.5724 | 1247171.1002 | 2704159.8225 | 1247188.9474 | 2704166.5542 | 1247224.4037
65 | 2704173.5875 | 1247272.2995 | 2704174.0871 | 1247264.0796
66 | 2704160.7 | 1247158.7945 | 2704194.6252 | 1247160.4501
67 | 2704160.7 | 1247158.7945 | 2704166.9661 | 1247139.278 | 2704168.4646 | 1247137.1184
68 | 2704178.7416 | 1247272.6236 | 2704173.5875 | 1247272.2995
69 | 2704173.5875 | 1247272.2995 | 2704131.7197 | 1247269.5597
70 | 2704224.8154 | 1247161.9234 | 2704194.6252 | 1247160.4501
71 | 2704168.4646 | 1247137.1184 | 2704174.2128 | 1247128.8345
72 | 2704210.3551 | 1247265.4734 | 2704208.7092 | 1247265.3444
73 | 2704210.3551 | 1247265.4734 | 2704209.6323 | 1247275.2129
74 | 2704209.6323 | 1247275.2129 | 2704178.7416 | 1247272.6236
75 | 2704178.7416 | 1247272.6236 | 2704177.6259 | 1247286.2526
76 | 2704028.6549 | 1247260.5015 | 2704118.7585 | 1247268.7115 | 2704131.7197 | 1247269.5597
77 | 2704224.8154 | 1247161.9234 | 2704225.5768 | 1247156.4325 | 2704230.1416 | 1247151.6089 | 2704237.9086 | 1247151.145
78 | 2704178.4921 | 1247122.6673 | 2704174.2128 | 1247128.8345
79 | 2704177.6259 | 1247286.2526 | 2704177.2388 | 1247290.9812
80 | 2704028.6549 | 1247260.5015 | 2704026.6397 | 1247289.2222
81 | 2704028.6549 | 1247260.5015 | 2703975.2991 | 1247256.04 | 2703960.6063 | 1247254.6925 | 2703934.6545 | 1247252.429
82 | 2704252.3724 | 1247157.3236 | 2704237.9086 | 1247151.145
83 | 2704178.4921 | 1247122.6673 | 2704211.169 | 1247098.8555
84 | 2704176.5335 | 1247299.596 | 2704177.2388 | 1247290.9812
85 | 2704026.6397 | 1247289.2222 | 2704007.0427 | 1247287.1886
86 | 2704026.6397 | 1247289.2222 | 2704032.6623 | 1247291.2851 | 2704043.1078 | 1247292.1402
87 | 2703934.6545 | 1247252.429 | 2703794.2964 | 1247041.5579
88 | 2704261.5287 | 1247161.2349 | 2704246.2689 | 1247167.2705
89 | 2704261.5287 | 1247161.2349 | 2704252.3724 | 1247157.3236
90 | 2704261.5287 | 1247161.2349 | 2704287.4875 | 1247162.5569
91 | 2704232.0894 | 1247082.512 | 2704220.9429 | 1247091.7332 | 2704211.169 | 1247098.8555
92 | 2704272.2982 | 1247310.6795 | 2704272.9715 | 1247316.37 | 2704276.3527 | 1247323.7583
93 | 2704287.4875 | 1247162.5569 | 2704287.9809 | 1247162.582
94 | 2704308.0964 | 1247383.4893 | 2704317.0386 | 1247378.0939 | 2704321.3769 | 1247379.6937 | 2704321.3769 | 1247379.6937
95 | 2704308.0964 | 1247383.4893 | 2704291.467 | 1247393.523 | 2704285.5343 | 1247386.0308
96 | 2704321.3769 | 1247379.6937 | 2704331.3396 | 1247395.4015
97 | 2704285.5343 | 1247386.0308 | 2704283.1799 | 1247383.0574
98 | 2704333.4882 | 1247398.7891 | 2704331.3396 | 1247395.4015
99 | 2704266.1927 | 1247375.5362 | 2704274.4916 | 1247372.0852 | 2704283.1799 | 1247383.0574
100 | 2704350.955 | 1247426.3288 | 2704333.4882 | 1247398.7891
101 | 2704266.1927 | 1247375.5362 | 2704259.5401 | 1247378.3025
102 | 2704350.955 | 1247426.3288 | 2704362.5231 | 1247418.8313
103 | 2704338.0261 | 1247434.6634 | 2704350.955 | 1247426.3288
104 | 2704254.13 | 1247380.5521 | 2704259.5401 | 1247378.3025
105 | 2704362.5231 | 1247418.8313 | 2704363.0713 | 1247418.476
106 | 2704338.0261 | 1247434.6634 | 2704347.4944 | 1247449.1132
107 | 2704338.0261 | 1247434.6634 | 2704313.6397 | 1247450.4735
108 | 2703792.1335 | 1247041.8512 | 2703794.2964 | 1247041.5579
109 | 2704396.7884 | 1247451.8688 | 2704395.7616 | 1247453.7058 | 2704388.7932 | 1247458.4006
110 | 2704407.5736 | 1247434.1649 | 2704400.8782 | 1247439.429 | 2704398.2421 | 1247449.2681 | 2704396.7884 | 1247451.8688
111 | 2704380.8995 | 1247463.7187 | 2704388.7932 | 1247458.4006
112 | 2704380.8995 | 1247463.7187 | 2704402.9214 | 1247493.5403
113 | 2704380.8995 | 1247463.7187 | 2704367.1884 | 1247463.2771 | 2704359.1422 | 1247462.0345 | 2704352.6954 | 1247457.0504 | 2704350.4944 | 1247453.6915
114 | 2704415.6275 | 1247504.4179 | 2704408.0887 | 1247500.5377 | 2704402.9214 | 1247493.5403
115 | 2704347.4944 | 1247449.1132 | 2704350.4944 | 1247453.6915
116 | 2704202.3168 | 1247485.851 | 2704210.2802 | 1247484.9347 | 2704220.7953 | 1247483.2515 | 2704229.7455 | 1247481.5375
117 | 2704117.7876 | 1247507.1165 | 2704125.8652 | 1247501.4093 | 2704134.5014 | 1247496.5905 | 2704142.0538 | 1247493.2649 | 2704152.0917 | 1247490.3612 | 2704160.822 | 1247488.791 | 2704169.7883 | 1247487.9701 | 2704185.0443 | 1247487.3265 | 2704192.2838 | 1247486.7644 | 2704200.1369 | 1247486.1018 | 2704202.3168 | 1247485.851
118 | 2704302.8258 | 1247456.5833 | 2704293.6324 | 1247461.4926 | 2704279.9356 | 1247467.5343 | 2704270.6644 | 1247470.6515 | 2704259.4439 | 1247474.2126 | 2704247.3414 | 1247477.6693 | 2704234.0905 | 1247480.7054 | 2704229.7455 | 1247481.5375
119 | 2704023.0875 | 1247454.1237 | 2704042.7188 | 1247471.0481 | 2704053.0173 | 1247479.5466 | 2704063.2715 | 1247484.5417 | 2704104.4588 | 1247495.2397 | 2704109.4851 | 1247497.2407 | 2704117.7876 | 1247507.1165
120 | 2704310.7072 | 1247452.3746 | 2704302.8258 | 1247456.5833
121 | 2704023.0875 | 1247454.1237 | 2704039.373 | 1247434.0045 | 2704035.2295 | 1247430.7396
122 | 2704310.7072 | 1247452.3746 | 2704324.4951 | 1247477.167
123 | 2704310.7072 | 1247452.3746 | 2704313.6397 | 1247450.4735
124 | 2704329.0984 | 1247485.4444 | 2704324.4951 | 1247477.167
125 | 2704309.1418 | 1247334.1446 | 2704303.0466 | 1247337.3037
126 | 2704095.4004 | 1247292.7427 | 2704094.3409 | 1247308.0045
127 | 2704099.6175 | 1247320.6054 | 2704095.0679 | 1247316.8337 | 2704093.9238 | 1247314.0114 | 2704094.3409 | 1247308.0045
128 | 2704099.6175 | 1247320.6054 | 2704095.786 | 1247341.3212
129 | 2704095.786 | 1247341.3212 | 2704083.999 | 1247338.0396
130 | 2704095.786 | 1247341.3212 | 2704105.875 | 1247343.6891 | 2704106.1218 | 1247343.7254
131 | 2704083.999 | 1247338.0396 | 2704081.0361 | 1247337.2146 | 2704069.0905 | 1247334.7364 | 2704055.9675 | 1247333.3698
132 | 2704106.1218 | 1247343.7254 | 2704116.6803 | 1247345.2801 | 2704127.2322 | 1247345.8102 | 2704141.1986 | 1247345.066 | 2704145.3079 | 1247343.7182
133 | 2704055.7244 | 1247333.3445 | 2704055.9675 | 1247333.3698
134 | 2704145.3079 | 1247343.7182 | 2704153.5231 | 1247341.0237 | 2704164.1083 | 1247333.2145 | 2704171.0069 | 1247324.1174 | 2704171.0069 | 1247324.1174
135 | 2704055.7244 | 1247333.3445 | 2704049.6957 | 1247332.7167 | 2704019.8749 | 1247329.8362
136 | 2704171.0069 | 1247324.1174 | 2704174.7482 | 1247314.5645 | 2704175.9227 | 1247307.0569 | 2704176.5335 | 1247299.596
137 | 2704058.9448 | 1247293.4368 | 2704043.1078 | 1247292.1402
138 | 2704016.353 | 1247329.496 | 2704019.8749 | 1247329.8362
139 | 2704000.7345 | 1247327.9874 | 2704016.353 | 1247329.496

## bus_geodata
| x | y | coords
0 | 2704389.0013 | 1247244.1337
1 | 2704403.5729 | 1247244.4758
2 | 2704365.9434 | 1247243.5923
3 | 2704424.7625 | 1247244.9733
4 | 2704365.7104 | 1247220.6134
5 | 2704363.9403 | 1247254.8104
6 | 2704425.0376 | 1247252.5174
7 | 2704340.1836 | 1247211.1739
8 | 2704345.3618 | 1247254.4309
9 | 2704406.8796 | 1247275.4715
10 | 2704439.7696 | 1247252.3319
11 | 2704411.2392 | 1247174.257
12 | 2704403.7629 | 1247127.4652
13 | 2704387.9624 | 1247167.6737
14 | 2704327.7763 | 1247211.0283
15 | 2704407.7626 | 1247290.9548
16 | 2704450.9918 | 1247301.5801
17 | 2704461.7565 | 1247304.6165
18 | 2704418.8853 | 1247292.0412
19 | 2704361.9191 | 1247302.2235
20 | 2704352.429 | 1247297.1636
21 | 2704362.2056 | 1247328.2457
22 | 2704501.4696 | 1247313.2675
23 | 2704520.478 | 1247336.5713
24 | 2704488.9127 | 1247318.9063
25 | 2704481.3797 | 1247313.8251
26 | 2704444.6054 | 1247364.7398
27 | 2704465.8917 | 1247252.0029
28 | 2704361.9248 | 1247166.3477
29 | 2704452.2674 | 1247327.1769
30 | 2704413.7698 | 1247385.7217
31 | 2704456.3879 | 1247377.9777
32 | 2704257.443 | 1247280.0904
33 | 2704271.3273 | 1247302.4745
34 | 2704226.4015 | 1247277.0815
35 | 2704284.7885 | 1247276.0126
36 | 2704229.2091 | 1247270.2688
37 | 2704481.2036 | 1247270.2613
38 | 2704481.0358 | 1247267.0863
39 | 2704296.5494 | 1247299.6269
40 | 2704324.7455 | 1247324.0131
41 | 2704371.2693 | 1247332.6749
42 | 2704500.67 | 1247420.2938
43 | 2704474.2678 | 1247457.9584
44 | 2704478.7167 | 1247399.3152
45 | 2704423.3344 | 1247351.1543
46 | 2704399.9755 | 1247394.5577
47 | 2704458.8141 | 1247380.2962
48 | 2704397.5562 | 1247345.5205
49 | 2704369.5742 | 1247414.2614
50 | 2704471.927 | 1247392.8269
51 | 2704480.2292 | 1247251.8224
52 | 2704481.0542 | 1247251.7866
53 | 2704505.4738 | 1247250.5147
54 | 2704349.0958 | 1247165.6944
55 | 2704326.6822 | 1247164.5529
56 | 2704325.0543 | 1247164.47
57 | 2704289.7934 | 1247162.6743
58 | 2704166.5542 | 1247224.4037
59 | 2704174.0871 | 1247264.0796
60 | 2704160.7 | 1247158.7945
61 | 2704173.5875 | 1247272.2995
62 | 2704194.6252 | 1247160.4501
63 | 2704168.4646 | 1247137.1184
64 | 2704208.7092 | 1247265.3444
65 | 2704210.3551 | 1247265.4734
66 | 2704178.7416 | 1247272.6236
67 | 2704131.7197 | 1247269.5597
68 | 2704224.8154 | 1247161.9234
69 | 2704174.2128 | 1247128.8345
70 | 2704209.6323 | 1247275.2129
71 | 2704177.6259 | 1247286.2526
72 | 2704028.6549 | 1247260.5015
73 | 2704237.9086 | 1247151.145
74 | 2704178.4921 | 1247122.6673
75 | 2704177.2388 | 1247290.9812
76 | 2704026.6397 | 1247289.2222
77 | 2703934.6545 | 1247252.429
78 | 2704246.2689 | 1247167.2705
79 | 2704261.5287 | 1247161.2349
80 | 2704252.3724 | 1247157.3236
81 | 2704211.169 | 1247098.8555
82 | 2704272.2982 | 1247310.6795
83 | 2704287.4875 | 1247162.5569
84 | 2704287.9809 | 1247162.582
85 | 2704308.0964 | 1247383.4893
86 | 2704321.3769 | 1247379.6937
87 | 2704285.5343 | 1247386.0308
88 | 2704331.3396 | 1247395.4015
89 | 2704283.1799 | 1247383.0574
90 | 2704333.4882 | 1247398.7891
91 | 2704266.1927 | 1247375.5362
92 | 2704350.955 | 1247426.3288
93 | 2704259.5401 | 1247378.3025
94 | 2704362.5231 | 1247418.8313
95 | 2704338.0261 | 1247434.6634
96 | 2704254.13 | 1247380.5522
97 | 2703794.2964 | 1247041.5579
98 | 2703792.1335 | 1247041.8512
99 | 2704396.7884 | 1247451.8688
100 | 2704388.7932 | 1247458.4006
101 | 2704407.5736 | 1247434.1649
102 | 2704380.8995 | 1247463.7187
103 | 2704402.9214 | 1247493.5403
104 | 2704350.4944 | 1247453.6915
105 | 2704415.6275 | 1247504.4179
106 | 2704347.4944 | 1247449.1132
107 | 2704202.3168 | 1247485.851
108 | 2704229.7455 | 1247481.5375
109 | 2704117.7876 | 1247507.1165
110 | 2704302.8258 | 1247456.5833
111 | 2704023.0875 | 1247454.1237
112 | 2704310.7072 | 1247452.3746
113 | 2704035.2295 | 1247430.7397
114 | 2704324.4951 | 1247477.167
115 | 2704313.6397 | 1247450.4735
116 | 2704329.0984 | 1247485.4444
117 | 2704385.3019 | 1247339.5322
118 | 2704298.124 | 1247311.6864
119 | 2704309.1418 | 1247334.1446
120 | 2704094.3409 | 1247308.0045
121 | 2704095.4004 | 1247292.7427
122 | 2704099.6175 | 1247320.6054
123 | 2704095.786 | 1247341.3212
124 | 2704083.999 | 1247338.0396
125 | 2704106.1218 | 1247343.7254
126 | 2704055.9675 | 1247333.3698
127 | 2704145.3079 | 1247343.7182
128 | 2704055.7244 | 1247333.3445
129 | 2704171.0069 | 1247324.1174
130 | 2704232.0894 | 1247082.512
131 | 2704276.3527 | 1247323.7583
132 | 2704363.0713 | 1247418.476
133 | 2704176.5335 | 1247299.596
134 | 2704007.0427 | 1247287.1886
135 | 2704043.1078 | 1247292.1402
136 | 2704058.9448 | 1247293.4368
137 | 2704303.0467 | 1247337.3037
138 | 2704019.8749 | 1247329.8362
139 | 2704016.353 | 1247329.496
140 | 2704000.7345 | 1247327.9874
141 | 2704271.3273 | 1247302.4745

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97467 | -0.48749 | 0.0096564 | 0.0024201
1 | 0.97513 | -0.47831 | 0.0056803 | 0.0014236
2 | 0.97414 | -0.49795 | 0 | 0
3 | 0.97592 | -0.46278 | 0 | 0
4 | 0.97372 | -0.50616 | 0.0096594 | 0.0024209
5 | 0.97408 | -0.49904 | 0 | 0
6 | 0.9762 | -0.45725 | 0 | 0
7 | 0.9734 | -0.51239 | 0.0066781 | 0.0016737
8 | 0.97399 | -0.50083 | 0.0052342 | 0.0013118
9 | 0.97824 | -0.41734 | 0 | 0
10 | 0.97592 | -0.46276 | 0.0036118 | 0.00090519
11 | 0.97706 | -0.4421 | 0 | 0
12 | 0.97687 | -0.44587 | 0.0043436 | 0.0010886
13 | 0.97716 | -0.44014 | 0.0026108 | 0.00065432
14 | 0.97337 | -0.5131 | 0.0031115 | 0.00077982
15 | 0.97911 | -0.40028 | 0 | 0
16 | 0.98186 | -0.34672 | 0 | 0
17 | 0.98256 | -0.33308 | 0 | 0
18 | 0.97974 | -0.38797 | 0.0072209 | 0.0018097
19 | 0.99179 | -0.15548 | 0 | 0
20 | 0.99244 | -0.1431 | 0 | 0
21 | 0.98996 | -0.19038 | 0.0015305 | 0.00038358
22 | 0.98143 | -0.35502 | 0 | 0
23 | 0.98113 | -0.36093 | 0.010813 | 0.0027099
24 | 0.98158 | -0.35208 | 0.0046072 | 0.0011547
25 | 0.98171 | -0.34954 | 0 | 0
26 | 0.97949 | -0.39299 | 0 | 0
27 | 0.97551 | -0.4708 | 0.0016713 | 0.00041886
28 | 0.97733 | -0.43683 | 0.0061882 | 0.0015509
29 | 0.98389 | -0.30725 | 0.0092541 | 0.0023193
30 | 0.9784 | -0.41431 | 0.0086853 | 0.0021767
31 | 0.97907 | -0.40114 | 0.0049001 | 0.0012281
32 | 0.99641 | -0.067939 | 0 | 0
33 | 0.99762 | -0.044776 | 0 | 0
34 | 0.99499 | -0.094871 | 0.0041678 | 0.0010446
35 | 0.99346 | -0.12437 | 0.0083718 | 0.0020982
36 | 0.99388 | -0.11609 | 0.0040145 | 0.0010061
37 | 0.97519 | -0.47713 | 0.0019575 | 0.00049058
38 | 0.9752 | -0.47701 | 0.0060072 | 0.0015056
39 | 0.99606 | -0.074377 | 0 | 0
40 | 0.99228 | -0.14611 | 0.0017638 | 0.00044205
41 | 0.98935 | -0.202 | 0.0066847 | 0.0016753
42 | 0.97852 | -0.41204 | 0 | 0
43 | 0.9783 | -0.41618 | 0.0046963 | 0.001177
44 | 0.97865 | -0.40944 | 0.0064301 | 0.0016115
45 | 0.98609 | -0.26475 | 0.0031091 | 0.0007792
46 | 0.97795 | -0.42304 | 0.0042886 | 0.0010748
47 | 0.97901 | -0.40238 | 0.0047068 | 0.0011796
48 | 0.98765 | -0.23477 | 0.0032957 | 0.00082599
49 | 0.977 | -0.44166 | 0.0048483 | 0.0012151
50 | 0.97874 | -0.40754 | 0.0045111 | 0.0011306
51 | 0.97531 | -0.47478 | 0 | 0
52 | 0.97531 | -0.47489 | 0.0048672 | 0.0012198
53 | 0.97525 | -0.47593 | 0.0023181 | 0.00058096
54 | 0.97749 | -0.43375 | 0.0044249 | 0.001109
55 | 0.97785 | -0.42655 | 0.006924 | 0.0017353
56 | 0.97789 | -0.42583 | 0.002061 | 0.00051654
57 | 0.97876 | -0.40875 | 0.0098563 | 0.0024702
58 | 0.9882 | -0.22502 | 0.010447 | 0.0026183
59 | 0.99082 | -0.17468 | 0 | 0
60 | 0.98454 | -0.29595 | 0 | 0
61 | 0.99135 | -0.16445 | 0 | 0
62 | 0.98294 | -0.32694 | 0.0052326 | 0.0013114
63 | 0.98435 | -0.29965 | 0.00038189 | 9.5709e-05
64 | 0.9941 | -0.11193 | 0.0031759 | 0.00079596
65 | 0.9941 | -0.11184 | 0 | 0
66 | 0.99172 | -0.15742 | 0 | 0
67 | 0.99108 | -0.16971 | 0.0014338 | 0.00035934
68 | 0.98167 | -0.35175 | 0 | 0
69 | 0.98427 | -0.30119 | 0.005015 | 0.0012569
70 | 0.99424 | -0.10916 | 0 | 0
71 | 0.99046 | -0.18158 | 0.0019368 | 0.00048541
72 | 0.99055 | -0.18005 | 0 | 0
73 | 0.98083 | -0.36817 | 0.0008976 | 0.00022496
74 | 0.98425 | -0.30166 | 0 | 0
75 | 0.99003 | -0.18981 | 0.0023712 | 0.00059429
76 | 0.99052 | -0.18063 | 0 | 0
77 | 0.99017 | -0.18755 | 0.0014104 | 0.00035348
78 | 0.97979 | -0.38856 | 0.00093277 | 0.00023377
79 | 0.9798 | -0.38828 | 0 | 0
80 | 0.98018 | -0.38087 | 0.0035292 | 0.00088449
81 | 0.98412 | -0.30421 | 0.0018192 | 0.00045593
82 | 0.99851 | -0.028038 | 0.00058745 | 0.00014723
83 | 0.97884 | -0.40721 | 0.0019111 | 0.00047896
84 | 0.97882 | -0.40755 | 0.0017468 | 0.00043779
85 | 0.97561 | -0.46893 | 0.002211 | 0.00055413
86 | 0.9757 | -0.46724 | 0.0045957 | 0.0011518
87 | 0.97551 | -0.47101 | 0.00062735 | 0.00015723
88 | 0.97589 | -0.46359 | 0.0034479 | 0.00086412
89 | 0.9755 | -0.47123 | 0.00070164 | 0.00017585
90 | 0.97594 | -0.46255 | 0.0028712 | 0.0007196
91 | 0.97544 | -0.47232 | 0.00083994 | 0.00021051
92 | 0.97645 | -0.45239 | 0 | 0
93 | 0.97543 | -0.47255 | 0.00096046 | 0.00024071
94 | 0.97679 | -0.4458 | 0.0021737 | 0.00054478
95 | 0.97614 | -0.45854 | 0 | 0
96 | 0.97543 | -0.47263 | 0.00077801 | 0.00019499
97 | 0.98946 | -0.20133 | 0.0023252 | 0.00058275
98 | 0.98946 | -0.20135 | 0.00072807 | 0.00018247
99 | 0.97373 | -0.50609 | 0.0066593 | 0.001669
100 | 0.97396 | -0.50148 | 0.0027359 | 0.00068569
101 | 0.97338 | -0.51296 | 0.017218 | 0.0043154
102 | 0.9742 | -0.49683 | 0 | 0
103 | 0.97366 | -0.50733 | 0.0041847 | 0.0010488
104 | 0.97553 | -0.4706 | 0.0033687 | 0.00084428
105 | 0.97348 | -0.51088 | 0.011232 | 0.0028151
106 | 0.97576 | -0.46605 | 0.002067 | 0.00051805
107 | 0.9745 | -0.4908 | 0.01984 | 0.0049724
108 | 0.97482 | -0.48457 | 0.0021933 | 0.00054969
109 | 0.97413 | -0.49828 | 0 | 0
110 | 0.97578 | -0.46566 | 0.0023252 | 0.00058276
111 | 0.97365 | -0.50766 | 0 | 0
112 | 0.97584 | -0.46448 | 0 | 0
113 | 0.97352 | -0.51029 | 0.0045753 | 0.0011467
114 | 0.97563 | -0.46862 | 0.006491 | 0.0016268
115 | 0.97587 | -0.46389 | 0.0032639 | 0.00081801
116 | 0.97562 | -0.46888 | 0.0014824 | 0.00037154
117 | 0.98844 | -0.21957 | 0.002657 | 0.0006659
118 | 0.99604 | -0.074781 | 0.0018923 | 0.00047424
119 | 0.99224 | -0.14692 | 0.0013305 | 0.00033345
120 | 0.9817 | -0.35156 | 0.0022168 | 0.00055558
121 | 0.98166 | -0.35218 | 0.002213 | 0.00055464
122 | 0.98176 | -0.35036 | 0 | 0
123 | 0.98184 | -0.34868 | 0 | 0
124 | 0.98127 | -0.35978 | 0.0051377 | 0.0012876
125 | 0.98238 | -0.3382 | 0.0084456 | 0.0021167
126 | 0.98009 | -0.38302 | 0.0076049 | 0.001906
127 | 0.98469 | -0.29327 | 0.014838 | 0.0037187
128 | 0.98008 | -0.38319 | 0.005531 | 0.0013862
129 | 0.98708 | -0.24687 | 0.015833 | 0.003968
130 | 0.98407 | -0.30501 | 0.0016768 | 0.00042024
131 | 1 | 0 | -0.47392 | -0.12169
132 | 0.97681 | -0.44548 | 0.00096944 | 0.00024297
133 | 0.98927 | -0.20447 | 0.0015353 | 0.00038479
134 | 0.99051 | -0.18084 | 0.00058082 | 0.00014557
135 | 0.99051 | -0.1808 | 0.00031134 | 7.8028e-05
136 | 0.99051 | -0.18088 | 0.00025558 | 6.4054e-05
137 | 0.99223 | -0.14705 | 0.001127 | 0.00028245
138 | 0.97901 | -0.40407 | 0.006271 | 0.0015717
139 | 0.97893 | -0.40572 | 0.012916 | 0.0032372
140 | 0.97875 | -0.40935 | 0.012718 | 0.0031873
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034363 | -0.0086199 | 0.034378 | 0.0086294 | 1.5045e-05 | 9.4471e-06 | 0.052465 | 0.052465 | 0.052465 | 0.97467 | -0.48749 | 0.97513 | -0.47831 | 14.4134
1 | 0.024707 | 0.0061998 | -0.024695 | -0.0061922 | 1.2308e-05 | 7.5896e-06 | 0.037723 | 0.037723 | 0.037723 | 0.97467 | -0.48749 | 0.97414 | -0.49795 | 10.3634
2 | -0.040059 | -0.010053 | 0.040088 | 0.010072 | 2.9704e-05 | 1.8746e-05 | 0.061133 | 0.061133 | 0.061133 | 0.97513 | -0.47831 | 0.97592 | -0.46278 | 16.7947
3 | 0.01946 | 0.0048803 | -0.019452 | -0.0048757 | 7.615e-06 | 4.5876e-06 | 0.029726 | 0.029726 | 0.029726 | 0.97414 | -0.49795 | 0.97372 | -0.50616 | 8.1666
4 | 0.0052349 | 0.0013119 | -0.0052346 | -0.0013119 | 2.7326e-07 | 3.302e-08 | 0.0079964 | 0.0079964 | 0.0079964 | 0.97414 | -0.49795 | 0.97408 | -0.49904 | 2.1968
5 | -0.040088 | -0.010072 | 0.040099 | 0.010078 | 1.0581e-05 | 6.6774e-06 | 0.061133 | 0.061133 | 0.061133 | 0.97592 | -0.46278 | 0.9762 | -0.45725 | 16.7947
6 | 0.0097926 | 0.0024549 | -0.0097897 | -0.0024534 | 2.9039e-06 | 1.4286e-06 | 0.014965 | 0.014965 | 0.014965 | 0.97372 | -0.50616 | 0.9734 | -0.51239 | 4.1113
7 | 0.0052346 | 0.0013119 | -0.0052342 | -0.0013118 | 4.4558e-07 | 5.3882e-08 | 0.0079964 | 0.0079965 | 0.0079965 | 0.97408 | -0.49904 | 0.97399 | -0.50083 | 2.1968
8 | -0.060548 | -0.015208 | 0.060663 | 0.015282 | 0.00011555 | 7.3496e-05 | 0.092304 | 0.092304 | 0.092304 | 0.9762 | -0.45725 | 0.97824 | -0.41734 | 25.3583
9 | 0.020449 | 0.0051298 | -0.020443 | -0.0051266 | 5.3684e-06 | 3.2517e-06 | 0.031172 | 0.031172 | 0.031172 | 0.9762 | -0.45725 | 0.97592 | -0.46276 | 8.5636
10 | 0.0031116 | 0.00077974 | -0.0031115 | -0.00077982 | 1.0528e-07 | -8.6858e-08 | 0.0047566 | 0.0047567 | 0.0047567 | 0.9734 | -0.51239 | 0.97337 | -0.5131 | 1.3068
11 | -0.060663 | -0.015282 | 0.060713 | 0.015313 | 4.955e-05 | 3.1517e-05 | 0.092304 | 0.092304 | 0.092304 | 0.97824 | -0.41734 | 0.97911 | -0.40028 | 25.3583
12 | 0.016832 | 0.0042214 | -0.016825 | -0.0042176 | 6.4528e-06 | 3.8035e-06 | 0.025665 | 0.025665 | 0.025665 | 0.97592 | -0.46276 | 0.97551 | -0.4708 | 7.0508
13 | 0.0043444 | 0.0010885 | -0.0043436 | -0.0010886 | 7.7919e-07 | -9.5671e-08 | 0.0066162 | 0.0066164 | 0.0066164 | 0.97706 | -0.4421 | 0.97687 | -0.44587 | 1.8177
14 | -0.0043444 | -0.0010885 | 0.0043448 | 0.0010885 | 4.067e-07 | -5.0044e-08 | 0.0066162 | 0.0066161 | 0.0066162 | 0.97706 | -0.4421 | 0.97716 | -0.44014 | 1.8176
15 | -0.0069556 | -0.0017428 | 0.0069567 | 0.0017432 | 1.0968e-06 | 3.7531e-07 | 0.010592 | 0.010592 | 0.010592 | 0.97716 | -0.44014 | 0.97733 | -0.43683 | 2.9098
16 | -0.060713 | -0.015313 | 0.060748 | 0.015336 | 3.5797e-05 | 2.2769e-05 | 0.092304 | 0.092304 | 0.092304 | 0.97911 | -0.40028 | 0.97974 | -0.38797 | 25.3582
17 | -0.068104 | -0.017231 | 0.068148 | 0.01726 | 4.4608e-05 | 2.8408e-05 | 0.10327 | 0.10327 | 0.10327 | 0.98186 | -0.34672 | 0.98256 | -0.33308 | 28.3711
18 | 0.068104 | 0.017231 | -0.067969 | -0.017146 | 0.00013451 | 8.5662e-05 | 0.10327 | 0.10327 | 0.10327 | 0.98186 | -0.34672 | 0.97974 | -0.38797 | 28.3711
19 | -0.23545 | -0.059552 | 0.23574 | 0.059738 | 0.00029224 | 0.00018579 | 0.35676 | 0.35676 | 0.35676 | 0.98256 | -0.33308 | 0.98389 | -0.30725 | 24.5029
20 | 0.1673 | 0.042292 | -0.16717 | -0.042209 | 0.00013194 | 8.3334e-05 | 0.25349 | 0.25349 | 0.25349 | 0.98256 | -0.33308 | 0.98171 | -0.34954 | 17.4101
21 | -0.26412 | -0.067567 | 0.26428 | 0.067668 | 0.00015836 | 0.00010079 | 0.39677 | 0.39677 | 0.39677 | 0.99179 | -0.15548 | 0.99244 | -0.1431 | 27.2504
22 | 0.26412 | 0.067567 | -0.26368 | -0.067283 | 0.00044534 | 0.00028346 | 0.39677 | 0.39677 | 0.39677 | 0.99179 | -0.15548 | 0.98996 | -0.19038 | 27.2504
23 | -0.2685 | -0.068725 | 0.2694 | 0.069296 | 0.00089675 | 0.00057087 | 0.4031 | 0.40309 | 0.4031 | 0.99244 | -0.1431 | 0.99606 | -0.074377 | 27.6851
24 | 0.004222 | 0.0010576 | -0.0042214 | -0.0010577 | 6.0506e-07 | -1.3298e-07 | 0.0063301 | 0.0063303 | 0.0063303 | 0.99244 | -0.1431 | 0.99228 | -0.14611 | 1.7391
25 | 0.26215 | 0.0669 | -0.262 | -0.066806 | 0.00014716 | 9.3665e-05 | 0.39447 | 0.39447 | 0.39447 | 0.98996 | -0.19038 | 0.98935 | -0.202 | 27.0924
26 | 0.010816 | 0.0027115 | -0.010813 | -0.0027099 | 3.0443e-06 | 1.567e-06 | 0.016399 | 0.016399 | 0.016399 | 0.98143 | -0.35502 | 0.98113 | -0.36093 | 4.5052
27 | -0.010816 | -0.0027115 | 0.010817 | 0.0027123 | 1.5157e-06 | 7.801e-07 | 0.016399 | 0.016399 | 0.016399 | 0.98143 | -0.35502 | 0.98158 | -0.35208 | 4.5051
28 | -0.015424 | -0.0038669 | 0.015426 | 0.003868 | 1.8631e-06 | 1.0775e-06 | 0.023383 | 0.023383 | 0.023383 | 0.98158 | -0.35208 | 0.98171 | -0.34954 | 6.4239
29 | 0.15174 | 0.038341 | -0.15142 | -0.038142 | 0.00031535 | 0.00019862 | 0.23011 | 0.23011 | 0.23011 | 0.98171 | -0.34954 | 0.97949 | -0.39299 | 15.8042
30 | 0.12616 | 0.031806 | -0.12603 | -0.031725 | 0.00012859 | 8.0419e-05 | 0.19173 | 0.19173 | 0.19173 | 0.97949 | -0.39299 | 0.9784 | -0.41431 | 13.1683
31 | 0.025262 | 0.0063364 | -0.025252 | -0.0063303 | 9.8045e-06 | 6.0515e-06 | 0.038379 | 0.038379 | 0.038379 | 0.97949 | -0.39299 | 0.97907 | -0.40114 | 10.5438
32 | 0.015154 | 0.0037987 | -0.015151 | -0.003797 | 2.8731e-06 | 1.6598e-06 | 0.023115 | 0.023116 | 0.023116 | 0.97551 | -0.4708 | 0.97531 | -0.47478 | 6.3504
33 | -0.013145 | -0.0032941 | 0.013147 | 0.0032952 | 1.9294e-06 | 1.0738e-06 | 0.020013 | 0.020013 | 0.020013 | 0.97733 | -0.43683 | 0.97749 | -0.43375 | 5.4982
34 | -0.24499 | -0.062057 | 0.24549 | 0.062376 | 0.00050117 | 0.00031877 | 0.37076 | 0.37076 | 0.37076 | 0.98389 | -0.30725 | 0.98609 | -0.26475 | 25.4641
35 | 0.11735 | 0.029549 | -0.1173 | -0.029518 | 4.8946e-05 | 3.0503e-05 | 0.17852 | 0.17852 | 0.17852 | 0.9784 | -0.41431 | 0.97795 | -0.42304 | 12.2611
36 | 0.020352 | 0.0051022 | -0.020351 | -0.0051015 | 1.2041e-06 | 7.2842e-07 | 0.030932 | 0.030932 | 0.030932 | 0.97907 | -0.40114 | 0.97901 | -0.40238 | 8.4978
37 | -0.19875 | -0.050725 | 0.19897 | 0.050867 | 0.00022269 | 0.00014112 | 0.29713 | 0.29713 | 0.29713 | 0.99641 | -0.067939 | 0.99762 | -0.044776 | 20.4074
38 | 0.19875 | 0.050725 | -0.19849 | -0.050562 | 0.00025824 | 0.00016365 | 0.29713 | 0.29713 | 0.29713 | 0.99641 | -0.067939 | 0.99499 | -0.094871 | 20.4075
39 | 0.27168 | 0.070019 | -0.27129 | -0.06977 | 0.00039094 | 0.00024888 | 0.40592 | 0.40592 | 0.40592 | 0.99762 | -0.044776 | 0.99606 | -0.074377 | 27.8792
40 | -0.47065 | -0.12089 | 0.47104 | 0.12113 | 0.00038286 | 0.0002446 | 0.70305 | 0.70305 | 0.70305 | 0.99762 | -0.044776 | 0.99851 | -0.028038 | 48.2865
41 | 0.19432 | 0.049517 | -0.19419 | -0.049432 | 0.00013386 | 8.4794e-05 | 0.2909 | 0.2909 | 0.2909 | 0.99499 | -0.094871 | 0.99424 | -0.10916 | 19.9794
42 | -0.0083718 | -0.0020982 | 0.0083751 | 0.0020996 | 3.3041e-06 | 1.3887e-06 | 0.012539 | 0.012539 | 0.012539 | 0.99346 | -0.12437 | 0.99388 | -0.11609 | 3.4449
43 | -0.01239 | -0.0031057 | 0.012392 | 0.0031071 | 2.5102e-06 | 1.3544e-06 | 0.01855 | 0.01855 | 0.01855 | 0.99388 | -0.11609 | 0.9941 | -0.11184 | 5.0961
44 | -0.0019575 | -0.00049058 | 0.0019575 | 0.00049055 | 1.0637e-08 | -3.2861e-08 | 0.0029868 | 0.0029868 | 0.0029868 | 0.97519 | -0.47713 | 0.9752 | -0.47701 | 0.82055
45 | -0.0079647 | -0.0019961 | 0.0079655 | 0.0019965 | 8.4658e-07 | 3.5108e-07 | 0.012153 | 0.012153 | 0.012153 | 0.9752 | -0.47701 | 0.97531 | -0.47478 | 3.3387
46 | 0.0018923 | 0.00047411 | -0.0018923 | -0.00047424 | 3.6446e-08 | -1.3497e-07 | 0.0028269 | 0.0028269 | 0.0028269 | 0.99606 | -0.074377 | 0.99604 | -0.074781 | 0.77662
47 | 0.0024576 | 0.00061565 | -0.0024575 | -0.00061583 | 9.4807e-08 | -1.7977e-07 | 0.0036853 | 0.0036854 | 0.0036854 | 0.99228 | -0.14611 | 0.99224 | -0.14692 | 1.0125
48 | 0.25532 | 0.065131 | -0.2551 | -0.064993 | 0.00021637 | 0.00013768 | 0.38441 | 0.38441 | 0.38441 | 0.98935 | -0.202 | 0.98844 | -0.21957 | 26.4019
49 | 0.0046972 | 0.001177 | -0.0046963 | -0.001177 | 9.2674e-07 | -1.5179e-08 | 0.0071429 | 0.0071431 | 0.0071431 | 0.97852 | -0.41204 | 0.9783 | -0.41618 | 1.9624
50 | -0.0046972 | -0.001177 | 0.0046978 | 0.001177 | 5.8097e-07 | -9.6683e-09 | 0.0071429 | 0.0071428 | 0.0071429 | 0.97852 | -0.41204 | 0.97865 | -0.40944 | 1.9623
51 | -0.011128 | -0.0027885 | 0.011129 | 0.002789 | 1.0082e-06 | 5.2722e-07 | 0.01692 | 0.01692 | 0.01692 | 0.97865 | -0.40944 | 0.97874 | -0.40754 | 4.6483
52 | -0.2486 | -0.063155 | 0.24896 | 0.063384 | 0.00035935 | 0.00022859 | 0.37545 | 0.37545 | 0.37545 | 0.98609 | -0.26475 | 0.98765 | -0.23477 | 25.7862
53 | 0.11301 | 0.028443 | -0.11291 | -0.028381 | 0.00010048 | 6.2488e-05 | 0.172 | 0.172 | 0.172 | 0.97795 | -0.42304 | 0.977 | -0.44166 | 11.813
54 | 0.015644 | 0.0039219 | -0.01564 | -0.0039196 | 3.8455e-06 | 2.2331e-06 | 0.023778 | 0.023778 | 0.023778 | 0.97901 | -0.40238 | 0.97874 | -0.40754 | 6.5324
55 | -0.25226 | -0.06421 | 0.25244 | 0.064327 | 0.00018504 | 0.00011773 | 0.38041 | 0.38041 | 0.38041 | 0.98765 | -0.23477 | 0.98844 | -0.21957 | 26.1272
56 | 0.10806 | 0.027166 | -0.10804 | -0.027153 | 1.9686e-05 | 1.2211e-05 | 0.16461 | 0.16461 | 0.16461 | 0.977 | -0.44166 | 0.97681 | -0.44548 | 11.3059
57 | 0.0071854 | 0.0018006 | -0.0071854 | -0.0018006 | 3.7215e-08 | 1.3513e-08 | 0.010963 | 0.010963 | 0.010963 | 0.97531 | -0.47478 | 0.97531 | -0.47489 | 3.0117
58 | 0.0023182 | 0.00058073 | -0.0023181 | -0.00058096 | 1.1473e-07 | -2.3179e-07 | 0.0035367 | 0.0035368 | 0.0035368 | 0.97531 | -0.47489 | 0.97525 | -0.47593 | 0.97166
59 | -0.017572 | -0.0044041 | 0.017578 | 0.0044077 | 6.0219e-06 | 3.5726e-06 | 0.026749 | 0.026749 | 0.026749 | 0.97749 | -0.43375 | 0.97785 | -0.42655 | 7.3487
60 | -0.024502 | -0.006143 | 0.024503 | 0.0061435 | 8.4977e-07 | 5.234e-07 | 0.037286 | 0.037286 | 0.037286 | 0.97785 | -0.42655 | 0.97789 | -0.42583 | 10.2433
61 | -0.026564 | -0.0066601 | 0.026585 | 0.0066735 | 2.1633e-05 | 1.3402e-05 | 0.040422 | 0.040422 | 0.040422 | 0.97789 | -0.42583 | 0.97876 | -0.40875 | 11.1049
62 | -0.036442 | -0.0091437 | 0.036444 | 0.009145 | 2.0894e-06 | 1.3144e-06 | 0.055406 | 0.055406 | 0.055406 | 0.97876 | -0.40875 | 0.97882 | -0.40755 | 15.2215
63 | -0.070484 | -0.017848 | 0.070655 | 0.017957 | 0.0001708 | 0.00010879 | 0.1062 | 0.1062 | 0.1062 | 0.9882 | -0.22502 | 0.99082 | -0.17468 | 29.1754
64 | 0.060037 | 0.015229 | -0.059833 | -0.0151 | 0.000204 | 0.00012971 | 0.090468 | 0.090468 | 0.090468 | 0.9882 | -0.22502 | 0.98454 | -0.29595 | 24.8538
65 | -0.070655 | -0.017957 | 0.07069 | 0.017979 | 3.4832e-05 | 2.2187e-05 | 0.1062 | 0.1062 | 0.1062 | 0.99082 | -0.17468 | 0.99135 | -0.16445 | 29.1754
66 | 0.050937 | 0.012871 | -0.050862 | -0.012823 | 7.5564e-05 | 4.793e-05 | 0.077023 | 0.077024 | 0.077024 | 0.98454 | -0.29595 | 0.98294 | -0.32694 | 21.1603
67 | 0.0088956 | 0.0022291 | -0.008894 | -0.0022284 | 1.5676e-06 | 7.0922e-07 | 0.013444 | 0.013445 | 0.013445 | 0.98454 | -0.29595 | 0.98435 | -0.29965 | 3.6936
68 | -0.077743 | -0.019742 | 0.077769 | 0.019759 | 2.6334e-05 | 1.6787e-05 | 0.11678 | 0.11678 | 0.11678 | 0.99135 | -0.16445 | 0.99172 | -0.15742 | 32.0835
69 | 0.0070534 | 0.0017635 | -0.0070516 | -0.0017629 | 1.7631e-06 | 5.8757e-07 | 0.010586 | 0.010586 | 0.010586 | 0.99135 | -0.16445 | 0.99108 | -0.16971 | 2.9082
70 | 0.045629 | 0.011511 | -0.045575 | -0.011477 | 5.4125e-05 | 3.4258e-05 | 0.069102 | 0.069103 | 0.069103 | 0.98294 | -0.32694 | 0.98167 | -0.35175 | 18.9842
71 | 0.0085121 | 0.0021327 | -0.0085115 | -0.0021324 | 6.2603e-07 | 2.725e-07 | 0.012867 | 0.012867 | 0.012867 | 0.98435 | -0.29965 | 0.98427 | -0.30119 | 3.535
72 | -0.0031759 | -0.00079596 | 0.0031759 | 0.00079594 | 1.3991e-08 | -1.245e-08 | 0.0047538 | 0.0047538 | 0.0047538 | 0.9941 | -0.11193 | 0.9941 | -0.11184 | 1.306
73 | -0.015568 | -0.003903 | 0.01557 | 0.0039041 | 1.989e-06 | 1.1463e-06 | 0.023303 | 0.023303 | 0.023303 | 0.9941 | -0.11184 | 0.99424 | -0.10916 | 6.402
74 | -0.1782 | -0.045263 | 0.17862 | 0.045528 | 0.00041499 | 0.00026479 | 0.2676 | 0.2676 | 0.2676 | 0.99172 | -0.15742 | 0.99424 | -0.10916 | 36.7578
75 | 0.10043 | 0.025504 | -0.10032 | -0.02543 | 0.00011663 | 7.4469e-05 | 0.15081 | 0.15081 | 0.15081 | 0.99172 | -0.15742 | 0.99046 | -0.18158 | 41.4322
76 | 0.0056178 | 0.0014036 | -0.0056151 | -0.0014031 | 2.7595e-06 | 4.3348e-07 | 0.0084331 | 0.0084336 | 0.0084336 | 0.99108 | -0.16971 | 0.99055 | -0.18005 | 2.3169
77 | 0.045575 | 0.011477 | -0.045539 | -0.011454 | 3.5752e-05 | 2.2629e-05 | 0.069103 | 0.069103 | 0.069103 | 0.98167 | -0.35175 | 0.98083 | -0.36817 | 18.9842
78 | 0.0034965 | 0.00087558 | -0.0034964 | -0.00087562 | 7.8646e-08 | -4.5069e-08 | 0.0052857 | 0.0052858 | 0.0052858 | 0.98427 | -0.30119 | 0.98425 | -0.30166 | 1.4521
79 | 0.09838 | 0.024945 | -0.098341 | -0.02492 | 3.892e-05 | 2.4848e-05 | 0.1479 | 0.1479 | 0.1479 | 0.99046 | -0.18158 | 0.99003 | -0.18981 | 40.6328
80 | 0.0011478 | 0.00028663 | -0.0011477 | -0.00028698 | 3.2089e-08 | -3.501e-07 | 0.0017238 | 0.001724 | 0.001724 | 0.99055 | -0.18005 | 0.99052 | -0.18063 | 0.47362
81 | 0.0044673 | 0.0011165 | -0.0044657 | -0.0011167 | 1.5929e-06 | -1.9454e-07 | 0.0067097 | 0.0067102 | 0.0067102 | 0.99055 | -0.18005 | 0.99017 | -0.18755 | 1.8435
82 | 0.044642 | 0.011229 | -0.044615 | -0.011212 | 2.7065e-05 | 1.7123e-05 | 0.067741 | 0.067741 | 0.067741 | 0.98083 | -0.36817 | 0.98018 | -0.38087 | 18.6101
83 | 0.0034964 | 0.00087562 | -0.003496 | -0.00087587 | 4.2364e-07 | -2.4267e-07 | 0.0052858 | 0.005286 | 0.005286 | 0.98425 | -0.30166 | 0.98412 | -0.30421 | 1.4522
84 | 0.09597 | 0.024325 | -0.095902 | -0.024282 | 6.753e-05 | 4.3108e-05 | 0.14434 | 0.14434 | 0.14434 | 0.99003 | -0.18981 | 0.98927 | -0.20447 | 39.6537
85 | 0.00058083 | 0.00014532 | -0.00058082 | -0.00014557 | 5.6246e-09 | -2.5e-07 | 0.00087247 | 0.00087256 | 0.00087256 | 0.99052 | -0.18063 | 0.99051 | -0.18084 | 0.23971
86 | 0.00056692 | 0.00014166 | -0.00056691 | -0.00014188 | 4.581e-09 | -2.1391e-07 | 0.00085151 | 0.00085159 | 0.00085159 | 0.99052 | -0.18063 | 0.99051 | -0.1808 | 0.23395
87 | 0.0030553 | 0.00076322 | -0.0030533 | -0.0007652 | 2.0023e-06 | -1.9744e-06 | 0.0045906 | 0.0045917 | 0.0045917 | 0.99017 | -0.18755 | 0.98946 | -0.20133 | 1.2615
88 | -0.00093277 | -0.00023377 | 0.00093278 | 0.00023358 | 1.2349e-08 | -1.9877e-07 | 0.0014166 | 0.0014165 | 0.0014166 | 0.97979 | -0.38856 | 0.9798 | -0.38828 | 0.38918
89 | -0.041071 | -0.010319 | 0.041086 | 0.010328 | 1.4531e-05 | 9.1742e-06 | 0.062383 | 0.062383 | 0.062383 | 0.9798 | -0.38828 | 0.98018 | -0.38087 | 17.1383
90 | 0.040138 | 0.010085 | -0.040102 | -0.010062 | 3.623e-05 | 2.286e-05 | 0.060967 | 0.060967 | 0.060967 | 0.9798 | -0.38828 | 0.97884 | -0.40721 | 16.7492
91 | 0.0016768 | 0.00041994 | -0.0016768 | -0.00042024 | 6.4024e-08 | -2.9648e-07 | 0.0025353 | 0.0025354 | 0.0025354 | 0.98412 | -0.30421 | 0.98407 | -0.30501 | 0.69655
92 | -0.47163 | -0.12128 | 0.47227 | 0.12169 | 0.00064364 | 0.00041121 | 0.70393 | 0.70393 | 0.70393 | 0.99851 | -0.028038 | 1 | 0 | 48.3466
93 | 0.038191 | 0.0095832 | -0.03819 | -0.0095828 | 6.2444e-07 | 3.9344e-07 | 0.058062 | 0.058062 | 0.058062 | 0.97884 | -0.40721 | 0.97882 | -0.40755 | 15.951
94 | -0.006119 | -0.0015329 | 0.0061195 | 0.001533 | 4.9212e-07 | 1.2679e-07 | 0.0093325 | 0.0093324 | 0.0093325 | 0.97561 | -0.46893 | 0.9757 | -0.46724 | 2.5639
95 | 0.003908 | 0.0009788 | -0.0039076 | -0.00097891 | 3.8605e-07 | -1.1475e-07 | 0.0059603 | 0.0059604 | 0.0059604 | 0.97561 | -0.46893 | 0.97551 | -0.47101 | 1.6375
96 | -0.010715 | -0.0026848 | 0.010717 | 0.0026858 | 1.8626e-06 | 9.5972e-07 | 0.016341 | 0.016341 | 0.016341 | 0.9757 | -0.46724 | 0.97589 | -0.46359 | 4.4893
97 | 0.0032802 | 0.00082168 | -0.0032802 | -0.00082171 | 3.5605e-08 | -2.4561e-08 | 0.0050034 | 0.0050035 | 0.0050035 | 0.97551 | -0.47101 | 0.9755 | -0.47123 | 1.3746
98 | -0.014165 | -0.0035499 | 0.014166 | 0.0035503 | 7.0175e-07 | 3.99e-07 | 0.021598 | 0.021598 | 0.021598 | 0.97589 | -0.46359 | 0.97594 | -0.46255 | 5.9336
99 | 0.0025786 | 0.00064586 | -0.0025784 | -0.00064606 | 1.3334e-07 | -2.0158e-07 | 0.0039332 | 0.0039333 | 0.0039333 | 0.9755 | -0.47123 | 0.97544 | -0.47232 | 1.0806
100 | -0.017037 | -0.0042699 | 0.017045 | 0.0042748 | 8.2518e-06 | 4.8735e-06 | 0.025976 | 0.025976 | 0.025976 | 0.97594 | -0.46255 | 0.97645 | -0.45239 | 7.1363
101 | 0.0017385 | 0.00043555 | -0.0017385 | -0.00043563 | 1.9002e-08 | -7.7774e-08 | 0.002652 | 0.002652 | 0.002652 | 0.97544 | -0.47232 | 0.97543 | -0.47255 | 0.72857
102 | -0.10486 | -0.026344 | 0.1049 | 0.026365 | 3.3012e-05 | 2.0438e-05 | 0.15983 | 0.15983 | 0.15983 | 0.97645 | -0.45239 | 0.97679 | -0.4458 | 10.977
103 | 0.08782 | 0.022069 | -0.087794 | -0.022054 | 2.5785e-05 | 1.5735e-05 | 0.13385 | 0.13385 | 0.13385 | 0.97645 | -0.45239 | 0.97614 | -0.45854 | 9.193
104 | 0.00077801 | 0.00019492 | -0.00077801 | -0.00019499 | 3.095e-09 | -7.1156e-08 | 0.0011868 | 0.0011869 | 0.0011869 | 0.97543 | -0.47255 | 0.97543 | -0.47263 | 0.32606
105 | -0.10707 | -0.026909 | 0.10707 | 0.02691 | 1.6299e-06 | 1.0104e-06 | 0.16314 | 0.16314 | 0.16314 | 0.97679 | -0.4458 | 0.97681 | -0.44548 | 11.2044
106 | 0.047572 | 0.011962 | -0.047555 | -0.011951 | 1.7041e-05 | 1.0475e-05 | 0.072533 | 0.072533 | 0.072533 | 0.97614 | -0.45854 | 0.97576 | -0.46605 | 9.9633
107 | 0.040221 | 0.010092 | -0.040211 | -0.010087 | 1.0244e-05 | 5.1034e-06 | 0.061317 | 0.061318 | 0.061318 | 0.97614 | -0.45854 | 0.97587 | -0.46389 | 4.2114
108 | 0.00072807 | 0.00018244 | -0.00072807 | -0.00018247 | 9.8127e-10 | -2.7406e-08 | 0.0010949 | 0.0010949 | 0.0010949 | 0.98946 | -0.20133 | 0.98946 | -0.20135 | 0.3008
109 | -0.023883 | -0.0059877 | 0.023889 | 0.0059909 | 5.2487e-06 | 3.2285e-06 | 0.036498 | 0.036498 | 0.036498 | 0.97373 | -0.50609 | 0.97396 | -0.50148 | 10.0271
110 | 0.017224 | 0.0043187 | -0.017218 | -0.0043154 | 5.6335e-06 | 3.3358e-06 | 0.026322 | 0.026322 | 0.026322 | 0.97373 | -0.50609 | 0.97338 | -0.51296 | 7.2313
111 | -0.026625 | -0.0066766 | 0.02663 | 0.0066802 | 5.9062e-06 | 3.6615e-06 | 0.040678 | 0.040678 | 0.040678 | 0.97396 | -0.50148 | 0.9742 | -0.49683 | 11.1754
112 | 0.015427 | 0.0038693 | -0.015419 | -0.0038649 | 7.7193e-06 | 4.479e-06 | 0.023564 | 0.023564 | 0.023564 | 0.9742 | -0.49683 | 0.97366 | -0.50733 | 6.4737
113 | -0.042057 | -0.01055 | 0.04211 | 0.010583 | 5.2658e-05 | 3.3277e-05 | 0.064243 | 0.064242 | 0.064243 | 0.9742 | -0.49683 | 0.97553 | -0.4706 | 17.649
114 | 0.011234 | 0.0028161 | -0.011232 | -0.0028151 | 1.8988e-06 | 1.0016e-06 | 0.017169 | 0.017169 | 0.017169 | 0.97366 | -0.50733 | 0.97348 | -0.51088 | 4.7168
115 | -0.045478 | -0.011427 | 0.045488 | 0.011433 | 9.8807e-06 | 6.2553e-06 | 0.069381 | 0.069381 | 0.069381 | 0.97553 | -0.4706 | 0.97576 | -0.46605 | 19.0607
116 | -0.02442 | -0.0061189 | 0.024427 | 0.0061229 | 7.2413e-06 | 3.942e-06 | 0.037287 | 0.037287 | 0.037287 | 0.9745 | -0.4908 | 0.97482 | -0.48457 | 5.1219
117 | 0.0045795 | 0.0011465 | -0.0045779 | -0.0011466 | 1.6312e-06 | -6.3985e-08 | 0.0069923 | 0.0069927 | 0.0069927 | 0.9745 | -0.4908 | 0.97413 | -0.49828 | 1.9211
118 | -0.02662 | -0.0066726 | 0.026644 | 0.006686 | 2.4009e-05 | 1.343e-05 | 0.040635 | 0.040634 | 0.040635 | 0.97482 | -0.48457 | 0.97578 | -0.46566 | 5.5817
119 | 0.0045779 | 0.0011466 | -0.0045759 | -0.0011467 | 2.0455e-06 | -7.8841e-08 | 0.0069927 | 0.0069932 | 0.0069932 | 0.97413 | -0.49828 | 0.97365 | -0.50766 | 1.9212
120 | -0.02897 | -0.0072688 | 0.028971 | 0.0072694 | 1.6349e-06 | 5.9991e-07 | 0.04418 | 0.04418 | 0.04418 | 0.97578 | -0.46566 | 0.97584 | -0.46448 | 3.0343
121 | 0.0045759 | 0.0011467 | -0.0045753 | -0.0011467 | 5.7145e-07 | -2.1749e-08 | 0.0069932 | 0.0069933 | 0.0069933 | 0.97365 | -0.50766 | 0.97352 | -0.51029 | 1.9212
122 | 0.007975 | 0.0019989 | -0.0079734 | -0.0019982 | 1.5732e-06 | 6.5255e-07 | 0.012161 | 0.012161 | 0.012161 | 0.97584 | -0.46448 | 0.97563 | -0.46862 | 3.3409
123 | -0.036946 | -0.0092682 | 0.036947 | 0.0092687 | 1.04e-06 | 4.9097e-07 | 0.056341 | 0.056341 | 0.056341 | 0.97584 | -0.46448 | 0.97587 | -0.46389 | 3.8696
124 | 0.0014825 | 0.00037143 | -0.0014824 | -0.00037154 | 1.8157e-08 | -1.0665e-07 | 0.002261 | 0.002261 | 0.002261 | 0.97563 | -0.46862 | 0.97562 | -0.46888 | 0.62116
125 | 0.001127 | 0.00028237 | -0.001127 | -0.00028245 | 7.3539e-09 | -8.3967e-08 | 0.0016901 | 0.0016901 | 0.0016901 | 0.99224 | -0.14692 | 0.99223 | -0.14705 | 0.46432
126 | 0.0022131 | 0.00055449 | -0.002213 | -0.00055464 | 6.4557e-08 | -1.521e-07 | 0.0033545 | 0.0033546 | 0.0033546 | 0.9817 | -0.35156 | 0.98166 | -0.35218 | 0.92158
127 | -0.0044299 | -0.0011101 | 0.0044301 | 0.00111 | 2.5321e-07 | -2.7313e-08 | 0.0067146 | 0.0067145 | 0.0067146 | 0.9817 | -0.35156 | 0.98176 | -0.35036 | 1.8447
128 | -0.0044301 | -0.00111 | 0.0044305 | 0.00111 | 3.5619e-07 | -3.8467e-08 | 0.0067145 | 0.0067144 | 0.0067145 | 0.98176 | -0.35036 | 0.98184 | -0.34868 | 1.8447
129 | 0.050292 | 0.012647 | -0.050265 | -0.01263 | 2.6665e-05 | 1.6911e-05 | 0.076234 | 0.076234 | 0.076234 | 0.98184 | -0.34868 | 0.98127 | -0.35978 | 20.9434
130 | -0.054722 | -0.013757 | 0.05475 | 0.013774 | 2.7382e-05 | 1.739e-05 | 0.082948 | 0.082948 | 0.082948 | 0.98184 | -0.34868 | 0.98238 | -0.3382 | 22.788
131 | 0.045127 | 0.011343 | -0.045077 | -0.011311 | 5.0012e-05 | 3.1648e-05 | 0.068443 | 0.068443 | 0.068443 | 0.98127 | -0.35978 | 0.98009 | -0.38302 | 18.8031
132 | -0.063195 | -0.015891 | 0.063331 | 0.015978 | 0.00013594 | 8.6502e-05 | 0.095741 | 0.095741 | 0.095741 | 0.98238 | -0.3382 | 0.98469 | -0.29327 | 26.3025
133 | 0.037472 | 0.0094049 | -0.037472 | -0.0094047 | 2.9664e-07 | 1.8677e-07 | 0.056897 | 0.056897 | 0.056897 | 0.98009 | -0.38302 | 0.98008 | -0.38319 | 15.6311
134 | -0.078169 | -0.019696 | 0.078343 | 0.019807 | 0.00017392 | 0.00011089 | 0.11816 | 0.11816 | 0.11816 | 0.98469 | -0.29327 | 0.98708 | -0.24687 | 32.4623
135 | 0.031941 | 0.0080185 | -0.031909 | -0.0079986 | 3.1773e-05 | 1.9882e-05 | 0.0485 | 0.0485 | 0.0485 | 0.98008 | -0.38319 | 0.97901 | -0.40407 | 13.3241
136 | -0.094175 | -0.023775 | 0.094367 | 0.023898 | 0.00019172 | 0.00012238 | 0.14203 | 0.14203 | 0.14203 | 0.98708 | -0.24687 | 0.98927 | -0.20447 | 39.0193
137 | 0.00025558 | 6.385e-05 | -0.00025558 | -6.4054e-05 | 8.7824e-10 | -2.0397e-07 | 0.00038387 | 0.00038395 | 0.00038395 | 0.99051 | -0.1808 | 0.99051 | -0.18088 | 0.10548
138 | 0.025638 | 0.006427 | -0.025636 | -0.0064257 | 2.0149e-06 | 1.2451e-06 | 0.038968 | 0.038968 | 0.038968 | 0.97901 | -0.40407 | 0.97893 | -0.40572 | 10.7056
139 | 0.01272 | 0.0031886 | -0.012718 | -0.0031873 | 2.1998e-06 | 1.2106e-06 | 0.019335 | 0.019335 | 0.019335 | 0.97893 | -0.40572 | 0.97875 | -0.40935 | 5.3118

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47499 | 0.12196

## res_load
| p_mw | q_mvar
0 | 0.0096564 | 0.0024201
1 | 0.0056803 | 0.0014236
2 | 0.0096594 | 0.0024209
3 | 0.0066781 | 0.0016737
4 | 0.0052342 | 0.0013118
5 | 0.0036118 | 0.00090519
6 | 0.0043436 | 0.0010886
7 | 0.0026108 | 0.00065432
8 | 0.0031115 | 0.00077982
9 | 0.0072209 | 0.0018097
10 | 0.0015305 | 0.00038358
11 | 0.010813 | 0.0027099
12 | 0.0046072 | 0.0011547
13 | 0.0016713 | 0.00041886
14 | 0.0061882 | 0.0015509
15 | 0.0092541 | 0.0023193
16 | 0.0086853 | 0.0021767
17 | 0.0049001 | 0.0012281
18 | 0.0041678 | 0.0010446
19 | 0.0083718 | 0.0020982
20 | 0.0040145 | 0.0010061
21 | 0.0019575 | 0.00049058
22 | 0.0060072 | 0.0015056
23 | 0.0017638 | 0.00044205
24 | 0.0066847 | 0.0016753
25 | 0.0046963 | 0.001177
26 | 0.0064301 | 0.0016115
27 | 0.0031091 | 0.0007792
28 | 0.0042886 | 0.0010748
29 | 0.0047068 | 0.0011796
30 | 0.0032957 | 0.00082599
31 | 0.0048483 | 0.0012151
32 | 0.0045111 | 0.0011306
33 | 0.0048672 | 0.0012198
34 | 0.0023181 | 0.00058096
35 | 0.0044249 | 0.001109
36 | 0.006924 | 0.0017353
37 | 0.002061 | 0.00051654
38 | 0.0098563 | 0.0024702
39 | 0.010447 | 0.0026183
40 | 0.0052326 | 0.0013114
41 | 0.00038189 | 9.5709e-05
42 | 0.0031759 | 0.00079596
43 | 0.0014338 | 0.00035934
44 | 0.005015 | 0.0012569
45 | 0.0019368 | 0.00048541
46 | 0.0008976 | 0.00022496
47 | 0.0023712 | 0.00059429
48 | 0.0014104 | 0.00035348
49 | 0.00093277 | 0.00023377
50 | 0.0035292 | 0.00088449
51 | 0.0018192 | 0.00045593
52 | 0.00058745 | 0.00014723
53 | 0.0019111 | 0.00047896
54 | 0.0017468 | 0.00043779
55 | 0.002211 | 0.00055413
56 | 0.0045957 | 0.0011518
57 | 0.00062735 | 0.00015723
58 | 0.0034479 | 0.00086412
59 | 0.00070164 | 0.00017585
60 | 0.0028712 | 0.0007196
61 | 0.00083994 | 0.00021051
62 | 0.00096046 | 0.00024071
63 | 0.0021737 | 0.00054478
64 | 0.00077801 | 0.00019499
65 | 0.0023252 | 0.00058275
66 | 0.00072807 | 0.00018247
67 | 0.0066593 | 0.001669
68 | 0.0027359 | 0.00068569
69 | 0.017218 | 0.0043154
70 | 0.0041847 | 0.0010488
71 | 0.0033687 | 0.00084428
72 | 0.011232 | 0.0028151
73 | 0.002067 | 0.00051805
74 | 0.01984 | 0.0049724
75 | 0.0021933 | 0.00054969
76 | 0.0023252 | 0.00058276
77 | 0.0045753 | 0.0011467
78 | 0.006491 | 0.0016268
79 | 0.0032639 | 0.00081801
80 | 0.0014824 | 0.00037154
81 | 0.002657 | 0.0006659
82 | 0.0018923 | 0.00047424
83 | 0.0013305 | 0.00033345
84 | 0.0022168 | 0.00055558
85 | 0.002213 | 0.00055464
86 | 0.0051377 | 0.0012876
87 | 0.0084456 | 0.0021167
88 | 0.0076049 | 0.001906
89 | 0.014838 | 0.0037187
90 | 0.005531 | 0.0013862
91 | 0.015833 | 0.003968
92 | 0.0016768 | 0.00042024
93 | 0.0010693 | 0.000268
94 | 0.00096944 | 0.00024297
95 | 0.0015353 | 0.00038479
96 | 0.00058082 | 0.00014557
97 | 0.00031134 | 7.8028e-05
98 | 0.00025558 | 6.4054e-05
99 | 0.001127 | 0.00028245
100 | 0.006271 | 0.0015717
101 | 0.012916 | 0.0032372
102 | 0.012718 | 0.0031873

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1