## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_177-25_1_1_node_134 | 0.4 | n |  | TRUE
1 | bus_LV_177-25_1_1_node_135 | 0.4 | n |  | TRUE
2 | bus_LV_177-25_1_1_node_136 | 0.4 | n |  | TRUE
3 | bus_LV_177-25_1_1_node_336 | 0.4 | n |  | TRUE
4 | bus_LV_177-25_1_1_node_137 | 0.4 | n |  | TRUE
5 | bus_LV_177-25_1_1_node_138 | 0.4 | n |  | TRUE
6 | bus_LV_177-25_1_1_node_290 | 0.4 | n |  | TRUE
7 | bus_LV_177-25_1_1_node_291 | 0.4 | n |  | TRUE
8 | bus_LV_177-25_1_1_node_323 | 0.4 | n |  | TRUE
9 | bus_LV_177-25_1_1_node_292 | 0.4 | n |  | TRUE
10 | bus_LV_177-25_1_1_node_293 | 0.4 | n |  | TRUE
11 | bus_LV_177-25_1_1_node_316 | 0.4 | n |  | TRUE
12 | bus_LV_177-25_1_1_node_295 | 0.4 | n |  | TRUE
13 | bus_LV_177-25_1_1_node_335 | 0.4 | n |  | TRUE
14 | bus_LV_177-25_1_1_node_300 | 0.4 | n |  | TRUE
15 | bus_LV_177-25_1_1_node_301 | 0.4 | n |  | TRUE
16 | bus_LV_177-25_1_1_node_302 | 0.4 | n |  | TRUE
17 | bus_LV_177-25_1_1_node_303 | 0.4 | n |  | TRUE
18 | bus_LV_177-25_1_1_node_304 | 0.4 | n |  | TRUE
19 | bus_LV_177-25_1_1_node_305 | 0.4 | n |  | TRUE
20 | bus_LV_177-25_1_1_node_306 | 0.4 | n |  | TRUE
21 | bus_LV_177-25_1_1_node_314 | 0.4 | n |  | TRUE
22 | bus_LV_177-25_1_1_node_307 | 0.4 | n |  | TRUE
23 | bus_LV_177-25_1_1_node_308 | 0.4 | n |  | TRUE
24 | bus_LV_177-25_1_1_node_309 | 0.4 | n |  | TRUE
25 | bus_LV_177-25_1_1_node_310 | 0.4 | n |  | TRUE
26 | bus_LV_177-25_1_1_node_311 | 0.4 | n |  | TRUE
27 | bus_LV_177-25_1_1_node_312 | 0.4 | n |  | TRUE
28 | bus_LV_177-25_1_1_node_313 | 0.4 | n |  | TRUE
29 | bus_LV_177-25_1_1_node_315 | 0.4 | n |  | TRUE
30 | bus_LV_177-25_1_1_node_319 | 0.4 | n |  | TRUE
31 | bus_LV_177-25_1_1_node_187 | 0.4 | n |  | TRUE
32 | bus_LV_177-25_1_1_node_188 | 0.4 | n |  | TRUE
33 | bus_LV_177-25_1_1_node_189 | 0.4 | n |  | TRUE
34 | bus_LV_177-25_1_1_node_190 | 0.4 | n |  | TRUE
35 | bus_LV_177-25_1_1_node_191 | 0.4 | n |  | TRUE
36 | bus_LV_177-25_1_1_node_192 | 0.4 | n |  | TRUE
37 | bus_LV_177-25_1_1_node_193 | 0.4 | n |  | TRUE
38 | bus_LV_177-25_1_1_node_194 | 0.4 | n |  | TRUE
39 | bus_LV_177-25_1_1_node_239 | 0.4 | n |  | TRUE
40 | bus_LV_177-25_1_1_node_338 | 0.4 | n |  | TRUE
41 | bus_LV_177-25_1_1_node_249 | 0.4 | n |  | TRUE
42 | bus_LV_177-25_1_1_node_195 | 0.4 | n |  | TRUE
43 | bus_LV_177-25_1_1_node_337 | 0.4 | n |  | TRUE
44 | bus_LV_177-25_1_1_node_317 | 0.4 | n |  | TRUE
45 | bus_LV_177-25_1_1_node_318 | 0.4 | n |  | TRUE
46 | bus_LV_177-25_1_1_node_320 | 0.4 | n |  | TRUE
47 | bus_LV_177-25_1_1_node_321 | 0.4 | n |  | TRUE
48 | bus_LV_177-25_1_1_node_322 | 0.4 | n |  | TRUE
49 | bus_LV_177-25_1_1_node_325 | 0.4 | n |  | TRUE
50 | bus_LV_177-25_1_1_node_324 | 0.4 | n |  | TRUE
51 | bus_LV_177-25_1_1_node_326 | 0.4 | n |  | TRUE
52 | bus_LV_177-25_1_1_node_341 | 0.4 | n |  | TRUE
53 | bus_LV_177-25_1_1_node_327 | 0.4 | n |  | TRUE
54 | bus_LV_177-25_1_1_node_328 | 0.4 | n |  | TRUE
55 | bus_LV_177-25_1_1_node_329 | 0.4 | n |  | TRUE
56 | bus_LV_177-25_1_1_node_330 | 0.4 | n |  | TRUE
57 | bus_LV_177-25_1_1_node_331 | 0.4 | n |  | TRUE
58 | bus_LV_177-25_1_1_node_332 | 0.4 | n |  | TRUE
59 | bus_LV_177-25_1_1_node_333 | 0.4 | n |  | TRUE
60 | bus_LV_177-25_1_1_node_334 | 0.4 | n |  | TRUE
61 | bus_LV_177-25_1_1_node_233 | 0.4 | n |  | TRUE
62 | bus_LV_177-25_1_1_node_235 | 0.4 | n |  | TRUE
63 | bus_LV_177-25_1_1_node_237 | 0.4 | n |  | TRUE
64 | bus_LV_177-25_1_1_node_238 | 0.4 | n |  | TRUE
65 | bus_LV_177-25_1_1_node_240 | 0.4 | n |  | TRUE
66 | bus_MV_6_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_177-25_1_1_load_134 | 0 | 0.00061049 | 0.000153 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_177-25_1_1_load_336 | 3 | 0.0080803 | 0.0020251 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_177-25_1_1_load_137 | 4 | 0.00015175 | 3.8033e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_177-25_1_1_load_138 | 5 | 0.0001543 | 3.8672e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_177-25_1_1_load_290 | 6 | 0.0062536 | 0.0015673 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_177-25_1_1_load_291 | 7 | 0.0024724 | 0.00061964 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_177-25_1_1_load_292 | 9 | 0.00053543 | 0.00013419 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_177-25_1_1_load_293 | 10 | 0.00076646 | 0.00019209 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_177-25_1_1_load_316 | 11 | 0.0044547 | 0.0011165 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_177-25_1_1_load_295 | 12 | 0.019684 | 0.0049332 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_177-25_1_1_load_335 | 13 | 0.0052159 | 0.0013072 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_177-25_1_1_load_300 | 14 | 0.000522 | 0.00013082 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_177-25_1_1_load_301 | 15 | 0.0016566 | 0.00041519 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_177-25_1_1_load_303 | 17 | 0.0018827 | 0.00047185 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_177-25_1_1_load_304 | 18 | 0.00088545 | 0.00022191 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_177-25_1_1_load_305 | 19 | 0.0010191 | 0.00025541 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_177-25_1_1_load_314 | 21 | 0.00063097 | 0.00015814 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_177-25_1_1_load_307 | 22 | 0.0009607 | 0.00024077 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_177-25_1_1_load_308 | 23 | 0.00095451 | 0.00023922 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_177-25_1_1_load_310 | 25 | 0.00051027 | 0.00012789 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_177-25_1_1_load_311 | 26 | 0.0016539 | 0.0004145 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_177-25_1_1_load_312 | 27 | 0.00064742 | 0.00016226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_177-25_1_1_load_313 | 28 | 0.0010824 | 0.00027127 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_177-25_1_1_load_315 | 29 | 0.00061832 | 0.00015497 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_177-25_1_1_load_319 | 30 | 0.0014305 | 0.00035851 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_177-25_1_1_load_187 | 31 | 0.0016269 | 0.00040773 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_177-25_1_1_load_188 | 32 | 0.0040817 | 0.001023 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_177-25_1_1_load_190 | 34 | 0.00055343 | 0.0001387 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_177-25_1_1_load_192 | 36 | 0.00087517 | 0.00021934 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_177-25_1_1_load_193 | 37 | 0.0012013 | 0.00030107 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_177-25_1_1_load_239 | 39 | 0.00045705 | 0.00011455 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_177-25_1_1_load_338 | 40 | 0.00089601 | 0.00022456 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_177-25_1_1_load_249 | 41 | 0.0015629 | 0.0003917 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_177-25_1_1_load_337 | 43 | 0.00052406 | 0.00013134 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_177-25_1_1_load_320 | 46 | 0.0045543 | 0.0011414 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_177-25_1_1_load_321 | 47 | 0.0035393 | 0.00088704 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_177-25_1_1_load_322 | 48 | 0.0011379 | 0.00028518 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_177-25_1_1_load_325 | 49 | 0.0010985 | 0.00027531 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_177-25_1_1_load_324 | 50 | 0.0076956 | 0.0019287 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_177-25_1_1_load_341 | 52 | 0.0013376 | 0.00033524 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_177-25_1_1_load_327 | 53 | 0.0013071 | 0.00032759 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_177-25_1_1_load_328 | 54 | 0.00066666 | 0.00016708 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_177-25_1_1_load_329 | 55 | 0.00060476 | 0.00015157 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_177-25_1_1_load_330 | 56 | 0.00050442 | 0.00012642 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_177-25_1_1_load_331 | 57 | 0.00051895 | 0.00013006 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_177-25_1_1_load_332 | 58 | 0.00084099 | 0.00021077 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_177-25_1_1_load_333 | 59 | 0.0011183 | 0.00028026 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_177-25_1_1_load_334 | 60 | 0.0026923 | 0.00067476 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_177-25_1_1_load_233 | 61 | 0.00045051 | 0.00011291 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_177-25_1_1_load_237 | 63 | 0.00069071 | 0.00017311 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_177-25_1_1_load_238 | 64 | 0.00068139 | 0.00017077 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_177-25_1_1_load_240 | 65 | 0.0038522 | 0.00096544 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_177-25_1_1_line_0 |  | 0 | 1 | 0.0037038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_177-25_1_1_line_1 |  | 0 | 2 | 0.015029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_177-25_1_1_line_2 |  | 1 | 3 | 0.38464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_177-25_1_1_line_3 |  | 2 | 4 | 0.010944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_177-25_1_1_line_4 |  | 3 | 51 | 0.22628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_177-25_1_1_line_5 |  | 4 | 5 | 0.0046006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_177-25_1_1_line_6 |  | 6 | 7 | 0.14812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_177-25_1_1_line_7 |  | 6 | 8 | 0.1885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_177-25_1_1_line_8 |  | 7 | 9 | 0.0020031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_177-25_1_1_line_9 |  | 8 | 50 | 0.0006402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_177-25_1_1_line_10 |  | 9 | 10 | 0.011443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_177-25_1_1_line_11 |  | 10 | 11 | 0.0079014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_177-25_1_1_line_12 |  | 11 | 44 | 0.022352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_177-25_1_1_line_13 |  | 12 | 13 | 0.019036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_177-25_1_1_line_14 |  | 13 | 51 | 0.058377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_177-25_1_1_line_15 |  | 14 | 15 | 0.0028367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_177-25_1_1_line_16 |  | 14 | 16 | 0.015413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_177-25_1_1_line_17 |  | 15 | 17 | 0.004362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_177-25_1_1_line_18 |  | 16 | 18 | 0.011506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_177-25_1_1_line_19 |  | 16 | 19 | 0.025955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_177-25_1_1_line_20 |  | 17 | 20 | 0.048427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_177-25_1_1_line_21 |  | 20 | 21 | 0.026823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_177-25_1_1_line_22 |  | 21 | 26 | 0.024975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_177-25_1_1_line_23 |  | 22 | 23 | 0.013185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_177-25_1_1_line_24 |  | 22 | 24 | 0.0043437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_177-25_1_1_line_25 |  | 23 | 25 | 0.0035328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_177-25_1_1_line_26 |  | 24 | 26 | 0.13314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_177-25_1_1_line_27 |  | 24 | 27 | 0.02514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_177-25_1_1_line_28 |  | 25 | 28 | 0.00063392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_177-25_1_1_line_29 |  | 27 | 29 | 0.0038602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_177-25_1_1_line_30 |  | 28 | 30 | 0.00080191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_177-25_1_1_line_31 |  | 29 | 42 | 0.0096845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_177-25_1_1_line_32 |  | 30 | 44 | 0.015412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_177-25_1_1_line_33 |  | 31 | 32 | 0.029428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_177-25_1_1_line_34 |  | 31 | 33 | 0.025676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_177-25_1_1_line_35 |  | 32 | 34 | 0.098875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_177-25_1_1_line_36 |  | 33 | 35 | 0.11978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_177-25_1_1_line_37 |  | 34 | 36 | 0.033811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_177-25_1_1_line_38 |  | 35 | 37 | 0.0050325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_177-25_1_1_line_39 |  | 35 | 38 | 0.028658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_177-25_1_1_line_40 |  | 36 | 39 | 0.10814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_177-25_1_1_line_41 |  | 37 | 40 | 0.0013525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_177-25_1_1_line_42 |  | 38 | 41 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_177-25_1_1_line_43 |  | 39 | 63 | 0.01208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_177-25_1_1_line_44 |  | 40 | 42 | 0.041013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_177-25_1_1_line_45 |  | 41 | 60 | 0.079657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_177-25_1_1_line_46 |  | 42 | 43 | 0.01225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_177-25_1_1_line_47 |  | 43 | 58 | 0.0045504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_177-25_1_1_line_48 |  | 44 | 45 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_177-25_1_1_line_49 |  | 45 | 46 | 0.011448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_177-25_1_1_line_50 |  | 46 | 47 | 0.0060311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_177-25_1_1_line_51 |  | 48 | 49 | 0.0025783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_177-25_1_1_line_52 |  | 49 | 52 | 0.0042806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_177-25_1_1_line_53 |  | 50 | 51 | 0.027258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_177-25_1_1_line_54 |  | 52 | 59 | 0.00031588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_177-25_1_1_line_55 |  | 53 | 54 | 0.0072822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_177-25_1_1_line_56 |  | 53 | 55 | 0.00088855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_177-25_1_1_line_57 |  | 54 | 56 | 0.0027757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_177-25_1_1_line_58 |  | 55 | 57 | 0.00073607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_177-25_1_1_line_59 |  | 56 | 58 | 0.0020043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_177-25_1_1_line_60 |  | 57 | 59 | 4.9268e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_177-25_1_1_line_61 |  | 61 | 62 | 0.01306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_177-25_1_1_line_62 |  | 62 | 63 | 0.0323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_177-25_1_1_line_63 |  | 62 | 64 | 0.16271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_177-25_1_1_line_64 |  | 64 | 65 | 0.0021141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_177-25_1_1_trafo_321 | 0.63 MVA 20/0.4 kV | 66 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2703730.4084 | 1244104.4095 | 2703729.6696 | 1244108.0389
1 | 2703725.9106 | 1244122.5784 | 2703727.1524 | 1244118.5637 | 2703728.6966 | 1244112.8195 | 2703729.6696 | 1244108.0389
2 | 2703730.4084 | 1244104.4095 | 2704080.7219 | 1243945.5646
3 | 2703725.9106 | 1244122.5784 | 2703723.2848 | 1244123.1774 | 2703719.4402 | 1244123.4549 | 2703715.1566 | 1244122.4681
4 | 2704190.9496 | 1244143.187 | 2704080.7219 | 1243945.5646
5 | 2703711.3623 | 1244119.8664 | 2703715.1566 | 1244122.4681
6 | 2704321.607 | 1244308.8125 | 2704321.4482 | 1244309.0655 | 2704277.4994 | 1244377.1908 | 2704269.6209 | 1244386.3706 | 2704263.0132 | 1244390.3354 | 2704253.6976 | 1244391.4058 | 2704244.0499 | 1244389.4459 | 2704234.4137 | 1244385.1065 | 2704228.4581 | 1244383.3672 | 2704222.2092 | 1244381.5449 | 2704217.7625 | 1244381.4517
7 | 2704321.607 | 1244308.8125 | 2704192.9852 | 1244171.0112
8 | 2704217.7625 | 1244381.4517 | 2704215.7599 | 1244381.4097
9 | 2704192.9384 | 1244170.3727 | 2704192.9852 | 1244171.0112
10 | 2704204.3803 | 1244382.3425 | 2704212.3492 | 1244381.3382 | 2704215.7599 | 1244381.4097
11 | 2704204.3803 | 1244382.3425 | 2704196.5409 | 1244383.3304
12 | 2704175.0977 | 1244388.8788 | 2704184.8591 | 1244384.8026 | 2704196.5409 | 1244383.3304
13 | 2704245.1387 | 1244123.9331 | 2704262.726 | 1244116.6505
14 | 2704190.9496 | 1244143.187 | 2704199.7019 | 1244143.2185 | 2704222.2677 | 1244130.9942 | 2704240.91 | 1244125.6842 | 2704245.1387 | 1244123.9331
15 | 2704280.3937 | 1244554.3093 | 2704278.1503 | 1244556.0454
16 | 2704292.5836 | 1244544.8762 | 2704280.3937 | 1244554.3093
17 | 2704274.7006 | 1244558.7149 | 2704278.1503 | 1244556.0454
18 | 2704292.5836 | 1244544.8762 | 2704303.708 | 1244541.9361
19 | 2704292.5836 | 1244544.8762 | 2704293.8175 | 1244529.7305 | 2704295.8758 | 1244519.1703
20 | 2704247.4771 | 1244597.2912 | 2704256.5062 | 1244588.8544 | 2704260.892 | 1244580.1357 | 2704263.9057 | 1244569.9362 | 2704269.9488 | 1244562.3921 | 2704274.7006 | 1244558.7149
21 | 2704247.4771 | 1244597.2912 | 2704240.3113 | 1244588.7364 | 2704235.5456 | 1244580.802 | 2704232.982 | 1244574.9291
22 | 2704222.9901 | 1244552.0396 | 2704232.982 | 1244574.9291
23 | 2704185.2038 | 1244420.4958 | 2704182.9448 | 1244407.5061
24 | 2704185.948 | 1244424.7752 | 2704185.2038 | 1244420.4958
25 | 2704182.0847 | 1244404.087 | 2704182.6873 | 1244406.0255 | 2704182.9448 | 1244407.5061
26 | 2704185.948 | 1244424.7752 | 2704192.7658 | 1244461.7461 | 2704197.0244 | 1244483.9161 | 2704204.9805 | 1244509.0088 | 2704212.4825 | 1244527.2548 | 2704217.3823 | 1244539.1725 | 2704217.7597 | 1244540.0576 | 2704222.9901 | 1244552.0396
27 | 2704185.948 | 1244424.7752 | 2704181.5369 | 1244425.465 | 2704161.3644 | 1244429.9948
28 | 2704182.0847 | 1244404.087 | 2704181.8966 | 1244403.4816
29 | 2704157.598 | 1244430.8406 | 2704161.3644 | 1244429.9948
30 | 2704181.8966 | 1244403.4816 | 2704181.6585 | 1244402.7159
31 | 2704148.1488 | 1244432.9624 | 2704157.598 | 1244430.8406
32 | 2704175.0977 | 1244388.8788 | 2704179.8687 | 1244396.9578 | 2704181.6585 | 1244402.7159
33 | 2703997.8911 | 1244579.4583 | 2704004.2411 | 1244581.0762 | 2704012.1639 | 1244578.8133 | 2704018.684 | 1244565.7106
34 | 2704032.578 | 1244544.8001 | 2704027.1118 | 1244548.7741 | 2704018.684 | 1244565.7106
35 | 2703961.3704 | 1244493.5621 | 2703963.5747 | 1244498.988 | 2703967.0459 | 1244513.0933 | 2703970.8455 | 1244529.595 | 2703977.9012 | 1244561.2545 | 2703981.638 | 1244570.5606 | 2703988.9138 | 1244577.1711 | 2703997.8911 | 1244579.4583
36 | 2704032.578 | 1244544.8001 | 2704033.1942 | 1244535.9596 | 2704035.7577 | 1244528.5654 | 2704043.9291 | 1244513.4302 | 2704053.7357 | 1244500.7367 | 2704064.0227 | 1244491.243 | 2704079.0615 | 1244480.1648 | 2704112.1526 | 1244462.8763
37 | 2703951.0016 | 1244461.7052 | 2703951.4313 | 1244469.0963 | 2703961.3704 | 1244493.5621
38 | 2704112.1526 | 1244462.8763 | 2704113.5495 | 1244462.0891 | 2704116.4981 | 1244460.3387
39 | 2704096.6056 | 1244443.922 | 2704102.1305 | 1244442.6401 | 2704108.1922 | 1244453.3994 | 2704108.0525 | 1244456.188 | 2704112.1526 | 1244462.8763
40 | 2703951.0016 | 1244461.7052 | 2703923.2842 | 1244462.2201 | 2703907.8551 | 1244467.1203 | 2703877.554 | 1244486.1157 | 2703867.4714 | 1244489.5641 | 2703858.1259 | 1244490.201 | 2703850.0376 | 1244487.7749
41 | 2704117.6611 | 1244459.6483 | 2704116.4981 | 1244460.3387
42 | 2704096.6056 | 1244443.922 | 2704089.8338 | 1244430.9819 | 2704089.7171 | 1244430.7399
43 | 2703840.1165 | 1244481.1908 | 2703847.1411 | 1244486.9061 | 2703850.0376 | 1244487.7749
44 | 2704148.1488 | 1244432.9624 | 2704143.847 | 1244439.9146 | 2704137.5725 | 1244445.1419 | 2704122.883 | 1244456.5485 | 2704117.6611 | 1244459.6483
45 | 2704101.4163 | 1244369.2479 | 2704072.4608 | 1244394.1928 | 2704071.7562 | 1244397.7277 | 2704072.7388 | 1244401.6035 | 2704082.0378 | 1244414.8214 | 2704089.7171 | 1244430.7399
46 | 2704148.1488 | 1244432.9624 | 2704144.3604 | 1244421.3131
47 | 2704144.3604 | 1244421.3131 | 2704142.9531 | 1244416.9857
48 | 2704168.6198 | 1244377.723 | 2704170.9821 | 1244381.7899 | 2704175.0977 | 1244388.8788
49 | 2704168.6198 | 1244377.723 | 2704165.3023 | 1244370.8038 | 2704164.1391 | 1244367.2134
50 | 2704164.1391 | 1244367.2134 | 2704163.6103 | 1244365.5811 | 2704162.8611 | 1244361.3313 | 2704162.8611 | 1244361.3313
51 | 2704146.8568 | 1244397.2097 | 2704145.7547 | 1244399.5406
52 | 2704143.9251 | 1244403.4104 | 2704145.7547 | 1244399.5406
53 | 2704190.9496 | 1244143.187 | 2704192.9384 | 1244170.3727
54 | 2704143.7901 | 1244403.696 | 2704143.9251 | 1244403.4104
55 | 2704143.0746 | 1244405.2093 | 2704142.2413 | 1244406.9717 | 2704142.3018 | 1244412.3041
56 | 2704143.0746 | 1244405.2093 | 2704143.4544 | 1244404.406
57 | 2704142.3018 | 1244412.3041 | 2704142.3332 | 1244415.0797 | 2704142.3332 | 1244415.0797
58 | 2704143.4544 | 1244404.406 | 2704143.769 | 1244403.7405
59 | 2704142.9531 | 1244416.9857 | 2704142.3332 | 1244415.0797
60 | 2704143.769 | 1244403.7405 | 2704143.7901 | 1244403.696
61 | 2703814.2017 | 1244461.9212 | 2703801.8457 | 1244457.6905
62 | 2703814.2017 | 1244461.9212 | 2703835.7992 | 1244477.6782 | 2703840.1165 | 1244481.1908
63 | 2703814.2017 | 1244461.9212 | 2703850.5816 | 1244405.7028 | 2703863.2525 | 1244388.2665 | 2703877.5102 | 1244372.148 | 2703882.9656 | 1244366.6392 | 2703887.4593 | 1244362.0921 | 2703914.6141 | 1244334.7598
64 | 2703914.6141 | 1244334.7598 | 2703916.1041 | 1244333.2601

## bus_geodata
| x | y | coords
0 | 2703729.6696 | 1244108.0389
1 | 2703730.4084 | 1244104.4095
2 | 2703725.9106 | 1244122.5784
3 | 2704080.7219 | 1243945.5645
4 | 2703715.1566 | 1244122.4681
5 | 2703711.3623 | 1244119.8664
6 | 2704321.607 | 1244308.8125
7 | 2704217.7625 | 1244381.4517
8 | 2704192.9852 | 1244171.0112
9 | 2704215.7599 | 1244381.4097
10 | 2704204.3803 | 1244382.3425
11 | 2704196.5409 | 1244383.3304
12 | 2704262.726 | 1244116.6505
13 | 2704245.1387 | 1244123.9331
14 | 2704280.3937 | 1244554.3093
15 | 2704278.1503 | 1244556.0454
16 | 2704292.5836 | 1244544.8762
17 | 2704274.7006 | 1244558.7149
18 | 2704303.708 | 1244541.9361
19 | 2704295.8758 | 1244519.1703
20 | 2704247.4771 | 1244597.2912
21 | 2704232.982 | 1244574.9291
22 | 2704185.2038 | 1244420.4958
23 | 2704182.9448 | 1244407.5061
24 | 2704185.948 | 1244424.7752
25 | 2704182.0847 | 1244404.087
26 | 2704222.9902 | 1244552.0396
27 | 2704161.3644 | 1244429.9948
28 | 2704181.8966 | 1244403.4816
29 | 2704157.598 | 1244430.8406
30 | 2704181.6585 | 1244402.7159
31 | 2704018.684 | 1244565.7106
32 | 2703997.8911 | 1244579.4583
33 | 2704032.578 | 1244544.8001
34 | 2703961.3704 | 1244493.5621
35 | 2704112.1526 | 1244462.8763
36 | 2703951.0016 | 1244461.7052
37 | 2704116.4981 | 1244460.3387
38 | 2704096.6056 | 1244443.922
39 | 2703850.0376 | 1244487.7749
40 | 2704117.6611 | 1244459.6484
41 | 2704089.7171 | 1244430.7399
42 | 2704148.1488 | 1244432.9624
43 | 2704144.3604 | 1244421.3131
44 | 2704175.0977 | 1244388.8788
45 | 2704168.6198 | 1244377.723
46 | 2704164.1391 | 1244367.2134
47 | 2704162.8611 | 1244361.3313
48 | 2704146.8568 | 1244397.2097
49 | 2704145.7547 | 1244399.5406
50 | 2704192.9384 | 1244170.3727
51 | 2704190.9496 | 1244143.187
52 | 2704143.9251 | 1244403.4104
53 | 2704143.0746 | 1244405.2093
54 | 2704142.3018 | 1244412.3041
55 | 2704143.4544 | 1244404.406
56 | 2704142.3332 | 1244415.0797
57 | 2704143.769 | 1244403.7405
58 | 2704142.9531 | 1244416.9857
59 | 2704143.7901 | 1244403.696
60 | 2704101.4163 | 1244369.2479
61 | 2703801.8457 | 1244457.6905
62 | 2703814.2017 | 1244461.9212
63 | 2703840.1165 | 1244481.1908
64 | 2703914.6141 | 1244334.7598
65 | 2703916.1041 | 1244333.2601
66 | 2704168.6198 | 1244377.723

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9781 | -0.4222 | 0.00061049 | 0.000153
1 | 0.9781 | -0.42214 | 0 | 0
2 | 0.9781 | -0.42229 | 0 | 0
3 | 0.97843 | -0.41567 | 0.0080803 | 0.0020251
4 | 0.97809 | -0.42235 | 0.00015175 | 3.8033e-05
5 | 0.97809 | -0.42236 | 0.0001543 | 3.8672e-05
6 | 0.98846 | -0.22038 | 0.0062536 | 0.0015673
7 | 0.99502 | -0.094705 | 0.0024724 | 0.00061964
8 | 0.9812 | -0.36137 | 0 | 0
9 | 0.99511 | -0.092929 | 0.00053543 | 0.00013419
10 | 0.99565 | -0.082685 | 0.00076646 | 0.00019209
11 | 0.99603 | -0.075512 | 0.0044547 | 0.0011165
12 | 0.97862 | -0.41182 | 0.019684 | 0.0049332
13 | 0.97897 | -0.40501 | 0.0052159 | 0.0013072
14 | 0.99417 | -0.1117 | 0.000522 | 0.00013082
15 | 0.99418 | -0.11158 | 0.0016566 | 0.00041519
16 | 0.99414 | -0.11222 | 0 | 0
17 | 0.99419 | -0.11127 | 0.0018827 | 0.00047185
18 | 0.99414 | -0.1124 | 0.00088545 | 0.00022191
19 | 0.99412 | -0.11269 | 0.0010191 | 0.00025541
20 | 0.99446 | -0.10617 | 0 | 0
21 | 0.9946 | -0.10335 | 0.00063097 | 0.00015814
22 | 0.99591 | -0.078134 | 0.0009607 | 0.00024077
23 | 0.99639 | -0.068918 | 0.00095451 | 0.00023922
24 | 0.99575 | -0.081099 | 0 | 0
25 | 0.99652 | -0.06639 | 0.00051027 | 0.00012789
26 | 0.99475 | -0.10045 | 0.0016539 | 0.0004145
27 | 0.99505 | -0.09462 | 0.00064742 | 0.00016226
28 | 0.99654 | -0.065931 | 0.0010824 | 0.00027127
29 | 0.99495 | -0.096654 | 0.00061832 | 0.00015497
30 | 0.99657 | -0.065335 | 0.0014305 | 0.00035851
31 | 0.99208 | -0.15203 | 0.0016269 | 0.00040773
32 | 0.99177 | -0.15811 | 0.0040817 | 0.001023
33 | 0.9924 | -0.14599 | 0 | 0
34 | 0.99109 | -0.17139 | 0.00055343 | 0.0001387
35 | 0.99385 | -0.11786 | 0 | 0
36 | 0.99087 | -0.1756 | 0.00087517 | 0.00021934
37 | 0.99393 | -0.11631 | 0.0012013 | 0.00030107
38 | 0.99374 | -0.12002 | 0 | 0
39 | 0.99026 | -0.18739 | 0.00045705 | 0.00011455
40 | 0.99395 | -0.11586 | 0.00089601 | 0.00022456
41 | 0.99368 | -0.12114 | 0.0015629 | 0.0003917
42 | 0.99469 | -0.10165 | 0 | 0
43 | 0.99458 | -0.10374 | 0.00052406 | 0.00013134
44 | 0.99719 | -0.053502 | 0 | 0
45 | 0.99837 | -0.030959 | 0 | 0
46 | 0.99942 | -0.010985 | 0.0045543 | 0.0011414
47 | 1 | 0 | -0.10719 | -0.026881
48 | 0.99444 | -0.10646 | 0.0011379 | 0.00028518
49 | 0.99444 | -0.10641 | 0.0010985 | 0.00027531
50 | 0.98117 | -0.36185 | 0.0076956 | 0.0019287
51 | 0.98032 | -0.3786 | 0 | 0
52 | 0.99445 | -0.10624 | 0.0013376 | 0.00033524
53 | 0.99446 | -0.10606 | 0.0013071 | 0.00032759
54 | 0.99451 | -0.10514 | 0.00066666 | 0.00016708
55 | 0.99446 | -0.10615 | 0.00060476 | 0.00015157
56 | 0.99453 | -0.10476 | 0.00050442 | 0.00012642
57 | 0.99445 | -0.10622 | 0.00051895 | 0.00013006
58 | 0.99454 | -0.10447 | 0.00084099 | 0.00021077
59 | 0.99445 | -0.10622 | 0.0011183 | 0.00028026
60 | 0.99348 | -0.12492 | 0.0026923 | 0.00067476
61 | 0.99005 | -0.19158 | 0.00045051 | 0.00011291
62 | 0.99005 | -0.19148 | 0 | 0
63 | 0.9902 | -0.18861 | 0.00069071 | 0.00017311
64 | 0.98938 | -0.20461 | 0.00068139 | 0.00017077
65 | 0.98937 | -0.20476 | 0.0038522 | 0.00096544
66 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00091655 | -0.00022933 | 0.00091655 | 0.00022928 | 2.6999e-09 | -4.4759e-08 | 0.0013942 | 0.0013942 | 0.0013942 | 0.9781 | -0.4222 | 0.9781 | -0.42214 | 0.38303
1 | 0.00030606 | 7.6323e-05 | -0.00030606 | -7.6511e-05 | 1.2213e-09 | -1.8785e-07 | 0.00046548 | 0.00046555 | 0.00046555 | 0.9781 | -0.4222 | 0.9781 | -0.42229 | 0.1279
2 | -0.00091655 | -0.00022928 | 0.00091683 | 0.00022463 | 2.8004e-07 | -4.6501e-06 | 0.0013942 | 0.0013925 | 0.0013942 | 0.9781 | -0.42214 | 0.97843 | -0.41567 | 0.38303
3 | 0.00030606 | 7.6511e-05 | -0.00030606 | -7.6647e-05 | 8.8953e-10 | -1.3678e-07 | 0.00046555 | 0.0004656 | 0.0004656 | 0.9781 | -0.42229 | 0.97809 | -0.42235 | 0.12791
4 | -0.0089971 | -0.0022497 | 0.009013 | 0.002257 | 1.5882e-05 | 7.3168e-06 | 0.013681 | 0.01368 | 0.013681 | 0.97843 | -0.41567 | 0.98032 | -0.3786 | 3.7585
5 | 0.0001543 | 3.8614e-05 | -0.0001543 | -3.8672e-05 | 9.5062e-11 | -5.768e-08 | 0.00023473 | 0.00023475 | 0.00023475 | 0.97809 | -0.42235 | 0.97809 | -0.42236 | 0.064491
6 | -0.04821 | -0.012213 | 0.048503 | 0.012398 | 0.00029294 | 0.00018557 | 0.072621 | 0.072621 | 0.072621 | 0.98846 | -0.22038 | 0.99502 | -0.094705 | 19.9509
7 | 0.041956 | 0.010645 | -0.041674 | -0.010467 | 0.00028241 | 0.00017835 | 0.063207 | 0.063208 | 0.063208 | 0.98846 | -0.22038 | 0.9812 | -0.36137 | 17.3649
8 | -0.050975 | -0.013018 | 0.05098 | 0.013021 | 4.3751e-06 | 2.774e-06 | 0.076318 | 0.076318 | 0.076318 | 0.99502 | -0.094705 | 0.99511 | -0.092929 | 20.9665
9 | 0.041674 | 0.010467 | -0.041673 | -0.010466 | 9.5917e-07 | 6.0578e-07 | 0.063208 | 0.063208 | 0.063208 | 0.9812 | -0.36137 | 0.98117 | -0.36185 | 17.3649
10 | -0.051515 | -0.013155 | 0.051541 | 0.013171 | 2.5521e-05 | 1.6185e-05 | 0.077119 | 0.077119 | 0.077119 | 0.99511 | -0.092929 | 0.99565 | -0.082685 | 21.1864
11 | -0.052307 | -0.013363 | 0.052325 | 0.013375 | 1.8149e-05 | 1.1513e-05 | 0.078264 | 0.078264 | 0.078264 | 0.99565 | -0.082685 | 0.99603 | -0.075512 | 21.5011
12 | -0.05678 | -0.014491 | 0.056841 | 0.014529 | 6.0446e-05 | 3.8394e-05 | 0.084919 | 0.084919 | 0.084919 | 0.99603 | -0.075512 | 0.99719 | -0.053502 | 23.3294
13 | -0.019684 | -0.0049332 | 0.01969 | 0.0049371 | 6.3943e-06 | 3.8531e-06 | 0.02993 | 0.029929 | 0.02993 | 0.97862 | -0.41182 | 0.97897 | -0.40501 | 8.2224
14 | -0.024906 | -0.0062443 | 0.024937 | 0.0062636 | 3.1374e-05 | 1.9345e-05 | 0.037857 | 0.037857 | 0.037857 | 0.97897 | -0.40501 | 0.98032 | -0.3786 | 10.4004
15 | -0.0024266 | -0.00060751 | 0.0024266 | 0.00060748 | 1.4031e-08 | -2.7804e-08 | 0.0036318 | 0.0036318 | 0.0036318 | 0.99417 | -0.1117 | 0.99418 | -0.11158 | 0.99774
16 | 0.0019046 | 0.00047669 | -0.0019046 | -0.00047686 | 4.6966e-08 | -1.698e-07 | 0.0028505 | 0.0028506 | 0.0028506 | 0.99417 | -0.1117 | 0.99414 | -0.11222 | 0.78312
17 | -0.0040832 | -0.0010227 | 0.0040833 | 0.0010227 | 6.1092e-08 | -1.7464e-08 | 0.0061113 | 0.0061113 | 0.0061113 | 0.99418 | -0.11158 | 0.99419 | -0.11127 | 1.6789
18 | 0.00088545 | 0.00022177 | -0.00088545 | -0.00022191 | 7.5788e-09 | -1.4434e-07 | 0.0013253 | 0.0013253 | 0.0013253 | 0.99414 | -0.11222 | 0.99414 | -0.1124 | 0.3641
19 | 0.0010191 | 0.00025509 | -0.0010191 | -0.00025541 | 2.2645e-08 | -3.2203e-07 | 0.0015253 | 0.0015254 | 0.0015254 | 0.99414 | -0.11222 | 0.99412 | -0.11269 | 0.41906
20 | -0.005966 | -0.0014945 | 0.0059675 | 0.0014948 | 1.4479e-06 | 2.9849e-07 | 0.0089291 | 0.0089289 | 0.0089291 | 0.99419 | -0.11127 | 0.99446 | -0.10617 | 2.4531
21 | -0.0059675 | -0.0014948 | 0.0059683 | 0.001495 | 8.0192e-07 | 1.6517e-07 | 0.0089289 | 0.0089288 | 0.0089289 | 0.99446 | -0.10617 | 0.9946 | -0.10335 | 2.453
22 | -0.0065993 | -0.0016531 | 0.0066002 | 0.0016534 | 9.1289e-07 | 2.6007e-07 | 0.0098728 | 0.0098727 | 0.0098728 | 0.9946 | -0.10335 | 0.99475 | -0.10045 | 2.7123
23 | -0.039861 | -0.010015 | 0.039878 | 0.010026 | 1.7542e-05 | 1.1056e-05 | 0.059566 | 0.059566 | 0.059566 | 0.99591 | -0.078134 | 0.99639 | -0.068918 | 16.3642
24 | 0.0389 | 0.009774 | -0.038894 | -0.0097705 | 5.5042e-06 | 3.4662e-06 | 0.05813 | 0.05813 | 0.05813 | 0.99591 | -0.078134 | 0.99575 | -0.081099 | 15.9699
25 | -0.040833 | -0.010265 | 0.040838 | 0.010268 | 4.9282e-06 | 3.108e-06 | 0.060991 | 0.060991 | 0.060991 | 0.99639 | -0.068918 | 0.99652 | -0.06639 | 16.7558
26 | 0.0082616 | 0.002071 | -0.008254 | -0.0020679 | 7.6107e-06 | 3.1407e-06 | 0.012346 | 0.012347 | 0.012347 | 0.99575 | -0.081099 | 0.99475 | -0.10045 | 3.3919
27 | 0.030633 | 0.0076995 | -0.030613 | -0.0076872 | 1.9762e-05 | 1.2321e-05 | 0.045784 | 0.045784 | 0.045784 | 0.99575 | -0.081099 | 0.99505 | -0.09462 | 12.5781
28 | -0.041348 | -0.010396 | 0.041349 | 0.010397 | 9.0652e-07 | 5.7192e-07 | 0.061753 | 0.061753 | 0.061753 | 0.99652 | -0.06639 | 0.99654 | -0.065931 | 16.9651
29 | 0.029966 | 0.0075249 | -0.029963 | -0.0075231 | 2.9075e-06 | 1.8106e-06 | 0.044816 | 0.044816 | 0.044816 | 0.99505 | -0.09462 | 0.99495 | -0.096654 | 12.3122
30 | -0.042431 | -0.010668 | 0.042432 | 0.010669 | 1.2076e-06 | 7.6239e-07 | 0.063369 | 0.063369 | 0.063369 | 0.99654 | -0.065931 | 0.99657 | -0.065335 | 17.4091
31 | 0.029344 | 0.0073681 | -0.029337 | -0.0073638 | 6.9963e-06 | 4.3519e-06 | 0.043891 | 0.043892 | 0.043892 | 0.99495 | -0.096654 | 0.99469 | -0.10165 | 12.0581
32 | -0.043863 | -0.011027 | 0.043888 | 0.011043 | 2.48e-05 | 1.5671e-05 | 0.065505 | 0.065505 | 0.065505 | 0.99657 | -0.065335 | 0.99719 | -0.053502 | 17.9959
33 | 0.011659 | 0.0029223 | -0.011656 | -0.0029205 | 3.3747e-06 | 1.78e-06 | 0.017487 | 0.017487 | 0.017487 | 0.99208 | -0.15203 | 0.99177 | -0.15811 | 4.8042
34 | -0.013286 | -0.00333 | 0.01329 | 0.0033321 | 3.8234e-06 | 2.1154e-06 | 0.019927 | 0.019927 | 0.019927 | 0.99208 | -0.15203 | 0.9924 | -0.14599 | 5.4746
35 | 0.0075739 | 0.0018975 | -0.0075692 | -0.0018957 | 4.788e-06 | 1.7893e-06 | 0.011363 | 0.011364 | 0.011364 | 0.99177 | -0.15811 | 0.99109 | -0.17139 | 3.1219
36 | -0.01329 | -0.0033321 | 0.013308 | 0.003342 | 1.7836e-05 | 9.8651e-06 | 0.019927 | 0.019927 | 0.019927 | 0.9924 | -0.14599 | 0.99385 | -0.11786 | 5.4745
37 | 0.0070157 | 0.001757 | -0.0070143 | -0.0017566 | 1.4067e-06 | 4.6467e-07 | 0.010533 | 0.010533 | 0.010533 | 0.99109 | -0.17139 | 0.99087 | -0.1756 | 2.8937
38 | -0.017564 | -0.0044076 | 0.017565 | 0.0044083 | 1.3053e-06 | 7.7015e-07 | 0.026299 | 0.026299 | 0.026299 | 0.99385 | -0.11786 | 0.99393 | -0.11631 | 7.225
39 | 0.0042564 | 0.0010656 | -0.0042559 | -0.0010657 | 4.364e-07 | -9.2025e-08 | 0.0063723 | 0.0063725 | 0.0063725 | 0.99385 | -0.11786 | 0.99374 | -0.12002 | 1.7507
40 | 0.0061392 | 0.0015372 | -0.0061357 | -0.0015364 | 3.4467e-06 | 8.1378e-07 | 0.0092189 | 0.0092193 | 0.0092193 | 0.99087 | -0.1756 | 0.99026 | -0.18739 | 2.5328
41 | -0.018767 | -0.0047094 | 0.018767 | 0.0047097 | 4.004e-07 | 2.3873e-07 | 0.028098 | 0.028098 | 0.028098 | 0.99393 | -0.11631 | 0.99395 | -0.11586 | 7.7191
42 | 0.0042559 | 0.0010657 | -0.0042557 | -0.0010657 | 2.265e-07 | -4.7724e-08 | 0.0063725 | 0.0063725 | 0.0063725 | 0.99374 | -0.12002 | 0.99368 | -0.12114 | 1.7507
43 | 0.0056787 | 0.0014219 | -0.0056783 | -0.0014218 | 3.298e-07 | 5.5676e-08 | 0.0085326 | 0.0085326 | 0.0085326 | 0.99026 | -0.18739 | 0.9902 | -0.18861 | 2.3441
44 | -0.019663 | -0.0049342 | 0.019676 | 0.0049422 | 1.3329e-05 | 7.9985e-06 | 0.029439 | 0.029439 | 0.029439 | 0.99395 | -0.11586 | 0.99469 | -0.10165 | 8.0876
45 | 0.0026928 | 0.00067404 | -0.0026923 | -0.00067476 | 4.8569e-07 | -7.2083e-07 | 0.0040321 | 0.0040325 | 0.0040325 | 0.99368 | -0.12114 | 0.99348 | -0.12492 | 1.1078
46 | 0.0096612 | 0.0024216 | -0.0096602 | -0.0024211 | 9.5955e-07 | 4.5512e-07 | 0.014453 | 0.014453 | 0.014453 | 0.99469 | -0.10165 | 0.99458 | -0.10374 | 3.9706
47 | 0.0091361 | 0.0022898 | -0.0091358 | -0.0022896 | 3.1882e-07 | 1.4499e-07 | 0.013669 | 0.013669 | 0.013669 | 0.99458 | -0.10374 | 0.99454 | -0.10447 | 3.7552
48 | -0.10073 | -0.025572 | 0.10084 | 0.025642 | 0.00010938 | 6.9837e-05 | 0.15042 | 0.15042 | 0.15042 | 0.99719 | -0.053502 | 0.99837 | -0.030959 | 41.3252
49 | -0.10084 | -0.025642 | 0.10093 | 0.025704 | 9.7135e-05 | 6.2017e-05 | 0.15042 | 0.15042 | 0.15042 | 0.99837 | -0.030959 | 0.99942 | -0.010985 | 41.3252
50 | -0.10549 | -0.026846 | 0.10554 | 0.026881 | 5.5893e-05 | 3.5693e-05 | 0.1572 | 0.1572 | 0.1572 | 0.99942 | -0.010985 | 1 | 0 | 43.188
51 | -0.0011379 | -0.00028518 | 0.0011379 | 0.00028515 | 2.803e-09 | -3.1657e-08 | 0.0017027 | 0.0017027 | 0.0017027 | 0.99444 | -0.10646 | 0.99444 | -0.10641 | 0.46777
52 | -0.0022364 | -0.00056046 | 0.0022364 | 0.00056042 | 1.7975e-08 | -4.4032e-08 | 0.0033464 | 0.0033463 | 0.0033464 | 0.99444 | -0.10641 | 0.99445 | -0.10624 | 0.91933
53 | 0.033977 | 0.0085377 | -0.03395 | -0.0085207 | 2.715e-05 | 1.7032e-05 | 0.051537 | 0.051537 | 0.051537 | 0.98117 | -0.36185 | 0.98032 | -0.3786 | 14.1586
54 | -0.003574 | -0.00089566 | 0.003574 | 0.00089565 | 3.3878e-09 | -1.9299e-09 | 0.0053479 | 0.0053479 | 0.0053479 | 0.99445 | -0.10624 | 0.99445 | -0.10622 | 1.4692
55 | -0.0071232 | -0.0017851 | 0.0071235 | 0.0017852 | 3.1023e-07 | 1.0406e-07 | 0.010658 | 0.010658 | 0.010658 | 0.99446 | -0.10606 | 0.99451 | -0.10514 | 2.9281
56 | 0.005816 | 0.0014576 | -0.005816 | -0.0014575 | 2.5235e-08 | 4.6221e-09 | 0.0087025 | 0.0087025 | 0.0087025 | 0.99446 | -0.10606 | 0.99446 | -0.10615 | 2.3908
57 | -0.0077901 | -0.0019523 | 0.0077903 | 0.0019524 | 1.4142e-07 | 5.4488e-08 | 0.011656 | 0.011656 | 0.011656 | 0.99451 | -0.10514 | 0.99453 | -0.10476 | 3.2022
58 | 0.0052113 | 0.001306 | -0.0052112 | -0.001306 | 1.6783e-08 | 1.1913e-09 | 0.0077976 | 0.0077976 | 0.0077976 | 0.99446 | -0.10615 | 0.99445 | -0.10622 | 2.1422
59 | -0.0082947 | -0.0020788 | 0.0082948 | 0.0020789 | 1.1577e-07 | 4.8081e-08 | 0.012411 | 0.012411 | 0.012411 | 0.99453 | -0.10476 | 0.99454 | -0.10447 | 3.4095
60 | 0.0046923 | 0.0011759 | -0.0046923 | -0.0011759 | 9.0959e-10 | -5.7449e-11 | 0.0070211 | 0.0070211 | 0.0070211 | 0.99445 | -0.10622 | 0.99445 | -0.10622 | 1.9289
61 | -0.00045051 | -0.00011291 | 0.00045052 | 0.00011274 | 2.2453e-09 | -1.6651e-07 | 0.00067711 | 0.00067705 | 0.00067711 | 0.99005 | -0.19158 | 0.99005 | -0.19148 | 0.18602
62 | -0.0049869 | -0.0012487 | 0.0049876 | 0.0012487 | 6.8037e-07 | 2.0011e-08 | 0.0074948 | 0.0074946 | 0.0074948 | 0.99005 | -0.19148 | 0.9902 | -0.18861 | 2.059
63 | 0.0045364 | 0.0011359 | -0.0045336 | -0.0011362 | 2.8364e-06 | -2.7563e-07 | 0.0068177 | 0.0068185 | 0.0068185 | 0.99005 | -0.19148 | 0.98938 | -0.20461 | 1.8732
64 | 0.0038522 | 0.00096543 | -0.0038522 | -0.00096544 | 2.6611e-08 | -1.0118e-08 | 0.0057937 | 0.0057937 | 0.0057937 | 0.98938 | -0.20461 | 0.98937 | -0.20476 | 1.5917

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.11073 | 0.027768

## res_load
| p_mw | q_mvar
0 | 0.00061049 | 0.000153
1 | 0.0080803 | 0.0020251
2 | 0.00015175 | 3.8033e-05
3 | 0.0001543 | 3.8672e-05
4 | 0.0062536 | 0.0015673
5 | 0.0024724 | 0.00061964
6 | 0.00053543 | 0.00013419
7 | 0.00076646 | 0.00019209
8 | 0.0044547 | 0.0011165
9 | 0.019684 | 0.0049332
10 | 0.0052159 | 0.0013072
11 | 0.000522 | 0.00013082
12 | 0.0016566 | 0.00041519
13 | 0.0018827 | 0.00047185
14 | 0.00088545 | 0.00022191
15 | 0.0010191 | 0.00025541
16 | 0.00063097 | 0.00015814
17 | 0.0009607 | 0.00024077
18 | 0.00095451 | 0.00023922
19 | 0.00051027 | 0.00012789
20 | 0.0016539 | 0.0004145
21 | 0.00064742 | 0.00016226
22 | 0.0010824 | 0.00027127
23 | 0.00061832 | 0.00015497
24 | 0.0014305 | 0.00035851
25 | 0.0016269 | 0.00040773
26 | 0.0040817 | 0.001023
27 | 0.00055343 | 0.0001387
28 | 0.00087517 | 0.00021934
29 | 0.0012013 | 0.00030107
30 | 0.00045705 | 0.00011455
31 | 0.00089601 | 0.00022456
32 | 0.0015629 | 0.0003917
33 | 0.00052406 | 0.00013134
34 | 0.0045543 | 0.0011414
35 | 0.0035393 | 0.00088704
36 | 0.0011379 | 0.00028518
37 | 0.0010985 | 0.00027531
38 | 0.0076956 | 0.0019287
39 | 0.0013376 | 0.00033524
40 | 0.0013071 | 0.00032759
41 | 0.00066666 | 0.00016708
42 | 0.00060476 | 0.00015157
43 | 0.00050442 | 0.00012642
44 | 0.00051895 | 0.00013006
45 | 0.00084099 | 0.00021077
46 | 0.0011183 | 0.00028026
47 | 0.0026923 | 0.00067476
48 | 0.00045051 | 0.00011291
49 | 0.00069071 | 0.00017311
50 | 0.00068139 | 0.00017077
51 | 0.0038522 | 0.00096544

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1