## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_177-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_177-5_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_177-5_0_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_177-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_177-5_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_177-5_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_177-5_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_177-5_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_177-5_0_4_node_82 | 0.4 | n |  | TRUE
9 | bus_LV_177-5_0_4_node_110 | 0.4 | n |  | TRUE
10 | bus_LV_177-5_0_4_node_84 | 0.4 | n |  | TRUE
11 | bus_LV_177-5_0_4_node_132 | 0.4 | n |  | TRUE
12 | bus_LV_177-5_0_4_node_68 | 0.4 | n |  | TRUE
13 | bus_LV_177-5_0_4_node_70 | 0.4 | n |  | TRUE
14 | bus_LV_177-5_0_4_node_85 | 0.4 | n |  | TRUE
15 | bus_LV_177-5_0_4_node_131 | 0.4 | n |  | TRUE
16 | bus_LV_177-5_0_4_node_126 | 0.4 | n |  | TRUE
17 | bus_LV_177-5_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_177-5_0_4_node_83 | 0.4 | n |  | TRUE
19 | bus_LV_177-5_0_4_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_177-5_0_4_node_111 | 0.4 | n |  | TRUE
21 | bus_LV_177-5_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_177-5_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_177-5_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_177-5_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_177-5_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_177-5_0_4_node_140 | 0.4 | n |  | TRUE
27 | bus_LV_177-5_0_4_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_177-5_0_4_node_139 | 0.4 | n |  | TRUE
29 | bus_LV_177-5_0_4_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_177-5_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_177-5_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_177-5_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_177-5_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_177-5_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_177-5_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_177-5_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_177-5_0_4_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_177-5_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_177-5_0_4_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_177-5_0_4_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_177-5_0_4_node_102 | 0.4 | n |  | TRUE
42 | bus_LV_177-5_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_177-5_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_177-5_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_177-5_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_177-5_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_177-5_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_177-5_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_177-5_0_4_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_177-5_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_177-5_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_177-5_0_4_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_177-5_0_4_node_61 | 0.4 | n |  | TRUE
54 | bus_LV_177-5_0_4_node_76 | 0.4 | n |  | TRUE
55 | bus_LV_177-5_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_177-5_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_177-5_0_4_node_69 | 0.4 | n |  | TRUE
58 | bus_LV_177-5_0_4_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_177-5_0_4_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_177-5_0_4_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_177-5_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_177-5_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_177-5_0_4_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_177-5_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_177-5_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_177-5_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_177-5_0_4_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_177-5_0_4_node_130 | 0.4 | n |  | TRUE
69 | bus_LV_177-5_0_4_node_94 | 0.4 | n |  | TRUE
70 | bus_LV_177-5_0_4_node_155 | 0.4 | n |  | TRUE
71 | bus_LV_177-5_0_4_node_143 | 0.4 | n |  | TRUE
72 | bus_LV_177-5_0_4_node_115 | 0.4 | n |  | TRUE
73 | bus_LV_177-5_0_4_node_92 | 0.4 | n |  | TRUE
74 | bus_LV_177-5_0_4_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_177-5_0_4_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_177-5_0_4_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_177-5_0_4_node_47 | 0.4 | n |  | TRUE
78 | bus_LV_177-5_0_4_node_48 | 0.4 | n |  | TRUE
79 | bus_LV_177-5_0_4_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_177-5_0_4_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_177-5_0_4_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_177-5_0_4_node_52 | 0.4 | n |  | TRUE
83 | bus_LV_177-5_0_4_node_154 | 0.4 | n |  | TRUE
84 | bus_LV_177-5_0_4_node_101 | 0.4 | n |  | TRUE
85 | bus_LV_177-5_0_4_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_177-5_0_4_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_177-5_0_4_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_177-5_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_177-5_0_4_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_177-5_0_4_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_177-5_0_4_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_177-5_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_177-5_0_4_node_103 | 0.4 | n |  | TRUE
94 | bus_LV_177-5_0_4_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_177-5_0_4_node_104 | 0.4 | n |  | TRUE
96 | bus_LV_177-5_0_4_node_124 | 0.4 | n |  | TRUE
97 | bus_LV_177-5_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_177-5_0_4_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_177-5_0_4_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_177-5_0_4_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_177-5_0_4_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_177-5_0_4_node_114 | 0.4 | n |  | TRUE
103 | bus_LV_177-5_0_4_node_117 | 0.4 | n |  | TRUE
104 | bus_LV_177-5_0_4_node_116 | 0.4 | n |  | TRUE
105 | bus_LV_177-5_0_4_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_177-5_0_4_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_177-5_0_4_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_177-5_0_4_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_177-5_0_4_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_177-5_0_4_node_121 | 0.4 | n |  | TRUE
111 | bus_LV_177-5_0_4_node_122 | 0.4 | n |  | TRUE
112 | bus_LV_177-5_0_4_node_157 | 0.4 | n |  | TRUE
113 | bus_LV_177-5_0_4_node_142 | 0.4 | n |  | TRUE
114 | bus_LV_177-5_0_4_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_177-5_0_4_node_93 | 0.4 | n |  | TRUE
116 | bus_LV_177-5_0_4_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_177-5_0_4_node_138 | 0.4 | n |  | TRUE
118 | bus_LV_177-5_0_4_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_177-5_0_4_node_137 | 0.4 | n |  | TRUE
120 | bus_LV_177-5_0_4_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_177-5_0_4_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_177-5_0_4_node_98 | 0.4 | n |  | TRUE
123 | bus_LV_177-5_0_4_node_99 | 0.4 | n |  | TRUE
124 | bus_LV_177-5_0_4_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_177-5_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_177-5_0_4_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_177-5_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_177-5_0_4_node_123 | 0.4 | n |  | TRUE
129 | bus_LV_177-5_0_4_node_112 | 0.4 | n |  | TRUE
130 | bus_LV_177-5_0_4_node_105 | 0.4 | n |  | TRUE
131 | bus_LV_177-5_0_4_node_106 | 0.4 | n |  | TRUE
132 | bus_LV_177-5_0_4_node_107 | 0.4 | n |  | TRUE
133 | bus_LV_177-5_0_4_node_108 | 0.4 | n |  | TRUE
134 | bus_LV_177-5_0_4_node_113 | 0.4 | n |  | TRUE
135 | bus_LV_177-5_0_4_node_147 | 0.4 | n |  | TRUE
136 | bus_LV_177-5_0_4_node_145 | 0.4 | n |  | TRUE
137 | bus_LV_177-5_0_4_node_146 | 0.4 | n |  | TRUE
138 | bus_LV_177-5_0_4_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_177-5_0_4_node_129 | 0.4 | n |  | TRUE
140 | bus_LV_177-5_0_4_node_125 | 0.4 | n |  | TRUE
141 | bus_LV_177-5_0_4_node_144 | 0.4 | n |  | TRUE
142 | bus_LV_177-5_0_4_node_133 | 0.4 | n |  | TRUE
143 | bus_LV_177-5_0_4_node_134 | 0.4 | n |  | TRUE
144 | bus_LV_177-5_0_4_node_135 | 0.4 | n |  | TRUE
145 | bus_LV_177-5_0_4_node_136 | 0.4 | n |  | TRUE
146 | bus_LV_177-5_0_4_node_141 | 0.4 | n |  | TRUE
147 | bus_LV_177-5_0_4_node_148 | 0.4 | n |  | TRUE
148 | bus_LV_177-5_0_4_node_149 | 0.4 | n |  | TRUE
149 | bus_LV_177-5_0_4_node_150 | 0.4 | n |  | TRUE
150 | bus_LV_177-5_0_4_node_151 | 0.4 | n |  | TRUE
151 | bus_LV_177-5_0_4_node_152 | 0.4 | n |  | TRUE
152 | bus_LV_177-5_0_4_node_153 | 0.4 | n |  | TRUE
153 | bus_MV_7_2_node_189 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_177-5_0_4_load_0 | 0 | 0.0030688 | 0.00076911 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_177-5_0_4_load_6 | 5 | 0.0031735 | 0.00079536 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_177-5_0_4_load_10 | 6 | 0.00042981 | 0.00010772 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_177-5_0_4_load_110 | 9 | 0.0058535 | 0.001467 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_177-5_0_4_load_70 | 13 | 0.023677 | 0.005934 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_177-5_0_4_load_131 | 15 | 0.02516 | 0.0063057 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_177-5_0_4_load_126 | 16 | 0.0085888 | 0.0021526 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_177-5_0_4_load_11 | 17 | 0.010012 | 0.0025092 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_177-5_0_4_load_83 | 18 | 0.021025 | 0.0052693 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_177-5_0_4_load_67 | 19 | 0.0071919 | 0.0018024 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_177-5_0_4_load_12 | 21 | 0.0037957 | 0.0009513 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_177-5_0_4_load_13 | 22 | 0.0013646 | 0.00034201 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_177-5_0_4_load_14 | 23 | 0.0017103 | 0.00042864 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_177-5_0_4_load_15 | 24 | 0.0013975 | 0.00035025 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_177-5_0_4_load_16 | 25 | 0.0013652 | 0.00034216 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_177-5_0_4_load_140 | 26 | 0.0014794 | 0.00037076 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_177-5_0_4_load_57 | 27 | 0.0019373 | 0.00048554 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_177-5_0_4_load_17 | 30 | 0.0020332 | 0.00050957 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_177-5_0_4_load_18 | 31 | 0.0022351 | 0.00056018 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_177-5_0_4_load_19 | 32 | 0.0014372 | 0.0003602 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_177-5_0_4_load_20 | 33 | 0.00088432 | 0.00022163 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_177-5_0_4_load_22 | 35 | 0.0032858 | 0.00082351 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_177-5_0_4_load_31 | 36 | 0.0017054 | 0.0004274 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_177-5_0_4_load_54 | 37 | 0.005543 | 0.0013892 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_177-5_0_4_load_30 | 38 | 0.0019333 | 0.00048453 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_177-5_0_4_load_53 | 39 | 0.0031278 | 0.00078391 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_177-5_0_4_load_56 | 40 | 0.0011152 | 0.00027949 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_177-5_0_4_load_102 | 41 | 0.00061256 | 0.00015352 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_177-5_0_4_load_24 | 42 | 0.0018969 | 0.00047541 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_177-5_0_4_load_25 | 43 | 0.0017271 | 0.00043285 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_177-5_0_4_load_29 | 46 | 0.0013232 | 0.00033163 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_177-5_0_4_load_42 | 47 | 0.0014796 | 0.00037083 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_177-5_0_4_load_34 | 48 | 0.0015507 | 0.00038864 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_177-5_0_4_load_45 | 49 | 0.0010654 | 0.00026702 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_177-5_0_4_load_43 | 50 | 0.0014482 | 0.00036295 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_177-5_0_4_load_33 | 51 | 0.0014919 | 0.00037392 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_177-5_0_4_load_61 | 53 | 0.0013275 | 0.0003327 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_177-5_0_4_load_76 | 54 | 0.00085213 | 0.00021356 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_177-5_0_4_load_46 | 55 | 0.001052 | 0.00026366 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_177-5_0_4_load_59 | 56 | 0.0014694 | 0.00036826 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_177-5_0_4_load_69 | 57 | 0.0013124 | 0.00032893 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_177-5_0_4_load_36 | 59 | 0.0054712 | 0.0013712 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_177-5_0_4_load_37 | 60 | 0.0019126 | 0.00047933 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_177-5_0_4_load_50 | 62 | 0.0018944 | 0.00047478 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_177-5_0_4_load_40 | 63 | 0.00092624 | 0.00023214 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_177-5_0_4_load_41 | 64 | 0.0010199 | 0.00025562 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_177-5_0_4_load_51 | 65 | 0.0018014 | 0.00045147 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_177-5_0_4_load_55 | 67 | 0.0016226 | 0.00040667 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_177-5_0_4_load_130 | 68 | 0.0017795 | 0.00044599 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_177-5_0_4_load_94 | 69 | 0.00089823 | 0.00022512 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_177-5_0_4_load_155 | 70 | 0.001672 | 0.00041905 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_177-5_0_4_load_143 | 71 | 0.00092554 | 0.00023196 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_177-5_0_4_load_92 | 73 | 0.00089489 | 0.00022428 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_177-5_0_4_load_44 | 74 | 0.0012825 | 0.00032143 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_177-5_0_4_load_62 | 75 | 0.0013184 | 0.00033043 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_177-5_0_4_load_63 | 76 | 0.0030204 | 0.00075698 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_177-5_0_4_load_47 | 77 | 0.0011942 | 0.00029929 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_177-5_0_4_load_48 | 78 | 0.0012749 | 0.00031951 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_177-5_0_4_load_49 | 79 | 0.0067681 | 0.0016963 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_177-5_0_4_load_60 | 80 | 0.0014657 | 0.00036734 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_177-5_0_4_load_58 | 81 | 0.0010159 | 0.00025461 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_177-5_0_4_load_52 | 82 | 0.004415 | 0.0011065 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_177-5_0_4_load_154 | 83 | 0.0015434 | 0.00038682 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_177-5_0_4_load_101 | 84 | 0.00056489 | 0.00014158 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_177-5_0_4_load_64 | 85 | 0.034792 | 0.0087198 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_177-5_0_4_load_71 | 88 | 0.00082969 | 0.00020794 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_177-5_0_4_load_72 | 89 | 0.00067179 | 0.00016837 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_177-5_0_4_load_73 | 90 | 0.0012321 | 0.0003088 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_177-5_0_4_load_74 | 91 | 0.00077056 | 0.00019312 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_177-5_0_4_load_103 | 93 | 0.0011912 | 0.00029854 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_177-5_0_4_load_120 | 94 | 0.0010381 | 0.00026017 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_177-5_0_4_load_104 | 95 | 0.001066 | 0.00026717 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_177-5_0_4_load_77 | 97 | 0.0035105 | 0.00087981 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_177-5_0_4_load_78 | 98 | 0.0080174 | 0.0020094 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_177-5_0_4_load_79 | 99 | 0.0035306 | 0.00088485 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_177-5_0_4_load_80 | 100 | 0.011063 | 0.0027726 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_177-5_0_4_load_117 | 103 | 0.0096552 | 0.0024198 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_177-5_0_4_load_116 | 104 | 0.0071907 | 0.0018021 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_177-5_0_4_load_86 | 105 | 0.0032782 | 0.00082158 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_177-5_0_4_load_87 | 106 | 0.00086015 | 0.00021557 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_177-5_0_4_load_89 | 108 | 0.00092579 | 0.00023202 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_177-5_0_4_load_121 | 110 | 0.0071275 | 0.0017863 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_177-5_0_4_load_157 | 112 | 0.0055176 | 0.0013829 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_177-5_0_4_load_91 | 114 | 0.00097517 | 0.0002444 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_177-5_0_4_load_93 | 115 | 0.00099358 | 0.00024901 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_177-5_0_4_load_138 | 117 | 0.0013992 | 0.00035068 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_177-5_0_4_load_109 | 118 | 0.0013995 | 0.00035074 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_177-5_0_4_load_137 | 119 | 0.0013629 | 0.00034158 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_177-5_0_4_load_96 | 120 | 0.005645 | 0.0014148 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_177-5_0_4_load_97 | 121 | 0.0030431 | 0.00076266 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_177-5_0_4_load_98 | 122 | 0.0030423 | 0.00076248 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_177-5_0_4_load_99 | 123 | 0.0056466 | 0.0014152 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_177-5_0_4_load_119 | 125 | 0.003531 | 0.00088494 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_177-5_0_4_load_127 | 126 | 0.0031041 | 0.00077795 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_177-5_0_4_load_118 | 127 | 0.0034609 | 0.00086739 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_177-5_0_4_load_123 | 128 | 0.0056457 | 0.0014149 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_177-5_0_4_load_112 | 129 | 0.0061699 | 0.0015463 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_177-5_0_4_load_105 | 130 | 0.00088696 | 0.00022229 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_177-5_0_4_load_106 | 131 | 0.0041 | 0.0010275 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_177-5_0_4_load_107 | 132 | 0.0013639 | 0.00034182 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_177-5_0_4_load_108 | 133 | 0.0038749 | 0.00097113 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_177-5_0_4_load_147 | 135 | 0.0034802 | 0.00087221 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_177-5_0_4_load_145 | 136 | 0.00097073 | 0.00024329 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_177-5_0_4_load_146 | 137 | 0.01466 | 0.0036741 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_177-5_0_4_load_128 | 138 | 0.0096558 | 0.00242 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_177-5_0_4_load_129 | 139 | 0.020603 | 0.0051635 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_177-5_0_4_load_125 | 140 | 0.0014447 | 0.00036208 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_177-5_0_4_load_144 | 141 | 0.0010203 | 0.00025571 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_177-5_0_4_load_133 | 142 | 0.00097607 | 0.00024463 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_177-5_0_4_load_134 | 143 | 0.0019844 | 0.00049733 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_177-5_0_4_load_135 | 144 | 0.00089416 | 0.0002241 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_177-5_0_4_load_136 | 145 | 0.00089827 | 0.00022513 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_177-5_0_4_load_141 | 146 | 0.0016007 | 0.00040117 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_177-5_0_4_load_148 | 147 | 0.0015429 | 0.0003867 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_177-5_0_4_load_149 | 148 | 0.0015777 | 0.00039542 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_177-5_0_4_load_150 | 149 | 0.0015494 | 0.00038832 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_177-5_0_4_load_151 | 150 | 0.0015959 | 0.00039997 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_177-5_0_4_load_152 | 151 | 0.0015547 | 0.00038964 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_177-5_0_4_load_153 | 152 | 0.0016817 | 0.00042148 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 139 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_177-5_0_4_line_0 |  | 0 | 1 | 0.050138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_177-5_0_4_line_1 |  | 1 | 2 | 0.040701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_177-5_0_4_line_2 |  | 2 | 6 | 0.028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_177-5_0_4_line_3 |  | 2 | 5 | 0.021796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_177-5_0_4_line_4 |  | 3 | 4 | 0.044638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_177-5_0_4_line_5 |  | 3 | 5 | 0.014774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_177-5_0_4_line_6 |  | 4 | 10 | 0.008618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_177-5_0_4_line_7 |  | 6 | 17 | 0.004066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_177-5_0_4_line_8 |  | 7 | 8 | 0.029175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_177-5_0_4_line_9 |  | 7 | 9 | 0.031103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_177-5_0_4_line_10 |  | 8 | 18 | 0.027223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_177-5_0_4_line_11 |  | 8 | 19 | 0.027725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_177-5_0_4_line_12 |  | 9 | 20 | 0.022025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_177-5_0_4_line_13 |  | 10 | 18 | 0.0021062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_177-5_0_4_line_14 |  | 10 | 14 | 0.01767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_177-5_0_4_line_15 |  | 11 | 12 | 0.048077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_177-5_0_4_line_16 |  | 11 | 13 | 0.010583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_177-5_0_4_line_17 |  | 12 | 14 | 0.025959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_177-5_0_4_line_18 |  | 12 | 15 | 0.011389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_177-5_0_4_line_19 |  | 14 | 16 | 0.023246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_177-5_0_4_line_20 |  | 19 | 86 | 0.009199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_177-5_0_4_line_21 |  | 20 | 129 | 0.028319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_177-5_0_4_line_22 |  | 20 | 134 | 0.016167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_177-5_0_4_line_23 |  | 21 | 22 | 0.014857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_177-5_0_4_line_24 |  | 21 | 23 | 0.011898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_177-5_0_4_line_25 |  | 22 | 24 | 5.4701e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_177-5_0_4_line_26 |  | 23 | 25 | 6.5693e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_177-5_0_4_line_27 |  | 24 | 26 | 0.012607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_177-5_0_4_line_28 |  | 25 | 27 | 0.0011005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_177-5_0_4_line_29 |  | 26 | 28 | 0.010839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_177-5_0_4_line_30 |  | 27 | 29 | 0.0092767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_177-5_0_4_line_31 |  | 28 | 146 | 0.014606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_177-5_0_4_line_32 |  | 28 | 119 | 0.0041339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_177-5_0_4_line_33 |  | 29 | 40 | 0.024912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_177-5_0_4_line_34 |  | 30 | 31 | 0.029744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_177-5_0_4_line_35 |  | 30 | 32 | 0.010554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_177-5_0_4_line_36 |  | 31 | 33 | 0.017512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_177-5_0_4_line_37 |  | 32 | 34 | 0.011376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_177-5_0_4_line_38 |  | 33 | 35 | 0.021693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_177-5_0_4_line_39 |  | 34 | 36 | 0.026069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_177-5_0_4_line_40 |  | 34 | 37 | 0.005873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_177-5_0_4_line_41 |  | 36 | 38 | 0.010369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_177-5_0_4_line_42 |  | 37 | 39 | 0.019882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_177-5_0_4_line_43 |  | 39 | 66 | 0.029015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_177-5_0_4_line_44 |  | 40 | 41 | 0.0028402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_177-5_0_4_line_45 |  | 41 | 84 | 0.0059904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_177-5_0_4_line_46 |  | 42 | 43 | 0.020335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_177-5_0_4_line_47 |  | 42 | 44 | 0.012411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_177-5_0_4_line_48 |  | 43 | 45 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_177-5_0_4_line_49 |  | 44 | 46 | 0.013633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_177-5_0_4_line_50 |  | 45 | 47 | 0.01747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_177-5_0_4_line_51 |  | 45 | 48 | 0.0060977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_177-5_0_4_line_52 |  | 46 | 49 | 0.00059678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_177-5_0_4_line_53 |  | 47 | 50 | 0.00072029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_177-5_0_4_line_54 |  | 48 | 51 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_177-5_0_4_line_55 |  | 49 | 55 | 0.024373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_177-5_0_4_line_56 |  | 50 | 74 | 0.021948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_177-5_0_4_line_57 |  | 51 | 58 | 0.022283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_177-5_0_4_line_58 |  | 52 | 53 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_177-5_0_4_line_59 |  | 52 | 54 | 0.033274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_177-5_0_4_line_60 |  | 53 | 56 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_177-5_0_4_line_61 |  | 54 | 57 | 0.0084126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_177-5_0_4_line_62 |  | 55 | 77 | 0.0015975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_177-5_0_4_line_63 |  | 56 | 81 | 0.0015678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_177-5_0_4_line_64 |  | 57 | 87 | 0.031154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_177-5_0_4_line_65 |  | 58 | 59 | 0.0071512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_177-5_0_4_line_66 |  | 58 | 60 | 0.017187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_177-5_0_4_line_67 |  | 59 | 61 | 0.026685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_177-5_0_4_line_68 |  | 60 | 62 | 0.0056554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_177-5_0_4_line_69 |  | 61 | 63 | 0.015591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_177-5_0_4_line_70 |  | 61 | 64 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_177-5_0_4_line_71 |  | 62 | 65 | 0.016147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_177-5_0_4_line_72 |  | 63 | 68 | 0.027849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_177-5_0_4_line_73 |  | 64 | 69 | 0.0069016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_177-5_0_4_line_74 |  | 65 | 82 | 0.01289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_177-5_0_4_line_75 |  | 66 | 67 | 0.011747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_177-5_0_4_line_76 |  | 67 | 70 | 0.0071215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_177-5_0_4_line_77 |  | 68 | 71 | 0.011414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_177-5_0_4_line_78 |  | 68 | 72 | 0.042452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_177-5_0_4_line_79 |  | 69 | 73 | 0.0064632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_177-5_0_4_line_80 |  | 70 | 83 | 0.0055733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_177-5_0_4_line_81 |  | 71 | 141 | 0.0069849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_177-5_0_4_line_82 |  | 72 | 138 | 0.029888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_177-5_0_4_line_83 |  | 72 | 102 | 0.006651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_177-5_0_4_line_84 |  | 73 | 114 | 0.0066016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_177-5_0_4_line_85 |  | 74 | 75 | 0.0011481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_177-5_0_4_line_86 |  | 75 | 76 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_177-5_0_4_line_87 |  | 77 | 78 | 0.016527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_177-5_0_4_line_88 |  | 78 | 79 | 0.0066877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_177-5_0_4_line_89 |  | 79 | 80 | 0.0064988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_177-5_0_4_line_90 |  | 80 | 81 | 0.018179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_177-5_0_4_line_91 |  | 83 | 152 | 0.0070051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_177-5_0_4_line_92 |  | 84 | 91 | 0.024873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_177-5_0_4_line_93 |  | 85 | 86 | 0.030162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_177-5_0_4_line_94 |  | 85 | 87 | 0.015876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_177-5_0_4_line_95 |  | 88 | 89 | 0.01696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_177-5_0_4_line_96 |  | 88 | 90 | 0.003075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_177-5_0_4_line_97 |  | 89 | 91 | 0.024271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_177-5_0_4_line_98 |  | 90 | 92 | 0.028762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_177-5_0_4_line_99 |  | 91 | 93 | 0.019786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_177-5_0_4_line_100 |  | 92 | 94 | 0.045311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_177-5_0_4_line_101 |  | 93 | 95 | 0.015249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_177-5_0_4_line_102 |  | 94 | 96 | 0.04533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_177-5_0_4_line_103 |  | 95 | 130 | 0.032731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_177-5_0_4_line_104 |  | 96 | 140 | 0.044915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_177-5_0_4_line_105 |  | 97 | 98 | 0.039571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_177-5_0_4_line_106 |  | 97 | 99 | 0.0256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_177-5_0_4_line_107 |  | 98 | 100 | 0.030618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_177-5_0_4_line_108 |  | 99 | 101 | 0.046723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_177-5_0_4_line_109 |  | 100 | 102 | 0.016146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_177-5_0_4_line_110 |  | 101 | 103 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_177-5_0_4_line_111 |  | 103 | 104 | 0.0227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_177-5_0_4_line_112 |  | 104 | 127 | 0.0054366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_177-5_0_4_line_113 |  | 105 | 106 | 0.029779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_177-5_0_4_line_114 |  | 105 | 107 | 0.023311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_177-5_0_4_line_115 |  | 106 | 108 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_177-5_0_4_line_116 |  | 107 | 109 | 0.01987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_177-5_0_4_line_117 |  | 108 | 110 | 0.0066101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_177-5_0_4_line_118 |  | 109 | 111 | 0.036432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_177-5_0_4_line_119 |  | 111 | 112 | 0.034853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_177-5_0_4_line_120 |  | 111 | 113 | 0.04853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_177-5_0_4_line_121 |  | 113 | 118 | 0.019633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_177-5_0_4_line_122 |  | 113 | 116 | 0.047838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_177-5_0_4_line_123 |  | 114 | 115 | 0.0068142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_177-5_0_4_line_124 |  | 115 | 116 | 0.028872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_177-5_0_4_line_125 |  | 116 | 117 | 0.026005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_177-5_0_4_line_126 |  | 117 | 119 | 5.4439e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_177-5_0_4_line_127 |  | 118 | 132 | 0.00010693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_177-5_0_4_line_128 |  | 120 | 121 | 0.025027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_177-5_0_4_line_129 |  | 120 | 122 | 0.0088779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_177-5_0_4_line_130 |  | 121 | 123 | 0.015658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_177-5_0_4_line_131 |  | 122 | 124 | 0.021233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_177-5_0_4_line_132 |  | 123 | 125 | 0.0014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_177-5_0_4_line_133 |  | 124 | 126 | 0.048453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_177-5_0_4_line_134 |  | 125 | 127 | 0.017826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_177-5_0_4_line_135 |  | 128 | 129 | 0.0032301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_177-5_0_4_line_136 |  | 131 | 132 | 0.0070337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_177-5_0_4_line_137 |  | 131 | 133 | 0.012802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_177-5_0_4_line_138 |  | 134 | 135 | 0.02415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_177-5_0_4_line_139 |  | 134 | 136 | 0.077612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_177-5_0_4_line_140 |  | 136 | 137 | 0.016187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_177-5_0_4_line_141 |  | 138 | 139 | 0.014788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_177-5_0_4_line_142 |  | 141 | 145 | 0.006881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_177-5_0_4_line_143 |  | 142 | 143 | 0.0068113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_177-5_0_4_line_144 |  | 142 | 144 | 0.0065734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_177-5_0_4_line_145 |  | 144 | 145 | 0.0064616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_177-5_0_4_line_146 |  | 146 | 147 | 0.0062799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_177-5_0_4_line_147 |  | 147 | 148 | 0.0076008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_177-5_0_4_line_148 |  | 148 | 149 | 0.0050747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_177-5_0_4_line_149 |  | 149 | 150 | 0.0059829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_177-5_0_4_line_150 |  | 150 | 151 | 0.0068949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_177-5_0_4_line_151 |  | 151 | 152 | 0.0057586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_177-5_0_4_trafo_129 | 0.63 MVA 20/0.4 kV | 153 | 139 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2701263.1392 | 1247587.556 | 2701282.7497 | 1247588.8809 | 2701279.5423 | 1247619.1943
1 | 2701245.7674 | 1247614.8141 | 2701246.7386 | 1247603.0659 | 2701258.4755 | 1247604.0782 | 2701263.1392 | 1247587.556
2 | 2701245.7674 | 1247614.8141 | 2701232.3767 | 1247613.3288 | 2701233.479 | 1247608.4993 | 2701223.8488 | 1247608.1289
3 | 2701245.7674 | 1247614.8141 | 2701243.9622 | 1247636.5354
4 | 2701245.2936 | 1247688.5193 | 2701243.1336 | 1247682.7446 | 2701245.0982 | 1247662.3733 | 2701240.9392 | 1247655.1077 | 2701249.0652 | 1247649.9312
5 | 2701249.0652 | 1247649.9312 | 2701243.6753 | 1247639.987 | 2701243.9622 | 1247636.5354
6 | 2701245.2936 | 1247688.5193 | 2701246.0972 | 1247694.093 | 2701246.2276 | 1247697.0753
7 | 2701219.7858 | 1247607.9726 | 2701223.8488 | 1247608.1289
8 | 2701205.4125 | 1247677.2297 | 2701217.7724 | 1247703.6725
9 | 2701205.4125 | 1247677.2297 | 2701174.7391 | 1247682.3826
10 | 2701217.7724 | 1247703.6725 | 2701237.4969 | 1247697.8602 | 2701244.1299 | 1247697.2639
11 | 2701217.7724 | 1247703.6725 | 2701231.0774 | 1247727.9965
12 | 2701153.0188 | 1247686.0315 | 2701174.7391 | 1247682.3826
13 | 2701246.2276 | 1247697.0753 | 2701244.1299 | 1247697.2639
14 | 2701246.2276 | 1247697.0753 | 2701251.2582 | 1247696.6498 | 2701263.903 | 1247695.7983
15 | 2701283.8754 | 1247711.2849 | 2701306.064 | 1247724.3853 | 2701301.9835 | 1247725.7945 | 2701296.4788 | 1247726.1118 | 2701296.6124 | 1247728.0156 | 2701302.0876 | 1247727.6533 | 2701302.4996 | 1247732.7199
16 | 2701302.4996 | 1247732.7199 | 2701291.9467 | 1247733.518
17 | 2701263.903 | 1247695.7983 | 2701264.152 | 1247698.0266 | 2701283.8754 | 1247711.2849
18 | 2701283.8754 | 1247711.2849 | 2701292.7723 | 1247704.1745
19 | 2701263.903 | 1247695.7983 | 2701263.6619 | 1247692.6695 | 2701263.5527 | 1247691.5446 | 2701280.5162 | 1247690.3778 | 2701280.3988 | 1247688.4076
20 | 2701235.4919 | 1247736.067 | 2701231.0774 | 1247727.9965
21 | 2701153.0188 | 1247686.0315 | 2701125.6483 | 1247693.2999
22 | 2701147.5147 | 1247670.8257 | 2701153.0188 | 1247686.0315
23 | 2701111.9186 | 1248068.7356 | 2701108.3358 | 1248054.3174
24 | 2701111.9186 | 1248068.7356 | 2701114.7879 | 1248080.2825
25 | 2701108.3358 | 1248054.3174 | 2701108.3226 | 1248054.2643
26 | 2701114.8038 | 1248080.3463 | 2701114.7879 | 1248080.2825
27 | 2701105.2823 | 1248042.0296 | 2701108.3226 | 1248054.2643
28 | 2701114.8038 | 1248080.3463 | 2701115.0692 | 1248081.4143
29 | 2701102.6683 | 1248031.5103 | 2701105.2823 | 1248042.0296
30 | 2701117.3063 | 1248090.4172 | 2701115.0692 | 1248081.4143
31 | 2701102.6683 | 1248031.5103 | 2701115.7018 | 1248024.9172
32 | 2701102.6683 | 1248031.5103 | 2701101.6715 | 1248027.4983
33 | 2701117.3063 | 1248090.4172 | 2701116.0671 | 1248097.9686 | 2701114.8593 | 1248106.3324 | 2701112.7959 | 1248114.8962
34 | 2701197.7584 | 1248048.0233 | 2701200.5867 | 1248044.6688 | 2701215.5905 | 1248024.228
35 | 2701221.8355 | 1248015.7201 | 2701215.5905 | 1248024.228
36 | 2701197.7584 | 1248048.0233 | 2701194.4035 | 1248052.0023 | 2701185.8815 | 1248059.6184 | 2701185.1214 | 1248060.0573
37 | 2701228.5667 | 1248006.5498 | 2701221.8355 | 1248015.7201
38 | 2701166.3357 | 1248070.9054 | 2701185.1214 | 1248060.0573
39 | 2701228.5667 | 1248006.5498 | 2701233.841 | 1248005.5502 | 2701238.5695 | 1248004.2299 | 2701247.9788 | 1248001.2771 | 2701253.549 | 1247999.2449
40 | 2701228.5667 | 1248006.5498 | 2701222.7026 | 1248006.8728
41 | 2701263.1683 | 1247995.3859 | 2701258.1109 | 1247997.5805 | 2701253.549 | 1247999.2449
42 | 2701202.8406 | 1248006.4661 | 2701210.4535 | 1248006.9743 | 2701220.8623 | 1248006.9742 | 2701222.7026 | 1248006.8728
43 | 2701177.3076 | 1247993.7538 | 2701177.9962 | 1247994.5662 | 2701182.7554 | 1247998.5171 | 2701188.8302 | 1248001.9568 | 2701196.1198 | 1248005.0281 | 2701202.8406 | 1248006.4661 | 2701202.8406 | 1248006.4661
44 | 2701112.1306 | 1248117.6574 | 2701112.7959 | 1248114.8962
45 | 2701110.7273 | 1248123.4811 | 2701112.1306 | 1248117.6574
46 | 2701248.557 | 1247925.1113 | 2701266.6653 | 1247915.8601
47 | 2701277.7178 | 1247910.2135 | 2701266.6653 | 1247915.8601
48 | 2701236.3324 | 1247931.3567 | 2701248.557 | 1247925.1113
49 | 2701277.7178 | 1247910.2135 | 2701271.7844 | 1247897.9393
50 | 2701236.3324 | 1247931.3567 | 2701228.1852 | 1247915.9032
51 | 2701236.3324 | 1247931.3567 | 2701230.8754 | 1247934.0776
52 | 2701271.7844 | 1247897.9393 | 2701271.5247 | 1247897.402
53 | 2701227.8493 | 1247915.2661 | 2701228.1852 | 1247915.9032
54 | 2701212.2847 | 1247943.3468 | 2701230.8754 | 1247934.0776
55 | 2701271.5247 | 1247897.402 | 2701260.917 | 1247875.4585
56 | 2701227.8493 | 1247915.2661 | 2701217.6136 | 1247895.851
57 | 2701192.3429 | 1247953.2897 | 2701212.2847 | 1247943.3468
58 | 2701309.3742 | 1247826.3441 | 2701297.9124 | 1247833.0156
59 | 2701309.3742 | 1247826.3441 | 2701294.3063 | 1247796.6776
60 | 2701281.4916 | 1247842.5736 | 2701297.9124 | 1247833.0156
61 | 2701290.4967 | 1247789.177 | 2701294.3063 | 1247796.6776
62 | 2701260.2218 | 1247874.0203 | 2701260.917 | 1247875.4585
63 | 2701280.1367 | 1247843.3622 | 2701281.4916 | 1247842.5736
64 | 2701270.3684 | 1247766.1194 | 2701285.3314 | 1247779.0073 | 2701290.4967 | 1247789.177
65 | 2701192.3429 | 1247953.2897 | 2701185.9643 | 1247956.5227
66 | 2701192.3429 | 1247953.2897 | 2701183.9784 | 1247938.2751
67 | 2701162.1618 | 1247968.5867 | 2701185.9643 | 1247956.5227
68 | 2701181.2261 | 1247933.3346 | 2701183.9784 | 1247938.2751
69 | 2701162.1618 | 1247968.5867 | 2701154.923 | 1247954.7778
70 | 2701162.1618 | 1247968.5867 | 2701145.0231 | 1247977.0704
71 | 2701181.2261 | 1247933.3346 | 2701173.3677 | 1247919.2284
72 | 2701141.9932 | 1247930.1125 | 2701154.923 | 1247954.7778
73 | 2701145.0231 | 1247977.0704 | 2701138.8378 | 1247980.1321
74 | 2701167.0945 | 1247907.9678 | 2701173.3677 | 1247919.2284
75 | 2701177.3076 | 1247993.7538 | 2701166.8249 | 1247999.0564
76 | 2701166.8249 | 1247999.0564 | 2701160.4702 | 1248002.271
77 | 2701141.9932 | 1247930.1125 | 2701131.8913 | 1247935.4262
78 | 2701122.4382 | 1247892.405 | 2701141.9932 | 1247930.1125
79 | 2701138.8378 | 1247980.1321 | 2701133.0454 | 1247982.9993
80 | 2701155.497 | 1248004.7867 | 2701160.4702 | 1248002.271
81 | 2701131.8913 | 1247935.4262 | 2701125.7095 | 1247938.678
82 | 2701122.4382 | 1247892.405 | 2701149.1031 | 1247878.9043
83 | 2701122.4382 | 1247892.405 | 2701119.4045 | 1247886.4819
84 | 2701127.129 | 1247985.9279 | 2701133.0454 | 1247982.9993
85 | 2701217.0781 | 1247894.8354 | 2701217.6136 | 1247895.851
86 | 2701212.0779 | 1247885.351 | 2701217.0781 | 1247894.8354
87 | 2701260.2218 | 1247874.0203 | 2701253.0289 | 1247859.1407 | 2701253.0289 | 1247859.1407
88 | 2701258.8088 | 1247855.7765 | 2701253.0289 | 1247859.1407
89 | 2701258.8088 | 1247855.7765 | 2701264.4254 | 1247852.5072
90 | 2701280.1367 | 1247843.3622 | 2701264.4254 | 1247852.5072
91 | 2701155.497 | 1248004.7867 | 2701149.2461 | 1248007.9487
92 | 2701104.9011 | 1248147.6617 | 2701110.7273 | 1248123.4811
93 | 2701235.4919 | 1247736.067 | 2701258.3411 | 1247755.7558
94 | 2701270.3684 | 1247766.1194 | 2701258.3411 | 1247755.7558
95 | 2701098.2587 | 1248188.1135 | 2701097.8798 | 1248181.5463 | 2701098.967 | 1248172.2798 | 2701099.2136 | 1248171.2568
96 | 2701098.2587 | 1248188.1135 | 2701098.2587 | 1248188.1135 | 2701099.2479 | 1248191.025
97 | 2701104.9011 | 1248147.6617 | 2701099.2136 | 1248171.2568
98 | 2701114.9771 | 1248214.9418 | 2701104.5927 | 1248200.698 | 2701100.402 | 1248194.4216 | 2701099.2479 | 1248191.025
99 | 2701104.9011 | 1248147.6617 | 2701124.0938 | 1248142.8523
100 | 2701114.9771 | 1248214.9418 | 2701152.1662 | 1248189.0557
101 | 2701124.0938 | 1248142.8523 | 2701138.8856 | 1248139.1457
102 | 2701189.3703 | 1248163.1592 | 2701152.1662 | 1248189.0557
103 | 2701156.9205 | 1248156.1111 | 2701143.134 | 1248157.5326 | 2701138.8856 | 1248139.1457
104 | 2701166.285 | 1248134.9765 | 2701170.8517 | 1248134.7209 | 2701174.7229 | 1248135.3763 | 2701178.4169 | 1248136.6848 | 2701182.173 | 1248138.7728 | 2701186.1827 | 1248142.3774 | 2701188.8143 | 1248146.1808 | 2701191.3792 | 1248150.7949 | 2701192.144 | 1248156.4346 | 2701189.3703 | 1248163.1592
105 | 2701055.7219 | 1247875.9275 | 2701076.7718 | 1247908.1498 | 2701077.7438 | 1247907.6742
106 | 2701051.7782 | 1247855.9595 | 2701047.0333 | 1247857.6367 | 2701048.6656 | 1247865.1259 | 2701055.7219 | 1247875.9275
107 | 2701105.2413 | 1247894.2073 | 2701104.5749 | 1247894.5465 | 2701077.7438 | 1247907.6742
108 | 2701095.8303 | 1247840.3883 | 2701051.7782 | 1247855.9595
109 | 2701119.4045 | 1247886.4819 | 2701114.6789 | 1247889.4036 | 2701105.2413 | 1247894.2073
110 | 2701095.8303 | 1247840.3883 | 2701092.9461 | 1247833.6672 | 2701091.1585 | 1247829.5046
111 | 2701082.2014 | 1247808.6465 | 2701091.1585 | 1247829.5046
112 | 2701080.0562 | 1247803.6511 | 2701082.2014 | 1247808.6465
113 | 2700985.5702 | 1248106.9503 | 2700981.3615 | 1248108.8927 | 2700973.9395 | 1248106.0529 | 2700965.5045 | 1248091.0667
114 | 2700957.859 | 1248069.2169 | 2700961.9452 | 1248084.7431 | 2700965.5045 | 1248091.0667
115 | 2700992.662 | 1248098.666 | 2700992.662 | 1248098.666 | 2700989.8427 | 1248104.9785 | 2700985.5702 | 1248106.9503
116 | 2700976.0064 | 1248061.0084 | 2700957.859 | 1248069.2169
117 | 2700992.662 | 1248098.666 | 2700989.9883 | 1248092.6208
118 | 2701009.1044 | 1248045.5822 | 2700993.5601 | 1248053.0678 | 2700976.0064 | 1248061.0084
119 | 2701009.1044 | 1248045.5822 | 2701013.6389 | 1248059.1813 | 2701010.1788 | 1248074.2786 | 2701011.7363 | 1248079.0644
120 | 2701052.9275 | 1248024.4679 | 2701038.867 | 1248031.3115 | 2701033.3692 | 1248033.8976 | 2701009.1044 | 1248045.5822
121 | 2701052.9275 | 1248024.4679 | 2701061.3826 | 1248042.1876
122 | 2701095.3882 | 1248002.2076 | 2701057.5504 | 1248022.245 | 2701052.9275 | 1248024.4679
123 | 2701127.129 | 1247985.9279 | 2701121.022 | 1247988.9509
124 | 2701095.3882 | 1248002.2076 | 2701101.8579 | 1247998.4372 | 2701121.022 | 1247988.9509
125 | 2701095.3882 | 1248002.2076 | 2701101.6584 | 1248027.4455
126 | 2701101.6584 | 1248027.4455 | 2701101.6715 | 1248027.4983
127 | 2701061.4286 | 1248042.2841 | 2701061.3826 | 1248042.1876
128 | 2701067.6136 | 1247770.9766 | 2701059.0216 | 1247747.4706
129 | 2701055.9738 | 1247739.1323 | 2701059.0216 | 1247747.4706
130 | 2701067.6136 | 1247770.9766 | 2701072.9891 | 1247785.683
131 | 2701048.6843 | 1247719.1897 | 2701055.9738 | 1247739.1323
132 | 2701073.5005 | 1247787.082 | 2701072.9891 | 1247785.683
133 | 2701048.6843 | 1247719.1897 | 2701002.3751 | 1247733.4415
134 | 2701080.0562 | 1247803.6511 | 2701076.7011 | 1247795.8384 | 2701073.5005 | 1247787.082
135 | 2701125.6483 | 1247693.2999 | 2701122.5264 | 1247694.1289
136 | 2701064.4576 | 1248048.6321 | 2701061.4286 | 1248042.2841
137 | 2701069.9708 | 1248060.1864 | 2701064.4576 | 1248048.6321
138 | 2701139.7468 | 1247647.953 | 2701147.5147 | 1247670.8257
139 | 2701147.5147 | 1247670.8257 | 2701089.5888 | 1247689.0855 | 2701082.5323 | 1247685.1622 | 2701080.0298 | 1247676.7231
140 | 2701081.6906 | 1247661.8851 | 2701077.7465 | 1247669.0235 | 2701080.0298 | 1247676.7231
141 | 2701162.2963 | 1247872.2246 | 2701149.1031 | 1247878.9043
142 | 2701125.7095 | 1247938.678 | 2701119.6196 | 1247941.8813
143 | 2701108.0832 | 1247947.9496 | 2701102.055 | 1247951.1205
144 | 2701113.9009 | 1247944.8894 | 2701108.0832 | 1247947.9496
145 | 2701113.9009 | 1247944.8894 | 2701119.6196 | 1247941.8813
146 | 2701121.3055 | 1248022.0826 | 2701115.7018 | 1248024.9172
147 | 2701121.3055 | 1248022.0826 | 2701128.088 | 1248018.6516
148 | 2701132.6163 | 1248016.361 | 2701128.088 | 1248018.6516
149 | 2701132.6163 | 1248016.361 | 2701137.955 | 1248013.6604
150 | 2701144.1075 | 1248010.5481 | 2701137.955 | 1248013.6604
151 | 2701144.1075 | 1248010.5481 | 2701149.2461 | 1248007.9487

## bus_geodata
| x | y | coords
0 | 2701279.5423 | 1247619.1943
1 | 2701263.1392 | 1247587.556
2 | 2701245.7674 | 1247614.8141
3 | 2701249.0652 | 1247649.9312
4 | 2701245.2936 | 1247688.5193
5 | 2701243.9622 | 1247636.5354
6 | 2701223.8488 | 1247608.1289
7 | 2701205.4125 | 1247677.2297
8 | 2701217.7724 | 1247703.6725
9 | 2701174.7391 | 1247682.3826
10 | 2701246.2276 | 1247697.0753
11 | 2701302.4996 | 1247732.7199
12 | 2701283.8754 | 1247711.2849
13 | 2701291.9467 | 1247733.518
14 | 2701263.903 | 1247695.7983
15 | 2701292.7723 | 1247704.1745
16 | 2701280.3988 | 1247688.4076
17 | 2701219.7858 | 1247607.9726
18 | 2701244.1299 | 1247697.2639
19 | 2701231.0774 | 1247727.9965
20 | 2701153.0188 | 1247686.0315
21 | 2701111.9186 | 1248068.7356
22 | 2701108.3358 | 1248054.3174
23 | 2701114.7879 | 1248080.2825
24 | 2701108.3226 | 1248054.2643
25 | 2701114.8038 | 1248080.3463
26 | 2701105.2823 | 1248042.0296
27 | 2701115.0692 | 1248081.4143
28 | 2701102.6683 | 1248031.5103
29 | 2701117.3063 | 1248090.4172
30 | 2701215.5905 | 1248024.228
31 | 2701197.7584 | 1248048.0233
32 | 2701221.8355 | 1248015.7201
33 | 2701185.1214 | 1248060.0573
34 | 2701228.5667 | 1248006.5498
35 | 2701166.3357 | 1248070.9054
36 | 2701253.549 | 1247999.2449
37 | 2701222.7026 | 1248006.8728
38 | 2701263.1683 | 1247995.3859
39 | 2701202.8406 | 1248006.4661
40 | 2701112.7959 | 1248114.8962
41 | 2701112.1306 | 1248117.6574
42 | 2701266.6653 | 1247915.8601
43 | 2701248.557 | 1247925.1113
44 | 2701277.7178 | 1247910.2135
45 | 2701236.3324 | 1247931.3567
46 | 2701271.7844 | 1247897.9393
47 | 2701228.1852 | 1247915.9032
48 | 2701230.8754 | 1247934.0776
49 | 2701271.5247 | 1247897.402
50 | 2701227.8493 | 1247915.2661
51 | 2701212.2847 | 1247943.3468
52 | 2701309.3742 | 1247826.3441
53 | 2701297.9124 | 1247833.0156
54 | 2701294.3063 | 1247796.6776
55 | 2701260.917 | 1247875.4585
56 | 2701281.4916 | 1247842.5736
57 | 2701290.4967 | 1247789.177
58 | 2701192.3429 | 1247953.2897
59 | 2701185.9643 | 1247956.5227
60 | 2701183.9784 | 1247938.2751
61 | 2701162.1618 | 1247968.5867
62 | 2701181.2261 | 1247933.3346
63 | 2701154.923 | 1247954.7778
64 | 2701145.0231 | 1247977.0704
65 | 2701173.3677 | 1247919.2284
66 | 2701177.3076 | 1247993.7538
67 | 2701166.8249 | 1247999.0564
68 | 2701141.9932 | 1247930.1125
69 | 2701138.8378 | 1247980.1321
70 | 2701160.4702 | 1248002.271
71 | 2701131.8913 | 1247935.4262
72 | 2701122.4382 | 1247892.405
73 | 2701133.0454 | 1247982.9993
74 | 2701217.6136 | 1247895.851
75 | 2701217.0781 | 1247894.8354
76 | 2701212.0779 | 1247885.351
77 | 2701260.2218 | 1247874.0203
78 | 2701253.0289 | 1247859.1407
79 | 2701258.8088 | 1247855.7765
80 | 2701264.4254 | 1247852.5072
81 | 2701280.1367 | 1247843.3622
82 | 2701167.0945 | 1247907.9678
83 | 2701155.497 | 1248004.7867
84 | 2701110.7274 | 1248123.4811
85 | 2701258.3411 | 1247755.7558
86 | 2701235.4919 | 1247736.067
87 | 2701270.3684 | 1247766.1194
88 | 2701098.2587 | 1248188.1135
89 | 2701099.2136 | 1248171.2568
90 | 2701099.2479 | 1248191.025
91 | 2701104.9011 | 1248147.6617
92 | 2701114.9771 | 1248214.9418
93 | 2701124.0938 | 1248142.8523
94 | 2701152.1662 | 1248189.0557
95 | 2701138.8856 | 1248139.1457
96 | 2701189.3703 | 1248163.1592
97 | 2701055.7219 | 1247875.9275
98 | 2701077.7438 | 1247907.6742
99 | 2701051.7782 | 1247855.9595
100 | 2701105.2413 | 1247894.2073
101 | 2701095.8303 | 1247840.3883
102 | 2701119.4045 | 1247886.4819
103 | 2701091.1585 | 1247829.5046
104 | 2701082.2014 | 1247808.6465
105 | 2700965.5045 | 1248091.0667
106 | 2700985.5702 | 1248106.9503
107 | 2700957.859 | 1248069.2169
108 | 2700992.662 | 1248098.666
109 | 2700976.0064 | 1248061.0084
110 | 2700989.9883 | 1248092.6208
111 | 2701009.1044 | 1248045.5822
112 | 2701011.7363 | 1248079.0644
113 | 2701052.9275 | 1248024.4679
114 | 2701127.129 | 1247985.9279
115 | 2701121.022 | 1247988.9509
116 | 2701095.3882 | 1248002.2076
117 | 2701101.6584 | 1248027.4455
118 | 2701061.3826 | 1248042.1876
119 | 2701101.6715 | 1248027.4983
120 | 2701059.0216 | 1247747.4706
121 | 2701067.6136 | 1247770.9766
122 | 2701055.9738 | 1247739.1323
123 | 2701072.9891 | 1247785.683
124 | 2701048.6843 | 1247719.1897
125 | 2701073.5005 | 1247787.082
126 | 2701002.3751 | 1247733.4415
127 | 2701080.0562 | 1247803.6511
128 | 2701122.5264 | 1247694.1289
129 | 2701125.6483 | 1247693.2999
130 | 2701156.9205 | 1248156.1111
131 | 2701064.4576 | 1248048.6321
132 | 2701061.4286 | 1248042.2841
133 | 2701069.9708 | 1248060.1864
134 | 2701147.5147 | 1247670.8257
135 | 2701139.7468 | 1247647.953
136 | 2701080.0298 | 1247676.7231
137 | 2701081.6906 | 1247661.8851
138 | 2701149.1031 | 1247878.9044
139 | 2701162.2963 | 1247872.2246
140 | 2701166.285 | 1248134.9765
141 | 2701125.7095 | 1247938.678
142 | 2701108.0832 | 1247947.9496
143 | 2701102.055 | 1247951.1205
144 | 2701113.9009 | 1247944.8894
145 | 2701119.6196 | 1247941.8813
146 | 2701115.7018 | 1248024.9172
147 | 2701121.3055 | 1248022.0826
148 | 2701128.088 | 1248018.6516
149 | 2701132.6163 | 1248016.361
150 | 2701137.955 | 1248013.6604
151 | 2701144.1075 | 1248010.5481
152 | 2701149.2461 | 1248007.9487
153 | 2701122.4382 | 1247892.405

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97015 | -0.57564 | 0.0030688 | 0.00076911
1 | 0.97029 | -0.57279 | 0 | 0
2 | 0.97041 | -0.57047 | 0 | 0
3 | 0.97091 | -0.56046 | 0 | 0
4 | 0.97126 | -0.55358 | 0 | 0
5 | 0.97068 | -0.56502 | 0.0031735 | 0.00079536
6 | 0.97013 | -0.5759 | 0.00042981 | 0.00010772
7 | 0.97169 | -0.54519 | 0 | 0
8 | 0.97194 | -0.54023 | 0 | 0
9 | 0.97142 | -0.55047 | 0.0058535 | 0.001467
10 | 0.9713 | -0.55291 | 0 | 0
11 | 0.9705 | -0.56873 | 0 | 0
12 | 0.97076 | -0.56346 | 0 | 0
13 | 0.97038 | -0.57105 | 0.023677 | 0.005934
14 | 0.97106 | -0.5576 | 0 | 0
15 | 0.97049 | -0.56876 | 0.02516 | 0.0063057
16 | 0.97087 | -0.56129 | 0.0085888 | 0.0021526
17 | 0.9701 | -0.57665 | 0.010012 | 0.0025092
18 | 0.97133 | -0.55219 | 0.021025 | 0.0052693
19 | 0.97279 | -0.52337 | 0.0071919 | 0.0018024
20 | 0.97126 | -0.55362 | 0 | 0
21 | 0.97998 | -0.38392 | 0.0037957 | 0.0009513
22 | 0.98025 | -0.37846 | 0.0013646 | 0.00034201
23 | 0.97979 | -0.38747 | 0.0017103 | 0.00042864
24 | 0.98025 | -0.37844 | 0.0013975 | 0.00035025
25 | 0.97979 | -0.38749 | 0.0013652 | 0.00034216
26 | 0.98052 | -0.37318 | 0.0014794 | 0.00037076
27 | 0.97978 | -0.38775 | 0.0019373 | 0.00048554
28 | 0.98077 | -0.36837 | 0 | 0
29 | 0.97968 | -0.38968 | 0 | 0
30 | 0.9772 | -0.43842 | 0.0020332 | 0.00050957
31 | 0.97702 | -0.4419 | 0.0022351 | 0.00056018
32 | 0.97728 | -0.43679 | 0.0014372 | 0.0003602
33 | 0.97695 | -0.44323 | 0.00088432 | 0.00022163
34 | 0.97738 | -0.43474 | 0 | 0
35 | 0.97689 | -0.44453 | 0.0032858 | 0.00082351
36 | 0.9773 | -0.43647 | 0.0017054 | 0.0004274
37 | 0.97746 | -0.43329 | 0.005543 | 0.0013892
38 | 0.97728 | -0.43684 | 0.0019333 | 0.00048453
39 | 0.97781 | -0.42638 | 0.0031278 | 0.00078391
40 | 0.97942 | -0.39485 | 0.0011152 | 0.00027949
41 | 0.97939 | -0.39539 | 0.00061256 | 0.00015352
42 | 0.98352 | -0.31401 | 0.0018969 | 0.00047541
43 | 0.98445 | -0.29608 | 0.0017271 | 0.00043285
44 | 0.98295 | -0.32487 | 0 | 0
45 | 0.98508 | -0.28388 | 0 | 0
46 | 0.98234 | -0.33681 | 0.0013232 | 0.00033163
47 | 0.98494 | -0.28656 | 0.0014796 | 0.00037083
48 | 0.98537 | -0.27823 | 0.0015507 | 0.00038864
49 | 0.98231 | -0.33733 | 0.0010654 | 0.00026702
50 | 0.98494 | -0.28666 | 0.0014482 | 0.00036295
51 | 0.98638 | -0.25888 | 0.0014919 | 0.00037392
52 | 0.97769 | -0.42719 | 0 | 0
53 | 0.97823 | -0.41655 | 0.0013275 | 0.0003327
54 | 0.97632 | -0.45394 | 0.00085213 | 0.00021356
55 | 0.98122 | -0.35846 | 0.001052 | 0.00026366
56 | 0.97902 | -0.40121 | 0.0014694 | 0.00036826
57 | 0.97598 | -0.46069 | 0.0013124 | 0.00032893
58 | 0.98747 | -0.23801 | 0 | 0
59 | 0.98783 | -0.231 | 0.0054712 | 0.0013712
60 | 0.98731 | -0.24109 | 0.0019126 | 0.00047933
61 | 0.98923 | -0.20425 | 0 | 0
62 | 0.98727 | -0.24191 | 0.0018944 | 0.00047478
63 | 0.9904 | -0.18182 | 0.00092624 | 0.00023214
64 | 0.98748 | -0.2379 | 0.0010199 | 0.00025562
65 | 0.98717 | -0.24371 | 0.0018014 | 0.00045147
66 | 0.97841 | -0.41465 | 0 | 0
67 | 0.97865 | -0.40991 | 0.0016226 | 0.00040667
68 | 0.9925 | -0.14178 | 0.0017795 | 0.00044599
69 | 0.98686 | -0.24995 | 0.00089823 | 0.00022512
70 | 0.97881 | -0.40682 | 0.001672 | 0.00041905
71 | 0.99243 | -0.14313 | 0.00092554 | 0.00023196
72 | 0.99579 | -0.079473 | 0 | 0
73 | 0.98628 | -0.26114 | 0.00089489 | 0.00022428
74 | 0.98482 | -0.28887 | 0.0012825 | 0.00032143
75 | 0.98482 | -0.28896 | 0.0013184 | 0.00033043
76 | 0.98479 | -0.28954 | 0.0030204 | 0.00075698
77 | 0.98115 | -0.35983 | 0.0011942 | 0.00029929
78 | 0.98042 | -0.37402 | 0.0012749 | 0.00031951
79 | 0.98012 | -0.37973 | 0.0067681 | 0.0016963
80 | 0.97985 | -0.38507 | 0.0014657 | 0.00036734
81 | 0.97909 | -0.39993 | 0.0010159 | 0.00025461
82 | 0.98712 | -0.24472 | 0.004415 | 0.0011065
83 | 0.97894 | -0.40424 | 0.0015434 | 0.00038682
84 | 0.97934 | -0.39644 | 0.00056489 | 0.00014158
85 | 0.97407 | -0.49819 | 0.034792 | 0.0087198
86 | 0.97309 | -0.51748 | 0 | 0
87 | 0.97471 | -0.48551 | 0 | 0
88 | 0.97894 | -0.40428 | 0.00082969 | 0.00020794
89 | 0.97901 | -0.40288 | 0.00067179 | 0.00016837
90 | 0.97893 | -0.40449 | 0.0012321 | 0.0003088
91 | 0.97913 | -0.40057 | 0.00077056 | 0.00019312
92 | 0.97886 | -0.40579 | 0 | 0
93 | 0.97907 | -0.40171 | 0.0011912 | 0.00029854
94 | 0.97876 | -0.40784 | 0.0010381 | 0.00026017
95 | 0.97904 | -0.40225 | 0.001066 | 0.00026717
96 | 0.9787 | -0.40904 | 0 | 0
97 | 0.99077 | -0.17588 | 0.0035105 | 0.00087981
98 | 0.99264 | -0.13985 | 0.0080174 | 0.0020094
99 | 0.98965 | -0.19766 | 0.0035306 | 0.00088485
100 | 0.99431 | -0.10774 | 0.011063 | 0.0027726
101 | 0.98774 | -0.23458 | 0 | 0
102 | 0.99536 | -0.087712 | 0 | 0
103 | 0.98726 | -0.24397 | 0.0096552 | 0.0024198
104 | 0.98654 | -0.25805 | 0.0071907 | 0.0018021
105 | 0.97963 | -0.39066 | 0.0032782 | 0.00082158
106 | 0.97939 | -0.39549 | 0.00086015 | 0.00021557
107 | 0.9799 | -0.3855 | 0 | 0
108 | 0.9793 | -0.39719 | 0.00092579 | 0.00023202
109 | 0.98012 | -0.38111 | 0 | 0
110 | 0.97926 | -0.39804 | 0.0071275 | 0.0017863
111 | 0.98053 | -0.37305 | 0 | 0
112 | 0.98035 | -0.37654 | 0.0055176 | 0.0013829
113 | 0.98133 | -0.35748 | 0 | 0
114 | 0.98569 | -0.27248 | 0.00097517 | 0.0002444
115 | 0.9851 | -0.28408 | 0.00099358 | 0.00024901
116 | 0.98259 | -0.33287 | 0 | 0
117 | 0.98101 | -0.36361 | 0.0013992 | 0.00035068
118 | 0.98113 | -0.36129 | 0.0013995 | 0.00035074
119 | 0.98101 | -0.36368 | 0.0013629 | 0.00034158
120 | 0.98549 | -0.27841 | 0.005645 | 0.0014148
121 | 0.98577 | -0.27311 | 0.0030431 | 0.00076266
122 | 0.98544 | -0.27938 | 0.0030423 | 0.00076248
123 | 0.98598 | -0.26894 | 0.0056466 | 0.0014152
124 | 0.98538 | -0.28057 | 0 | 0
125 | 0.98601 | -0.2684 | 0.003531 | 0.00088494
126 | 0.98525 | -0.28327 | 0.0031041 | 0.00077795
127 | 0.9864 | -0.26072 | 0.0034609 | 0.00086739
128 | 0.97093 | -0.56014 | 0.0056457 | 0.0014149
129 | 0.97095 | -0.5598 | 0.0061699 | 0.0015463
130 | 0.97902 | -0.40278 | 0.00088696 | 0.00022229
131 | 0.98108 | -0.36233 | 0.0041 | 0.0010275
132 | 0.98113 | -0.36131 | 0.0013639 | 0.00034182
133 | 0.98103 | -0.36323 | 0.0038749 | 0.00097113
134 | 0.97119 | -0.55505 | 0 | 0
135 | 0.97111 | -0.5566 | 0.0034802 | 0.00087221
136 | 0.97081 | -0.56252 | 0.00097073 | 0.00024329
137 | 0.97059 | -0.56691 | 0.01466 | 0.0036741
138 | 0.99858 | -0.026649 | 0.0096558 | 0.00242
139 | 1 | 0 | -0.42262 | -0.10861
140 | 0.97864 | -0.41022 | 0.0014447 | 0.00036208
141 | 0.99239 | -0.14384 | 0.0010203 | 0.00025571
142 | 0.99232 | -0.14521 | 0.00097607 | 0.00024463
143 | 0.99231 | -0.14545 | 0.0019844 | 0.00049733
144 | 0.99234 | -0.14486 | 0.00089416 | 0.0002241
145 | 0.99236 | -0.14442 | 0.00089827 | 0.00022513
146 | 0.98025 | -0.37847 | 0.0016007 | 0.00040117
147 | 0.98004 | -0.38263 | 0.0015429 | 0.0003867
148 | 0.97979 | -0.38745 | 0.0015777 | 0.00039542
149 | 0.97964 | -0.39053 | 0.0015494 | 0.00038832
150 | 0.97946 | -0.394 | 0.0015959 | 0.00039997
151 | 0.97927 | -0.39779 | 0.0015547 | 0.00038964
152 | 0.97911 | -0.40079 | 0.0016817 | 0.00042148
153 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0030688 | -0.00076911 | 0.0030692 | 0.00076876 | 4.1654e-07 | -3.526e-07 | 0.0047069 | 0.0047067 | 0.0047069 | 0.97015 | -0.57564 | 0.97029 | -0.57279 | 1.2931
1 | -0.0030692 | -0.00076876 | 0.0030696 | 0.00076847 | 3.3811e-07 | -2.8638e-07 | 0.0047067 | 0.0047065 | 0.0047067 | 0.97029 | -0.57279 | 0.97041 | -0.57047 | 1.2931
2 | 0.010445 | 0.0026185 | -0.010442 | -0.0026171 | 2.6995e-06 | 1.3811e-06 | 0.016016 | 0.016016 | 0.016016 | 0.97041 | -0.57047 | 0.97013 | -0.5759 | 4.4
3 | -0.013514 | -0.0033869 | 0.013518 | 0.0033889 | 3.5099e-06 | 1.977e-06 | 0.020723 | 0.020722 | 0.020723 | 0.97041 | -0.57047 | 0.97068 | -0.56502 | 5.693
4 | -0.016695 | -0.0041864 | 0.0167 | 0.0041888 | 5.4795e-06 | 2.4024e-06 | 0.025587 | 0.025587 | 0.025587 | 0.97091 | -0.56046 | 0.97126 | -0.55358 | 3.5147
5 | 0.016695 | 0.0041864 | -0.016691 | -0.0041843 | 3.6274e-06 | 2.1388e-06 | 0.025587 | 0.025587 | 0.025587 | 0.97091 | -0.56046 | 0.97068 | -0.56502 | 7.0295
6 | -0.0167 | -0.0041888 | 0.016701 | 0.0041887 | 5.2894e-07 | -8.812e-08 | 0.025587 | 0.025587 | 0.025587 | 0.97126 | -0.55358 | 0.9713 | -0.55291 | 1.7573
7 | 0.010012 | 0.0025094 | -0.010012 | -0.0025092 | 3.5959e-07 | 1.7993e-07 | 0.015357 | 0.015357 | 0.015357 | 0.97013 | -0.5759 | 0.9701 | -0.57665 | 4.2189
8 | -0.036808 | -0.0092285 | 0.036816 | 0.0092326 | 8.6904e-06 | 4.1159e-06 | 0.056368 | 0.056367 | 0.056368 | 0.97169 | -0.54519 | 0.97194 | -0.54023 | 3.8714
9 | 0.036808 | 0.0092285 | -0.036798 | -0.0092241 | 9.2649e-06 | 4.3889e-06 | 0.056368 | 0.056368 | 0.056368 | 0.97169 | -0.54519 | 0.97142 | -0.55047 | 3.8714
10 | 0.095251 | 0.023907 | -0.095197 | -0.023874 | 5.4283e-05 | 3.3392e-05 | 0.14584 | 0.14584 | 0.14584 | 0.97194 | -0.54023 | 0.97133 | -0.55219 | 10.0166
11 | -0.13207 | -0.03314 | 0.13217 | 0.033207 | 0.00010628 | 6.6642e-05 | 0.20221 | 0.20221 | 0.20221 | 0.97194 | -0.54023 | 0.97279 | -0.52337 | 13.8879
12 | 0.030945 | 0.007757 | -0.03094 | -0.0077552 | 4.6395e-06 | 1.8788e-06 | 0.047402 | 0.047402 | 0.047402 | 0.97142 | -0.55047 | 0.97126 | -0.55362 | 3.2556
13 | -0.07417 | -0.018603 | 0.074172 | 0.018605 | 2.5496e-06 | 1.5274e-06 | 0.11363 | 0.11363 | 0.11363 | 0.9713 | -0.55291 | 0.97133 | -0.55219 | 7.8044
14 | 0.057469 | 0.014414 | -0.057456 | -0.014407 | 1.2842e-05 | 7.3442e-06 | 0.088046 | 0.088046 | 0.088046 | 0.9713 | -0.55291 | 0.97106 | -0.5576 | 6.0471
15 | -0.02368 | -0.0059355 | 0.023686 | 0.0059369 | 5.9414e-06 | 1.4256e-06 | 0.036307 | 0.036306 | 0.036307 | 0.9705 | -0.56873 | 0.97076 | -0.56346 | 2.4936
16 | 0.02368 | 0.0059355 | -0.023677 | -0.005934 | 2.6158e-06 | 1.4126e-06 | 0.036307 | 0.036307 | 0.036307 | 0.9705 | -0.56873 | 0.97038 | -0.57105 | 4.9873
17 | -0.048852 | -0.012246 | 0.048866 | 0.012254 | 1.3647e-05 | 7.4496e-06 | 0.074883 | 0.074882 | 0.074883 | 0.97076 | -0.56346 | 0.97106 | -0.5576 | 5.1431
18 | 0.025166 | 0.0063096 | -0.02516 | -0.0063057 | 6.3558e-06 | 3.9269e-06 | 0.038577 | 0.038577 | 0.038577 | 0.97076 | -0.56346 | 0.97049 | -0.56876 | 10.598
19 | 0.0085903 | 0.0021532 | -0.0085888 | -0.0021526 | 1.5105e-06 | 6.7921e-07 | 0.013164 | 0.013164 | 0.013164 | 0.97106 | -0.5576 | 0.97087 | -0.56129 | 3.6164
20 | -0.13937 | -0.035009 | 0.13941 | 0.035034 | 3.9203e-05 | 2.4633e-05 | 0.21321 | 0.21321 | 0.21321 | 0.97279 | -0.52337 | 0.97309 | -0.51748 | 14.6434
21 | 0.011819 | 0.0029632 | -0.011816 | -0.0029613 | 3.4822e-06 | 1.8782e-06 | 0.018108 | 0.018108 | 0.018108 | 0.97126 | -0.55362 | 0.97095 | -0.5598 | 4.9747
22 | 0.019121 | 0.004792 | -0.01912 | -0.004792 | 1.3007e-06 | 3.2168e-08 | 0.029294 | 0.029295 | 0.029295 | 0.97126 | -0.55362 | 0.97119 | -0.55505 | 2.012
23 | -0.020243 | -0.0050733 | 0.020249 | 0.0050765 | 5.2639e-06 | 3.1816e-06 | 0.030738 | 0.030738 | 0.030738 | 0.97998 | -0.38392 | 0.98025 | -0.37846 | 8.4445
24 | 0.016448 | 0.004122 | -0.016445 | -0.0041204 | 2.7829e-06 | 1.6312e-06 | 0.024975 | 0.024975 | 0.024975 | 0.97998 | -0.38392 | 0.97979 | -0.38747 | 6.8611
25 | -0.021613 | -0.0054185 | 0.021613 | 0.0054185 | 2.2082e-08 | 1.3442e-08 | 0.032809 | 0.032809 | 0.032809 | 0.98025 | -0.37846 | 0.98025 | -0.37844 | 9.0136
26 | 0.014735 | 0.0036917 | -0.014735 | -0.0036917 | 1.2334e-08 | 7.066e-09 | 0.022377 | 0.022377 | 0.022377 | 0.97979 | -0.38747 | 0.97979 | -0.38749 | 6.1476
27 | -0.023011 | -0.0057688 | 0.023017 | 0.0057723 | 5.7684e-06 | 3.5328e-06 | 0.034931 | 0.034931 | 0.034931 | 0.98025 | -0.37844 | 0.98052 | -0.37318 | 9.5964
28 | 0.013369 | 0.0033496 | -0.013369 | -0.0033495 | 1.7013e-07 | 9.5023e-08 | 0.020304 | 0.020304 | 0.020304 | 0.97979 | -0.38749 | 0.97978 | -0.38775 | 5.5779
29 | -0.024496 | -0.0061431 | 0.024502 | 0.0061465 | 5.6176e-06 | 3.4585e-06 | 0.037176 | 0.037176 | 0.037176 | 0.98052 | -0.37318 | 0.98077 | -0.36837 | 10.2131
30 | 0.011432 | 0.0028639 | -0.011431 | -0.0028634 | 1.0486e-06 | 5.5427e-07 | 0.017361 | 0.017362 | 0.017362 | 0.97978 | -0.38775 | 0.97968 | -0.38968 | 4.7696
31 | 0.038219 | 0.0096114 | -0.038201 | -0.0095998 | 1.8424e-05 | 1.1607e-05 | 0.057998 | 0.057998 | 0.057998 | 0.98077 | -0.36837 | 0.98025 | -0.37847 | 15.9334
32 | -0.062721 | -0.015758 | 0.062735 | 0.015767 | 1.4042e-05 | 8.9346e-06 | 0.095173 | 0.095173 | 0.095173 | 0.98077 | -0.36837 | 0.98101 | -0.36368 | 26.1466
33 | 0.011431 | 0.0028634 | -0.011428 | -0.0028619 | 2.8159e-06 | 1.4886e-06 | 0.017362 | 0.017362 | 0.017362 | 0.97968 | -0.38968 | 0.97942 | -0.39485 | 4.7697
34 | 0.0064068 | 0.0016054 | -0.0064058 | -0.0016051 | 1.0616e-06 | 3.0687e-07 | 0.0097558 | 0.009756 | 0.009756 | 0.9772 | -0.43842 | 0.97702 | -0.4419 | 2.6802
35 | -0.00844 | -0.002115 | 0.0084407 | 0.0021153 | 6.537e-07 | 2.8614e-07 | 0.012852 | 0.012852 | 0.012852 | 0.9772 | -0.43842 | 0.97728 | -0.43679 | 3.5307
36 | 0.0041706 | 0.0010449 | -0.0041704 | -0.001045 | 2.6495e-07 | -4.9722e-08 | 0.0063518 | 0.0063519 | 0.0063519 | 0.97702 | -0.4419 | 0.97695 | -0.44323 | 1.745
37 | -0.0098779 | -0.0024755 | 0.0098789 | 0.002476 | 9.6496e-07 | 4.7502e-07 | 0.01504 | 0.01504 | 0.01504 | 0.97728 | -0.43679 | 0.97738 | -0.43474 | 4.1319
38 | 0.003286 | 0.00082337 | -0.0032858 | -0.00082351 | 2.0378e-07 | -1.4119e-07 | 0.005005 | 0.0050051 | 0.0050051 | 0.97695 | -0.44323 | 0.97689 | -0.44453 | 1.375
39 | 0.003639 | 0.00091169 | -0.0036387 | -0.00091183 | 3.0005e-07 | -1.3465e-07 | 0.0055401 | 0.0055402 | 0.0055402 | 0.97738 | -0.43474 | 0.9773 | -0.43647 | 1.522
40 | -0.013518 | -0.0033877 | 0.013519 | 0.0033882 | 9.328e-07 | 5.2338e-07 | 0.02058 | 0.02058 | 0.02058 | 0.97738 | -0.43474 | 0.97746 | -0.43329 | 5.6539
41 | 0.0019333 | 0.00048442 | -0.0019333 | -0.00048453 | 3.3693e-08 | -1.0836e-07 | 0.0029436 | 0.0029437 | 0.0029437 | 0.9773 | -0.43647 | 0.97728 | -0.43684 | 0.8087
42 | -0.019062 | -0.0047774 | 0.019068 | 0.0047812 | 6.2781e-06 | 3.7687e-06 | 0.029018 | 0.029018 | 0.029018 | 0.97746 | -0.43329 | 0.97781 | -0.42638 | 7.9721
43 | -0.022196 | -0.0055651 | 0.022208 | 0.0055726 | 1.2414e-05 | 7.5809e-06 | 0.033778 | 0.033778 | 0.033778 | 0.97781 | -0.42638 | 0.97841 | -0.41465 | 9.2797
44 | 0.010313 | 0.0025824 | -0.010313 | -0.0025823 | 2.6144e-07 | 1.3158e-07 | 0.015667 | 0.015667 | 0.015667 | 0.97942 | -0.39485 | 0.97939 | -0.39539 | 4.3042
45 | 0.0097 | 0.0024287 | -0.0096995 | -0.0024285 | 4.8785e-07 | 2.3684e-07 | 0.014737 | 0.014737 | 0.014737 | 0.97939 | -0.39539 | 0.97934 | -0.39644 | 4.0485
46 | -0.19796 | -0.050376 | 0.19813 | 0.050485 | 0.00017132 | 0.00010861 | 0.29978 | 0.29978 | 0.29978 | 0.98352 | -0.31401 | 0.98445 | -0.29608 | 20.5893
47 | 0.19606 | 0.049901 | -0.19596 | -0.049836 | 0.00010257 | 6.5018e-05 | 0.29691 | 0.29691 | 0.29691 | 0.98352 | -0.31401 | 0.98295 | -0.32487 | 20.3922
48 | -0.19986 | -0.050918 | 0.19998 | 0.050992 | 0.00011768 | 7.4616e-05 | 0.30239 | 0.30239 | 0.30239 | 0.98445 | -0.29608 | 0.98508 | -0.28388 | 20.7686
49 | 0.19596 | 0.049836 | -0.19585 | -0.049764 | 0.00011267 | 7.142e-05 | 0.29691 | 0.29691 | 0.29691 | 0.98295 | -0.32487 | 0.98234 | -0.33681 | 20.3922
50 | 0.008551 | 0.0021431 | -0.0085499 | -0.0021426 | 1.093e-06 | 4.7716e-07 | 0.012917 | 0.012917 | 0.012917 | 0.98508 | -0.28388 | 0.98494 | -0.28656 | 3.5486
51 | -0.20853 | -0.053136 | 0.20858 | 0.053172 | 5.6834e-05 | 3.6063e-05 | 0.31531 | 0.31531 | 0.31531 | 0.98508 | -0.28388 | 0.98537 | -0.27823 | 21.6557
52 | 0.19453 | 0.049433 | -0.19452 | -0.04943 | 4.8658e-06 | 3.0839e-06 | 0.29491 | 0.29491 | 0.29491 | 0.98234 | -0.33681 | 0.98231 | -0.33733 | 20.2546
53 | 0.0070702 | 0.0017718 | -0.0070702 | -0.0017718 | 3.0817e-08 | 1.0556e-08 | 0.010681 | 0.010681 | 0.010681 | 0.98494 | -0.28656 | 0.98494 | -0.28666 | 2.9345
54 | -0.21014 | -0.05356 | 0.21033 | 0.053685 | 0.0001965 | 0.0001247 | 0.31765 | 0.31765 | 0.31765 | 0.98537 | -0.27823 | 0.98638 | -0.25888 | 21.8165
55 | 0.19346 | 0.049163 | -0.19326 | -0.049038 | 0.00019655 | 0.00012456 | 0.29329 | 0.29329 | 0.29329 | 0.98231 | -0.33733 | 0.98122 | -0.35846 | 20.1438
56 | 0.005622 | 0.0014089 | -0.0056215 | -0.0014088 | 5.9376e-07 | 1.0071e-07 | 0.0084936 | 0.0084937 | 0.0084937 | 0.98494 | -0.28666 | 0.98482 | -0.28887 | 2.3334
57 | -0.21182 | -0.054059 | 0.21204 | 0.054195 | 0.00021378 | 0.00013568 | 0.3199 | 0.3199 | 0.3199 | 0.98638 | -0.25888 | 0.98747 | -0.23801 | 21.9711
58 | -0.17709 | -0.044754 | 0.17718 | 0.044811 | 9.0407e-05 | 5.7195e-05 | 0.26966 | 0.26966 | 0.26966 | 0.97769 | -0.42719 | 0.97823 | -0.41655 | 18.5203
59 | 0.17709 | 0.044754 | -0.17686 | -0.044611 | 0.00022683 | 0.0001435 | 0.26966 | 0.26966 | 0.26966 | 0.97769 | -0.42719 | 0.97632 | -0.45394 | 18.5203
60 | -0.1785 | -0.045144 | 0.17864 | 0.045227 | 0.00013147 | 8.3185e-05 | 0.27167 | 0.27167 | 0.27167 | 0.97823 | -0.41655 | 0.97902 | -0.40121 | 18.659
61 | 0.17601 | 0.044397 | -0.17595 | -0.044361 | 5.6797e-05 | 3.593e-05 | 0.26836 | 0.26836 | 0.26836 | 0.97632 | -0.45394 | 0.97598 | -0.46069 | 18.4312
62 | 0.19221 | 0.048775 | -0.19219 | -0.048766 | 1.2743e-05 | 8.0748e-06 | 0.2917 | 0.2917 | 0.2917 | 0.98122 | -0.35846 | 0.98115 | -0.35983 | 20.0342
63 | -0.18011 | -0.045595 | 0.18012 | 0.045602 | 1.1027e-05 | 6.9784e-06 | 0.27391 | 0.27391 | 0.27391 | 0.97902 | -0.40121 | 0.97909 | -0.39993 | 18.8123
64 | 0.17464 | 0.044032 | -0.17443 | -0.043901 | 0.00020721 | 0.00013106 | 0.26636 | 0.26636 | 0.26636 | 0.97598 | -0.46069 | 0.97471 | -0.48551 | 18.2938
65 | -0.22206 | -0.056708 | 0.22214 | 0.056755 | 7.5241e-05 | 4.7788e-05 | 0.33501 | 0.33501 | 0.33501 | 0.98747 | -0.23801 | 0.98783 | -0.231 | 23.0087
66 | 0.010026 | 0.002513 | -0.010024 | -0.0025123 | 1.4712e-06 | 7.2172e-07 | 0.015108 | 0.015108 | 0.015108 | 0.98747 | -0.23801 | 0.98731 | -0.24109 | 4.1506
67 | -0.22761 | -0.058127 | 0.2279 | 0.058314 | 0.00029475 | 0.00018727 | 0.34325 | 0.34325 | 0.34325 | 0.98783 | -0.231 | 0.98923 | -0.20425 | 23.5747
68 | 0.0081119 | 0.002033 | -0.0081115 | -0.0020329 | 3.1699e-07 | 1.3055e-07 | 0.012226 | 0.012226 | 0.012226 | 0.98731 | -0.24109 | 0.98727 | -0.24191 | 3.3587
69 | -0.32739 | -0.083579 | 0.32774 | 0.083806 | 0.00035527 | 0.00022657 | 0.49301 | 0.49301 | 0.49301 | 0.98923 | -0.20425 | 0.9904 | -0.18182 | 33.8604
70 | 0.099481 | 0.025265 | -0.099321 | -0.025163 | 0.00016084 | 0.00010269 | 0.14976 | 0.14976 | 0.14976 | 0.98923 | -0.20425 | 0.98748 | -0.2379 | 41.1431
71 | 0.0062172 | 0.0015581 | -0.0062166 | -0.001558 | 5.317e-07 | 1.3383e-07 | 0.0093705 | 0.0093706 | 0.0093706 | 0.98727 | -0.24191 | 0.98717 | -0.24371 | 2.5743
72 | -0.32867 | -0.084038 | 0.32931 | 0.084445 | 0.00063816 | 0.00040699 | 0.4944 | 0.4944 | 0.4944 | 0.9904 | -0.18182 | 0.9925 | -0.14178 | 33.956
73 | 0.098301 | 0.024907 | -0.098244 | -0.024871 | 5.6861e-05 | 3.6303e-05 | 0.14822 | 0.14822 | 0.14822 | 0.98748 | -0.2379 | 0.98686 | -0.24995 | 40.7209
74 | 0.0044153 | 0.0011065 | -0.004415 | -0.0011065 | 2.1411e-07 | -2.7762e-08 | 0.0066553 | 0.0066554 | 0.0066554 | 0.98717 | -0.24371 | 0.98712 | -0.24472 | 1.8284
75 | -0.022208 | -0.0055726 | 0.022213 | 0.0055757 | 5.0263e-06 | 3.0692e-06 | 0.033778 | 0.033778 | 0.033778 | 0.97841 | -0.41465 | 0.97865 | -0.40991 | 9.2797
76 | -0.023836 | -0.0059824 | 0.023839 | 0.0059845 | 3.5084e-06 | 2.1559e-06 | 0.036245 | 0.036245 | 0.036245 | 0.97865 | -0.40991 | 0.97881 | -0.40682 | 9.9575
77 | 0.0066996 | 0.0016789 | -0.0066992 | -0.0016787 | 4.3184e-07 | 1.2888e-07 | 0.010044 | 0.010044 | 0.010044 | 0.9925 | -0.14178 | 0.99243 | -0.14313 | 2.7595
78 | -0.33779 | -0.08657 | 0.33881 | 0.087223 | 0.0010235 | 0.00065282 | 0.50711 | 0.50711 | 0.50711 | 0.9925 | -0.14178 | 0.99579 | -0.079473 | 34.829
79 | 0.097346 | 0.024646 | -0.097293 | -0.024612 | 5.2281e-05 | 3.3377e-05 | 0.14687 | 0.14687 | 0.14687 | 0.98686 | -0.24995 | 0.98628 | -0.26114 | 40.3488
80 | -0.025512 | -0.0064036 | 0.025515 | 0.0064055 | 3.1443e-06 | 1.9423e-06 | 0.038787 | 0.038787 | 0.038787 | 0.97881 | -0.40682 | 0.97894 | -0.40424 | 10.6558
81 | 0.0057736 | 0.0014468 | -0.0057734 | -0.0014467 | 1.9629e-07 | 3.5374e-08 | 0.0086567 | 0.0086567 | 0.0086567 | 0.99243 | -0.14313 | 0.99239 | -0.14384 | 2.3782
82 | -0.40972 | -0.10517 | 0.41077 | 0.10584 | 0.0010533 | 0.00067258 | 0.61313 | 0.61313 | 0.61313 | 0.99579 | -0.079473 | 0.99858 | -0.026649 | 42.1107
83 | 0.070908 | 0.017949 | -0.07088 | -0.017931 | 2.8036e-05 | 1.7856e-05 | 0.10602 | 0.10602 | 0.10602 | 0.99579 | -0.079473 | 0.99536 | -0.087712 | 29.127
84 | 0.096398 | 0.024388 | -0.096346 | -0.024355 | 5.2423e-05 | 3.3466e-05 | 0.14552 | 0.14552 | 0.14552 | 0.98628 | -0.26114 | 0.98569 | -0.27248 | 39.9779
85 | 0.0043389 | 0.0010873 | -0.0043389 | -0.0010873 | 1.8504e-08 | -2.7657e-09 | 0.0065559 | 0.0065559 | 0.0065559 | 0.98482 | -0.28887 | 0.98482 | -0.28896 | 1.8011
86 | 0.0030205 | 0.0007569 | -0.0030204 | -0.00075698 | 8.3743e-08 | -8.2824e-08 | 0.0045638 | 0.0045638 | 0.0045638 | 0.98482 | -0.28896 | 0.98479 | -0.28954 | 1.2538
87 | 0.191 | 0.048467 | -0.19087 | -0.048385 | 0.0001302 | 8.2495e-05 | 0.28989 | 0.28989 | 0.28989 | 0.98115 | -0.35983 | 0.98042 | -0.37402 | 19.9098
88 | 0.18959 | 0.048065 | -0.18954 | -0.048032 | 5.1986e-05 | 3.2934e-05 | 0.28795 | 0.28795 | 0.28795 | 0.98042 | -0.37402 | 0.98012 | -0.37973 | 19.7769
89 | 0.18277 | 0.046336 | -0.18273 | -0.046306 | 4.6977e-05 | 2.9738e-05 | 0.27768 | 0.27768 | 0.27768 | 0.98012 | -0.37973 | 0.97985 | -0.38507 | 19.0712
90 | 0.18126 | 0.045939 | -0.18113 | -0.045857 | 0.00012931 | 8.1843e-05 | 0.27545 | 0.27545 | 0.27545 | 0.97985 | -0.38507 | 0.97909 | -0.39993 | 18.9184
91 | -0.027058 | -0.0067924 | 0.027063 | 0.0067951 | 4.4446e-06 | 2.7564e-06 | 0.041133 | 0.041133 | 0.041133 | 0.97894 | -0.40424 | 0.97911 | -0.40079 | 11.3003
92 | 0.0091346 | 0.0022869 | -0.0091328 | -0.0022861 | 1.7965e-06 | 8.3688e-07 | 0.013878 | 0.013878 | 0.013878 | 0.97934 | -0.39644 | 0.97913 | -0.40057 | 3.8128
93 | 0.13953 | 0.035115 | -0.13941 | -0.035034 | 0.00012854 | 8.0765e-05 | 0.21321 | 0.21321 | 0.21321 | 0.97407 | -0.49819 | 0.97309 | -0.51748 | 14.6434
94 | -0.17433 | -0.043834 | 0.17443 | 0.043901 | 0.0001056 | 6.6791e-05 | 0.26636 | 0.26636 | 0.26636 | 0.97407 | -0.49819 | 0.97471 | -0.48551 | 18.2938
95 | -0.0045452 | -0.0011373 | 0.0045455 | 0.0011372 | 3.0352e-07 | -1.8995e-08 | 0.0069082 | 0.0069081 | 0.0069082 | 0.97894 | -0.40428 | 0.97901 | -0.40288 | 1.8979
96 | 0.0037155 | 0.00092933 | -0.0037155 | -0.00092934 | 3.6772e-08 | -1.5126e-08 | 0.005647 | 0.0056471 | 0.0056471 | 0.97894 | -0.40428 | 0.97893 | -0.40449 | 1.5514
97 | -0.0052173 | -0.0013056 | 0.0052179 | 0.0013057 | 5.7223e-07 | 6.0998e-08 | 0.0079292 | 0.0079291 | 0.0079292 | 0.97901 | -0.40288 | 0.97913 | -0.40057 | 2.1783
98 | 0.0024834 | 0.00062055 | -0.0024832 | -0.00062081 | 1.5364e-07 | -2.6324e-07 | 0.0037742 | 0.0037743 | 0.0037743 | 0.97893 | -0.40449 | 0.97886 | -0.40579 | 1.0369
99 | 0.0031444 | 0.0007873 | -0.0031442 | -0.00078744 | 1.6942e-07 | -1.4041e-07 | 0.0047784 | 0.0047785 | 0.0047785 | 0.97913 | -0.40057 | 0.97907 | -0.40171 | 1.3128
100 | 0.0024832 | 0.00062081 | -0.002483 | -0.00062123 | 2.4207e-07 | -4.146e-07 | 0.0037743 | 0.0037745 | 0.0037745 | 0.97886 | -0.40579 | 0.97876 | -0.40784 | 1.037
101 | 0.001953 | 0.0004889 | -0.001953 | -0.00048906 | 5.0378e-08 | -1.5952e-07 | 0.0029681 | 0.0029681 | 0.0029681 | 0.97907 | -0.40171 | 0.97904 | -0.40225 | 0.81542
102 | 0.0014449 | 0.00036105 | -0.0014448 | -0.00036157 | 8.2003e-08 | -5.1718e-07 | 0.0021963 | 0.0021965 | 0.0021965 | 0.97876 | -0.40784 | 0.9787 | -0.40904 | 0.60343
103 | 0.00088698 | 0.0002219 | -0.00088696 | -0.00022229 | 2.2304e-08 | -3.9731e-07 | 0.001348 | 0.0013481 | 0.0013481 | 0.97904 | -0.40225 | 0.97902 | -0.40278 | 0.37036
104 | 0.0014448 | 0.00036157 | -0.0014447 | -0.00036208 | 8.1268e-08 | -5.1237e-07 | 0.0021965 | 0.0021967 | 0.0021967 | 0.9787 | -0.40904 | 0.97864 | -0.41022 | 0.60349
105 | -0.051551 | -0.012991 | 0.05164 | 0.013048 | 8.9007e-05 | 5.6454e-05 | 0.077448 | 0.077448 | 0.077448 | 0.99077 | -0.17588 | 0.99264 | -0.13985 | 21.277
106 | 0.04804 | 0.012111 | -0.04799 | -0.01208 | 5.001e-05 | 3.1677e-05 | 0.072176 | 0.072176 | 0.072176 | 0.99077 | -0.17588 | 0.98965 | -0.19766 | 19.8286
107 | -0.059657 | -0.015057 | 0.059749 | 0.015115 | 9.1903e-05 | 5.8422e-05 | 0.089466 | 0.089466 | 0.089466 | 0.99264 | -0.13985 | 0.99431 | -0.10774 | 24.5787
108 | 0.04446 | 0.011195 | -0.044382 | -0.011145 | 7.8342e-05 | 4.954e-05 | 0.066867 | 0.066868 | 0.066868 | 0.98965 | -0.19766 | 0.98774 | -0.23458 | 18.3702
109 | -0.070812 | -0.017888 | 0.07088 | 0.017931 | 6.8058e-05 | 4.3348e-05 | 0.10602 | 0.10602 | 0.10602 | 0.99431 | -0.10774 | 0.99536 | -0.087712 | 29.127
110 | 0.044382 | 0.011145 | -0.044362 | -0.011133 | 1.9859e-05 | 1.2558e-05 | 0.066868 | 0.066868 | 0.066868 | 0.98774 | -0.23458 | 0.98726 | -0.24397 | 18.3703
111 | 0.034706 | 0.0087128 | -0.034683 | -0.0086982 | 2.3298e-05 | 1.4621e-05 | 0.052315 | 0.052315 | 0.052315 | 0.98726 | -0.24397 | 0.98654 | -0.25805 | 14.3724
112 | 0.027493 | 0.0068961 | -0.027489 | -0.0068939 | 3.5061e-06 | 2.1745e-06 | 0.04147 | 0.04147 | 0.04147 | 0.98654 | -0.25805 | 0.9864 | -0.26072 | 11.3928
113 | 0.0089164 | 0.0022352 | -0.0089144 | -0.0022343 | 2.0485e-06 | 9.3618e-07 | 0.013544 | 0.013544 | 0.013544 | 0.97963 | -0.39066 | 0.97939 | -0.39549 | 3.7209
114 | -0.012195 | -0.0030568 | 0.012198 | 0.0030584 | 2.9994e-06 | 1.626e-06 | 0.018523 | 0.018523 | 0.018523 | 0.97963 | -0.39066 | 0.9799 | -0.3855 | 5.0888
115 | 0.0080542 | 0.0020187 | -0.0080536 | -0.0020184 | 6.5247e-07 | 2.7138e-07 | 0.012237 | 0.012237 | 0.012237 | 0.97939 | -0.39549 | 0.9793 | -0.39719 | 3.3619
116 | -0.012198 | -0.0030584 | 0.0122 | 0.0030598 | 2.5565e-06 | 1.3858e-06 | 0.018523 | 0.018523 | 0.018523 | 0.9799 | -0.3855 | 0.98012 | -0.38111 | 5.0888
117 | 0.0071278 | 0.0017864 | -0.0071275 | -0.0017863 | 2.9076e-07 | 1.0292e-07 | 0.01083 | 0.01083 | 0.01083 | 0.9793 | -0.39719 | 0.97926 | -0.39804 | 2.9754
118 | -0.0122 | -0.0030598 | 0.012205 | 0.0030624 | 4.6874e-06 | 2.5406e-06 | 0.018523 | 0.018523 | 0.018523 | 0.98012 | -0.38111 | 0.98053 | -0.37305 | 5.0887
119 | 0.0055186 | 0.001383 | -0.0055176 | -0.0013829 | 9.1668e-07 | 1.4714e-07 | 0.0083747 | 0.0083749 | 0.0083749 | 0.98053 | -0.37305 | 0.98035 | -0.37654 | 2.3008
120 | -0.017723 | -0.0044454 | 0.017737 | 0.0044532 | 1.3166e-05 | 7.8138e-06 | 0.026898 | 0.026897 | 0.026898 | 0.98053 | -0.37305 | 0.98133 | -0.35748 | 7.3894
121 | 0.010741 | 0.0026923 | -0.010739 | -0.0026913 | 1.9529e-06 | 1.0019e-06 | 0.016287 | 0.016287 | 0.016287 | 0.98133 | -0.35748 | 0.98113 | -0.36129 | 4.4744
122 | -0.028477 | -0.0071455 | 0.028511 | 0.0071663 | 3.3454e-05 | 2.0805e-05 | 0.043184 | 0.043184 | 0.043184 | 0.98133 | -0.35748 | 0.98259 | -0.33287 | 11.8637
123 | 0.095371 | 0.02411 | -0.095318 | -0.024076 | 5.3022e-05 | 3.3848e-05 | 0.14405 | 0.14405 | 0.14405 | 0.98569 | -0.27248 | 0.9851 | -0.28408 | 39.5735
124 | 0.094324 | 0.023827 | -0.094104 | -0.023687 | 0.00022 | 0.00014043 | 0.14255 | 0.14255 | 0.14255 | 0.9851 | -0.28408 | 0.98259 | -0.33287 | 39.1612
125 | 0.065593 | 0.016521 | -0.065497 | -0.016459 | 9.6281e-05 | 6.1291e-05 | 0.099363 | 0.099363 | 0.099363 | 0.98259 | -0.33287 | 0.98101 | -0.36361 | 27.2976
126 | 0.064098 | 0.016109 | -0.064098 | -0.016108 | 1.9304e-07 | 1.2286e-07 | 0.097241 | 0.097241 | 0.097241 | 0.98101 | -0.36361 | 0.98101 | -0.36368 | 26.7145
127 | 0.0093392 | 0.0023406 | -0.0093392 | -0.0023406 | 8.0448e-09 | 3.7983e-09 | 0.014164 | 0.014164 | 0.014164 | 0.98113 | -0.36129 | 0.98113 | -0.36131 | 3.8913
128 | -0.011792 | -0.0029547 | 0.011795 | 0.0029563 | 2.9753e-06 | 1.5852e-06 | 0.017805 | 0.017805 | 0.017805 | 0.98549 | -0.27841 | 0.98577 | -0.27311 | 4.8915
129 | 0.0061473 | 0.00154 | -0.006147 | -0.0015399 | 2.8681e-07 | 7.0446e-08 | 0.0092816 | 0.0092817 | 0.0092817 | 0.98549 | -0.27841 | 0.98544 | -0.27938 | 2.5499
130 | -0.014838 | -0.003719 | 0.014841 | 0.0037207 | 2.9458e-06 | 1.6856e-06 | 0.022398 | 0.022398 | 0.022398 | 0.98577 | -0.27311 | 0.98598 | -0.26894 | 6.1534
131 | 0.0031046 | 0.00077743 | -0.0031045 | -0.00077759 | 1.7498e-07 | -1.5851e-07 | 0.0046877 | 0.0046878 | 0.0046878 | 0.98544 | -0.27938 | 0.98538 | -0.28057 | 1.2879
132 | -0.020488 | -0.0051359 | 0.020488 | 0.0051362 | 5.3402e-07 | 3.2277e-07 | 0.03092 | 0.03092 | 0.03092 | 0.98598 | -0.26894 | 0.98601 | -0.2684 | 8.4945
133 | 0.0031045 | 0.00077759 | -0.0031041 | -0.00077795 | 3.9931e-07 | -3.6157e-07 | 0.0046878 | 0.0046881 | 0.0046881 | 0.98538 | -0.28057 | 0.98525 | -0.28327 | 1.2879
134 | -0.024019 | -0.0060211 | 0.024028 | 0.0060265 | 8.7834e-06 | 5.3939e-06 | 0.036249 | 0.036249 | 0.036249 | 0.98601 | -0.2684 | 0.9864 | -0.26072 | 9.9585
135 | -0.0056457 | -0.0014149 | 0.0056458 | 0.001415 | 9.0681e-08 | 1.8087e-08 | 0.0086524 | 0.0086524 | 0.0086524 | 0.97093 | -0.56014 | 0.97095 | -0.5598 | 2.377
136 | -0.007975 | -0.0019986 | 0.0079754 | 0.0019988 | 3.859e-07 | 1.5815e-07 | 0.012096 | 0.012096 | 0.012096 | 0.98108 | -0.36233 | 0.98113 | -0.36131 | 3.323
137 | 0.003875 | 0.00097108 | -0.0038749 | -0.00097113 | 1.6583e-07 | -5.552e-08 | 0.0058773 | 0.0058773 | 0.0058773 | 0.98108 | -0.36233 | 0.98103 | -0.36323 | 1.6146
138 | 0.0034804 | 0.00087208 | -0.0034802 | -0.00087221 | 2.5753e-07 | -1.34e-07 | 0.0053325 | 0.0053326 | 0.0053326 | 0.97119 | -0.55505 | 0.97111 | -0.5566 | 1.465
139 | 0.015639 | 0.0039199 | -0.015634 | -0.0039192 | 5.5707e-06 | 6.8521e-07 | 0.023962 | 0.023963 | 0.023963 | 0.97119 | -0.55505 | 0.97081 | -0.56252 | 2.1944
140 | 0.014663 | 0.0036759 | -0.01466 | -0.0036741 | 3.0662e-06 | 1.7623e-06 | 0.022475 | 0.022475 | 0.022475 | 0.97081 | -0.56252 | 0.97059 | -0.56691 | 6.1746
141 | -0.42043 | -0.10826 | 0.42097 | 0.10861 | 0.00054592 | 0.00034861 | 0.62752 | 0.62752 | 0.62752 | 0.99858 | -0.026649 | 1 | 0 | 43.0988
142 | 0.0047531 | 0.001191 | -0.004753 | -0.001191 | 1.3106e-07 | -5.0223e-09 | 0.0071269 | 0.0071269 | 0.0071269 | 0.99239 | -0.14384 | 0.99236 | -0.14442 | 1.9579
143 | 0.0019844 | 0.00049726 | -0.0019844 | -0.00049733 | 2.2616e-08 | -7.3518e-08 | 0.0029756 | 0.0029756 | 0.0029756 | 0.99232 | -0.14521 | 0.99231 | -0.14545 | 0.81748
144 | -0.0029605 | -0.00074188 | 0.0029605 | 0.00074183 | 4.8578e-08 | -5.3831e-08 | 0.0044393 | 0.0044392 | 0.0044393 | 0.99232 | -0.14521 | 0.99234 | -0.14486 | 1.2196
145 | -0.0038547 | -0.00096593 | 0.0038548 | 0.00096589 | 8.0952e-08 | -3.1671e-08 | 0.00578 | 0.00578 | 0.00578 | 0.99234 | -0.14486 | 0.99236 | -0.14442 | 1.5879
146 | 0.0366 | 0.0091987 | -0.036593 | -0.0091941 | 7.2716e-06 | 4.5747e-06 | 0.055568 | 0.055568 | 0.055568 | 0.98025 | -0.37847 | 0.98004 | -0.38263 | 15.2659
147 | 0.03505 | 0.0088074 | -0.035042 | -0.0088023 | 8.0748e-06 | 5.0721e-06 | 0.053225 | 0.053225 | 0.053225 | 0.98004 | -0.38263 | 0.97979 | -0.38745 | 14.6223
148 | 0.033464 | 0.0084069 | -0.033459 | -0.0084038 | 4.9167e-06 | 3.0828e-06 | 0.050829 | 0.050829 | 0.050829 | 0.97979 | -0.38745 | 0.97964 | -0.39053 | 13.9641
149 | 0.03191 | 0.0080155 | -0.031904 | -0.0080122 | 5.2722e-06 | 3.2989e-06 | 0.048476 | 0.048476 | 0.048476 | 0.97964 | -0.39053 | 0.97946 | -0.394 | 13.3175
150 | 0.030309 | 0.0076122 | -0.030303 | -0.0076088 | 5.4833e-06 | 3.4226e-06 | 0.046051 | 0.046051 | 0.046051 | 0.97946 | -0.394 | 0.97927 | -0.39779 | 12.6514
151 | 0.028748 | 0.0072192 | -0.028744 | -0.0072166 | 4.1219e-06 | 2.5656e-06 | 0.043689 | 0.043689 | 0.043689 | 0.97927 | -0.39779 | 0.97911 | -0.40079 | 12.0025

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44322 | 0.11378

## res_load
| p_mw | q_mvar
0 | 0.0030688 | 0.00076911
1 | 0.0031735 | 0.00079536
2 | 0.00042981 | 0.00010772
3 | 0.0058535 | 0.001467
4 | 0.023677 | 0.005934
5 | 0.02516 | 0.0063057
6 | 0.0085888 | 0.0021526
7 | 0.010012 | 0.0025092
8 | 0.021025 | 0.0052693
9 | 0.0071919 | 0.0018024
10 | 0.0037957 | 0.0009513
11 | 0.0013646 | 0.00034201
12 | 0.0017103 | 0.00042864
13 | 0.0013975 | 0.00035025
14 | 0.0013652 | 0.00034216
15 | 0.0014794 | 0.00037076
16 | 0.0019373 | 0.00048554
17 | 0.0020332 | 0.00050957
18 | 0.0022351 | 0.00056018
19 | 0.0014372 | 0.0003602
20 | 0.00088432 | 0.00022163
21 | 0.0032858 | 0.00082351
22 | 0.0017054 | 0.0004274
23 | 0.005543 | 0.0013892
24 | 0.0019333 | 0.00048453
25 | 0.0031278 | 0.00078391
26 | 0.0011152 | 0.00027949
27 | 0.00061256 | 0.00015352
28 | 0.0018969 | 0.00047541
29 | 0.0017271 | 0.00043285
30 | 0.0013232 | 0.00033163
31 | 0.0014796 | 0.00037083
32 | 0.0015507 | 0.00038864
33 | 0.0010654 | 0.00026702
34 | 0.0014482 | 0.00036295
35 | 0.0014919 | 0.00037392
36 | 0.0013275 | 0.0003327
37 | 0.00085213 | 0.00021356
38 | 0.001052 | 0.00026366
39 | 0.0014694 | 0.00036826
40 | 0.0013124 | 0.00032893
41 | 0.0054712 | 0.0013712
42 | 0.0019126 | 0.00047933
43 | 0.0018944 | 0.00047478
44 | 0.00092624 | 0.00023214
45 | 0.0010199 | 0.00025562
46 | 0.0018014 | 0.00045147
47 | 0.0016226 | 0.00040667
48 | 0.0017795 | 0.00044599
49 | 0.00089823 | 0.00022512
50 | 0.001672 | 0.00041905
51 | 0.00092554 | 0.00023196
52 | 0.00089489 | 0.00022428
53 | 0.0012825 | 0.00032143
54 | 0.0013184 | 0.00033043
55 | 0.0030204 | 0.00075698
56 | 0.0011942 | 0.00029929
57 | 0.0012749 | 0.00031951
58 | 0.0067681 | 0.0016963
59 | 0.0014657 | 0.00036734
60 | 0.0010159 | 0.00025461
61 | 0.004415 | 0.0011065
62 | 0.0015434 | 0.00038682
63 | 0.00056489 | 0.00014158
64 | 0.034792 | 0.0087198
65 | 0.00082969 | 0.00020794
66 | 0.00067179 | 0.00016837
67 | 0.0012321 | 0.0003088
68 | 0.00077056 | 0.00019312
69 | 0.0011912 | 0.00029854
70 | 0.0010381 | 0.00026017
71 | 0.001066 | 0.00026717
72 | 0.0035105 | 0.00087981
73 | 0.0080174 | 0.0020094
74 | 0.0035306 | 0.00088485
75 | 0.011063 | 0.0027726
76 | 0.0096552 | 0.0024198
77 | 0.0071907 | 0.0018021
78 | 0.0032782 | 0.00082158
79 | 0.00086015 | 0.00021557
80 | 0.00092579 | 0.00023202
81 | 0.0071275 | 0.0017863
82 | 0.0055176 | 0.0013829
83 | 0.00097517 | 0.0002444
84 | 0.00099358 | 0.00024901
85 | 0.0013992 | 0.00035068
86 | 0.0013995 | 0.00035074
87 | 0.0013629 | 0.00034158
88 | 0.005645 | 0.0014148
89 | 0.0030431 | 0.00076266
90 | 0.0030423 | 0.00076248
91 | 0.0056466 | 0.0014152
92 | 0.003531 | 0.00088494
93 | 0.0031041 | 0.00077795
94 | 0.0034609 | 0.00086739
95 | 0.0056457 | 0.0014149
96 | 0.0061699 | 0.0015463
97 | 0.00088696 | 0.00022229
98 | 0.0041 | 0.0010275
99 | 0.0013639 | 0.00034182
100 | 0.0038749 | 0.00097113
101 | 0.0034802 | 0.00087221
102 | 0.00097073 | 0.00024329
103 | 0.01466 | 0.0036741
104 | 0.0096558 | 0.00242
105 | 0.020603 | 0.0051635
106 | 0.0014447 | 0.00036208
107 | 0.0010203 | 0.00025571
108 | 0.00097607 | 0.00024463
109 | 0.0019844 | 0.00049733
110 | 0.00089416 | 0.0002241
111 | 0.00089827 | 0.00022513
112 | 0.0016007 | 0.00040117
113 | 0.0015429 | 0.0003867
114 | 0.0015777 | 0.00039542
115 | 0.0015494 | 0.00038832
116 | 0.0015959 | 0.00039997
117 | 0.0015547 | 0.00038964
118 | 0.0016817 | 0.00042148

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1