## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_178-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_178-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_178-2_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_178-2_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_178-2_0_6_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_178-2_0_6_node_60 | 0.4 | n |  | TRUE
6 | bus_LV_178-2_0_6_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_178-2_0_6_node_61 | 0.4 | n |  | TRUE
8 | bus_LV_178-2_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_178-2_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_178-2_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_178-2_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_178-2_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_178-2_0_6_node_65 | 0.4 | n |  | TRUE
14 | bus_LV_178-2_0_6_node_70 | 0.4 | n |  | TRUE
15 | bus_LV_178-2_0_6_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_178-2_0_6_node_68 | 0.4 | n |  | TRUE
17 | bus_LV_178-2_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_178-2_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_178-2_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_178-2_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_178-2_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_178-2_0_6_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_178-2_0_6_node_55 | 0.4 | n |  | TRUE
24 | bus_LV_178-2_0_6_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_178-2_0_6_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_178-2_0_6_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_178-2_0_6_node_126 | 0.4 | n |  | TRUE
28 | bus_LV_178-2_0_6_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_178-2_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_178-2_0_6_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_178-2_0_6_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_178-2_0_6_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_178-2_0_6_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_178-2_0_6_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_178-2_0_6_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_178-2_0_6_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_178-2_0_6_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_178-2_0_6_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_178-2_0_6_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_178-2_0_6_node_137 | 0.4 | n |  | TRUE
41 | bus_LV_178-2_0_6_node_136 | 0.4 | n |  | TRUE
42 | bus_LV_178-2_0_6_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_178-2_0_6_node_67 | 0.4 | n |  | TRUE
44 | bus_LV_178-2_0_6_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_178-2_0_6_node_109 | 0.4 | n |  | TRUE
46 | bus_LV_178-2_0_6_node_111 | 0.4 | n |  | TRUE
47 | bus_LV_178-2_0_6_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_178-2_0_6_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_178-2_0_6_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_178-2_0_6_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_178-2_0_6_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_178-2_0_6_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_178-2_0_6_node_63 | 0.4 | n |  | TRUE
54 | bus_LV_178-2_0_6_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_178-2_0_6_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_178-2_0_6_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_178-2_0_6_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_178-2_0_6_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_178-2_0_6_node_94 | 0.4 | n |  | TRUE
60 | bus_LV_178-2_0_6_node_92 | 0.4 | n |  | TRUE
61 | bus_LV_178-2_0_6_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_178-2_0_6_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_178-2_0_6_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_178-2_0_6_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_178-2_0_6_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_178-2_0_6_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_178-2_0_6_node_81 | 0.4 | n |  | TRUE
68 | bus_LV_178-2_0_6_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_178-2_0_6_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_178-2_0_6_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_178-2_0_6_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_178-2_0_6_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_178-2_0_6_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_178-2_0_6_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_178-2_0_6_node_138 | 0.4 | n |  | TRUE
76 | bus_LV_178-2_0_6_node_125 | 0.4 | n |  | TRUE
77 | bus_LV_178-2_0_6_node_135 | 0.4 | n |  | TRUE
78 | bus_LV_178-2_0_6_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_178-2_0_6_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_178-2_0_6_node_82 | 0.4 | n |  | TRUE
81 | bus_LV_178-2_0_6_node_124 | 0.4 | n |  | TRUE
82 | bus_LV_178-2_0_6_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_178-2_0_6_node_130 | 0.4 | n |  | TRUE
84 | bus_LV_178-2_0_6_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_178-2_0_6_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_178-2_0_6_node_86 | 0.4 | n |  | TRUE
87 | bus_LV_178-2_0_6_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_178-2_0_6_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_178-2_0_6_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_178-2_0_6_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_178-2_0_6_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_178-2_0_6_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_178-2_0_6_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_178-2_0_6_node_75 | 0.4 | n |  | TRUE
95 | bus_LV_178-2_0_6_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_178-2_0_6_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_178-2_0_6_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_178-2_0_6_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_178-2_0_6_node_123 | 0.4 | n |  | TRUE
100 | bus_LV_178-2_0_6_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_178-2_0_6_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_178-2_0_6_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_178-2_0_6_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_178-2_0_6_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_178-2_0_6_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_178-2_0_6_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_178-2_0_6_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_178-2_0_6_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_178-2_0_6_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_178-2_0_6_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_178-2_0_6_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_178-2_0_6_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_178-2_0_6_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_178-2_0_6_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_178-2_0_6_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_178-2_0_6_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_178-2_0_6_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_178-2_0_6_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_178-2_0_6_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_178-2_0_6_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_178-2_0_6_node_121 | 0.4 | n |  | TRUE
122 | bus_LV_178-2_0_6_node_122 | 0.4 | n |  | TRUE
123 | bus_LV_178-2_0_6_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_178-2_0_6_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_178-2_0_6_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_178-2_0_6_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_178-2_0_6_node_127 | 0.4 | n |  | TRUE
128 | bus_LV_178-2_0_6_node_128 | 0.4 | n |  | TRUE
129 | bus_LV_178-2_0_6_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_178-2_0_6_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_178-2_0_6_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_178-2_0_6_node_132 | 0.4 | n |  | TRUE
133 | bus_LV_178-2_0_6_node_133 | 0.4 | n |  | TRUE
134 | bus_LV_178-2_0_6_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_178-2_0_6_node_129 | 0.4 | n |  | TRUE
136 | bus_LV_178-2_0_6_node_134 | 0.4 | n |  | TRUE
137 | bus_MV_26_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_178-2_0_6_load_0 | 0 | 0.0064765 | 0.0016232 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_178-2_0_6_load_3 | 2 | 0.0017949 | 0.00044985 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_178-2_0_6_load_22 | 4 | 0.0019624 | 0.00049183 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_178-2_0_6_load_60 | 5 | 0.001748 | 0.00043808 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_178-2_0_6_load_23 | 6 | 0.0018071 | 0.00045291 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_178-2_0_6_load_61 | 7 | 0.0011783 | 0.00029531 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_178-2_0_6_load_5 | 8 | 0.0021931 | 0.00054965 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_178-2_0_6_load_6 | 9 | 0.0029438 | 0.00073779 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_178-2_0_6_load_7 | 10 | 0.0030174 | 0.00075624 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_178-2_0_6_load_8 | 11 | 0.0031113 | 0.00077976 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_178-2_0_6_load_9 | 12 | 0.0019498 | 0.00048866 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_178-2_0_6_load_65 | 13 | 0.0025691 | 0.00064388 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_178-2_0_6_load_70 | 14 | 0.0033661 | 0.00084363 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_178-2_0_6_load_64 | 15 | 0.002147 | 0.0005381 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_178-2_0_6_load_68 | 16 | 0.0021953 | 0.00055019 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_178-2_0_6_load_10 | 17 | 0.0017558 | 0.00044004 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_178-2_0_6_load_11 | 18 | 0.0016806 | 0.00042119 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_178-2_0_6_load_12 | 19 | 0.0021645 | 0.00054247 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_178-2_0_6_load_13 | 20 | 0.0043443 | 0.0010888 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_178-2_0_6_load_14 | 21 | 0.0014733 | 0.00036925 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_178-2_0_6_load_78 | 22 | 0.0054214 | 0.0013587 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_178-2_0_6_load_55 | 23 | 0.0020626 | 0.00051693 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_178-2_0_6_load_56 | 24 | 0.0010118 | 0.00025358 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_178-2_0_6_load_34 | 25 | 0.0013464 | 0.00033743 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_178-2_0_6_load_57 | 26 | 0.0016143 | 0.00040459 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_178-2_0_6_load_126 | 27 | 0.002857 | 0.00071604 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_178-2_0_6_load_39 | 28 | 0.0033727 | 0.00084528 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_178-2_0_6_load_21 | 29 | 0.001534 | 0.00038447 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_178-2_0_6_load_15 | 30 | 0.0020686 | 0.00051843 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_178-2_0_6_load_31 | 32 | 0.0020442 | 0.00051232 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_178-2_0_6_load_20 | 33 | 0.0022404 | 0.0005615 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_178-2_0_6_load_30 | 34 | 0.0018202 | 0.00045617 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_178-2_0_6_load_32 | 35 | 0.0018255 | 0.00045752 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_178-2_0_6_load_18 | 38 | 0.0045603 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_178-2_0_6_load_19 | 39 | 0.0032134 | 0.00080534 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_178-2_0_6_load_137 | 40 | 0.003622 | 0.00090776 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_178-2_0_6_load_136 | 41 | 0.0051824 | 0.0012988 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_178-2_0_6_load_67 | 43 | 0.0024676 | 0.00061843 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_178-2_0_6_load_24 | 44 | 0.0015882 | 0.00039804 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_178-2_0_6_load_109 | 45 | 0.0016588 | 0.00041572 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_178-2_0_6_load_111 | 46 | 0.0029931 | 0.00075014 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_178-2_0_6_load_25 | 47 | 0.0082479 | 0.0020671 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_178-2_0_6_load_26 | 48 | 0.0074639 | 0.0018706 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_178-2_0_6_load_27 | 49 | 0.0097322 | 0.0024391 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_178-2_0_6_load_28 | 50 | 0.0021708 | 0.00054405 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_178-2_0_6_load_29 | 51 | 0.0058205 | 0.0014587 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_178-2_0_6_load_51 | 52 | 0.0015782 | 0.00039553 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_178-2_0_6_load_63 | 53 | 0.0086211 | 0.0021606 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_178-2_0_6_load_50 | 54 | 0.0022011 | 0.00055164 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_178-2_0_6_load_35 | 55 | 0.0029735 | 0.00074522 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_178-2_0_6_load_36 | 56 | 0.0036544 | 0.00091588 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_178-2_0_6_load_37 | 57 | 0.0031718 | 0.00079492 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_178-2_0_6_load_38 | 58 | 0.0038622 | 0.00096795 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_178-2_0_6_load_94 | 59 | 0.0020585 | 0.0005159 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_178-2_0_6_load_92 | 60 | 0.0015934 | 0.00039934 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_178-2_0_6_load_40 | 61 | 0.0020814 | 0.00052164 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_178-2_0_6_load_41 | 62 | 0.0014629 | 0.00036664 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_178-2_0_6_load_42 | 63 | 0.0036802 | 0.00092235 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_178-2_0_6_load_43 | 64 | 0.0017079 | 0.00042804 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_178-2_0_6_load_44 | 65 | 0.0025838 | 0.00064756 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_178-2_0_6_load_83 | 66 | 0.0055425 | 0.0013891 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_178-2_0_6_load_45 | 68 | 0.0028296 | 0.00070918 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_178-2_0_6_load_46 | 69 | 0.0019731 | 0.00049452 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_178-2_0_6_load_47 | 70 | 0.0010077 | 0.00025254 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_178-2_0_6_load_48 | 71 | 0.0015914 | 0.00039884 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_178-2_0_6_load_54 | 73 | 0.001628 | 0.00040802 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_178-2_0_6_load_62 | 74 | 0.003004 | 0.00075286 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_178-2_0_6_load_138 | 75 | 0.0032146 | 0.00080565 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_178-2_0_6_load_125 | 76 | 0.0014947 | 0.00037461 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_178-2_0_6_load_135 | 77 | 0.0019942 | 0.00049979 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_178-2_0_6_load_52 | 78 | 0.0033251 | 0.00083334 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_178-2_0_6_load_53 | 79 | 0.0035111 | 0.00087996 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_178-2_0_6_load_80 | 82 | 0.0019807 | 0.00049642 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_178-2_0_6_load_130 | 83 | 0.0012 | 0.00030076 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_178-2_0_6_load_58 | 84 | 0.0015362 | 0.000385 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_178-2_0_6_load_59 | 85 | 0.0018782 | 0.00047073 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_178-2_0_6_load_86 | 86 | 0.0014933 | 0.00037425 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_178-2_0_6_load_85 | 87 | 0.0011801 | 0.00029576 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_178-2_0_6_load_69 | 88 | 0.0029174 | 0.00073117 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_178-2_0_6_load_71 | 89 | 0.0030566 | 0.00076607 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_178-2_0_6_load_89 | 90 | 0.0022455 | 0.00056277 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_178-2_0_6_load_72 | 91 | 0.0030585 | 0.00076653 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_178-2_0_6_load_73 | 92 | 0.0025103 | 0.00062915 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_178-2_0_6_load_77 | 96 | 0.0010671 | 0.00026745 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_178-2_0_6_load_87 | 97 | 0.0014665 | 0.00036753 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_178-2_0_6_load_84 | 98 | 0.0016639 | 0.00041702 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_178-2_0_6_load_123 | 99 | 0.0042313 | 0.0010605 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_178-2_0_6_load_88 | 100 | 0.0011584 | 0.00029032 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_178-2_0_6_load_99 | 101 | 0.0016357 | 0.00040995 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_178-2_0_6_load_79 | 102 | 0.0025521 | 0.00063961 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_178-2_0_6_load_102 | 103 | 0.0011876 | 0.00029765 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_178-2_0_6_load_97 | 104 | 0.0022999 | 0.00057641 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_178-2_0_6_load_90 | 105 | 0.0018928 | 0.00047438 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_178-2_0_6_load_91 | 106 | 0.0015598 | 0.00039093 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_178-2_0_6_load_93 | 107 | 0.0015153 | 0.00037977 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_178-2_0_6_load_98 | 108 | 0.001735 | 0.00043484 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_178-2_0_6_load_96 | 109 | 0.0024581 | 0.00061607 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_178-2_0_6_load_95 | 110 | 0.001863 | 0.00046692 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_178-2_0_6_load_100 | 111 | 0.0008 | 0.0002005 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_178-2_0_6_load_103 | 113 | 0.0013894 | 0.00034821 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_178-2_0_6_load_104 | 114 | 0.00055443 | 0.00013895 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_178-2_0_6_load_105 | 115 | 0.0079572 | 0.0019943 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_178-2_0_6_load_108 | 118 | 0.0011892 | 0.00029804 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_178-2_0_6_load_113 | 120 | 0.002539 | 0.00063633 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_178-2_0_6_load_121 | 121 | 0.0027124 | 0.00067979 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_178-2_0_6_load_122 | 122 | 0.0078598 | 0.0019699 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_178-2_0_6_load_114 | 123 | 0.0010548 | 0.00026436 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_178-2_0_6_load_110 | 125 | 0.0016211 | 0.00040628 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_178-2_0_6_load_115 | 126 | 0.0011829 | 0.00029647 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_178-2_0_6_load_127 | 127 | 0.0012405 | 0.00031091 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_178-2_0_6_load_128 | 128 | 0.0025191 | 0.00063136 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_178-2_0_6_load_117 | 129 | 0.00234 | 0.00058646 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_178-2_0_6_load_118 | 130 | 0.0025294 | 0.00063394 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_178-2_0_6_load_120 | 131 | 0.0036753 | 0.00092113 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_178-2_0_6_load_132 | 132 | 0.0067312 | 0.001687 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_178-2_0_6_load_133 | 133 | 0.003749 | 0.00093958 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_178-2_0_6_load_131 | 134 | 0.0019413 | 0.00048653 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_178-2_0_6_load_129 | 135 | 0.00082497 | 0.00020676 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_178-2_0_6_load_134 | 136 | 0.0044048 | 0.001104 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_178-2_0_6_line_0 |  | 0 | 1 | 0.035767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_178-2_0_6_line_1 |  | 1 | 2 | 0.020634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_178-2_0_6_line_2 |  | 1 | 3 | 0.004851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_178-2_0_6_line_3 |  | 2 | 4 | 0.0064151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_178-2_0_6_line_4 |  | 3 | 5 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_178-2_0_6_line_5 |  | 4 | 6 | 0.0039235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_178-2_0_6_line_6 |  | 5 | 7 | 0.0056625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_178-2_0_6_line_7 |  | 6 | 44 | 0.011238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_178-2_0_6_line_8 |  | 7 | 74 | 0.021313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_178-2_0_6_line_9 |  | 8 | 9 | 0.014547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_178-2_0_6_line_10 |  | 8 | 10 | 0.0052951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_178-2_0_6_line_11 |  | 9 | 11 | 0.025037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_178-2_0_6_line_12 |  | 10 | 12 | 0.018761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_178-2_0_6_line_13 |  | 11 | 13 | 0.0056813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_178-2_0_6_line_14 |  | 12 | 14 | 0.0046492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_178-2_0_6_line_15 |  | 13 | 15 | 0.015211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_178-2_0_6_line_16 |  | 14 | 16 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_178-2_0_6_line_17 |  | 15 | 42 | 0.01332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_178-2_0_6_line_18 |  | 16 | 88 | 0.0055742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_178-2_0_6_line_19 |  | 17 | 18 | 0.020143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_178-2_0_6_line_20 |  | 17 | 19 | 0.0036502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_178-2_0_6_line_21 |  | 18 | 20 | 0.020284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_178-2_0_6_line_22 |  | 19 | 21 | 0.02336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_178-2_0_6_line_23 |  | 20 | 22 | 0.0054109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_178-2_0_6_line_24 |  | 21 | 27 | 0.0012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_178-2_0_6_line_25 |  | 22 | 28 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_178-2_0_6_line_26 |  | 23 | 24 | 0.0034104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_178-2_0_6_line_27 |  | 23 | 25 | 0.018258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_178-2_0_6_line_28 |  | 24 | 26 | 0.021728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_178-2_0_6_line_29 |  | 25 | 35 | 0.0059269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_178-2_0_6_line_30 |  | 26 | 84 | 0.0019225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_178-2_0_6_line_31 |  | 27 | 29 | 0.025449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_178-2_0_6_line_32 |  | 28 | 57 | 0.0072208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_178-2_0_6_line_33 |  | 29 | 31 | 0.0031929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_178-2_0_6_line_34 |  | 30 | 31 | 0.034542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_178-2_0_6_line_35 |  | 30 | 32 | 0.06633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_178-2_0_6_line_36 |  | 31 | 33 | 0.023036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_178-2_0_6_line_37 |  | 32 | 36 | 0.012838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_178-2_0_6_line_38 |  | 32 | 34 | 0.0084516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_178-2_0_6_line_39 |  | 34 | 35 | 0.024797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_178-2_0_6_line_40 |  | 36 | 38 | 0.059959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_178-2_0_6_line_41 |  | 37 | 38 | 0.015986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_178-2_0_6_line_42 |  | 37 | 39 | 0.0019817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_178-2_0_6_line_43 |  | 39 | 40 | 0.019599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_178-2_0_6_line_44 |  | 40 | 41 | 0.021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_178-2_0_6_line_45 |  | 41 | 134 | 0.031665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_178-2_0_6_line_46 |  | 42 | 43 | 0.020496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_178-2_0_6_line_47 |  | 43 | 86 | 0.00029561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_178-2_0_6_line_48 |  | 44 | 45 | 0.014301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_178-2_0_6_line_49 |  | 45 | 46 | 0.00026213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_178-2_0_6_line_50 |  | 46 | 125 | 0.011265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_178-2_0_6_line_51 |  | 47 | 48 | 0.0057324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_178-2_0_6_line_52 |  | 47 | 49 | 0.023917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_178-2_0_6_line_53 |  | 48 | 50 | 0.017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_178-2_0_6_line_54 |  | 49 | 51 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_178-2_0_6_line_55 |  | 50 | 52 | 0.0058703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_178-2_0_6_line_56 |  | 51 | 53 | 0.0065219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_178-2_0_6_line_57 |  | 52 | 54 | 0.01688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_178-2_0_6_line_58 |  | 54 | 78 | 0.0062048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_178-2_0_6_line_59 |  | 55 | 56 | 0.0094622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_178-2_0_6_line_60 |  | 55 | 57 | 0.022787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_178-2_0_6_line_61 |  | 56 | 58 | 0.0094357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_178-2_0_6_line_62 |  | 58 | 59 | 0.013316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_178-2_0_6_line_63 |  | 59 | 60 | 0.02664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_178-2_0_6_line_64 |  | 60 | 105 | 0.00060556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_178-2_0_6_line_65 |  | 61 | 62 | 0.022512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_178-2_0_6_line_66 |  | 61 | 63 | 0.023133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_178-2_0_6_line_67 |  | 62 | 64 | 0.019833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_178-2_0_6_line_68 |  | 63 | 65 | 0.020605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_178-2_0_6_line_69 |  | 65 | 66 | 0.027881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_178-2_0_6_line_70 |  | 66 | 67 | 0.036055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_178-2_0_6_line_71 |  | 67 | 102 | 0.0045001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_178-2_0_6_line_72 |  | 67 | 95 | 0.01802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_178-2_0_6_line_73 |  | 68 | 69 | 0.014061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_178-2_0_6_line_74 |  | 68 | 70 | 0.00013579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_178-2_0_6_line_75 |  | 69 | 71 | 0.010652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_178-2_0_6_line_76 |  | 70 | 72 | 0.012496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_178-2_0_6_line_77 |  | 71 | 73 | 0.006377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_178-2_0_6_line_78 |  | 72 | 74 | 0.012943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_178-2_0_6_line_79 |  | 72 | 75 | 0.018717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_178-2_0_6_line_80 |  | 73 | 76 | 0.010778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_178-2_0_6_line_81 |  | 75 | 77 | 0.0027295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_178-2_0_6_line_82 |  | 76 | 83 | 0.0093185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_178-2_0_6_line_83 |  | 77 | 136 | 0.022529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_178-2_0_6_line_84 |  | 78 | 79 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_178-2_0_6_line_85 |  | 79 | 80 | 0.014838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_178-2_0_6_line_86 |  | 80 | 81 | 0.016761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_178-2_0_6_line_87 |  | 80 | 82 | 0.014663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_178-2_0_6_line_88 |  | 81 | 90 | 0.016533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_178-2_0_6_line_89 |  | 83 | 134 | 0.018683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_178-2_0_6_line_90 |  | 84 | 85 | 0.016791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_178-2_0_6_line_91 |  | 86 | 87 | 0.02891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_178-2_0_6_line_92 |  | 87 | 98 | 0.0012454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_178-2_0_6_line_93 |  | 88 | 89 | 0.029678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_178-2_0_6_line_94 |  | 89 | 90 | 0.016913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_178-2_0_6_line_95 |  | 91 | 92 | 0.020645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_178-2_0_6_line_96 |  | 91 | 93 | 0.014664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_178-2_0_6_line_97 |  | 92 | 94 | 0.030316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_178-2_0_6_line_98 |  | 93 | 95 | 0.01744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_178-2_0_6_line_99 |  | 93 | 96 | 0.034196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_178-2_0_6_line_100 |  | 94 | 97 | 0.033101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_178-2_0_6_line_101 |  | 94 | 98 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_178-2_0_6_line_102 |  | 95 | 99 | 0.020355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_178-2_0_6_line_103 |  | 96 | 100 | 0.02625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_178-2_0_6_line_104 |  | 97 | 101 | 0.0099147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_178-2_0_6_line_105 |  | 99 | 103 | 0.022722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_178-2_0_6_line_106 |  | 101 | 104 | 0.017876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_178-2_0_6_line_107 |  | 103 | 112 | 0.013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_178-2_0_6_line_108 |  | 104 | 110 | 0.0098691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_178-2_0_6_line_109 |  | 105 | 106 | 0.025378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_178-2_0_6_line_110 |  | 106 | 107 | 0.0068244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_178-2_0_6_line_111 |  | 107 | 108 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_178-2_0_6_line_112 |  | 108 | 109 | 0.0091445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_178-2_0_6_line_113 |  | 109 | 110 | 0.019147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_178-2_0_6_line_114 |  | 111 | 112 | 0.0088551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_178-2_0_6_line_115 |  | 112 | 113 | 0.015825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_178-2_0_6_line_116 |  | 114 | 115 | 0.0034205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_178-2_0_6_line_117 |  | 114 | 116 | 0.032977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_178-2_0_6_line_118 |  | 115 | 117 | 0.036868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_178-2_0_6_line_119 |  | 116 | 118 | 0.042018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_178-2_0_6_line_120 |  | 117 | 119 | 0.020386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_178-2_0_6_line_121 |  | 117 | 120 | 0.017324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_178-2_0_6_line_122 |  | 118 | 121 | 0.03357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_178-2_0_6_line_123 |  | 119 | 122 | 0.046085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_178-2_0_6_line_124 |  | 120 | 123 | 0.024013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_178-2_0_6_line_125 |  | 121 | 124 | 0.021359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_178-2_0_6_line_126 |  | 123 | 126 | 0.019514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_178-2_0_6_line_127 |  | 124 | 131 | 0.022083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_178-2_0_6_line_128 |  | 124 | 129 | 0.029026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_178-2_0_6_line_129 |  | 126 | 127 | 0.0064222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_178-2_0_6_line_130 |  | 127 | 128 | 0.036592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_178-2_0_6_line_131 |  | 128 | 135 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_178-2_0_6_line_132 |  | 129 | 130 | 0.01268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_178-2_0_6_line_133 |  | 131 | 132 | 0.0023029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_178-2_0_6_line_134 |  | 132 | 133 | 0.029287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_178-2_0_6_line_135 |  | 133 | 136 | 0.0055544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_178-2_0_6_trafo_70 | 0.63 MVA 20/0.4 kV | 137 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2702256.0335 | 1252094.3561 | 2702251.3359 | 1252084.0112 | 2702248.755 | 1252074.7926 | 2702245.0864 | 1252060.4206
1 | 2702256.0335 | 1252094.3561 | 2702245.4831 | 1252099.0333 | 2702236.4652 | 1252100.2008
2 | 2702258.4289 | 1252098.5785 | 2702256.0335 | 1252094.3561
3 | 2702230.2422 | 1252098.6424 | 2702236.4652 | 1252100.2008 | 2702236.4652 | 1252100.2008
4 | 2702258.4289 | 1252098.5785 | 2702252.901 | 1252122.506
5 | 2702226.491 | 1252097.5452 | 2702227.0703 | 1252097.848 | 2702230.2422 | 1252098.6424
6 | 2702251.6264 | 1252128.0231 | 2702252.901 | 1252122.506
7 | 2702226.491 | 1252097.5452 | 2702216.5312 | 1252092.3398
8 | 2702246.8289 | 1252148.7893 | 2702251.6264 | 1252128.0231
9 | 2702266.2463 | 1252299.5266 | 2702269.4804 | 1252300.8643 | 2702278.581 | 1252307.1264 | 2702278.581 | 1252307.1264
10 | 2702266.2463 | 1252299.5266 | 2702261.3533 | 1252297.5026
11 | 2702278.581 | 1252307.1264 | 2702296.3852 | 1252324.7297
12 | 2702243.8452 | 1252290.7882 | 2702250.7964 | 1252293.1357 | 2702261.3533 | 1252297.5026
13 | 2702296.3852 | 1252324.7297 | 2702296.5184 | 1252324.8614 | 2702298.8357 | 1252329.8427
14 | 2702239.4405 | 1252289.3006 | 2702243.8452 | 1252290.7882
15 | 2702305.2518 | 1252343.6345 | 2702298.8357 | 1252329.8427
16 | 2702220.1374 | 1252282.7815 | 2702239.4405 | 1252289.3006
17 | 2702310.8702 | 1252355.7116 | 2702305.2518 | 1252343.6345
18 | 2702220.1374 | 1252282.7815 | 2702214.8563 | 1252280.998
19 | 2702412.3049 | 1252412.5875 | 2702430.788 | 1252420.5938
20 | 2702412.3049 | 1252412.5875 | 2702408.9555 | 1252411.1366
21 | 2702430.788 | 1252420.5938 | 2702449.4004 | 1252428.6561
22 | 2702408.9555 | 1252411.1366 | 2702387.5202 | 1252401.8516
23 | 2702454.3655 | 1252430.8068 | 2702449.4004 | 1252428.6561
24 | 2702386.392 | 1252401.3629 | 2702387.5202 | 1252401.8516
25 | 2702446.6461 | 1252448.519 | 2702454.3655 | 1252430.8068 | 2702454.3655 | 1252430.8068
26 | 2702466.2965 | 1252351.7595 | 2702468.9459 | 1252353.907
27 | 2702466.2965 | 1252351.7595 | 2702452.1131 | 1252340.263
28 | 2702485.8255 | 1252367.589 | 2702468.9459 | 1252353.907
29 | 2702447.5088 | 1252336.5309 | 2702452.1131 | 1252340.263
30 | 2702487.319 | 1252368.7995 | 2702485.8255 | 1252367.589
31 | 2702386.392 | 1252401.3629 | 2702363.0399 | 1252391.2475
32 | 2702446.6461 | 1252448.519 | 2702443.7613 | 1252455.1385
33 | 2702360.1101 | 1252389.9784 | 2702363.0399 | 1252391.2475
34 | 2702360.1101 | 1252389.9784 | 2702366.6509 | 1252381.0064 | 2702373.6658 | 1252378.2254 | 2702376.7834 | 1252373.4087 | 2702376.4004 | 1252363.2607
35 | 2702376.4004 | 1252363.2607 | 2702422.0655 | 1252315.1524
36 | 2702360.1101 | 1252389.9784 | 2702341.7951 | 1252382.3226 | 2702339.0769 | 1252380.6619
37 | 2702412.7173 | 1252306.3538 | 2702422.0655 | 1252315.1524
38 | 2702422.0655 | 1252315.1524 | 2702427.8465 | 1252320.5934 | 2702428.2449 | 1252320.9163
39 | 2702447.5088 | 1252336.5309 | 2702428.2449 | 1252320.9163
40 | 2702377.3445 | 1252257.9406 | 2702412.7173 | 1252306.3538
41 | 2702369.5942 | 1252243.9587 | 2702377.3445 | 1252257.9406
42 | 2702369.5942 | 1252243.9587 | 2702368.6973 | 1252242.1916
43 | 2702368.6973 | 1252242.1916 | 2702359.8269 | 1252224.7147
44 | 2702346.3923 | 1252207.4193 | 2702349.4665 | 1252210.1395 | 2702359.4989 | 1252224.0684 | 2702359.8269 | 1252224.7147
45 | 2702346.3923 | 1252207.4193 | 2702334.5602 | 1252196.9493 | 2702320.656 | 1252189.308
46 | 2702310.8702 | 1252355.7116 | 2702296.056 | 1252369.8765
47 | 2702296.056 | 1252369.8765 | 2702295.8424 | 1252370.0808
48 | 2702216.5312 | 1252092.3398 | 2702203.8571 | 1252085.7159
49 | 2702203.6248 | 1252085.5944 | 2702203.8571 | 1252085.7159
50 | 2702203.6248 | 1252085.5944 | 2702193.641 | 1252080.3765
51 | 2702092.0636 | 1252279.456 | 2702091.0763 | 1252279.1927 | 2702086.3958 | 1252278.6605
52 | 2702062.6318 | 1252275.9587 | 2702086.3958 | 1252278.6605
53 | 2702092.0636 | 1252279.456 | 2702109.4382 | 1252284.0913
54 | 2702062.6318 | 1252275.9587 | 2702054.9913 | 1252275.09 | 2702047.0466 | 1252274.771
55 | 2702109.4382 | 1252284.0913 | 2702115.1101 | 1252285.6044
56 | 2702040.53 | 1252274.5093 | 2702047.0466 | 1252274.771
57 | 2702131.0826 | 1252291.015 | 2702120.1314 | 1252286.944 | 2702115.1101 | 1252285.6044
58 | 2702131.0826 | 1252291.015 | 2702136.8985 | 1252293.177
59 | 2702434.6572 | 1252476.0281 | 2702430.8768 | 1252484.7023
60 | 2702443.7613 | 1252455.1385 | 2702434.6572 | 1252476.0281
61 | 2702427.1069 | 1252493.3523 | 2702427.1069 | 1252493.3523 | 2702430.8768 | 1252484.7023
62 | 2702414.8479 | 1252488.1524 | 2702427.1069 | 1252493.3523
63 | 2702414.8479 | 1252488.1524 | 2702390.3229 | 1252477.7496
64 | 2702389.7654 | 1252477.5131 | 2702390.3229 | 1252477.7496
65 | 2702089.4334 | 1252331.0974 | 2702073.6244 | 1252330.0104 | 2702067.0822 | 1252328.7311
66 | 2702112.5265 | 1252332.4473 | 2702094.7793 | 1252331.4649 | 2702089.4334 | 1252331.0974
67 | 2702047.6183 | 1252324.925 | 2702067.0822 | 1252328.7311
68 | 2702132.0528 | 1252338.7438 | 2702114.9135 | 1252332.5794 | 2702112.5265 | 1252332.4473
69 | 2702158.2883 | 1252348.1797 | 2702132.0528 | 1252338.7438
70 | 2702192.4071 | 1252346.2931 | 2702176.1341 | 1252352.8177 | 2702167.3943 | 1252351.4548 | 2702158.2883 | 1252348.1797
71 | 2702192.4071 | 1252346.2931 | 2702190.2058 | 1252342.3682
72 | 2702192.4071 | 1252346.2931 | 2702201.7801 | 1252361.7004
73 | 2702270.1678 | 1252166.011 | 2702266.1397 | 1252164.7756 | 2702256.404 | 1252163.2971
74 | 2702256.2698 | 1252163.2767 | 2702256.404 | 1252163.2971
75 | 2702270.1678 | 1252166.011 | 2702280.352 | 1252169.1342
76 | 2702243.9154 | 1252161.4005 | 2702256.2698 | 1252163.2767
77 | 2702280.352 | 1252169.1342 | 2702285.1213 | 1252170.5968 | 2702286.3644 | 1252171.2152
78 | 2702243.9154 | 1252161.4005 | 2702246.8289 | 1252148.7893
79 | 2702243.9154 | 1252161.4005 | 2702225.3942 | 1252158.697
80 | 2702296.0144 | 1252176.0153 | 2702286.3644 | 1252171.2152
81 | 2702225.3942 | 1252158.697 | 2702222.6934 | 1252158.3028
82 | 2702304.2823 | 1252180.3096 | 2702300.8003 | 1252178.396 | 2702296.0144 | 1252176.0153
83 | 2702222.6934 | 1252158.3028 | 2702200.4008 | 1252155.0487
84 | 2702148.0612 | 1252297.1354 | 2702147.7991 | 1252297.2291 | 2702136.8985 | 1252293.177
85 | 2702162.0322 | 1252292.1371 | 2702148.0612 | 1252297.1354
86 | 2702154.4401 | 1252277.1831 | 2702162.0322 | 1252292.1371
87 | 2702162.0322 | 1252292.1371 | 2702169.2051 | 1252304.9259
88 | 2702154.4401 | 1252277.1831 | 2702169.9378 | 1252271.4235
89 | 2702320.656 | 1252189.308 | 2702304.2823 | 1252180.3096
90 | 2702500.3628 | 1252379.3723 | 2702487.319 | 1252368.7995
91 | 2702295.8424 | 1252370.0808 | 2702274.9468 | 1252390.0605
92 | 2702274.0467 | 1252390.9212 | 2702274.9468 | 1252390.0605
93 | 2702214.8563 | 1252280.998 | 2702186.7388 | 1252271.5021
94 | 2702186.7388 | 1252271.5021 | 2702184.9001 | 1252270.8811 | 2702169.9378 | 1252271.4235
95 | 2702223.4994 | 1252374.174 | 2702234.4304 | 1252375.8417 | 2702243.7307 | 1252378.1711
96 | 2702209.2141 | 1252377.4857 | 2702223.4994 | 1252374.174
97 | 2702263.0636 | 1252401.4229 | 2702244.1104 | 1252378.2662 | 2702243.7307 | 1252378.1711
98 | 2702209.2141 | 1252377.4857 | 2702201.7801 | 1252361.7004
99 | 2702209.2141 | 1252377.4857 | 2702223.7045 | 1252408.4598
100 | 2702263.0636 | 1252401.4229 | 2702278.9008 | 1252418.3765 | 2702286.8355 | 1252424.2985
101 | 2702263.0636 | 1252401.4229 | 2702274.0467 | 1252390.9212
102 | 2702201.7801 | 1252361.7004 | 2702196.2006 | 1252365.7185 | 2702193.4099 | 1252371.7196 | 2702192.616 | 1252378.5351
103 | 2702234.1753 | 1252432.5222 | 2702232.4499 | 1252428.027 | 2702227.1505 | 1252415.8258 | 2702223.7045 | 1252408.4598
104 | 2702294.7812 | 1252430.2287 | 2702286.8355 | 1252424.2985
105 | 2702190.0689 | 1252401.1133 | 2702191.1592 | 1252391.0407 | 2702192.616 | 1252378.5351
106 | 2702294.7812 | 1252430.2287 | 2702300.0866 | 1252434.1882 | 2702309.8534 | 1252439.7834
107 | 2702188.582 | 1252414.8486 | 2702190.0689 | 1252401.1133
108 | 2702318.4168 | 1252444.6891 | 2702309.8534 | 1252439.7834
109 | 2702389.7654 | 1252477.5131 | 2702366.4026 | 1252467.6033
110 | 2702366.4026 | 1252467.6033 | 2702360.12 | 1252464.9384
111 | 2702343.412 | 1252457.8514 | 2702360.12 | 1252464.9384
112 | 2702335.0303 | 1252454.2066 | 2702335.6328 | 1252454.5517 | 2702343.412 | 1252457.8514
113 | 2702318.4168 | 1252444.6891 | 2702335.0303 | 1252454.2066
114 | 2702188.582 | 1252414.8486 | 2702188.1839 | 1252423.6948
115 | 2702188.582 | 1252414.8486 | 2702174.7285 | 1252411.5182 | 2702173.2274 | 1252411.0359
116 | 2702075.8303 | 1252204.391 | 2702078.2851 | 1252206.7729
117 | 2702056.7624 | 1252178.4766 | 2702060.7571 | 1252189.7656 | 2702075.8303 | 1252204.391
118 | 2702104.7446 | 1252232.4464 | 2702078.2851 | 1252206.7729
119 | 2702056.7624 | 1252178.4766 | 2702064.3712 | 1252176.7174 | 2702068.3557 | 1252178.9656 | 2702097.2863 | 1252172.5504
120 | 2702104.7446 | 1252232.4464 | 2702084.585 | 1252235.8462
121 | 2702104.7446 | 1252232.4464 | 2702121.9297 | 1252230.255
122 | 2702097.2863 | 1252172.5504 | 2702102.4155 | 1252171.413 | 2702103.3045 | 1252173.2632 | 2702110.2254 | 1252172.0036 | 2702125.1898 | 1252159.9282
123 | 2702084.585 | 1252235.8462 | 2702046.2255 | 1252228.3683 | 2702039.5457 | 1252226.2633
124 | 2702144.2841 | 1252222.1409 | 2702140.3226 | 1252224.3865 | 2702128.173 | 1252229.4589 | 2702121.9297 | 1252230.255
125 | 2702141.7947 | 1252146.494 | 2702134.7133 | 1252152.2432 | 2702125.1898 | 1252159.9282
126 | 2702144.2841 | 1252222.1409 | 2702155.248 | 1252215.9259 | 2702162.1567 | 1252215.7492
127 | 2702141.7947 | 1252146.494 | 2702163.6461 | 1252149.6837
128 | 2702141.7947 | 1252146.494 | 2702137.0483 | 1252153.8403 | 2702121.3564 | 1252166.6868
129 | 2702168.5768 | 1252215.5849 | 2702162.1567 | 1252215.7492
130 | 2702168.5768 | 1252215.5849 | 2702173.9382 | 1252215.4478 | 2702184.7221 | 1252219.0922 | 2702203.9205 | 1252224.1182
131 | 2702219.8288 | 1252228.2829 | 2702203.9205 | 1252224.1182
132 | 2702121.3564 | 1252166.6868 | 2702111.8663 | 1252174.4561 | 2702111.4601 | 1252174.5434
133 | 2702165.9248 | 1252150.0163 | 2702163.6461 | 1252149.6837
134 | 2702194.9046 | 1252154.2465 | 2702165.9248 | 1252150.0163
135 | 2702194.9046 | 1252154.2465 | 2702200.4008 | 1252155.0487

## bus_geodata
| x | y | coords
0 | 2702245.0864 | 1252060.4206
1 | 2702256.0335 | 1252094.3561
2 | 2702236.4652 | 1252100.2008
3 | 2702258.4289 | 1252098.5785
4 | 2702230.2422 | 1252098.6424
5 | 2702252.901 | 1252122.506
6 | 2702226.491 | 1252097.5452
7 | 2702251.6264 | 1252128.0231
8 | 2702266.2463 | 1252299.5266
9 | 2702278.581 | 1252307.1264
10 | 2702261.3533 | 1252297.5026
11 | 2702296.3852 | 1252324.7297
12 | 2702243.8452 | 1252290.7882
13 | 2702298.8357 | 1252329.8427
14 | 2702239.4405 | 1252289.3006
15 | 2702305.2518 | 1252343.6345
16 | 2702220.1374 | 1252282.7815
17 | 2702412.3049 | 1252412.5875
18 | 2702430.788 | 1252420.5938
19 | 2702408.9555 | 1252411.1366
20 | 2702449.4004 | 1252428.6561
21 | 2702387.5202 | 1252401.8516
22 | 2702454.3655 | 1252430.8068
23 | 2702466.2965 | 1252351.7595
24 | 2702468.9459 | 1252353.907
25 | 2702452.1131 | 1252340.263
26 | 2702485.8255 | 1252367.589
27 | 2702386.392 | 1252401.3629
28 | 2702446.6461 | 1252448.519
29 | 2702363.0399 | 1252391.2475
30 | 2702376.4004 | 1252363.2607
31 | 2702360.1101 | 1252389.9784
32 | 2702422.0655 | 1252315.1524
33 | 2702339.0769 | 1252380.6619
34 | 2702428.2449 | 1252320.9163
35 | 2702447.5088 | 1252336.5309
36 | 2702412.7173 | 1252306.3538
37 | 2702369.5942 | 1252243.9587
38 | 2702377.3445 | 1252257.9406
39 | 2702368.6973 | 1252242.1916
40 | 2702359.8269 | 1252224.7147
41 | 2702346.3923 | 1252207.4193
42 | 2702310.8702 | 1252355.7116
43 | 2702296.056 | 1252369.8765
44 | 2702216.5312 | 1252092.3398
45 | 2702203.8571 | 1252085.7159
46 | 2702203.6248 | 1252085.5944
47 | 2702086.3958 | 1252278.6605
48 | 2702092.0636 | 1252279.456
49 | 2702062.6318 | 1252275.9587
50 | 2702109.4382 | 1252284.0913
51 | 2702047.0466 | 1252274.771
52 | 2702115.1101 | 1252285.6044
53 | 2702040.53 | 1252274.5093
54 | 2702131.0826 | 1252291.015
55 | 2702434.6572 | 1252476.0281
56 | 2702430.8768 | 1252484.7023
57 | 2702443.7613 | 1252455.1385
58 | 2702427.1069 | 1252493.3523
59 | 2702414.8479 | 1252488.1524
60 | 2702390.3229 | 1252477.7496
61 | 2702089.4334 | 1252331.0974
62 | 2702067.0822 | 1252328.7311
63 | 2702112.5265 | 1252332.4473
64 | 2702047.6183 | 1252324.925
65 | 2702132.0528 | 1252338.7438
66 | 2702158.2883 | 1252348.1797
67 | 2702192.4071 | 1252346.2931
68 | 2702256.404 | 1252163.2971
69 | 2702270.1678 | 1252166.011
70 | 2702256.2698 | 1252163.2767
71 | 2702280.352 | 1252169.1342
72 | 2702243.9154 | 1252161.4005
73 | 2702286.3644 | 1252171.2152
74 | 2702246.8289 | 1252148.7893
75 | 2702225.3942 | 1252158.697
76 | 2702296.0144 | 1252176.0153
77 | 2702222.6934 | 1252158.3028
78 | 2702136.8985 | 1252293.177
79 | 2702148.0612 | 1252297.1354
80 | 2702162.0322 | 1252292.1371
81 | 2702154.4401 | 1252277.1831
82 | 2702169.2052 | 1252304.9259
83 | 2702304.2823 | 1252180.3096
84 | 2702487.319 | 1252368.7995
85 | 2702500.3628 | 1252379.3723
86 | 2702295.8424 | 1252370.0808
87 | 2702274.9468 | 1252390.0605
88 | 2702214.8563 | 1252280.998
89 | 2702186.7388 | 1252271.5021
90 | 2702169.9378 | 1252271.4235
91 | 2702223.4994 | 1252374.174
92 | 2702243.7307 | 1252378.1711
93 | 2702209.2141 | 1252377.4857
94 | 2702263.0636 | 1252401.4229
95 | 2702201.7801 | 1252361.7004
96 | 2702223.7045 | 1252408.4598
97 | 2702286.8355 | 1252424.2985
98 | 2702274.0467 | 1252390.9212
99 | 2702192.616 | 1252378.5351
100 | 2702234.1753 | 1252432.5222
101 | 2702294.7812 | 1252430.2287
102 | 2702190.2058 | 1252342.3682
103 | 2702190.0689 | 1252401.1133
104 | 2702309.8534 | 1252439.7834
105 | 2702389.7654 | 1252477.5131
106 | 2702366.4026 | 1252467.6033
107 | 2702360.12 | 1252464.9384
108 | 2702343.412 | 1252457.8514
109 | 2702335.0303 | 1252454.2066
110 | 2702318.4168 | 1252444.6891
111 | 2702188.1839 | 1252423.6948
112 | 2702188.582 | 1252414.8486
113 | 2702173.2274 | 1252411.0359
114 | 2702075.8303 | 1252204.391
115 | 2702078.2851 | 1252206.7729
116 | 2702056.7624 | 1252178.4766
117 | 2702104.7446 | 1252232.4464
118 | 2702097.2863 | 1252172.5504
119 | 2702084.585 | 1252235.8462
120 | 2702121.9297 | 1252230.255
121 | 2702125.1898 | 1252159.9282
122 | 2702039.5457 | 1252226.2633
123 | 2702144.2841 | 1252222.1409
124 | 2702141.7947 | 1252146.494
125 | 2702193.641 | 1252080.3765
126 | 2702162.1567 | 1252215.7492
127 | 2702168.5768 | 1252215.5849
128 | 2702203.9205 | 1252224.1182
129 | 2702121.3564 | 1252166.6868
130 | 2702111.4601 | 1252174.5434
131 | 2702163.6461 | 1252149.6837
132 | 2702165.9248 | 1252150.0163
133 | 2702194.9046 | 1252154.2465
134 | 2702320.656 | 1252189.308
135 | 2702219.8288 | 1252228.2829
136 | 2702200.4008 | 1252155.0487
137 | 2702154.4401 | 1252277.1831

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97259 | -0.52885 | 0.0064765 | 0.0016232
1 | 0.97281 | -0.52458 | 0 | 0
2 | 0.97255 | -0.52969 | 0.0017949 | 0.00044985
3 | 0.9729 | -0.52281 | 0 | 0
4 | 0.97248 | -0.53106 | 0.0019624 | 0.00049183
5 | 0.97335 | -0.51381 | 0.001748 | 0.00043808
6 | 0.97244 | -0.53176 | 0.0018071 | 0.00045291
7 | 0.97347 | -0.51155 | 0.0011783 | 0.00029531
8 | 0.99867 | -0.025039 | 0.0021931 | 0.00054965
9 | 0.99801 | -0.037501 | 0.0029438 | 0.00073779
10 | 0.99891 | -0.020467 | 0.0030174 | 0.00075624
11 | 0.99689 | -0.058728 | 0.0031113 | 0.00077976
12 | 0.99978 | -0.0040864 | 0.0019498 | 0.00048866
13 | 0.99664 | -0.063489 | 0.0025691 | 0.00064388
14 | 1 | 0 | -0.32348 | -0.082474
15 | 0.99598 | -0.076112 | 0.002147 | 0.0005381
16 | 0.99879 | -0.023137 | 0.0021953 | 0.00055019
17 | 0.98284 | -0.32809 | 0.0017558 | 0.00044004
18 | 0.98338 | -0.31766 | 0.0016806 | 0.00042119
19 | 0.98275 | -0.32996 | 0.0021645 | 0.00054247
20 | 0.98393 | -0.30703 | 0.0043443 | 0.0010888
21 | 0.98214 | -0.34176 | 0.0014733 | 0.00036925
22 | 0.98408 | -0.30412 | 0.0054214 | 0.0013587
23 | 0.97839 | -0.41489 | 0.0020626 | 0.00051693
24 | 0.97837 | -0.41526 | 0.0010118 | 0.00025358
25 | 0.97853 | -0.41219 | 0.0013464 | 0.00033743
26 | 0.97827 | -0.41725 | 0.0016143 | 0.00040459
27 | 0.98211 | -0.34237 | 0.002857 | 0.00071604
28 | 0.98464 | -0.29333 | 0.0033727 | 0.00084528
29 | 0.98147 | -0.35484 | 0.001534 | 0.00038447
30 | 0.98054 | -0.37286 | 0.0020686 | 0.00051843
31 | 0.98139 | -0.35638 | 0 | 0
32 | 0.97894 | -0.40407 | 0.0020442 | 0.00051232
33 | 0.98134 | -0.35732 | 0.0022404 | 0.0005615
34 | 0.97884 | -0.40608 | 0.0018202 | 0.00045617
35 | 0.97858 | -0.41117 | 0.0018255 | 0.00045752
36 | 0.97867 | -0.40942 | 0 | 0
37 | 0.97706 | -0.44083 | 0 | 0
38 | 0.97739 | -0.43442 | 0.0045603 | 0.0011429
39 | 0.97702 | -0.44162 | 0.0032134 | 0.00080534
40 | 0.97663 | -0.44926 | 0.003622 | 0.00090776
41 | 0.97621 | -0.45754 | 0.0051824 | 0.0012988
42 | 0.9954 | -0.087078 | 0 | 0
43 | 0.99451 | -0.10398 | 0.0024676 | 0.00061843
44 | 0.97236 | -0.53339 | 0.0015882 | 0.00039804
45 | 0.97228 | -0.53504 | 0.0016588 | 0.00041572
46 | 0.97228 | -0.53507 | 0.0029931 | 0.00075014
47 | 0.99106 | -0.17193 | 0.0082479 | 0.0020671
48 | 0.99123 | -0.16863 | 0.0074639 | 0.0018706
49 | 0.99053 | -0.1822 | 0.0097322 | 0.0024391
50 | 0.99188 | -0.15592 | 0.0021708 | 0.00054405
51 | 0.99032 | -0.18621 | 0.0058205 | 0.0014587
52 | 0.99211 | -0.15154 | 0.0015782 | 0.00039553
53 | 0.99027 | -0.18721 | 0.0086211 | 0.0021606
54 | 0.99278 | -0.13851 | 0.0022011 | 0.00055164
55 | 0.98554 | -0.27598 | 0.0029735 | 0.00074522
56 | 0.98583 | -0.27039 | 0.0036544 | 0.00091588
57 | 0.98485 | -0.28922 | 0.0031718 | 0.00079492
58 | 0.98612 | -0.2647 | 0.0038622 | 0.00096795
59 | 0.98655 | -0.25648 | 0.0020585 | 0.0005159
60 | 0.98741 | -0.23987 | 0.0015934 | 0.00039934
61 | 0.98869 | -0.21615 | 0.0020814 | 0.00052164
62 | 0.98863 | -0.21742 | 0.0014629 | 0.00036664
63 | 0.9888 | -0.21398 | 0.0036802 | 0.00092235
64 | 0.98859 | -0.21803 | 0.0017079 | 0.00042804
65 | 0.98897 | -0.2107 | 0.0025838 | 0.00064756
66 | 0.98927 | -0.20498 | 0.0055425 | 0.0013891
67 | 0.98983 | -0.19403 | 0 | 0
68 | 0.97443 | -0.49256 | 0.0028296 | 0.00070918
69 | 0.97466 | -0.48802 | 0.0019731 | 0.00049452
70 | 0.97443 | -0.4926 | 0.0010077 | 0.00025254
71 | 0.97484 | -0.4845 | 0.0015914 | 0.00039884
72 | 0.97423 | -0.49646 | 0 | 0
73 | 0.97495 | -0.48236 | 0.001628 | 0.00040802
74 | 0.97392 | -0.50261 | 0.003004 | 0.00075286
75 | 0.97403 | -0.50047 | 0.0032146 | 0.00080565
76 | 0.97514 | -0.47868 | 0.0014947 | 0.00037461
77 | 0.974 | -0.50102 | 0.0019942 | 0.00049979
78 | 0.99304 | -0.13348 | 0.0033251 | 0.00083334
79 | 0.99358 | -0.12314 | 0.0035111 | 0.00087996
80 | 0.99429 | -0.10935 | 0 | 0
81 | 0.99513 | -0.093212 | 0 | 0
82 | 0.99427 | -0.10986 | 0.0019807 | 0.00049642
83 | 0.9753 | -0.47544 | 0.0012 | 0.00030076
84 | 0.97826 | -0.41737 | 0.0015362 | 0.000385
85 | 0.97823 | -0.41795 | 0.0018782 | 0.00047073
86 | 0.9945 | -0.10422 | 0.0014933 | 0.00037425
87 | 0.99326 | -0.1277 | 0.0011801 | 0.00029576
88 | 0.99847 | -0.029263 | 0.0029174 | 0.00073117
89 | 0.99684 | -0.060425 | 0.0030566 | 0.00076607
90 | 0.99596 | -0.07732 | 0.0022455 | 0.00056277
91 | 0.99098 | -0.17163 | 0.0030585 | 0.00076653
92 | 0.9916 | -0.15973 | 0.0025103 | 0.00062915
93 | 0.99059 | -0.1793 | 0 | 0
94 | 0.99257 | -0.14092 | 0 | 0
95 | 0.99015 | -0.18774 | 0 | 0
96 | 0.99052 | -0.18066 | 0.0010671 | 0.00026745
97 | 0.99139 | -0.16347 | 0.0014665 | 0.00036753
98 | 0.99321 | -0.12871 | 0.0016639 | 0.00041702
99 | 0.99001 | -0.1905 | 0.0042313 | 0.0010605
100 | 0.99049 | -0.1812 | 0.0011584 | 0.00029032
101 | 0.99104 | -0.17019 | 0.0016357 | 0.00040995
102 | 0.98982 | -0.19423 | 0.0025521 | 0.00063961
103 | 0.98994 | -0.19186 | 0.0011876 | 0.00029765
104 | 0.99041 | -0.1822 | 0.0022999 | 0.00057641
105 | 0.98743 | -0.23949 | 0.0018928 | 0.00047438
106 | 0.98827 | -0.22337 | 0.0015598 | 0.00039093
107 | 0.98849 | -0.21901 | 0.0015153 | 0.00037977
108 | 0.9891 | -0.20731 | 0.001735 | 0.00043484
109 | 0.98941 | -0.20136 | 0.0024581 | 0.00061607
110 | 0.99007 | -0.18875 | 0.001863 | 0.00046692
111 | 0.98991 | -0.19253 | 0.0008 | 0.0002005
112 | 0.98991 | -0.1924 | 0 | 0
113 | 0.98989 | -0.19279 | 0.0013894 | 0.00034821
114 | 0.97174 | -0.54566 | 0.00055443 | 0.00013895
115 | 0.97166 | -0.54725 | 0.0079572 | 0.0019943
116 | 0.97253 | -0.53 | 0 | 0
117 | 0.97107 | -0.55898 | 0 | 0
118 | 0.97304 | -0.52004 | 0.0011892 | 0.00029804
119 | 0.97092 | -0.56194 | 0 | 0
120 | 0.97091 | -0.56198 | 0.002539 | 0.00063633
121 | 0.97321 | -0.51671 | 0.0027124 | 0.00067979
122 | 0.97058 | -0.56864 | 0.0078598 | 0.0019699
123 | 0.97076 | -0.56501 | 0.0010548 | 0.00026436
124 | 0.97332 | -0.51438 | 0 | 0
125 | 0.97226 | -0.5354 | 0.0016211 | 0.00040628
126 | 0.97066 | -0.56709 | 0.0011829 | 0.00029647
127 | 0.97063 | -0.56764 | 0.0012405 | 0.00031091
128 | 0.97051 | -0.5699 | 0.0025191 | 0.00063136
129 | 0.97319 | -0.51698 | 0.00234 | 0.00058646
130 | 0.97316 | -0.51758 | 0.0025294 | 0.00063394
131 | 0.97347 | -0.51158 | 0.0036753 | 0.00092113
132 | 0.97348 | -0.51125 | 0.0067312 | 0.001687
133 | 0.97373 | -0.50642 | 0.003749 | 0.00093958
134 | 0.97563 | -0.46888 | 0.0019413 | 0.00048653
135 | 0.9705 | -0.57016 | 0.00082497 | 0.00020676
136 | 0.97378 | -0.50542 | 0.0044048 | 0.001104
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0064765 | -0.0016232 | 0.0064778 | 0.0016236 | 1.3169e-06 | 3.9884e-07 | 0.0099088 | 0.0099086 | 0.0099088 | 0.97259 | -0.52885 | 0.97281 | -0.52458 | 2.7222
1 | 0.013431 | 0.0033674 | -0.013428 | -0.0033656 | 3.266e-06 | 1.8341e-06 | 0.020545 | 0.020545 | 0.020545 | 0.97281 | -0.52458 | 0.97255 | -0.52969 | 5.6442
2 | -0.019909 | -0.004991 | 0.019911 | 0.004992 | 1.6871e-06 | 1.0195e-06 | 0.030453 | 0.030453 | 0.030453 | 0.97281 | -0.52458 | 0.9729 | -0.52281 | 8.3663
3 | 0.011633 | 0.0029158 | -0.011632 | -0.0029153 | 7.621e-07 | 4.0814e-07 | 0.017799 | 0.017799 | 0.017799 | 0.97255 | -0.52969 | 0.97248 | -0.53106 | 4.8897
4 | -0.019911 | -0.004992 | 0.019919 | 0.0049972 | 8.5406e-06 | 5.1609e-06 | 0.030453 | 0.030453 | 0.030453 | 0.9729 | -0.52281 | 0.97335 | -0.51381 | 8.3663
5 | 0.0096697 | 0.0024235 | -0.0096694 | -0.0024234 | 3.221e-07 | 1.5747e-07 | 0.014796 | 0.014796 | 0.014796 | 0.97248 | -0.53106 | 0.97244 | -0.53176 | 4.0648
6 | -0.021667 | -0.0054353 | 0.021669 | 0.0054367 | 2.33e-06 | 1.4208e-06 | 0.033125 | 0.033125 | 0.033125 | 0.97335 | -0.51381 | 0.97347 | -0.51155 | 9.1004
7 | 0.0078622 | 0.0019704 | -0.0078616 | -0.0019702 | 6.0996e-07 | 2.5097e-07 | 0.012031 | 0.012031 | 0.012031 | 0.97244 | -0.53176 | 0.97236 | -0.53339 | 3.3051
8 | -0.022848 | -0.005732 | 0.022858 | 0.005738 | 9.7496e-06 | 5.9747e-06 | 0.034927 | 0.034926 | 0.034927 | 0.97347 | -0.51155 | 0.97392 | -0.50261 | 9.5952
9 | 0.24883 | 0.063884 | -0.24868 | -0.063789 | 0.00015041 | 9.5312e-05 | 0.3713 | 0.3713 | 0.3713 | 0.99867 | -0.025039 | 0.99801 | -0.037501 | 20.4012
10 | -0.25103 | -0.064434 | 0.25108 | 0.064469 | 5.5718e-05 | 3.5313e-05 | 0.37457 | 0.37457 | 0.37457 | 0.99867 | -0.025039 | 0.99891 | -0.020467 | 20.5807
11 | 0.24574 | 0.063051 | -0.24549 | -0.062891 | 0.0002528 | 0.00016016 | 0.36691 | 0.36691 | 0.36691 | 0.99801 | -0.037501 | 0.99689 | -0.058728 | 20.1601
12 | -0.2541 | -0.065225 | 0.2543 | 0.065353 | 0.00020218 | 0.00012817 | 0.37906 | 0.37906 | 0.37906 | 0.99891 | -0.020467 | 0.99978 | -0.0040864 | 20.8277
13 | 0.24238 | 0.062111 | -0.24232 | -0.062076 | 5.592e-05 | 3.5419e-05 | 0.36227 | 0.36227 | 0.36227 | 0.99689 | -0.058728 | 0.99664 | -0.063489 | 19.9049
14 | -0.25625 | -0.065842 | 0.2563 | 0.065874 | 5.0873e-05 | 3.2254e-05 | 0.38197 | 0.38196 | 0.38197 | 0.99978 | -0.0040864 | 1 | 0 | 20.9871
15 | 0.23975 | 0.061432 | -0.2396 | -0.061339 | 0.00014657 | 9.2814e-05 | 0.35843 | 0.35843 | 0.35843 | 0.99664 | -0.063489 | 0.99598 | -0.076112 | 19.6942
16 | 0.065529 | 0.0166 | -0.065457 | -0.016554 | 7.2737e-05 | 4.6284e-05 | 0.097571 | 0.097571 | 0.097571 | 1 | 0 | 0.99879 | -0.023137 | 26.8053
17 | 0.23746 | 0.060801 | -0.23733 | -0.060721 | 0.00012606 | 7.9812e-05 | 0.35523 | 0.35523 | 0.35523 | 0.99598 | -0.076112 | 0.9954 | -0.087078 | 19.5179
18 | 0.063261 | 0.016003 | -0.063243 | -0.015992 | 1.8588e-05 | 1.1824e-05 | 0.094301 | 0.094301 | 0.094301 | 0.99879 | -0.023137 | 0.99847 | -0.029263 | 25.9068
19 | -0.14467 | -0.036638 | 0.14474 | 0.036683 | 7.2565e-05 | 4.5164e-05 | 0.21917 | 0.21917 | 0.21917 | 0.98284 | -0.32809 | 0.98338 | -0.31766 | 12.0421
20 | 0.14291 | 0.036198 | -0.1429 | -0.03619 | 1.2833e-05 | 7.9818e-06 | 0.21651 | 0.21651 | 0.21651 | 0.98284 | -0.32809 | 0.98275 | -0.32996 | 11.8961
21 | -0.14642 | -0.037104 | 0.1465 | 0.037151 | 7.4777e-05 | 4.657e-05 | 0.22171 | 0.22171 | 0.22171 | 0.98338 | -0.31766 | 0.98393 | -0.30703 | 12.1818
22 | 0.14074 | 0.035648 | -0.14066 | -0.035598 | 7.9659e-05 | 4.9503e-05 | 0.21323 | 0.21323 | 0.21323 | 0.98275 | -0.32996 | 0.98214 | -0.34176 | 11.716
23 | -0.15084 | -0.03824 | 0.15086 | 0.038253 | 2.1147e-05 | 1.3191e-05 | 0.22828 | 0.22828 | 0.22828 | 0.98393 | -0.30703 | 0.98408 | -0.30412 | 12.5428
24 | 0.13918 | 0.035229 | -0.13918 | -0.035226 | 4.1052e-06 | 2.5496e-06 | 0.211 | 0.211 | 0.211 | 0.98214 | -0.34176 | 0.98211 | -0.34237 | 11.5934
25 | -0.15629 | -0.039612 | 0.15637 | 0.039662 | 8.1034e-05 | 5.0634e-05 | 0.23648 | 0.23648 | 0.23648 | 0.98408 | -0.30412 | 0.98464 | -0.29333 | 12.9932
26 | 0.0060412 | 0.0015138 | -0.0060411 | -0.0015137 | 1.0796e-07 | 2.6266e-08 | 0.0091878 | 0.0091879 | 0.0091879 | 0.97839 | -0.41489 | 0.97837 | -0.41526 | 2.5241
27 | -0.0081038 | -0.0020307 | 0.0081048 | 0.0020311 | 1.04e-06 | 4.3627e-07 | 0.012325 | 0.012325 | 0.012325 | 0.97839 | -0.41489 | 0.97853 | -0.41219 | 3.3859
28 | 0.0050293 | 0.0012602 | -0.0050288 | -0.0012601 | 4.7673e-07 | 3.2272e-08 | 0.007649 | 0.0076491 | 0.0076491 | 0.97837 | -0.41526 | 0.97827 | -0.41725 | 2.1014
29 | -0.0094512 | -0.0023686 | 0.0094516 | 0.0023688 | 4.5908e-07 | 2.1936e-07 | 0.014372 | 0.014372 | 0.014372 | 0.97853 | -0.41219 | 0.97858 | -0.41117 | 3.9484
30 | 0.0034145 | 0.00085554 | -0.0034145 | -0.00085556 | 1.9446e-08 | -1.1692e-08 | 0.0051936 | 0.0051936 | 0.0051936 | 0.97827 | -0.41725 | 0.97826 | -0.41737 | 1.4268
31 | 0.13632 | 0.03451 | -0.13624 | -0.03446 | 8.1524e-05 | 5.0566e-05 | 0.20667 | 0.20667 | 0.20667 | 0.98211 | -0.34237 | 0.98147 | -0.35484 | 11.3556
32 | -0.15974 | -0.040508 | 0.15977 | 0.040527 | 3.1604e-05 | 1.9767e-05 | 0.24157 | 0.24157 | 0.24157 | 0.98464 | -0.29333 | 0.98485 | -0.28922 | 13.2732
33 | 0.13471 | 0.034075 | -0.1347 | -0.034069 | 9.9994e-06 | 6.1979e-06 | 0.20435 | 0.20435 | 0.20435 | 0.98147 | -0.35484 | 0.98139 | -0.35638 | 11.2278
34 | -0.13235 | -0.033443 | 0.13246 | 0.033508 | 0.00010461 | 6.4771e-05 | 0.20095 | 0.20095 | 0.20095 | 0.98054 | -0.37286 | 0.98139 | -0.35638 | 11.0412
35 | 0.13028 | 0.032924 | -0.13009 | -0.032804 | 0.00019466 | 0.00012041 | 0.19781 | 0.19781 | 0.19781 | 0.98054 | -0.37286 | 0.97894 | -0.40407 | 10.8688
36 | 0.0022405 | 0.00056127 | -0.0022404 | -0.0005615 | 9.9691e-08 | -2.2726e-07 | 0.003397 | 0.0033971 | 0.0033971 | 0.98139 | -0.35638 | 0.98134 | -0.35732 | 0.93328
37 | 0.11494 | 0.029007 | -0.11491 | -0.028989 | 2.9416e-05 | 1.8019e-05 | 0.17479 | 0.17479 | 0.17479 | 0.97894 | -0.40407 | 0.97867 | -0.40942 | 9.6039
38 | 0.013101 | 0.0032846 | -0.0131 | -0.0032839 | 1.257e-06 | 6.982e-07 | 0.019915 | 0.019915 | 0.019915 | 0.97894 | -0.40407 | 0.97884 | -0.40608 | 5.4711
39 | 0.01128 | 0.0028277 | -0.011277 | -0.0028263 | 2.7344e-06 | 1.4384e-06 | 0.017148 | 0.017148 | 0.017148 | 0.97884 | -0.40608 | 0.97858 | -0.41117 | 4.711
40 | 0.11491 | 0.028989 | -0.11478 | -0.028905 | 0.00013739 | 8.4167e-05 | 0.17479 | 0.17479 | 0.17479 | 0.97867 | -0.40942 | 0.97739 | -0.43442 | 9.6039
41 | -0.11018 | -0.027741 | 0.11022 | 0.027762 | 3.3779e-05 | 2.0617e-05 | 0.16785 | 0.16785 | 0.16785 | 0.97706 | -0.44083 | 0.97739 | -0.43442 | 9.2225
42 | 0.11018 | 0.027741 | -0.11018 | -0.027739 | 4.1874e-06 | 2.5559e-06 | 0.16785 | 0.16785 | 0.16785 | 0.97706 | -0.44083 | 0.97702 | -0.44162 | 9.2225
43 | 0.10697 | 0.026934 | -0.10693 | -0.02691 | 3.9033e-05 | 2.3754e-05 | 0.16296 | 0.16296 | 0.16296 | 0.97702 | -0.44162 | 0.97663 | -0.44926 | 8.9536
44 | 0.1033 | 0.026002 | -0.10326 | -0.025977 | 4.0889e-05 | 2.4794e-05 | 0.15744 | 0.15744 | 0.15744 | 0.97663 | -0.44926 | 0.97621 | -0.45754 | 8.6504
45 | 0.098081 | 0.024678 | -0.098028 | -0.024646 | 5.3106e-05 | 3.201e-05 | 0.14954 | 0.14954 | 0.14954 | 0.97621 | -0.45754 | 0.97563 | -0.46888 | 8.2164
46 | 0.23733 | 0.060721 | -0.23714 | -0.060598 | 0.00019398 | 0.00012281 | 0.35523 | 0.35523 | 0.35523 | 0.9954 | -0.087078 | 0.99451 | -0.10398 | 19.518
47 | 0.23467 | 0.05998 | -0.23467 | -0.059978 | 2.7398e-06 | 1.7343e-06 | 0.35153 | 0.35153 | 0.35153 | 0.99451 | -0.10398 | 0.9945 | -0.10422 | 19.3151
48 | 0.0062734 | 0.0015722 | -0.0062729 | -0.001572 | 4.9426e-07 | 1.3896e-07 | 0.0096003 | 0.0096003 | 0.0096003 | 0.97236 | -0.53339 | 0.97228 | -0.53504 | 2.6375
49 | 0.0046142 | 0.0011563 | -0.0046142 | -0.0011563 | 4.9026e-09 | -1.1351e-10 | 0.0070617 | 0.0070617 | 0.0070617 | 0.97228 | -0.53504 | 0.97228 | -0.53507 | 1.94
50 | 0.0016211 | 0.00040616 | -0.0016211 | -0.00040628 | 2.6003e-08 | -1.2307e-07 | 0.002481 | 0.002481 | 0.002481 | 0.97228 | -0.53507 | 0.97226 | -0.5354 | 0.6816
51 | -0.032437 | -0.0081346 | 0.032442 | 0.0081378 | 5.0991e-06 | 3.1895e-06 | 0.048704 | 0.048704 | 0.048704 | 0.99106 | -0.17193 | 0.99123 | -0.16863 | 13.3801
52 | 0.024189 | 0.0060675 | -0.024177 | -0.0060603 | 1.1831e-05 | 7.264e-06 | 0.03632 | 0.03632 | 0.03632 | 0.99106 | -0.17193 | 0.99053 | -0.1822 | 9.978
53 | -0.039906 | -0.010008 | 0.03993 | 0.010024 | 2.4202e-05 | 1.5257e-05 | 0.059908 | 0.059908 | 0.059908 | 0.99123 | -0.16863 | 0.99188 | -0.15592 | 16.4583
54 | 0.014445 | 0.0036211 | -0.014442 | -0.0036196 | 2.7619e-06 | 1.5663e-06 | 0.0217 | 0.0217 | 0.0217 | 0.99053 | -0.1822 | 0.99032 | -0.18621 | 5.9615
55 | -0.042101 | -0.010568 | 0.042109 | 0.010573 | 8.7829e-06 | 5.5453e-06 | 0.063165 | 0.063165 | 0.063165 | 0.99188 | -0.15592 | 0.99211 | -0.15154 | 17.353
56 | 0.0086215 | 0.0021608 | -0.0086211 | -0.0021606 | 4.1042e-07 | 1.7876e-07 | 0.012954 | 0.012954 | 0.012954 | 0.99032 | -0.18621 | 0.99027 | -0.18721 | 3.5589
57 | -0.043688 | -0.010969 | 0.043715 | 0.010986 | 2.7184e-05 | 1.718e-05 | 0.065532 | 0.065532 | 0.065532 | 0.99211 | -0.15154 | 0.99278 | -0.13851 | 18.0032
58 | -0.045916 | -0.011538 | 0.045927 | 0.011545 | 1.1024e-05 | 6.9748e-06 | 0.068831 | 0.068831 | 0.068831 | 0.99278 | -0.13851 | 0.99304 | -0.13348 | 18.9096
59 | -0.16602 | -0.042132 | 0.16606 | 0.04216 | 4.4657e-05 | 2.7978e-05 | 0.25085 | 0.25085 | 0.25085 | 0.98554 | -0.27598 | 0.98583 | -0.27039 | 13.7832
60 | 0.16305 | 0.041387 | -0.16294 | -0.041322 | 0.00010373 | 6.4937e-05 | 0.24636 | 0.24636 | 0.24636 | 0.98554 | -0.27598 | 0.98485 | -0.28922 | 13.5365
61 | -0.16972 | -0.043076 | 0.16977 | 0.043105 | 4.6512e-05 | 2.9166e-05 | 0.25637 | 0.25637 | 0.25637 | 0.98583 | -0.27039 | 0.98612 | -0.2647 | 14.0862
62 | -0.17363 | -0.044073 | 0.1737 | 0.044116 | 6.8659e-05 | 4.3092e-05 | 0.2622 | 0.2622 | 0.2622 | 0.98612 | -0.2647 | 0.98655 | -0.25648 | 14.4064
63 | -0.17575 | -0.044632 | 0.1759 | 0.044721 | 0.00014063 | 8.83e-05 | 0.2653 | 0.2653 | 0.2653 | 0.98655 | -0.25648 | 0.98741 | -0.23987 | 14.577
64 | -0.17749 | -0.04512 | 0.17749 | 0.045122 | 3.2548e-06 | 2.0443e-06 | 0.2677 | 0.2677 | 0.2677 | 0.98741 | -0.23987 | 0.98743 | -0.23949 | 14.7089
65 | 0.0031711 | 0.0007943 | -0.0031709 | -0.00079446 | 1.9228e-07 | -1.6562e-07 | 0.0047724 | 0.0047725 | 0.0047725 | 0.98869 | -0.21615 | 0.98863 | -0.21742 | 1.3111
66 | -0.0052524 | -0.0013159 | 0.005253 | 0.001316 | 5.4207e-07 | 5.0229e-08 | 0.007905 | 0.0079049 | 0.007905 | 0.98869 | -0.21615 | 0.9888 | -0.21398 | 2.1717
67 | 0.001708 | 0.00042782 | -0.0017079 | -0.00042804 | 4.9148e-08 | -2.2284e-07 | 0.0025706 | 0.0025707 | 0.0025707 | 0.98863 | -0.21742 | 0.98859 | -0.21803 | 0.70624
68 | -0.0089332 | -0.0022383 | 0.0089346 | 0.002239 | 1.3964e-06 | 6.2932e-07 | 0.013443 | 0.013443 | 0.013443 | 0.9888 | -0.21398 | 0.98897 | -0.2107 | 3.6932
69 | -0.011518 | -0.0028865 | 0.011522 | 0.0028882 | 3.1402e-06 | 1.6519e-06 | 0.017331 | 0.01733 | 0.017331 | 0.98897 | -0.2107 | 0.98927 | -0.20498 | 4.7612
70 | -0.017064 | -0.0042773 | 0.017073 | 0.0042825 | 8.9074e-06 | 5.2376e-06 | 0.025667 | 0.025667 | 0.025667 | 0.98927 | -0.20498 | 0.98983 | -0.19403 | 7.0515
71 | 0.0025521 | 0.00063957 | -0.0025521 | -0.00063961 | 2.4839e-08 | -4.1945e-08 | 0.0038366 | 0.0038366 | 0.0038366 | 0.98983 | -0.19403 | 0.98982 | -0.19423 | 1.054
72 | -0.019625 | -0.0049221 | 0.019631 | 0.0049256 | 5.8822e-06 | 3.5329e-06 | 0.029504 | 0.029504 | 0.029504 | 0.98983 | -0.19403 | 0.99015 | -0.18774 | 8.1054
73 | -0.088095 | -0.02212 | 0.088114 | 0.022132 | 1.9089e-05 | 1.1341e-05 | 0.13454 | 0.13454 | 0.13454 | 0.97443 | -0.49256 | 0.97466 | -0.48802 | 7.3924
74 | 0.085265 | 0.021411 | -0.085265 | -0.021411 | 1.7269e-07 | 1.0207e-07 | 0.13022 | 0.13022 | 0.13022 | 0.97443 | -0.49256 | 0.97443 | -0.4926 | 7.155
75 | -0.090087 | -0.022626 | 0.090102 | 0.022635 | 1.5116e-05 | 9.0106e-06 | 0.13755 | 0.13755 | 0.13755 | 0.97466 | -0.48802 | 0.97484 | -0.4845 | 7.5579
76 | 0.084257 | 0.021159 | -0.084242 | -0.021149 | 1.5519e-05 | 9.1541e-06 | 0.12868 | 0.12868 | 0.12868 | 0.97443 | -0.4926 | 0.97423 | -0.49646 | 7.0704
77 | -0.091694 | -0.023034 | 0.091703 | 0.02304 | 9.3718e-06 | 5.6004e-06 | 0.13998 | 0.13998 | 0.13998 | 0.97484 | -0.4845 | 0.97495 | -0.48236 | 7.6913
78 | 0.025869 | 0.0064955 | -0.025861 | -0.0064908 | 7.5793e-06 | 4.6896e-06 | 0.039516 | 0.039516 | 0.039516 | 0.97423 | -0.49646 | 0.97392 | -0.50261 | 10.8561
79 | 0.058373 | 0.014654 | -0.058362 | -0.014648 | 1.1161e-05 | 5.978e-06 | 0.089166 | 0.089166 | 0.089166 | 0.97423 | -0.49646 | 0.97403 | -0.50047 | 4.8993
80 | -0.093331 | -0.023448 | 0.093347 | 0.023458 | 1.6407e-05 | 9.8282e-06 | 0.14247 | 0.14247 | 0.14247 | 0.97495 | -0.48236 | 0.97514 | -0.47868 | 7.8279
81 | 0.055147 | 0.013842 | -0.055146 | -0.013842 | 1.4532e-06 | 7.6021e-07 | 0.084256 | 0.084256 | 0.084256 | 0.97403 | -0.50047 | 0.974 | -0.50102 | 4.6294
82 | -0.094842 | -0.023832 | 0.094857 | 0.023841 | 1.4643e-05 | 8.7902e-06 | 0.14475 | 0.14475 | 0.14475 | 0.97514 | -0.47868 | 0.9753 | -0.47544 | 7.9532
83 | 0.053152 | 0.013342 | -0.05314 | -0.013336 | 1.1143e-05 | 5.73e-06 | 0.081209 | 0.08121 | 0.08121 | 0.974 | -0.50102 | 0.97378 | -0.50542 | 4.4621
84 | -0.049252 | -0.012378 | 0.049276 | 0.012393 | 2.4329e-05 | 1.5417e-05 | 0.073813 | 0.073813 | 0.073813 | 0.99304 | -0.13348 | 0.99358 | -0.12314 | 20.2783
85 | -0.052787 | -0.013273 | 0.052822 | 0.013295 | 3.479e-05 | 2.2073e-05 | 0.079071 | 0.079071 | 0.079071 | 0.99358 | -0.12314 | 0.99429 | -0.10935 | 21.7229
86 | -0.054803 | -0.013792 | 0.054845 | 0.013819 | 4.23e-05 | 2.6854e-05 | 0.082036 | 0.082036 | 0.082036 | 0.99429 | -0.10935 | 0.99513 | -0.093212 | 22.5373
87 | 0.0019808 | 0.00049626 | -0.0019807 | -0.00049642 | 4.8318e-08 | -1.5925e-07 | 0.0029643 | 0.0029644 | 0.0029644 | 0.99429 | -0.10935 | 0.99427 | -0.10986 | 0.81439
88 | -0.054845 | -0.013819 | 0.054887 | 0.013845 | 4.1725e-05 | 2.6489e-05 | 0.082036 | 0.082036 | 0.082036 | 0.99513 | -0.093212 | 0.99596 | -0.07732 | 22.5372
89 | -0.096057 | -0.024142 | 0.096087 | 0.02416 | 3.0106e-05 | 1.8102e-05 | 0.14658 | 0.14658 | 0.14658 | 0.9753 | -0.47544 | 0.97563 | -0.46888 | 8.0538
90 | 0.0018783 | 0.00047056 | -0.0018782 | -0.00047073 | 5.1395e-08 | -1.7791e-07 | 0.002857 | 0.002857 | 0.002857 | 0.97826 | -0.41737 | 0.97823 | -0.41795 | 0.7849
91 | 0.23317 | 0.059604 | -0.23291 | -0.059436 | 0.00026455 | 0.00016744 | 0.3493 | 0.3493 | 0.3493 | 0.9945 | -0.10422 | 0.99326 | -0.1277 | 19.1924
92 | 0.23173 | 0.059141 | -0.23172 | -0.059133 | 1.1282e-05 | 7.1396e-06 | 0.34753 | 0.34753 | 0.34753 | 0.99326 | -0.1277 | 0.99321 | -0.12871 | 19.0952
93 | 0.060325 | 0.01526 | -0.060235 | -0.015203 | 9.0052e-05 | 5.7246e-05 | 0.089953 | 0.089953 | 0.089953 | 0.99847 | -0.029263 | 0.99684 | -0.060425 | 24.7124
94 | 0.057179 | 0.014437 | -0.057132 | -0.014408 | 4.6245e-05 | 2.9377e-05 | 0.08539 | 0.08539 | 0.08539 | 0.99684 | -0.060425 | 0.99596 | -0.07732 | 23.4589
95 | -0.032546 | -0.0081693 | 0.032565 | 0.0081809 | 1.8493e-05 | 1.157e-05 | 0.048875 | 0.048875 | 0.048875 | 0.99098 | -0.17163 | 0.9916 | -0.15973 | 13.4271
96 | 0.029488 | 0.0074028 | -0.029477 | -0.0073961 | 1.0783e-05 | 6.7124e-06 | 0.044282 | 0.044282 | 0.044282 | 0.99098 | -0.17163 | 0.99059 | -0.1793 | 12.1655
97 | -0.035075 | -0.0088101 | 0.035107 | 0.0088298 | 3.1503e-05 | 1.9771e-05 | 0.052642 | 0.052642 | 0.052642 | 0.9916 | -0.15973 | 0.99257 | -0.14092 | 14.462
98 | 0.027252 | 0.006839 | -0.027241 | -0.0068322 | 1.0961e-05 | 6.7907e-06 | 0.040939 | 0.040939 | 0.040939 | 0.99059 | -0.1793 | 0.99015 | -0.18774 | 11.247
99 | 0.0022257 | 0.0005571 | -0.0022255 | -0.00055745 | 1.4332e-07 | -3.4846e-07 | 0.0033431 | 0.0033432 | 0.0033432 | 0.99059 | -0.1793 | 0.99052 | -0.18066 | 0.91847
100 | 0.19481 | 0.049801 | -0.1946 | -0.049667 | 0.00021225 | 0.00013371 | 0.2924 | 0.2924 | 0.2924 | 0.99257 | -0.14092 | 0.99139 | -0.16347 | 16.066
101 | -0.22992 | -0.058631 | 0.23005 | 0.058716 | 0.00013568 | 8.5855e-05 | 0.34504 | 0.34504 | 0.34504 | 0.99257 | -0.14092 | 0.99321 | -0.12871 | 18.9583
102 | 0.0076096 | 0.0019066 | -0.0076086 | -0.0019062 | 9.9824e-07 | 3.771e-07 | 0.011436 | 0.011436 | 0.011436 | 0.99015 | -0.18774 | 0.99001 | -0.1905 | 3.1417
103 | 0.0011584 | 0.00029 | -0.0011584 | -0.00029032 | 2.9808e-08 | -3.1879e-07 | 0.0017401 | 0.0017402 | 0.0017402 | 0.99052 | -0.18066 | 0.99049 | -0.1812 | 0.47809
104 | 0.19313 | 0.049299 | -0.19307 | -0.04926 | 6.2623e-05 | 3.944e-05 | 0.2902 | 0.2902 | 0.2902 | 0.99139 | -0.16347 | 0.99104 | -0.17019 | 15.945
105 | 0.0033773 | 0.00084577 | -0.0033771 | -0.00084592 | 2.1954e-07 | -1.5164e-07 | 0.005076 | 0.0050761 | 0.0050761 | 0.99001 | -0.1905 | 0.98994 | -0.19186 | 1.3945
106 | 0.19143 | 0.04885 | -0.19132 | -0.04878 | 0.00011101 | 6.9892e-05 | 0.28774 | 0.28774 | 0.28774 | 0.99104 | -0.17019 | 0.99041 | -0.1822 | 15.8101
107 | 0.0021895 | 0.00054827 | -0.0021894 | -0.00054841 | 5.6109e-08 | -1.4171e-07 | 0.0032909 | 0.0032909 | 0.0032909 | 0.98994 | -0.19186 | 0.98991 | -0.1924 | 0.90411
108 | 0.18902 | 0.048204 | -0.18896 | -0.048166 | 5.9822e-05 | 3.7651e-05 | 0.28429 | 0.28429 | 0.28429 | 0.99041 | -0.1822 | 0.99007 | -0.18875 | 15.6203
109 | -0.17938 | -0.045596 | 0.17952 | 0.045684 | 0.00013932 | 8.7542e-05 | 0.27055 | 0.27055 | 0.27055 | 0.98743 | -0.23949 | 0.98827 | -0.22337 | 14.8656
110 | -0.18108 | -0.046075 | 0.18112 | 0.046099 | 3.8119e-05 | 2.3959e-05 | 0.2729 | 0.2729 | 0.2729 | 0.98827 | -0.22337 | 0.98849 | -0.21901 | 14.9946
111 | -0.18264 | -0.046479 | 0.18274 | 0.046543 | 0.00010308 | 6.4804e-05 | 0.27518 | 0.27518 | 0.27518 | 0.98849 | -0.21901 | 0.9891 | -0.20731 | 15.1199
112 | -0.18448 | -0.046978 | 0.18453 | 0.047012 | 5.2925e-05 | 3.3285e-05 | 0.27779 | 0.27779 | 0.27779 | 0.9891 | -0.20731 | 0.98941 | -0.20136 | 15.2633
113 | -0.18699 | -0.047628 | 0.1871 | 0.047699 | 0.00011378 | 7.159e-05 | 0.28149 | 0.28149 | 0.28149 | 0.98941 | -0.20136 | 0.99007 | -0.18875 | 15.4665
114 | -0.0008 | -0.0002005 | 0.0008 | 0.00020039 | 4.802e-09 | -1.1077e-07 | 0.0012025 | 0.0012025 | 0.0012025 | 0.98991 | -0.19253 | 0.98991 | -0.1924 | 0.33037
115 | 0.0013894 | 0.00034802 | -0.0013894 | -0.00034821 | 2.5884e-08 | -1.8687e-07 | 0.0020884 | 0.0020885 | 0.0020885 | 0.98991 | -0.1924 | 0.98989 | -0.19279 | 0.57377
116 | 0.025197 | 0.0063194 | -0.025195 | -0.0063182 | 1.9097e-06 | 1.1799e-06 | 0.038585 | 0.038586 | 0.038586 | 0.97174 | -0.54566 | 0.97166 | -0.54725 | 10.6004
117 | -0.025751 | -0.0064583 | 0.025771 | 0.0064702 | 1.9231e-05 | 1.1899e-05 | 0.039434 | 0.039434 | 0.039434 | 0.97174 | -0.54566 | 0.97253 | -0.53 | 10.8337
118 | 0.017238 | 0.0043239 | -0.017228 | -0.0043182 | 9.6356e-06 | 5.7104e-06 | 0.0264 | 0.0264 | 0.0264 | 0.97166 | -0.54725 | 0.97107 | -0.55898 | 7.2527
119 | -0.025771 | -0.0064702 | 0.025783 | 0.006477 | 1.2251e-05 | 6.7975e-06 | 0.039434 | 0.039434 | 0.039434 | 0.97253 | -0.53 | 0.97304 | -0.52004 | 5.4168
120 | 0.0078635 | 0.0019714 | -0.0078623 | -0.0019709 | 1.11e-06 | 4.5825e-07 | 0.01205 | 0.01205 | 0.01205 | 0.97107 | -0.55898 | 0.97092 | -0.56194 | 3.3104
121 | 0.0093647 | 0.0023469 | -0.0093634 | -0.0023462 | 1.3378e-06 | 6.4191e-07 | 0.01435 | 0.01435 | 0.01435 | 0.97107 | -0.55898 | 0.97091 | -0.56198 | 3.9423
122 | -0.026972 | -0.0067751 | 0.026976 | 0.0067757 | 4.2845e-06 | 6.5683e-07 | 0.041253 | 0.041252 | 0.041253 | 0.97304 | -0.52004 | 0.97321 | -0.51671 | 2.2666
123 | 0.0078623 | 0.0019709 | -0.0078598 | -0.0019699 | 2.5094e-06 | 1.0363e-06 | 0.01205 | 0.01205 | 0.01205 | 0.97092 | -0.56194 | 0.97058 | -0.56864 | 3.3105
124 | 0.0068244 | 0.0017099 | -0.0068235 | -0.0017096 | 9.8506e-07 | 3.3351e-07 | 0.010459 | 0.010459 | 0.010459 | 0.97091 | -0.56198 | 0.97076 | -0.56501 | 2.8734
125 | -0.029689 | -0.0074555 | 0.029692 | 0.0074563 | 3.3016e-06 | 7.8589e-07 | 0.045399 | 0.045399 | 0.045399 | 0.97321 | -0.51671 | 0.97332 | -0.51438 | 2.4945
126 | 0.0057686 | 0.0014452 | -0.0057681 | -0.0014451 | 5.7213e-07 | 1.2493e-07 | 0.0088421 | 0.0088422 | 0.0088422 | 0.97076 | -0.56501 | 0.97066 | -0.56709 | 2.4292
127 | -0.034562 | -0.0086766 | 0.034567 | 0.0086782 | 4.6249e-06 | 1.5874e-06 | 0.052844 | 0.052843 | 0.052844 | 0.97332 | -0.51438 | 0.97347 | -0.51158 | 2.9035
128 | 0.0048701 | 0.0012203 | -0.0048695 | -0.0012203 | 6.0339e-07 | 2.5462e-08 | 0.0074454 | 0.0074455 | 0.0074455 | 0.97332 | -0.51438 | 0.97319 | -0.51698 | 2.0455
129 | 0.0045851 | 0.0011486 | -0.004585 | -0.0011486 | 1.1898e-07 | -3.232e-09 | 0.0070288 | 0.0070288 | 0.0070288 | 0.97066 | -0.56709 | 0.97063 | -0.56764 | 1.931
130 | 0.0033445 | 0.00083769 | -0.0033441 | -0.00083792 | 3.6071e-07 | -2.2136e-07 | 0.005127 | 0.0051272 | 0.0051272 | 0.97063 | -0.56764 | 0.97051 | -0.5699 | 1.4086
131 | 0.00082498 | 0.00020656 | -0.00082497 | -0.00020676 | 9.8656e-09 | -1.9689e-07 | 0.0012648 | 0.0012649 | 0.0012649 | 0.97051 | -0.5699 | 0.9705 | -0.57016 | 0.34749
132 | 0.0025295 | 0.00063382 | -0.0025294 | -0.00063394 | 7.1128e-08 | -1.1203e-07 | 0.0038676 | 0.0038676 | 0.0038676 | 0.97319 | -0.51698 | 0.97316 | -0.51758 | 1.0625
133 | -0.038242 | -0.0095993 | 0.038243 | 0.0095996 | 5.9029e-07 | 2.3464e-07 | 0.058461 | 0.058461 | 0.058461 | 0.97347 | -0.51158 | 0.97348 | -0.51125 | 3.2122
134 | -0.044974 | -0.011287 | 0.044984 | 0.011291 | 1.0382e-05 | 4.8234e-06 | 0.06875 | 0.06875 | 0.06875 | 0.97348 | -0.51125 | 0.97373 | -0.50642 | 3.7775
135 | -0.048733 | -0.012231 | 0.048736 | 0.012232 | 2.3108e-06 | 1.1334e-06 | 0.074479 | 0.074479 | 0.074479 | 0.97373 | -0.50642 | 0.97378 | -0.50542 | 4.0922

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32685 | 0.083318

## res_load
| p_mw | q_mvar
0 | 0.0064765 | 0.0016232
1 | 0.0017949 | 0.00044985
2 | 0.0019624 | 0.00049183
3 | 0.001748 | 0.00043808
4 | 0.0018071 | 0.00045291
5 | 0.0011783 | 0.00029531
6 | 0.0021931 | 0.00054965
7 | 0.0029438 | 0.00073779
8 | 0.0030174 | 0.00075624
9 | 0.0031113 | 0.00077976
10 | 0.0019498 | 0.00048866
11 | 0.0025691 | 0.00064388
12 | 0.0033661 | 0.00084363
13 | 0.002147 | 0.0005381
14 | 0.0021953 | 0.00055019
15 | 0.0017558 | 0.00044004
16 | 0.0016806 | 0.00042119
17 | 0.0021645 | 0.00054247
18 | 0.0043443 | 0.0010888
19 | 0.0014733 | 0.00036925
20 | 0.0054214 | 0.0013587
21 | 0.0020626 | 0.00051693
22 | 0.0010118 | 0.00025358
23 | 0.0013464 | 0.00033743
24 | 0.0016143 | 0.00040459
25 | 0.002857 | 0.00071604
26 | 0.0033727 | 0.00084528
27 | 0.001534 | 0.00038447
28 | 0.0020686 | 0.00051843
29 | 0.0020442 | 0.00051232
30 | 0.0022404 | 0.0005615
31 | 0.0018202 | 0.00045617
32 | 0.0018255 | 0.00045752
33 | 0.0045603 | 0.0011429
34 | 0.0032134 | 0.00080534
35 | 0.003622 | 0.00090776
36 | 0.0051824 | 0.0012988
37 | 0.0024676 | 0.00061843
38 | 0.0015882 | 0.00039804
39 | 0.0016588 | 0.00041572
40 | 0.0029931 | 0.00075014
41 | 0.0082479 | 0.0020671
42 | 0.0074639 | 0.0018706
43 | 0.0097322 | 0.0024391
44 | 0.0021708 | 0.00054405
45 | 0.0058205 | 0.0014587
46 | 0.0015782 | 0.00039553
47 | 0.0086211 | 0.0021606
48 | 0.0022011 | 0.00055164
49 | 0.0029735 | 0.00074522
50 | 0.0036544 | 0.00091588
51 | 0.0031718 | 0.00079492
52 | 0.0038622 | 0.00096795
53 | 0.0020585 | 0.0005159
54 | 0.0015934 | 0.00039934
55 | 0.0020814 | 0.00052164
56 | 0.0014629 | 0.00036664
57 | 0.0036802 | 0.00092235
58 | 0.0017079 | 0.00042804
59 | 0.0025838 | 0.00064756
60 | 0.0055425 | 0.0013891
61 | 0.0028296 | 0.00070918
62 | 0.0019731 | 0.00049452
63 | 0.0010077 | 0.00025254
64 | 0.0015914 | 0.00039884
65 | 0.001628 | 0.00040802
66 | 0.003004 | 0.00075286
67 | 0.0032146 | 0.00080565
68 | 0.0014947 | 0.00037461
69 | 0.0019942 | 0.00049979
70 | 0.0033251 | 0.00083334
71 | 0.0035111 | 0.00087996
72 | 0.0019807 | 0.00049642
73 | 0.0012 | 0.00030076
74 | 0.0015362 | 0.000385
75 | 0.0018782 | 0.00047073
76 | 0.0014933 | 0.00037425
77 | 0.0011801 | 0.00029576
78 | 0.0029174 | 0.00073117
79 | 0.0030566 | 0.00076607
80 | 0.0022455 | 0.00056277
81 | 0.0030585 | 0.00076653
82 | 0.0025103 | 0.00062915
83 | 0.0010671 | 0.00026745
84 | 0.0014665 | 0.00036753
85 | 0.0016639 | 0.00041702
86 | 0.0042313 | 0.0010605
87 | 0.0011584 | 0.00029032
88 | 0.0016357 | 0.00040995
89 | 0.0025521 | 0.00063961
90 | 0.0011876 | 0.00029765
91 | 0.0022999 | 0.00057641
92 | 0.0018928 | 0.00047438
93 | 0.0015598 | 0.00039093
94 | 0.0015153 | 0.00037977
95 | 0.001735 | 0.00043484
96 | 0.0024581 | 0.00061607
97 | 0.001863 | 0.00046692
98 | 0.0008 | 0.0002005
99 | 0.0013894 | 0.00034821
100 | 0.00055443 | 0.00013895
101 | 0.0079572 | 0.0019943
102 | 0.0011892 | 0.00029804
103 | 0.002539 | 0.00063633
104 | 0.0027124 | 0.00067979
105 | 0.0078598 | 0.0019699
106 | 0.0010548 | 0.00026436
107 | 0.0016211 | 0.00040628
108 | 0.0011829 | 0.00029647
109 | 0.0012405 | 0.00031091
110 | 0.0025191 | 0.00063136
111 | 0.00234 | 0.00058646
112 | 0.0025294 | 0.00063394
113 | 0.0036753 | 0.00092113
114 | 0.0067312 | 0.001687
115 | 0.003749 | 0.00093958
116 | 0.0019413 | 0.00048653
117 | 0.00082497 | 0.00020676
118 | 0.0044048 | 0.001104

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1