## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_192-12_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_192-12_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_192-12_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_192-12_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_192-12_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_192-12_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_192-12_0_6_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_192-12_0_6_node_122 | 0.4 | n |  | TRUE
8 | bus_LV_192-12_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_192-12_0_6_node_68 | 0.4 | n |  | TRUE
10 | bus_LV_192-12_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_192-12_0_6_node_123 | 0.4 | n |  | TRUE
12 | bus_LV_192-12_0_6_node_138 | 0.4 | n |  | TRUE
13 | bus_LV_192-12_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_192-12_0_6_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_192-12_0_6_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_192-12_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_192-12_0_6_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_192-12_0_6_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_192-12_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_192-12_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_192-12_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_192-12_0_6_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_192-12_0_6_node_144 | 0.4 | n |  | TRUE
24 | bus_LV_192-12_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_192-12_0_6_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_192-12_0_6_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_192-12_0_6_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_192-12_0_6_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_192-12_0_6_node_153 | 0.4 | n |  | TRUE
30 | bus_LV_192-12_0_6_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_192-12_0_6_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_192-12_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_192-12_0_6_node_74 | 0.4 | n |  | TRUE
34 | bus_LV_192-12_0_6_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_192-12_0_6_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_192-12_0_6_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_192-12_0_6_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_192-12_0_6_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_192-12_0_6_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_192-12_0_6_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_192-12_0_6_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_192-12_0_6_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_192-12_0_6_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_192-12_0_6_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_192-12_0_6_node_145 | 0.4 | n |  | TRUE
46 | bus_LV_192-12_0_6_node_143 | 0.4 | n |  | TRUE
47 | bus_LV_192-12_0_6_node_79 | 0.4 | n |  | TRUE
48 | bus_LV_192-12_0_6_node_154 | 0.4 | n |  | TRUE
49 | bus_LV_192-12_0_6_node_76 | 0.4 | n |  | TRUE
50 | bus_LV_192-12_0_6_node_57 | 0.4 | n |  | TRUE
51 | bus_LV_192-12_0_6_node_93 | 0.4 | n |  | TRUE
52 | bus_LV_192-12_0_6_node_91 | 0.4 | n |  | TRUE
53 | bus_LV_192-12_0_6_node_92 | 0.4 | n |  | TRUE
54 | bus_LV_192-12_0_6_node_107 | 0.4 | n |  | TRUE
55 | bus_LV_192-12_0_6_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_192-12_0_6_node_109 | 0.4 | n |  | TRUE
57 | bus_LV_192-12_0_6_node_105 | 0.4 | n |  | TRUE
58 | bus_LV_192-12_0_6_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_192-12_0_6_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_192-12_0_6_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_192-12_0_6_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_192-12_0_6_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_192-12_0_6_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_192-12_0_6_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_192-12_0_6_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_192-12_0_6_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_192-12_0_6_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_192-12_0_6_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_192-12_0_6_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_192-12_0_6_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_192-12_0_6_node_45 | 0.4 | n |  | TRUE
72 | bus_LV_192-12_0_6_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_192-12_0_6_node_80 | 0.4 | n |  | TRUE
74 | bus_LV_192-12_0_6_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_192-12_0_6_node_47 | 0.4 | n |  | TRUE
76 | bus_LV_192-12_0_6_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_192-12_0_6_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_192-12_0_6_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_192-12_0_6_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_192-12_0_6_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_192-12_0_6_node_116 | 0.4 | n |  | TRUE
82 | bus_LV_192-12_0_6_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_192-12_0_6_node_140 | 0.4 | n |  | TRUE
84 | bus_LV_192-12_0_6_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_192-12_0_6_node_61 | 0.4 | n |  | TRUE
86 | bus_LV_192-12_0_6_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_192-12_0_6_node_88 | 0.4 | n |  | TRUE
88 | bus_LV_192-12_0_6_node_87 | 0.4 | n |  | TRUE
89 | bus_LV_192-12_0_6_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_192-12_0_6_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_192-12_0_6_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_192-12_0_6_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_192-12_0_6_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_192-12_0_6_node_59 | 0.4 | n |  | TRUE
95 | bus_LV_192-12_0_6_node_52 | 0.4 | n |  | TRUE
96 | bus_LV_192-12_0_6_node_151 | 0.4 | n |  | TRUE
97 | bus_LV_192-12_0_6_node_51 | 0.4 | n |  | TRUE
98 | bus_LV_192-12_0_6_node_53 | 0.4 | n |  | TRUE
99 | bus_LV_192-12_0_6_node_55 | 0.4 | n |  | TRUE
100 | bus_LV_192-12_0_6_node_56 | 0.4 | n |  | TRUE
101 | bus_LV_192-12_0_6_node_155 | 0.4 | n |  | TRUE
102 | bus_LV_192-12_0_6_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_192-12_0_6_node_156 | 0.4 | n |  | TRUE
104 | bus_LV_192-12_0_6_node_150 | 0.4 | n |  | TRUE
105 | bus_LV_192-12_0_6_node_75 | 0.4 | n |  | TRUE
106 | bus_LV_192-12_0_6_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_192-12_0_6_node_62 | 0.4 | n |  | TRUE
108 | bus_LV_192-12_0_6_node_137 | 0.4 | n |  | TRUE
109 | bus_LV_192-12_0_6_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_192-12_0_6_node_77 | 0.4 | n |  | TRUE
111 | bus_LV_192-12_0_6_node_78 | 0.4 | n |  | TRUE
112 | bus_LV_192-12_0_6_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_192-12_0_6_node_129 | 0.4 | n |  | TRUE
114 | bus_LV_192-12_0_6_node_97 | 0.4 | n |  | TRUE
115 | bus_LV_192-12_0_6_node_99 | 0.4 | n |  | TRUE
116 | bus_LV_192-12_0_6_node_130 | 0.4 | n |  | TRUE
117 | bus_LV_192-12_0_6_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_192-12_0_6_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_192-12_0_6_node_86 | 0.4 | n |  | TRUE
120 | bus_LV_192-12_0_6_node_90 | 0.4 | n |  | TRUE
121 | bus_LV_192-12_0_6_node_94 | 0.4 | n |  | TRUE
122 | bus_LV_192-12_0_6_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_192-12_0_6_node_98 | 0.4 | n |  | TRUE
124 | bus_LV_192-12_0_6_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_192-12_0_6_node_102 | 0.4 | n |  | TRUE
126 | bus_LV_192-12_0_6_node_103 | 0.4 | n |  | TRUE
127 | bus_LV_192-12_0_6_node_104 | 0.4 | n |  | TRUE
128 | bus_LV_192-12_0_6_node_120 | 0.4 | n |  | TRUE
129 | bus_LV_192-12_0_6_node_132 | 0.4 | n |  | TRUE
130 | bus_LV_192-12_0_6_node_131 | 0.4 | n |  | TRUE
131 | bus_LV_192-12_0_6_node_121 | 0.4 | n |  | TRUE
132 | bus_LV_192-12_0_6_node_136 | 0.4 | n |  | TRUE
133 | bus_LV_192-12_0_6_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_192-12_0_6_node_128 | 0.4 | n |  | TRUE
135 | bus_LV_192-12_0_6_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_192-12_0_6_node_111 | 0.4 | n |  | TRUE
137 | bus_LV_192-12_0_6_node_112 | 0.4 | n |  | TRUE
138 | bus_LV_192-12_0_6_node_141 | 0.4 | n |  | TRUE
139 | bus_LV_192-12_0_6_node_113 | 0.4 | n |  | TRUE
140 | bus_LV_192-12_0_6_node_114 | 0.4 | n |  | TRUE
141 | bus_LV_192-12_0_6_node_115 | 0.4 | n |  | TRUE
142 | bus_LV_192-12_0_6_node_142 | 0.4 | n |  | TRUE
143 | bus_LV_192-12_0_6_node_133 | 0.4 | n |  | TRUE
144 | bus_LV_192-12_0_6_node_134 | 0.4 | n |  | TRUE
145 | bus_LV_192-12_0_6_node_126 | 0.4 | n |  | TRUE
146 | bus_LV_192-12_0_6_node_148 | 0.4 | n |  | TRUE
147 | bus_LV_192-12_0_6_node_149 | 0.4 | n |  | TRUE
148 | bus_LV_192-12_0_6_node_124 | 0.4 | n |  | TRUE
149 | bus_LV_192-12_0_6_node_125 | 0.4 | n |  | TRUE
150 | bus_LV_192-12_0_6_node_127 | 0.4 | n |  | TRUE
151 | bus_LV_192-12_0_6_node_147 | 0.4 | n |  | TRUE
152 | bus_LV_192-12_0_6_node_146 | 0.4 | n |  | TRUE
153 | bus_MV_356_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_192-12_0_6_load_0 | 0 | 0.00055895 | 0.00014009 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_192-12_0_6_load_4 | 4 | 0.00030495 | 7.6429e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_192-12_0_6_load_5 | 5 | 0.0022293 | 0.00055872 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_192-12_0_6_load_7 | 6 | 0.0013894 | 0.00034821 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_192-12_0_6_load_122 | 7 | 0.0016613 | 0.00041637 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_192-12_0_6_load_6 | 8 | 0.0042938 | 0.0010761 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_192-12_0_6_load_8 | 10 | 0.00039841 | 9.9851e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_192-12_0_6_load_138 | 12 | 0.0067652 | 0.0016955 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_192-12_0_6_load_25 | 14 | 0.0026339 | 0.00066011 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_192-12_0_6_load_17 | 17 | 0.0016167 | 0.00040519 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_192-12_0_6_load_15 | 18 | 0.0063433 | 0.0015898 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_192-12_0_6_load_21 | 21 | 0.007744 | 0.0019408 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_192-12_0_6_load_32 | 26 | 0.020225 | 0.0050688 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_192-12_0_6_load_153 | 29 | 0.0050238 | 0.0012591 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_192-12_0_6_load_37 | 31 | 0.0081294 | 0.0020374 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_192-12_0_6_load_74 | 33 | 0.023294 | 0.0058381 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_192-12_0_6_load_27 | 34 | 0.001728 | 0.00043308 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_192-12_0_6_load_24 | 35 | 0.0015744 | 0.00039459 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_192-12_0_6_load_23 | 37 | 0.0045991 | 0.0011526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_192-12_0_6_load_35 | 39 | 0.001485 | 0.00037218 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_192-12_0_6_load_38 | 40 | 0.00092052 | 0.0002307 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_192-12_0_6_load_30 | 41 | 0.0014789 | 0.00037064 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_192-12_0_6_load_31 | 42 | 0.0073935 | 0.001853 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_192-12_0_6_load_145 | 45 | 0.0026328 | 0.00065984 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_192-12_0_6_load_143 | 46 | 0.0026314 | 0.0006595 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_192-12_0_6_load_154 | 48 | 0.0039705 | 0.00099511 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_192-12_0_6_load_76 | 49 | 0.0036967 | 0.00092648 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_192-12_0_6_load_91 | 52 | 0.0060039 | 0.0015047 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_192-12_0_6_load_92 | 53 | 0.0036191 | 0.00090702 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_192-12_0_6_load_109 | 56 | 0.0032103 | 0.00080457 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_192-12_0_6_load_105 | 57 | 0.0068309 | 0.001712 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_192-12_0_6_load_84 | 59 | 0.0011715 | 0.00029359 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_192-12_0_6_load_85 | 60 | 0.0045148 | 0.0011315 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_192-12_0_6_load_39 | 61 | 0.0060301 | 0.0015113 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_192-12_0_6_load_40 | 62 | 0.003866 | 0.00096891 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_192-12_0_6_load_42 | 64 | 0.0032765 | 0.00082118 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_192-12_0_6_load_43 | 65 | 0.010187 | 0.0025531 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_192-12_0_6_load_44 | 66 | 0.0048365 | 0.0012121 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_192-12_0_6_load_49 | 69 | 0.010209 | 0.0025586 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_192-12_0_6_load_50 | 70 | 0.0056462 | 0.0014151 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_192-12_0_6_load_81 | 72 | 0.0029428 | 0.00073754 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_192-12_0_6_load_80 | 73 | 0.0029574 | 0.00074118 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_192-12_0_6_load_60 | 76 | 0.010614 | 0.0026602 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_192-12_0_6_load_54 | 77 | 0.0028788 | 0.0007215 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_192-12_0_6_load_116 | 81 | 0.0025391 | 0.00063637 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_192-12_0_6_load_140 | 83 | 0.0067661 | 0.0016958 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_192-12_0_6_load_61 | 85 | 0.012075 | 0.0030262 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_192-12_0_6_load_88 | 87 | 0.016462 | 0.0041258 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_192-12_0_6_load_87 | 88 | 0.031146 | 0.0078059 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_192-12_0_6_load_89 | 91 | 0.0084801 | 0.0021253 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_192-12_0_6_load_73 | 92 | 0.0045946 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_192-12_0_6_load_71 | 93 | 0.0039544 | 0.00099107 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_192-12_0_6_load_52 | 95 | 0.0024804 | 0.00062164 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_192-12_0_6_load_51 | 97 | 0.013644 | 0.0034195 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_192-12_0_6_load_55 | 99 | 0.0064641 | 0.00162 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_192-12_0_6_load_155 | 101 | 0.007812 | 0.0019579 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_192-12_0_6_load_156 | 103 | 0.0082969 | 0.0020794 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_192-12_0_6_load_150 | 104 | 0.0018995 | 0.00047606 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_192-12_0_6_load_70 | 106 | 0.0053937 | 0.0013518 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_192-12_0_6_load_62 | 107 | 0.010617 | 0.0026609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_192-12_0_6_load_137 | 108 | 0.0053938 | 0.0013518 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_192-12_0_6_load_78 | 111 | 0.007219 | 0.0018092 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_192-12_0_6_load_101 | 112 | 0.0044094 | 0.0011051 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_192-12_0_6_load_129 | 113 | 0.0070262 | 0.0017609 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_192-12_0_6_load_99 | 115 | 0.0084768 | 0.0021245 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_192-12_0_6_load_130 | 116 | 0.0076495 | 0.0019172 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_192-12_0_6_load_118 | 117 | 0.0034798 | 0.00087212 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_192-12_0_6_load_119 | 118 | 0.0032167 | 0.00080618 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_192-12_0_6_load_94 | 121 | 0.031507 | 0.0078964 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_192-12_0_6_load_100 | 124 | 0.0045476 | 0.0011397 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_192-12_0_6_load_103 | 126 | 0.0053942 | 0.0013519 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_192-12_0_6_load_104 | 127 | 0.0043312 | 0.0010855 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_192-12_0_6_load_120 | 128 | 0.0059396 | 0.0014886 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_192-12_0_6_load_131 | 130 | 0.0066916 | 0.0016771 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_192-12_0_6_load_121 | 131 | 0.002333 | 0.0005847 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_192-12_0_6_load_136 | 132 | 0.0016341 | 0.00040955 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_192-12_0_6_load_135 | 133 | 0.003302 | 0.00082757 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_192-12_0_6_load_128 | 134 | 0.001867 | 0.00046791 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_192-12_0_6_load_106 | 135 | 0.0045759 | 0.0011468 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_192-12_0_6_load_111 | 136 | 0.0027395 | 0.00068659 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_192-12_0_6_load_112 | 137 | 0.0075547 | 0.0018934 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_192-12_0_6_load_141 | 138 | 0.0044895 | 0.0011252 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_192-12_0_6_load_115 | 141 | 0.0042794 | 0.0010725 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_192-12_0_6_load_142 | 142 | 0.0016704 | 0.00041863 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_192-12_0_6_load_133 | 143 | 0.0026314 | 0.00065949 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_192-12_0_6_load_148 | 146 | 0.0047597 | 0.0011929 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_192-12_0_6_load_149 | 147 | 0.0065097 | 0.0016315 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_192-12_0_6_load_124 | 148 | 0.0015558 | 0.00038992 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_192-12_0_6_load_147 | 151 | 0.001832 | 0.00045915 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_192-12_0_6_load_146 | 152 | 0.0015008 | 0.00037614 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 113 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_192-12_0_6_line_0 |  | 0 | 1 | 0.12623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_192-12_0_6_line_1 |  | 0 | 2 | 0.0074583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_192-12_0_6_line_2 |  | 1 | 3 | 0.11593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_192-12_0_6_line_3 |  | 2 | 4 | 0.0074199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_192-12_0_6_line_4 |  | 3 | 5 | 0.051838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_192-12_0_6_line_5 |  | 4 | 6 | 0.0068634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_192-12_0_6_line_6 |  | 5 | 7 | 0.028866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_192-12_0_6_line_7 |  | 6 | 10 | 0.020734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_192-12_0_6_line_8 |  | 7 | 11 | 0.018766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_192-12_0_6_line_9 |  | 8 | 9 | 0.015062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_192-12_0_6_line_10 |  | 9 | 12 | 0.023628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_192-12_0_6_line_11 |  | 11 | 148 | 0.023218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_192-12_0_6_line_12 |  | 12 | 84 | 0.025676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_192-12_0_6_line_13 |  | 13 | 14 | 0.0645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_192-12_0_6_line_14 |  | 13 | 15 | 0.015454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_192-12_0_6_line_15 |  | 14 | 23 | 0.021322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_192-12_0_6_line_16 |  | 15 | 18 | 0.03346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_192-12_0_6_line_17 |  | 16 | 17 | 0.027855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_192-12_0_6_line_18 |  | 16 | 18 | 0.0222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_192-12_0_6_line_19 |  | 17 | 21 | 0.037024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_192-12_0_6_line_20 |  | 19 | 20 | 0.045604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_192-12_0_6_line_21 |  | 19 | 21 | 0.043488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_192-12_0_6_line_22 |  | 20 | 22 | 0.03921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_192-12_0_6_line_23 |  | 22 | 26 | 0.029135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_192-12_0_6_line_24 |  | 23 | 45 | 0.016722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_192-12_0_6_line_25 |  | 23 | 46 | 0.036993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_192-12_0_6_line_26 |  | 24 | 25 | 0.053729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_192-12_0_6_line_27 |  | 24 | 26 | 0.036459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_192-12_0_6_line_28 |  | 25 | 38 | 0.036928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_192-12_0_6_line_29 |  | 25 | 39 | 0.019008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_192-12_0_6_line_30 |  | 27 | 28 | 0.01417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_192-12_0_6_line_31 |  | 27 | 29 | 0.019911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_192-12_0_6_line_32 |  | 28 | 33 | 0.039371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_192-12_0_6_line_33 |  | 29 | 50 | 0.025928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_192-12_0_6_line_34 |  | 30 | 31 | 0.029281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_192-12_0_6_line_35 |  | 30 | 32 | 0.030438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_192-12_0_6_line_36 |  | 32 | 41 | 0.0076862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_192-12_0_6_line_37 |  | 32 | 36 | 0.061066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_192-12_0_6_line_38 |  | 34 | 35 | 0.027633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_192-12_0_6_line_39 |  | 35 | 36 | 0.026291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_192-12_0_6_line_40 |  | 36 | 37 | 0.038426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_192-12_0_6_line_41 |  | 37 | 42 | 0.054685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_192-12_0_6_line_42 |  | 38 | 40 | 0.014319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_192-12_0_6_line_43 |  | 39 | 43 | 0.0035541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_192-12_0_6_line_44 |  | 40 | 58 | 0.012728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_192-12_0_6_line_45 |  | 41 | 43 | 0.021177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_192-12_0_6_line_46 |  | 42 | 44 | 0.026089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_192-12_0_6_line_47 |  | 44 | 55 | 0.007521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_192-12_0_6_line_48 |  | 45 | 152 | 0.029222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_192-12_0_6_line_49 |  | 46 | 143 | 0.0098913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_192-12_0_6_line_50 |  | 47 | 48 | 0.010358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_192-12_0_6_line_51 |  | 47 | 49 | 0.025725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_192-12_0_6_line_52 |  | 48 | 103 | 0.014193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_192-12_0_6_line_53 |  | 49 | 94 | 0.02932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_192-12_0_6_line_54 |  | 50 | 100 | 0.056713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_192-12_0_6_line_55 |  | 51 | 52 | 0.0035268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_192-12_0_6_line_56 |  | 51 | 53 | 0.024151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_192-12_0_6_line_57 |  | 53 | 120 | 0.018927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_192-12_0_6_line_58 |  | 54 | 55 | 0.033472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_192-12_0_6_line_59 |  | 54 | 56 | 0.013158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_192-12_0_6_line_60 |  | 54 | 57 | 0.02612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_192-12_0_6_line_61 |  | 55 | 136 | 0.013794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_192-12_0_6_line_62 |  | 56 | 137 | 0.029268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_192-12_0_6_line_63 |  | 57 | 135 | 0.023514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_192-12_0_6_line_64 |  | 58 | 59 | 0.012541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_192-12_0_6_line_65 |  | 58 | 60 | 0.031725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_192-12_0_6_line_66 |  | 59 | 119 | 0.013405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_192-12_0_6_line_67 |  | 61 | 62 | 0.0042482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_192-12_0_6_line_68 |  | 61 | 63 | 0.023787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_192-12_0_6_line_69 |  | 62 | 64 | 0.015907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_192-12_0_6_line_70 |  | 63 | 65 | 0.015659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_192-12_0_6_line_71 |  | 63 | 66 | 0.02787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_192-12_0_6_line_72 |  | 63 | 67 | 0.02902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_192-12_0_6_line_73 |  | 64 | 68 | 0.011848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_192-12_0_6_line_74 |  | 65 | 69 | 0.011331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_192-12_0_6_line_75 |  | 66 | 70 | 0.024056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_192-12_0_6_line_76 |  | 67 | 74 | 0.05552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_192-12_0_6_line_77 |  | 68 | 77 | 0.01154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_192-12_0_6_line_78 |  | 68 | 75 | 0.021999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_192-12_0_6_line_79 |  | 69 | 72 | 0.0082317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_192-12_0_6_line_80 |  | 70 | 78 | 0.021979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_192-12_0_6_line_81 |  | 71 | 72 | 0.01013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_192-12_0_6_line_82 |  | 71 | 73 | 0.014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_192-12_0_6_line_83 |  | 74 | 85 | 0.016708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_192-12_0_6_line_84 |  | 75 | 76 | 0.029899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_192-12_0_6_line_85 |  | 76 | 94 | 0.021542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_192-12_0_6_line_86 |  | 77 | 95 | 0.011721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_192-12_0_6_line_87 |  | 78 | 96 | 0.058949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_192-12_0_6_line_88 |  | 79 | 80 | 0.031232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_192-12_0_6_line_89 |  | 79 | 81 | 0.015552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_192-12_0_6_line_90 |  | 80 | 117 | 0.012621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_192-12_0_6_line_91 |  | 80 | 118 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_192-12_0_6_line_92 |  | 82 | 83 | 0.014068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_192-12_0_6_line_93 |  | 82 | 84 | 0.012936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_192-12_0_6_line_94 |  | 84 | 108 | 0.0071222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_192-12_0_6_line_95 |  | 85 | 107 | 0.025947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_192-12_0_6_line_96 |  | 86 | 87 | 0.028176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_192-12_0_6_line_97 |  | 86 | 88 | 0.026568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_192-12_0_6_line_98 |  | 88 | 89 | 0.010551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_192-12_0_6_line_99 |  | 89 | 90 | 0.017539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_192-12_0_6_line_100 |  | 90 | 91 | 0.0056673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_192-12_0_6_line_101 |  | 91 | 109 | 0.027205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_192-12_0_6_line_102 |  | 92 | 93 | 0.030613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_192-12_0_6_line_103 |  | 93 | 106 | 0.019477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_192-12_0_6_line_104 |  | 94 | 102 | 0.011912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_192-12_0_6_line_105 |  | 95 | 97 | 0.022898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_192-12_0_6_line_106 |  | 96 | 104 | 0.077611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_192-12_0_6_line_107 |  | 97 | 98 | 0.025094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_192-12_0_6_line_108 |  | 98 | 99 | 0.011637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_192-12_0_6_line_109 |  | 100 | 101 | 0.022389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_192-12_0_6_line_110 |  | 101 | 103 | 0.0028485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_192-12_0_6_line_111 |  | 102 | 105 | 0.008468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_192-12_0_6_line_112 |  | 102 | 106 | 0.015185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_192-12_0_6_line_113 |  | 104 | 118 | 0.014783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_192-12_0_6_line_114 |  | 105 | 110 | 0.051863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_192-12_0_6_line_115 |  | 105 | 111 | 0.030753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_192-12_0_6_line_116 |  | 108 | 126 | 0.024383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_192-12_0_6_line_117 |  | 109 | 115 | 0.0029768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_192-12_0_6_line_118 |  | 110 | 112 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_192-12_0_6_line_119 |  | 110 | 113 | 0.019826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_192-12_0_6_line_120 |  | 112 | 114 | 0.036918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_192-12_0_6_line_121 |  | 112 | 115 | 0.023862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_192-12_0_6_line_122 |  | 113 | 116 | 0.029091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_192-12_0_6_line_123 |  | 114 | 124 | 0.014545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_192-12_0_6_line_124 |  | 114 | 122 | 0.025258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_192-12_0_6_line_125 |  | 116 | 137 | 0.0092429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_192-12_0_6_line_126 |  | 119 | 120 | 0.010996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_192-12_0_6_line_127 |  | 121 | 122 | 0.024022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_192-12_0_6_line_128 |  | 122 | 123 | 0.023855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_192-12_0_6_line_129 |  | 123 | 125 | 0.027165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_192-12_0_6_line_130 |  | 123 | 126 | 0.024339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_192-12_0_6_line_131 |  | 123 | 127 | 0.04462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_192-12_0_6_line_132 |  | 124 | 128 | 0.0028684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_192-12_0_6_line_133 |  | 125 | 129 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_192-12_0_6_line_134 |  | 125 | 130 | 0.014844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_192-12_0_6_line_135 |  | 128 | 131 | 0.013903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_192-12_0_6_line_136 |  | 129 | 132 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_192-12_0_6_line_137 |  | 129 | 133 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_192-12_0_6_line_138 |  | 130 | 134 | 0.021126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_192-12_0_6_line_139 |  | 134 | 148 | 0.011237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_192-12_0_6_line_140 |  | 136 | 138 | 0.0082508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_192-12_0_6_line_141 |  | 138 | 142 | 0.020788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_192-12_0_6_line_142 |  | 139 | 140 | 0.018399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_192-12_0_6_line_143 |  | 139 | 141 | 0.026899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_192-12_0_6_line_144 |  | 140 | 143 | 0.01398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_192-12_0_6_line_145 |  | 140 | 144 | 0.01376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_192-12_0_6_line_146 |  | 140 | 145 | 0.035952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_192-12_0_6_line_147 |  | 144 | 146 | 0.028044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_192-12_0_6_line_148 |  | 145 | 147 | 0.034508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_192-12_0_6_line_149 |  | 147 | 150 | 0.0068311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_192-12_0_6_line_150 |  | 149 | 150 | 0.023397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_192-12_0_6_line_151 |  | 149 | 151 | 0.002068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_192-12_0_6_trafo_129 | 0.63 MVA 20/0.4 kV | 153 | 113 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2695242.3073 | 1239330.8035 | 2695238.0766 | 1239337.5406 | 2695225.0956 | 1239365.3865 | 2695182.6159 | 1239441.9432
1 | 2695178.9972 | 1239448.4649 | 2695182.6159 | 1239441.9432
2 | 2695157.3543 | 1239258.9436 | 2695212.0973 | 1239285.8856 | 2695224.2647 | 1239296.0215 | 2695229.5428 | 1239303.6785 | 2695242.3073 | 1239330.8035
3 | 2695178.9972 | 1239448.4649 | 2695174.3706 | 1239454.2656
4 | 2695157.3543 | 1239258.9436 | 2695139.4522 | 1239292.7263 | 2695130.6314 | 1239303.0838
5 | 2695170.0909 | 1239459.6313 | 2695174.3706 | 1239454.2656
6 | 2695111.9158 | 1239325.0599 | 2695130.6314 | 1239303.0838
7 | 2695170.0909 | 1239459.6313 | 2695157.1622 | 1239475.8409
8 | 2695099.7482 | 1239339.3473 | 2695111.9158 | 1239325.0599
9 | 2695063.4713 | 1239202.7759 | 2695075.6198 | 1239211.6792
10 | 2695063.4713 | 1239202.7759 | 2695050.3637 | 1239219.2005 | 2695048.921 | 1239221.3809
11 | 2695099.7482 | 1239339.3473 | 2695080.7047 | 1239326.0642
12 | 2695036.9133 | 1239243.8036 | 2695039.2393 | 1239236.0128 | 2695048.921 | 1239221.3809
13 | 2694894.5403 | 1239482.7823 | 2694928.2406 | 1239436.7978 | 2694934.321 | 1239441.1699
14 | 2694894.5403 | 1239482.7823 | 2694886.8769 | 1239479.5241 | 2694880.6399 | 1239475.9996
15 | 2694951.6324 | 1239453.6177 | 2694934.321 | 1239441.1699
16 | 2694880.6399 | 1239475.9996 | 2694854.8843 | 1239497.3588
17 | 2694837.7958 | 1239511.5305 | 2694816.0554 | 1239494.1156
18 | 2694837.7958 | 1239511.5305 | 2694854.8843 | 1239497.3588
19 | 2694816.0554 | 1239494.1156 | 2694801.8197 | 1239482.7123 | 2694792.5961 | 1239499.0756
20 | 2694732.9205 | 1239508.1205 | 2694730.5797 | 1239513.5539 | 2694750.2133 | 1239525.5761 | 2694758.7582 | 1239530.4716 | 2694765.5394 | 1239531.1804
21 | 2694765.5394 | 1239531.1804 | 2694773.7053 | 1239528.0751 | 2694781.2524 | 1239519.2 | 2694792.5961 | 1239499.0756
22 | 2694732.9205 | 1239508.1205 | 2694738.0424 | 1239496.2156 | 2694714.3269 | 1239484.9623
23 | 2694714.3269 | 1239484.9623 | 2694727.8111 | 1239459.136
24 | 2694951.6324 | 1239453.6177 | 2694965.2103 | 1239463.3788
25 | 2694951.6324 | 1239453.6177 | 2694956.3915 | 1239446.4551 | 2694971.1817 | 1239422.218
26 | 2694707.1764 | 1239439.1364 | 2694709.9723 | 1239431.264 | 2694717.1712 | 1239411.4974 | 2694722.1712 | 1239400.1243 | 2694732.6557 | 1239405.7847
27 | 2694707.1764 | 1239439.1364 | 2694711.1234 | 1239440.656 | 2694731.9221 | 1239451.2623 | 2694727.8111 | 1239459.136
28 | 2694750.3371 | 1239373.3426 | 2694732.6557 | 1239405.7847
29 | 2694732.6557 | 1239405.7847 | 2694735.4219 | 1239407.3522 | 2694742.0112 | 1239411.0934 | 2694744.7146 | 1239406.1662 | 2694747.0209 | 1239407.4329
30 | 2694779.2594 | 1239298.2706 | 2694776.6323 | 1239300.775 | 2694781.8422 | 1239305.6395 | 2694784.1239 | 1239308.1778
31 | 2694779.2594 | 1239298.2706 | 2694773.9652 | 1239293.0044 | 2694765.1444 | 1239284.2275
32 | 2694784.1239 | 1239308.1778 | 2694789.1547 | 1239302.465 | 2694790.6573 | 1239300.2651 | 2694801.9891 | 1239287.9368 | 2694810.6816 | 1239279.1644
33 | 2694746.7645 | 1239265.9391 | 2694765.1444 | 1239284.2275
34 | 2694760.1345 | 1239449.5 | 2694734.4048 | 1239435.5236
35 | 2694775.3815 | 1239423.1349 | 2694760.1345 | 1239449.5
36 | 2694775.3815 | 1239423.1349 | 2694768.6586 | 1239419.4091
37 | 2694775.3815 | 1239423.1349 | 2694782.6254 | 1239427.0868 | 2694794.3842 | 1239408.3717 | 2694796.8145 | 1239408.7107 | 2694808.5878 | 1239414.6586 | 2694814.9567 | 1239422.2438 | 2694817.3022 | 1239426.9403
38 | 2694799.5277 | 1239445.8846 | 2694795.298 | 1239452.975 | 2694787.1229 | 1239469.4345 | 2694786.9065 | 1239470.4101
39 | 2694817.3022 | 1239426.9403 | 2694809.6113 | 1239432.9775 | 2694803.8398 | 1239438.6562 | 2694799.5277 | 1239445.8846
40 | 2694817.3022 | 1239426.9403 | 2694822.8888 | 1239427.63 | 2694830.5691 | 1239423.2049 | 2694846.6341 | 1239405.4645
41 | 2694846.6341 | 1239405.4645 | 2694860.723 | 1239389.9062 | 2694882.83 | 1239364.4772
42 | 2694750.3371 | 1239373.3426 | 2694754.1533 | 1239374.0485 | 2694764.1064 | 1239377.1934
43 | 2694750.136 | 1239409.1438 | 2694747.0209 | 1239407.4329
44 | 2694776.2431 | 1239381.0284 | 2694764.1064 | 1239377.1934
45 | 2694750.136 | 1239409.1438 | 2694768.6586 | 1239419.4091
46 | 2694899.9469 | 1239344.7882 | 2694882.83 | 1239364.4772
47 | 2694899.9469 | 1239344.7882 | 2694893.76 | 1239340.4862
48 | 2694965.2103 | 1239463.3788 | 2694976.5796 | 1239471.5522 | 2694981.2131 | 1239473.6501 | 2694984.5568 | 1239474.1039 | 2694987.5147 | 1239473.1394 | 2694990.09 | 1239470.5564 | 2694990.09 | 1239470.5564
49 | 2694971.1817 | 1239422.218 | 2694974.3749 | 1239412.8564
50 | 2694828.208 | 1239251.4506 | 2694819.7946 | 1239245.4082
51 | 2694828.208 | 1239251.4506 | 2694842.3931 | 1239237.1443 | 2694846.2794 | 1239233.143
52 | 2694819.7946 | 1239245.4082 | 2694812.6898 | 1239240.3056 | 2694807.8212 | 1239237.8655
53 | 2694865.3996 | 1239210.9367 | 2694855.1223 | 1239223.5375 | 2694850.2841 | 1239229.0198 | 2694846.2794 | 1239233.143
54 | 2694746.7645 | 1239265.9391 | 2694783.0548 | 1239228.3014 | 2694786.1315 | 1239225.1148
55 | 2694810.3267 | 1239351.7507 | 2694808.959 | 1239355.0015
56 | 2694810.3267 | 1239351.7507 | 2694794.1843 | 1239344.6544 | 2694787.7055 | 1239343.9394
57 | 2694774.804 | 1239357.4657 | 2694785.1451 | 1239345.1105 | 2694787.7055 | 1239343.9394
58 | 2694893.76 | 1239340.4862 | 2694882.8972 | 1239332.9403 | 2694863.7551 | 1239326.1072
59 | 2694863.7551 | 1239326.1072 | 2694869.3231 | 1239314.1856
60 | 2694863.7551 | 1239326.1072 | 2694858.2566 | 1239342.1424 | 2694853.8644 | 1239350.19
61 | 2694893.76 | 1239340.4862 | 2694899.8736 | 1239333.2896 | 2694901.3189 | 1239329.186
62 | 2694869.3231 | 1239314.1856 | 2694877.6421 | 1239296.3736 | 2694881.9077 | 1239287.7628
63 | 2694853.8644 | 1239350.19 | 2694842.5994 | 1239370.8297
64 | 2694776.2431 | 1239381.0284 | 2694780.7626 | 1239369.3303
65 | 2694804.8525 | 1239394.6842 | 2694793.2905 | 1239387.8167 | 2694778.0719 | 1239381.6136 | 2694776.2431 | 1239381.0284
66 | 2694785.5934 | 1239356.8263 | 2694780.7626 | 1239369.3303
67 | 2694905.4309 | 1239142.4793 | 2694908.5172 | 1239139.56
68 | 2694925.7986 | 1239123.2144 | 2694908.5172 | 1239139.56
69 | 2694905.4309 | 1239142.4793 | 2694900.9205 | 1239146.7454 | 2694893.8645 | 1239153.3994
70 | 2694925.7986 | 1239123.2144 | 2694936.3201 | 1239111.6166
71 | 2694925.7986 | 1239123.2144 | 2694923.1752 | 1239121.7047 | 2694918.6316 | 1239120.1087 | 2694912.5592 | 1239119.5112 | 2694903.1221 | 1239119.7606 | 2694898.7439 | 1239120.7345
72 | 2694925.7986 | 1239123.2144 | 2694941.0957 | 1239134.4785 | 2694946.6073 | 1239138.4473 | 2694949.0085 | 1239140.6095
73 | 2694885.2447 | 1239161.5281 | 2694893.8645 | 1239153.3994
74 | 2694936.3201 | 1239111.6166 | 2694943.9334 | 1239103.2244
75 | 2694898.7439 | 1239120.7345 | 2694883.2093 | 1239124.1901 | 2694875.1071 | 1239124.9895
76 | 2694949.0085 | 1239140.6095 | 2694972.4036 | 1239116.6436 | 2694976.1501 | 1239117.9378 | 2694977.3764 | 1239118.3578 | 2694990.4063 | 1239122.8584 | 2694993.2276 | 1239123.8265
77 | 2694885.2447 | 1239161.5281 | 2694880.0546 | 1239157.3199 | 2694875.7823 | 1239155.0065
78 | 2694902.4224 | 1239175.3351 | 2694885.2447 | 1239161.5281
79 | 2694949.3498 | 1239097.0338 | 2694948.4688 | 1239098.225 | 2694943.9334 | 1239103.2244
80 | 2694853.1888 | 1239126.3343 | 2694862.8434 | 1239126.1996 | 2694875.1071 | 1239124.9895
81 | 2694955.0364 | 1239088.6784 | 2694953.8657 | 1239090.9281 | 2694949.3498 | 1239097.0338
82 | 2694955.0364 | 1239088.6784 | 2694956.2694 | 1239086.3186 | 2694959.8119 | 1239075.5488
83 | 2694993.2276 | 1239123.8265 | 2694987.8982 | 1239139.6617
84 | 2694902.4224 | 1239175.3351 | 2694901.354 | 1239176.3966 | 2694885.3992 | 1239193.4988 | 2694881.5428 | 1239196.688
85 | 2694865.3996 | 1239210.9367 | 2694873.8313 | 1239203.0656 | 2694881.5428 | 1239196.688
86 | 2694875.7823 | 1239155.0065 | 2694865.4753 | 1239149.4255
87 | 2694853.1888 | 1239126.3343 | 2694839.1211 | 1239111.0316 | 2694827.6128 | 1239093.6683 | 2694822.6594 | 1239077.0101
88 | 2694910.0013 | 1239033.0283 | 2694939.772 | 1239042.7447
89 | 2694939.772 | 1239042.7447 | 2694935.939 | 1239057.8168
90 | 2694910.0013 | 1239033.0283 | 2694913.4377 | 1239020.8837
91 | 2694910.0013 | 1239033.0283 | 2694901.2058 | 1239050.0224
92 | 2695017.3759 | 1239243.2238 | 2695027.653 | 1239252.8621
93 | 2695036.9133 | 1239243.8036 | 2695027.653 | 1239252.8621
94 | 2695036.9133 | 1239243.8036 | 2695034.8704 | 1239250.6265
95 | 2694987.8982 | 1239139.6617 | 2694983.7285 | 1239152.0511 | 2694995.6893 | 1239156.8161
96 | 2694960.9084 | 1239186.4117 | 2694941.2988 | 1239206.6435
97 | 2694960.9084 | 1239186.4117 | 2694963.7962 | 1239183.2221 | 2694979.7922 | 1239198.71
98 | 2694987.3726 | 1239206.0495 | 2694979.7922 | 1239198.71
99 | 2694987.3726 | 1239206.0495 | 2694975.1656 | 1239218.6748
100 | 2694975.1656 | 1239218.6748 | 2694971.2259 | 1239222.7486
101 | 2694952.3133 | 1239242.3047 | 2694971.2259 | 1239222.7486
102 | 2694919.413 | 1239168.6834 | 2694912.5724 | 1239175.4419 | 2694897.9631 | 1239190.523
103 | 2694884.4113 | 1239204.5125 | 2694897.9631 | 1239190.523
104 | 2694865.3996 | 1239210.9367 | 2694868.2819 | 1239213.7626 | 2694870.3483 | 1239211.7942 | 2694872.1487 | 1239213.6799 | 2694873.8456 | 1239215.4194
105 | 2694847.5198 | 1239162.4534 | 2694848.7526 | 1239161.0893 | 2694859.059 | 1239150.9353 | 2694865.4753 | 1239149.4255 | 2694865.4753 | 1239149.4255
106 | 2694822.6594 | 1239077.0101 | 2694839.3192 | 1239073.0732 | 2694860.3214 | 1239076.7003 | 2694876.3759 | 1239077.0348 | 2694886.4201 | 1239071.9359 | 2694894.2951 | 1239063.0722
107 | 2694830.6943 | 1239181.0713 | 2694847.5198 | 1239162.4534
108 | 2694830.6943 | 1239181.0713 | 2694839.5797 | 1239188.5861
109 | 2694786.1315 | 1239225.1148 | 2694794.7693 | 1239231.324 | 2694805.2746 | 1239236.5892
110 | 2694805.2746 | 1239236.5892 | 2694807.8212 | 1239237.8655
111 | 2694873.8456 | 1239215.4194 | 2694876.8927 | 1239216.9248 | 2694881.456 | 1239219.1771
112 | 2694873.8456 | 1239215.4194 | 2694884.4113 | 1239204.5125
113 | 2694894.2951 | 1239063.0722 | 2694894.6704 | 1239062.6497 | 2694901.2058 | 1239050.0224
114 | 2694923.8642 | 1239247.9207 | 2694909.3383 | 1239232.9218 | 2694881.456 | 1239219.1771
115 | 2694881.456 | 1239219.1771 | 2694877.2547 | 1239220.3108 | 2694866.6141 | 1239228.6582 | 2694857.8068 | 1239238.0523
116 | 2695034.8704 | 1239250.6265 | 2695032.9173 | 1239257.1495 | 2695025.0345 | 1239272.8567
117 | 2694952.3133 | 1239242.3047 | 2694950.3082 | 1239244.5048
118 | 2694923.8642 | 1239247.9207 | 2694934.2346 | 1239262.1415
119 | 2694923.8642 | 1239247.9207 | 2694909.0947 | 1239261.1476
120 | 2694968.8753 | 1239275.1829 | 2694934.2346 | 1239262.1415
121 | 2694934.2346 | 1239262.1415 | 2694950.3082 | 1239244.5048
122 | 2694909.0947 | 1239261.1476 | 2694887.4237 | 1239280.5552
123 | 2694968.8753 | 1239275.1829 | 2694963.4114 | 1239288.6621
124 | 2694992.1425 | 1239285.1735 | 2694968.8753 | 1239275.1829
125 | 2694887.4237 | 1239280.5552 | 2694883.9268 | 1239283.6868 | 2694881.9077 | 1239287.7628
126 | 2694785.5934 | 1239356.8263 | 2694783.2448 | 1239356.1105 | 2694775.817 | 1239357.5041 | 2694774.804 | 1239357.4657
127 | 2694992.1425 | 1239285.1735 | 2694994.4726 | 1239282.3198 | 2694979.7215 | 1239268.3189
128 | 2695014.1173 | 1239294.6099 | 2694992.1425 | 1239285.1735
129 | 2695014.1173 | 1239294.6099 | 2695040.035 | 1239302.9864
130 | 2695014.1173 | 1239294.6099 | 2695025.0345 | 1239272.8567
131 | 2695014.1173 | 1239294.6099 | 2694998.6395 | 1239304.1249 | 2694995.5524 | 1239307.011 | 2694995.5811 | 1239311.3591 | 2694998.5419 | 1239316.3658 | 2694995.0669 | 1239327.9153
132 | 2694962.3338 | 1239291.3204 | 2694963.4114 | 1239288.6621
133 | 2695034.4144 | 1239319.064 | 2695040.035 | 1239302.9864
134 | 2695040.035 | 1239302.9864 | 2695054.1604 | 1239307.5493
135 | 2694962.3338 | 1239291.3204 | 2694958.3066 | 1239301.2555 | 2694960.327 | 1239303.7151
136 | 2695015.5611 | 1239311.679 | 2695034.4144 | 1239319.064
137 | 2695034.4144 | 1239319.064 | 2695038.2297 | 1239321.2489 | 2695036.2857 | 1239328.8012 | 2695033.2911 | 1239334.9116
138 | 2695071.488 | 1239319.6355 | 2695054.1604 | 1239307.5493 | 2695054.1604 | 1239307.5493
139 | 2695071.488 | 1239319.6355 | 2695080.7047 | 1239326.0642
140 | 2694901.3189 | 1239329.186 | 2694901.4663 | 1239328.7673 | 2694899.4292 | 1239322.7636 | 2694899.7028 | 1239321.3224
141 | 2694911.785 | 1239305.0701 | 2694911.024 | 1239308.1936 | 2694907.0987 | 1239312.8788 | 2694899.9827 | 1239319.848 | 2694899.7028 | 1239321.3224
142 | 2694963.7464 | 1239389.1078 | 2694978.8882 | 1239399.6245
143 | 2694963.7464 | 1239389.1078 | 2694979.1485 | 1239367.0547
144 | 2694978.8882 | 1239399.6245 | 2694974.3749 | 1239412.8564
145 | 2694978.8882 | 1239399.6245 | 2694984.3343 | 1239403.4144 | 2694988.3169 | 1239397.507
146 | 2694978.8882 | 1239399.6245 | 2694984.3343 | 1239403.4144 | 2695008.4083 | 1239420.1453
147 | 2694988.3169 | 1239397.507 | 2695004.9622 | 1239374.9372
148 | 2695008.4083 | 1239420.1453 | 2695029.3751 | 1239392.7373
149 | 2695033.5256 | 1239387.3117 | 2695029.3751 | 1239392.7373
150 | 2695049.8239 | 1239370.4822 | 2695033.5256 | 1239387.3117
151 | 2695049.8239 | 1239370.4822 | 2695047.9347 | 1239369.6411

## bus_geodata
| x | y | coords
0 | 2695182.6159 | 1239441.9432
1 | 2695242.3073 | 1239330.8035
2 | 2695178.9972 | 1239448.4649
3 | 2695157.3543 | 1239258.9436
4 | 2695174.3706 | 1239454.2656
5 | 2695130.6314 | 1239303.0838
6 | 2695170.0909 | 1239459.6313
7 | 2695111.9158 | 1239325.0599
8 | 2695075.6198 | 1239211.6792
9 | 2695063.4713 | 1239202.7759
10 | 2695157.1622 | 1239475.8409
11 | 2695099.7482 | 1239339.3473
12 | 2695048.921 | 1239221.3809
13 | 2694894.5403 | 1239482.7823
14 | 2694934.321 | 1239441.1699
15 | 2694880.6399 | 1239475.9995
16 | 2694837.7958 | 1239511.5305
17 | 2694816.0554 | 1239494.1156
18 | 2694854.8843 | 1239497.3588
19 | 2694765.5394 | 1239531.1804
20 | 2694732.9205 | 1239508.1205
21 | 2694792.5961 | 1239499.0756
22 | 2694714.3269 | 1239484.9623
23 | 2694951.6324 | 1239453.6177
24 | 2694707.1764 | 1239439.1364
25 | 2694732.6557 | 1239405.7847
26 | 2694727.8111 | 1239459.136
27 | 2694779.2594 | 1239298.2706
28 | 2694784.1239 | 1239308.1778
29 | 2694765.1444 | 1239284.2275
30 | 2694760.1345 | 1239449.5
31 | 2694734.4048 | 1239435.5236
32 | 2694775.3815 | 1239423.1349
33 | 2694810.6816 | 1239279.1644
34 | 2694786.9065 | 1239470.4101
35 | 2694799.5277 | 1239445.8845
36 | 2694817.3022 | 1239426.9403
37 | 2694846.6341 | 1239405.4645
38 | 2694750.3371 | 1239373.3426
39 | 2694747.0209 | 1239407.4329
40 | 2694764.1064 | 1239377.1934
41 | 2694768.6586 | 1239419.4091
42 | 2694882.83 | 1239364.4772
43 | 2694750.136 | 1239409.1438
44 | 2694899.9469 | 1239344.7882
45 | 2694965.2103 | 1239463.3788
46 | 2694971.1817 | 1239422.218
47 | 2694828.208 | 1239251.4506
48 | 2694819.7946 | 1239245.4082
49 | 2694846.2794 | 1239233.143
50 | 2694746.7645 | 1239265.9391
51 | 2694810.3267 | 1239351.7507
52 | 2694808.959 | 1239355.0015
53 | 2694787.7055 | 1239343.9394
54 | 2694863.7551 | 1239326.1072
55 | 2694893.76 | 1239340.4862
56 | 2694869.3231 | 1239314.1856
57 | 2694853.8644 | 1239350.19
58 | 2694776.2431 | 1239381.0284
59 | 2694780.7626 | 1239369.3303
60 | 2694804.8525 | 1239394.6842
61 | 2694908.5172 | 1239139.56
62 | 2694905.4309 | 1239142.4793
63 | 2694925.7986 | 1239123.2144
64 | 2694893.8645 | 1239153.3994
65 | 2694936.3201 | 1239111.6166
66 | 2694898.7439 | 1239120.7345
67 | 2694949.0085 | 1239140.6095
68 | 2694885.2447 | 1239161.5281
69 | 2694943.9334 | 1239103.2244
70 | 2694875.1071 | 1239124.9895
71 | 2694955.0364 | 1239088.6784
72 | 2694949.3498 | 1239097.0338
73 | 2694959.8119 | 1239075.5488
74 | 2694993.2276 | 1239123.8265
75 | 2694902.4224 | 1239175.3351
76 | 2694881.5428 | 1239196.688
77 | 2694875.7823 | 1239155.0065
78 | 2694853.1888 | 1239126.3343
79 | 2694939.772 | 1239042.7447
80 | 2694910.0013 | 1239033.0283
81 | 2694935.939 | 1239057.8168
82 | 2695027.653 | 1239252.8621
83 | 2695017.3759 | 1239243.2238
84 | 2695036.9133 | 1239243.8036
85 | 2694987.8982 | 1239139.6617
86 | 2694960.9084 | 1239186.4117
87 | 2694941.2988 | 1239206.6435
88 | 2694979.7922 | 1239198.71
89 | 2694987.3726 | 1239206.0495
90 | 2694975.1656 | 1239218.6748
91 | 2694971.2259 | 1239222.7486
92 | 2694919.413 | 1239168.6834
93 | 2694897.9631 | 1239190.523
94 | 2694865.3996 | 1239210.9367
95 | 2694865.4753 | 1239149.4255
96 | 2694822.6594 | 1239077.0101
97 | 2694847.5198 | 1239162.4534
98 | 2694830.6943 | 1239181.0713
99 | 2694839.5797 | 1239188.5861
100 | 2694786.1315 | 1239225.1148
101 | 2694805.2746 | 1239236.5892
102 | 2694873.8456 | 1239215.4194
103 | 2694807.8212 | 1239237.8655
104 | 2694894.2951 | 1239063.0722
105 | 2694881.456 | 1239219.1771
106 | 2694884.4113 | 1239204.5125
107 | 2694995.6893 | 1239156.8161
108 | 2695034.8704 | 1239250.6265
109 | 2694952.3133 | 1239242.3047
110 | 2694923.8642 | 1239247.9207
111 | 2694857.8068 | 1239238.0523
112 | 2694934.2346 | 1239262.1415
113 | 2694909.0947 | 1239261.1476
114 | 2694968.8753 | 1239275.1829
115 | 2694950.3082 | 1239244.5048
116 | 2694887.4237 | 1239280.5552
117 | 2694913.4377 | 1239020.8837
118 | 2694901.2058 | 1239050.0224
119 | 2694785.5934 | 1239356.8263
120 | 2694774.804 | 1239357.4657
121 | 2694979.7215 | 1239268.3189
122 | 2694992.1425 | 1239285.1735
123 | 2695014.1173 | 1239294.6099
124 | 2694963.4114 | 1239288.6621
125 | 2695040.035 | 1239302.9864
126 | 2695025.0345 | 1239272.8567
127 | 2694995.0669 | 1239327.9153
128 | 2694962.3338 | 1239291.3204
129 | 2695034.4144 | 1239319.064
130 | 2695054.1604 | 1239307.5493
131 | 2694960.327 | 1239303.7151
132 | 2695015.5611 | 1239311.679
133 | 2695033.2911 | 1239334.9116
134 | 2695071.488 | 1239319.6355
135 | 2694842.5994 | 1239370.8297
136 | 2694901.3189 | 1239329.186
137 | 2694881.9077 | 1239287.7628
138 | 2694899.7028 | 1239321.3224
139 | 2694963.7464 | 1239389.1078
140 | 2694978.8882 | 1239399.6245
141 | 2694979.1485 | 1239367.0547
142 | 2694911.785 | 1239305.0701
143 | 2694974.3749 | 1239412.8564
144 | 2694988.3169 | 1239397.507
145 | 2695008.4083 | 1239420.1453
146 | 2695004.9622 | 1239374.9372
147 | 2695029.3751 | 1239392.7373
148 | 2695080.7047 | 1239326.0642
149 | 2695049.8239 | 1239370.4822
150 | 2695033.5256 | 1239387.3117
151 | 2695047.9347 | 1239369.6411
152 | 2694990.09 | 1239470.5564
153 | 2694923.8642 | 1239247.9207

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98779 | -0.23508 | 0.00055895 | 0.00014009
1 | 0.9881 | -0.22909 | 0 | 0
2 | 0.98778 | -0.23536 | 0 | 0
3 | 0.98838 | -0.22359 | 0 | 0
4 | 0.98776 | -0.23563 | 0.00030495 | 7.6429e-05
5 | 0.98851 | -0.22113 | 0.0022293 | 0.00055872
6 | 0.98775 | -0.23585 | 0.0013894 | 0.00034821
7 | 0.98864 | -0.21861 | 0.0016613 | 0.00041637
8 | 0.98824 | -0.22625 | 0.0042938 | 0.0010761
9 | 0.9883 | -0.22509 | 0 | 0
10 | 0.98774 | -0.236 | 0.00039841 | 9.9851e-05
11 | 0.98875 | -0.21642 | 0 | 0
12 | 0.98839 | -0.22328 | 0.0067652 | 0.0016955
13 | 0.97528 | -0.4765 | 0 | 0
14 | 0.97351 | -0.51134 | 0.0026339 | 0.00066011
15 | 0.9757 | -0.46817 | 0 | 0
16 | 0.97736 | -0.43566 | 0 | 0
17 | 0.97829 | -0.4175 | 0.0016167 | 0.00040519
18 | 0.97662 | -0.45016 | 0.0063433 | 0.0015898
19 | 0.9814 | -0.35674 | 0 | 0
20 | 0.98332 | -0.31956 | 0 | 0
21 | 0.97958 | -0.39232 | 0.007744 | 0.0019408
22 | 0.98497 | -0.28771 | 0 | 0
23 | 0.97297 | -0.52184 | 0 | 0
24 | 0.9873 | -0.24279 | 0 | 0
25 | 0.98838 | -0.22188 | 0 | 0
26 | 0.98619 | -0.26412 | 0.020225 | 0.0050688
27 | 0.98646 | -0.2601 | 0 | 0
28 | 0.98616 | -0.26601 | 0 | 0
29 | 0.98689 | -0.25179 | 0.0050238 | 0.0012591
30 | 0.98947 | -0.20101 | 0 | 0
31 | 0.98925 | -0.20524 | 0.0081294 | 0.0020374
32 | 0.9897 | -0.1966 | 0 | 0
33 | 0.98531 | -0.28246 | 0.023294 | 0.0058381
34 | 0.99132 | -0.16547 | 0.001728 | 0.00043308
35 | 0.99136 | -0.16462 | 0.0015744 | 0.00039459
36 | 0.99144 | -0.16308 | 0 | 0
37 | 0.99258 | -0.1413 | 0.0045991 | 0.0011526
38 | 0.98783 | -0.23258 | 0 | 0
39 | 0.98886 | -0.21266 | 0.001485 | 0.00037218
40 | 0.98762 | -0.23674 | 0.00092052 | 0.0002307
41 | 0.9895 | -0.20046 | 0.0014789 | 0.00037064
42 | 0.99427 | -0.10891 | 0.0073935 | 0.001853
43 | 0.98895 | -0.2109 | 0 | 0
44 | 0.99514 | -0.092358 | 0 | 0
45 | 0.97291 | -0.52312 | 0.0026328 | 0.00065984
46 | 0.97219 | -0.53728 | 0.0026314 | 0.0006595
47 | 0.99076 | -0.17675 | 0 | 0
48 | 0.9903 | -0.18566 | 0.0039705 | 0.00099511
49 | 0.9919 | -0.15467 | 0.0036967 | 0.00092648
50 | 0.98756 | -0.23866 | 0 | 0
51 | 0.9868 | -0.25269 | 0 | 0
52 | 0.98678 | -0.25307 | 0.0060039 | 0.0015047
53 | 0.98693 | -0.2501 | 0.0036191 | 0.00090702
54 | 0.9966 | -0.064672 | 0 | 0
55 | 0.99539 | -0.087593 | 0 | 0
56 | 0.99711 | -0.0548 | 0.0032103 | 0.00080457
57 | 0.99632 | -0.069903 | 0.0068309 | 0.001712
58 | 0.98744 | -0.24022 | 0 | 0
59 | 0.98732 | -0.24264 | 0.0011715 | 0.00029359
60 | 0.98731 | -0.24278 | 0.0045148 | 0.0011315
61 | 0.98328 | -0.32131 | 0.0060301 | 0.0015113
62 | 0.98358 | -0.31544 | 0.003866 | 0.00096891
63 | 0.98172 | -0.35164 | 0 | 0
64 | 0.98476 | -0.29239 | 0.0032765 | 0.00082118
65 | 0.98134 | -0.35909 | 0.010187 | 0.0025531
66 | 0.98117 | -0.36255 | 0.0048365 | 0.0012121
67 | 0.98111 | -0.36356 | 0 | 0
68 | 0.98568 | -0.27456 | 0 | 0
69 | 0.98117 | -0.36239 | 0.010209 | 0.0025586
70 | 0.98079 | -0.36986 | 0.0056462 | 0.0014151
71 | 0.9811 | -0.36382 | 0 | 0
72 | 0.98113 | -0.36327 | 0.0029428 | 0.00073754
73 | 0.98106 | -0.36457 | 0.0029574 | 0.00074118
74 | 0.97995 | -0.3864 | 0 | 0
75 | 0.9879 | -0.23154 | 0 | 0
76 | 0.99092 | -0.17337 | 0.010614 | 0.0026602
77 | 0.98541 | -0.27984 | 0.0028788 | 0.0007215
78 | 0.98057 | -0.3743 | 0 | 0
79 | 0.97885 | -0.40794 | 0 | 0
80 | 0.97892 | -0.40649 | 0 | 0
81 | 0.97881 | -0.40866 | 0.0025391 | 0.00063637
82 | 0.98857 | -0.21978 | 0 | 0
83 | 0.98849 | -0.22148 | 0.0067661 | 0.0016958
84 | 0.98865 | -0.21822 | 0 | 0
85 | 0.9796 | -0.39328 | 0.012075 | 0.0030262
86 | 0.99163 | -0.16065 | 0 | 0
87 | 0.99121 | -0.16888 | 0.016462 | 0.0041258
88 | 0.99203 | -0.1529 | 0.031146 | 0.0078059
89 | 0.99249 | -0.14401 | 0 | 0
90 | 0.99326 | -0.12925 | 0 | 0
91 | 0.9935 | -0.12448 | 0.0084801 | 0.0021253
92 | 0.99378 | -0.11872 | 0.0045946 | 0.0011515
93 | 0.9939 | -0.11624 | 0.0039544 | 0.00099107
94 | 0.9933 | -0.12764 | 0 | 0
95 | 0.98517 | -0.28459 | 0.0024804 | 0.00062164
96 | 0.97996 | -0.38621 | 0 | 0
97 | 0.98474 | -0.29286 | 0.013644 | 0.0034195
98 | 0.98459 | -0.29578 | 0 | 0
99 | 0.98452 | -0.29713 | 0.0064641 | 0.00162
100 | 0.98904 | -0.21 | 0 | 0
101 | 0.98962 | -0.1987 | 0.007812 | 0.0019579
102 | 0.99425 | -0.10956 | 0 | 0
103 | 0.98972 | -0.19687 | 0.0082969 | 0.0020794
104 | 0.97916 | -0.40192 | 0.0018995 | 0.00047606
105 | 0.99473 | -0.10031 | 0 | 0
106 | 0.99406 | -0.1133 | 0.0053937 | 0.0013518
107 | 0.97934 | -0.39829 | 0.010617 | 0.0026609
108 | 0.98877 | -0.21595 | 0.0053938 | 0.0013518
109 | 0.9949 | -0.097573 | 0 | 0
110 | 0.99781 | -0.041678 | 0 | 0
111 | 0.99453 | -0.10423 | 0.007219 | 0.0018092
112 | 0.99646 | -0.067549 | 0.0044094 | 0.0011051
113 | 1 | 0 | -0.5152 | -0.13095
114 | 0.99311 | -0.13185 | 0 | 0
115 | 0.99505 | -0.094634 | 0.0084768 | 0.0021245
116 | 0.99869 | -0.024836 | 0.0076495 | 0.0019172
117 | 0.97888 | -0.40729 | 0.0034798 | 0.00087212
118 | 0.97903 | -0.4044 | 0.0032167 | 0.00080618
119 | 0.9872 | -0.24495 | 0 | 0
120 | 0.9871 | -0.24684 | 0 | 0
121 | 0.99043 | -0.18379 | 0.031507 | 0.0078964
122 | 0.99112 | -0.17035 | 0 | 0
123 | 0.98993 | -0.19347 | 0 | 0
124 | 0.99294 | -0.13515 | 0.0045476 | 0.0011397
125 | 0.98939 | -0.20392 | 0 | 0
126 | 0.98929 | -0.20586 | 0.0053942 | 0.0013519
127 | 0.98975 | -0.19691 | 0.0043312 | 0.0010855
128 | 0.99292 | -0.13557 | 0.0059396 | 0.0014886
129 | 0.98931 | -0.20541 | 0 | 0
130 | 0.98916 | -0.20832 | 0.0066916 | 0.0016771
131 | 0.99289 | -0.13614 | 0.002333 | 0.0005847
132 | 0.98928 | -0.206 | 0.0016341 | 0.00040955
133 | 0.98926 | -0.20653 | 0.003302 | 0.00082757
134 | 0.98897 | -0.21208 | 0.001867 | 0.00046791
135 | 0.99623 | -0.071792 | 0.0045759 | 0.0011468
136 | 0.99528 | -0.089753 | 0.0027395 | 0.00068659
137 | 0.9983 | -0.032328 | 0.0075547 | 0.0018934
138 | 0.99523 | -0.090648 | 0.0044895 | 0.0011252
139 | 0.97171 | -0.54688 | 0 | 0
140 | 0.97178 | -0.54542 | 0 | 0
141 | 0.9716 | -0.549 | 0.0042794 | 0.0010725
142 | 0.9952 | -0.091259 | 0.0016704 | 0.00041863
143 | 0.97201 | -0.54094 | 0.0026314 | 0.00065949
144 | 0.97172 | -0.54663 | 0 | 0
145 | 0.9715 | -0.55096 | 0 | 0
146 | 0.97159 | -0.5491 | 0.0047597 | 0.0011929
147 | 0.97123 | -0.55628 | 0.0065097 | 0.0016315
148 | 0.98889 | -0.2137 | 0.0015558 | 0.00038992
149 | 0.97118 | -0.5573 | 0 | 0
150 | 0.97122 | -0.55651 | 0 | 0
151 | 0.97118 | -0.55737 | 0.001832 | 0.00045915
152 | 0.97287 | -0.52393 | 0.0015008 | 0.00037614
153 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0026518 | -0.00066408 | 0.0026525 | 0.00066294 | 7.5517e-07 | -1.1331e-06 | 0.0039944 | 0.0039939 | 0.0039944 | 0.98779 | -0.23508 | 0.9881 | -0.22909 | 1.0974
1 | 0.0020928 | 0.00052399 | -0.0020928 | -0.00052407 | 2.7795e-08 | -7.7683e-08 | 0.0031524 | 0.0031525 | 0.0031525 | 0.98779 | -0.23508 | 0.98778 | -0.23536 | 0.86606
2 | -0.0026525 | -0.00066294 | 0.0026532 | 0.0006619 | 6.9337e-07 | -1.0416e-06 | 0.0039939 | 0.0039933 | 0.0039939 | 0.9881 | -0.22909 | 0.98838 | -0.22359 | 1.0972
3 | 0.0020928 | 0.00052407 | -0.0020927 | -0.00052415 | 2.7652e-08 | -7.728e-08 | 0.0031525 | 0.0031525 | 0.0031525 | 0.98778 | -0.23536 | 0.98776 | -0.23563 | 0.86607
4 | -0.0026532 | -0.0006619 | 0.0026535 | 0.00066144 | 3.0997e-07 | -4.6606e-07 | 0.0039933 | 0.0039931 | 0.0039933 | 0.98838 | -0.22359 | 0.98851 | -0.22113 | 1.0971
5 | 0.0017878 | 0.00044772 | -0.0017878 | -0.00044779 | 1.8667e-08 | -7.5904e-08 | 0.0026931 | 0.0026931 | 0.0026931 | 0.98776 | -0.23563 | 0.98775 | -0.23585 | 0.73987
6 | -0.0048828 | -0.0012202 | 0.0048834 | 0.0012202 | 5.846e-07 | 4.0512e-09 | 0.007349 | 0.0073488 | 0.007349 | 0.98851 | -0.22113 | 0.98864 | -0.21861 | 2.0189
7 | 0.00039841 | 9.9587e-05 | -0.00039841 | -9.9851e-05 | 2.8005e-09 | -2.636e-07 | 0.0006001 | 0.0006002 | 0.0006002 | 0.98775 | -0.23585 | 0.98774 | -0.236 | 0.16489
8 | -0.0065448 | -0.0016365 | 0.0065454 | 0.0016367 | 6.8269e-07 | 1.9626e-07 | 0.0098493 | 0.0098493 | 0.0098493 | 0.98864 | -0.21861 | 0.98875 | -0.21642 | 2.7059
9 | -0.0042938 | -0.0010761 | 0.004294 | 0.0010761 | 2.3609e-07 | -4.1895e-08 | 0.0064652 | 0.0064652 | 0.0064652 | 0.98824 | -0.22625 | 0.9883 | -0.22509 | 1.7762
10 | -0.004294 | -0.0010761 | 0.0042944 | 0.001076 | 3.7035e-07 | -6.5777e-08 | 0.0064652 | 0.0064651 | 0.0064652 | 0.9883 | -0.22509 | 0.98839 | -0.22328 | 1.7761
11 | -0.0065454 | -0.0016367 | 0.0065463 | 0.001637 | 8.4463e-07 | 2.4273e-07 | 0.0098493 | 0.0098491 | 0.0098493 | 0.98875 | -0.21642 | 0.98889 | -0.2137 | 2.7058
12 | -0.01106 | -0.0027715 | 0.011062 | 0.0027729 | 2.6692e-06 | 1.3791e-06 | 0.01665 | 0.01665 | 0.01665 | 0.98839 | -0.22328 | 0.98865 | -0.21822 | 4.5742
13 | 0.029504 | 0.0074257 | -0.029455 | -0.0073951 | 4.9038e-05 | 3.0581e-05 | 0.045027 | 0.045027 | 0.045027 | 0.97528 | -0.4765 | 0.97351 | -0.51134 | 12.37
14 | -0.029504 | -0.0074257 | 0.029516 | 0.007433 | 1.1749e-05 | 7.3266e-06 | 0.045027 | 0.045026 | 0.045027 | 0.97528 | -0.4765 | 0.9757 | -0.46817 | 12.3699
15 | 0.026821 | 0.006735 | -0.026808 | -0.0067267 | 1.3442e-05 | 8.3376e-06 | 0.041001 | 0.041001 | 0.041001 | 0.97351 | -0.51134 | 0.97297 | -0.52184 | 11.264
16 | -0.029516 | -0.007433 | 0.029541 | 0.0074489 | 2.5438e-05 | 1.5862e-05 | 0.045026 | 0.045026 | 0.045026 | 0.9757 | -0.46817 | 0.97662 | -0.45016 | 12.3699
17 | -0.035909 | -0.0090543 | 0.03594 | 0.009074 | 3.1244e-05 | 1.9647e-05 | 0.054691 | 0.054691 | 0.054691 | 0.97736 | -0.43566 | 0.97829 | -0.4175 | 15.025
18 | 0.035909 | 0.0090543 | -0.035884 | -0.0090387 | 2.4901e-05 | 1.5659e-05 | 0.054691 | 0.054691 | 0.054691 | 0.97736 | -0.43566 | 0.97662 | -0.45016 | 15.025
19 | -0.037557 | -0.0094792 | 0.037603 | 0.0095077 | 4.5346e-05 | 2.8556e-05 | 0.05715 | 0.05715 | 0.05715 | 0.97829 | -0.4175 | 0.97958 | -0.39232 | 15.7006
20 | -0.045424 | -0.011498 | 0.045505 | 0.011549 | 8.1216e-05 | 5.1401e-05 | 0.068913 | 0.068913 | 0.068913 | 0.9814 | -0.35674 | 0.98332 | -0.31956 | 18.9322
21 | 0.045424 | 0.011498 | -0.045347 | -0.011449 | 7.7447e-05 | 4.9018e-05 | 0.068913 | 0.068913 | 0.068913 | 0.9814 | -0.35674 | 0.97958 | -0.39232 | 18.9323
22 | -0.045505 | -0.011549 | 0.045575 | 0.011593 | 6.9828e-05 | 4.4192e-05 | 0.068913 | 0.068913 | 0.068913 | 0.98332 | -0.31956 | 0.98497 | -0.28771 | 18.9321
23 | -0.045575 | -0.011593 | 0.045627 | 0.011626 | 5.1885e-05 | 3.2835e-05 | 0.068913 | 0.068913 | 0.068913 | 0.98497 | -0.28771 | 0.98619 | -0.26412 | 18.9321
24 | 0.0041339 | 0.0010356 | -0.0041337 | -0.0010357 | 2.5064e-07 | -4.7264e-08 | 0.0063221 | 0.0063221 | 0.0063221 | 0.97297 | -0.52184 | 0.97291 | -0.52312 | 1.7368
25 | 0.022674 | 0.0056911 | -0.022657 | -0.0056808 | 1.6683e-05 | 1.0218e-05 | 0.034679 | 0.034679 | 0.034679 | 0.97297 | -0.52184 | 0.97219 | -0.53728 | 9.5272
26 | -0.065919 | -0.016737 | 0.065986 | 0.016778 | 6.6396e-05 | 4.043e-05 | 0.099428 | 0.099428 | 0.099428 | 0.9873 | -0.24279 | 0.98838 | -0.22188 | 9.1052
27 | 0.065919 | 0.016737 | -0.065852 | -0.016695 | 6.7581e-05 | 4.232e-05 | 0.099428 | 0.099429 | 0.099429 | 0.9873 | -0.24279 | 0.98619 | -0.26412 | 13.6578
28 | 0.01625 | 0.0040781 | -0.016242 | -0.0040733 | 8.2894e-06 | 4.8322e-06 | 0.024466 | 0.024466 | 0.024466 | 0.98838 | -0.22188 | 0.98783 | -0.23258 | 6.7215
29 | -0.082236 | -0.020856 | 0.082272 | 0.020878 | 3.6471e-05 | 2.261e-05 | 0.12389 | 0.12389 | 0.12389 | 0.98838 | -0.22188 | 0.98886 | -0.21266 | 11.3456
30 | 0.023319 | 0.0058534 | -0.023313 | -0.0058493 | 6.5763e-06 | 4.028e-06 | 0.035179 | 0.035179 | 0.035179 | 0.98646 | -0.2601 | 0.98616 | -0.26601 | 9.6646
31 | -0.023319 | -0.0058534 | 0.023329 | 0.005859 | 9.2403e-06 | 5.6595e-06 | 0.035179 | 0.035179 | 0.035179 | 0.98646 | -0.2601 | 0.98689 | -0.25179 | 9.6645
32 | 0.023313 | 0.0058493 | -0.023294 | -0.0058381 | 1.8272e-05 | 1.1192e-05 | 0.035179 | 0.035179 | 0.035179 | 0.98616 | -0.26601 | 0.98531 | -0.28246 | 9.6646
33 | -0.028352 | -0.0071181 | 0.02837 | 0.0071291 | 1.7773e-05 | 1.1043e-05 | 0.042754 | 0.042754 | 0.042754 | 0.98689 | -0.25179 | 0.98756 | -0.23866 | 11.7455
34 | 0.008131 | 0.0020381 | -0.0081294 | -0.0020374 | 1.6418e-06 | 6.7475e-07 | 0.012228 | 0.012228 | 0.012228 | 0.98947 | -0.20101 | 0.98925 | -0.20524 | 3.3594
35 | -0.008131 | -0.0020381 | 0.0081327 | 0.0020388 | 1.7067e-06 | 7.0122e-07 | 0.012228 | 0.012228 | 0.012228 | 0.98947 | -0.20101 | 0.9897 | -0.1966 | 3.3593
36 | 0.085301 | 0.021662 | -0.085285 | -0.021652 | 1.5828e-05 | 9.8337e-06 | 0.12835 | 0.12835 | 0.12835 | 0.9897 | -0.1966 | 0.9895 | -0.20046 | 11.7538
37 | -0.093434 | -0.0237 | 0.093585 | 0.023795 | 0.00015085 | 9.4187e-05 | 0.14058 | 0.14058 | 0.14058 | 0.9897 | -0.1966 | 0.99144 | -0.16308 | 12.8736
38 | -0.001728 | -0.00043308 | 0.0017281 | 0.00043277 | 6.9715e-08 | -3.1166e-07 | 0.0025938 | 0.0025937 | 0.0025938 | 0.99132 | -0.16547 | 0.99136 | -0.16462 | 0.71259
39 | -0.0033025 | -0.00082736 | 0.0033027 | 0.00082717 | 2.4224e-07 | -1.8398e-07 | 0.0049569 | 0.0049568 | 0.0049569 | 0.99136 | -0.16462 | 0.99144 | -0.16308 | 1.3618
40 | -0.096887 | -0.024622 | 0.096989 | 0.024685 | 0.00010174 | 6.3622e-05 | 0.14554 | 0.14553 | 0.14554 | 0.99144 | -0.16308 | 0.99258 | -0.1413 | 13.3274
41 | -0.10159 | -0.025838 | 0.10175 | 0.025937 | 0.00015882 | 9.9522e-05 | 0.15243 | 0.15243 | 0.15243 | 0.99258 | -0.1413 | 0.99427 | -0.10891 | 13.9587
42 | 0.016242 | 0.0040733 | -0.016238 | -0.0040714 | 3.2143e-06 | 1.8739e-06 | 0.024466 | 0.024466 | 0.024466 | 0.98783 | -0.23258 | 0.98762 | -0.23674 | 6.7216
43 | -0.083757 | -0.021251 | 0.083764 | 0.021255 | 7.0674e-06 | 4.3863e-06 | 0.12613 | 0.12613 | 0.12613 | 0.98886 | -0.21266 | 0.98895 | -0.2109 | 11.5502
44 | 0.015318 | 0.0038407 | -0.015315 | -0.0038393 | 2.5425e-06 | 1.4643e-06 | 0.02308 | 0.02308 | 0.02308 | 0.98762 | -0.23674 | 0.98744 | -0.24022 | 6.3406
45 | 0.083806 | 0.021281 | -0.083764 | -0.021255 | 4.2111e-05 | 2.6135e-05 | 0.12613 | 0.12613 | 0.12613 | 0.9895 | -0.20046 | 0.98895 | -0.2109 | 11.5502
46 | -0.10914 | -0.02779 | 0.10923 | 0.027845 | 8.717e-05 | 5.4773e-05 | 0.16349 | 0.16349 | 0.16349 | 0.99427 | -0.10891 | 0.99514 | -0.092358 | 14.9719
47 | -0.10923 | -0.027845 | 0.10925 | 0.027861 | 2.513e-05 | 1.579e-05 | 0.16349 | 0.16349 | 0.16349 | 0.99514 | -0.092358 | 0.99539 | -0.087593 | 14.9719
48 | 0.0015009 | 0.00037581 | -0.0015008 | -0.00037614 | 5.774e-08 | -3.2591e-07 | 0.0022954 | 0.0022955 | 0.0022955 | 0.97291 | -0.52312 | 0.97287 | -0.52393 | 0.63064
49 | 0.020025 | 0.0050213 | -0.020022 | -0.0050192 | 3.4849e-06 | 2.1077e-06 | 0.030651 | 0.030652 | 0.030652 | 0.97219 | -0.53728 | 0.97201 | -0.54094 | 8.4207
50 | 0.048551 | 0.012225 | -0.048531 | -0.012212 | 2.0666e-05 | 1.3093e-05 | 0.07294 | 0.07294 | 0.07294 | 0.99076 | -0.17675 | 0.9903 | -0.18566 | 20.0384
51 | -0.048551 | -0.012225 | 0.048603 | 0.012258 | 5.1322e-05 | 3.2515e-05 | 0.07294 | 0.072939 | 0.07294 | 0.99076 | -0.17675 | 0.9919 | -0.15467 | 20.0383
52 | 0.04456 | 0.011217 | -0.044536 | -0.011202 | 2.3873e-05 | 1.5097e-05 | 0.066974 | 0.066974 | 0.066974 | 0.9903 | -0.18566 | 0.98972 | -0.19687 | 18.3993
53 | -0.052299 | -0.013184 | 0.052367 | 0.013227 | 6.7729e-05 | 4.2967e-05 | 0.078485 | 0.078485 | 0.078485 | 0.9919 | -0.15467 | 0.9933 | -0.12764 | 21.5618
54 | -0.02837 | -0.0071291 | 0.028409 | 0.0071533 | 3.8874e-05 | 2.4153e-05 | 0.042754 | 0.042753 | 0.042754 | 0.98756 | -0.23866 | 0.98904 | -0.21 | 11.7455
55 | 0.006004 | 0.0015047 | -0.0060039 | -0.0015047 | 1.0841e-07 | 2.4325e-08 | 0.0090536 | 0.0090536 | 0.0090536 | 0.9868 | -0.25269 | 0.98678 | -0.25307 | 2.4873
56 | -0.006004 | -0.0015047 | 0.0060048 | 0.0015049 | 7.4235e-07 | 1.6652e-07 | 0.0090536 | 0.0090535 | 0.0090536 | 0.9868 | -0.25269 | 0.98693 | -0.2501 | 2.4872
57 | -0.0096238 | -0.0024119 | 0.0096253 | 0.0024126 | 1.4943e-06 | 7.1447e-07 | 0.01451 | 0.01451 | 0.01451 | 0.98693 | -0.2501 | 0.9871 | -0.24684 | 3.9863
58 | 0.11828 | 0.030174 | -0.11815 | -0.030092 | 0.00013078 | 8.2394e-05 | 0.1768 | 0.1768 | 0.1768 | 0.9966 | -0.064672 | 0.99539 | -0.087593 | 16.1903
59 | -0.12969 | -0.033034 | 0.12976 | 0.033073 | 6.1795e-05 | 3.9034e-05 | 0.19383 | 0.19383 | 0.19383 | 0.9966 | -0.064672 | 0.99711 | -0.0548 | 17.7504
60 | 0.01141 | 0.0028603 | -0.011407 | -0.0028588 | 2.843e-06 | 1.4792e-06 | 0.017037 | 0.017037 | 0.017037 | 0.9966 | -0.064672 | 0.99632 | -0.069903 | 4.6804
61 | 0.0089006 | 0.0022306 | -0.0088997 | -0.0022302 | 9.1574e-07 | 4.0679e-07 | 0.013305 | 0.013306 | 0.013306 | 0.99539 | -0.087593 | 0.99528 | -0.089753 | 3.6554
62 | -0.13297 | -0.033878 | 0.13311 | 0.033969 | 0.00014434 | 9.1228e-05 | 0.19863 | 0.19862 | 0.19863 | 0.99711 | -0.0548 | 0.9983 | -0.032328 | 18.1891
63 | 0.0045763 | 0.0011468 | -0.0045759 | -0.0011468 | 4.1191e-07 | -4.2567e-08 | 0.0068347 | 0.0068348 | 0.0068348 | 0.99632 | -0.069903 | 0.99623 | -0.071792 | 1.8777
64 | 0.0108 | 0.0027078 | -0.010799 | -0.0027072 | 1.2457e-06 | 6.3685e-07 | 0.016275 | 0.016275 | 0.016275 | 0.98744 | -0.24022 | 0.98732 | -0.24264 | 4.4712
65 | 0.0045154 | 0.0011315 | -0.0045148 | -0.0011315 | 5.5083e-07 | -5.3235e-08 | 0.0068044 | 0.0068045 | 0.0068045 | 0.98744 | -0.24022 | 0.98731 | -0.24278 | 1.8694
66 | 0.0096272 | 0.0024136 | -0.0096262 | -0.0024131 | 1.0583e-06 | 5.0591e-07 | 0.01451 | 0.01451 | 0.01451 | 0.98732 | -0.24264 | 0.9872 | -0.24495 | 3.9862
67 | -0.076834 | -0.019327 | 0.076856 | 0.019341 | 2.1548e-05 | 1.3737e-05 | 0.1163 | 0.1163 | 0.1163 | 0.98328 | -0.32131 | 0.98358 | -0.31544 | 31.9507
68 | 0.070804 | 0.017816 | -0.070702 | -0.017751 | 0.00010246 | 6.5274e-05 | 0.10718 | 0.10718 | 0.10718 | 0.98328 | -0.32131 | 0.98172 | -0.35164 | 29.4438
69 | -0.080722 | -0.02031 | 0.080811 | 0.020367 | 8.9002e-05 | 5.6759e-05 | 0.12215 | 0.12215 | 0.12215 | 0.98358 | -0.31544 | 0.98476 | -0.29239 | 33.5575
70 | 0.026308 | 0.0065975 | -0.026299 | -0.0065918 | 9.3381e-06 | 5.7785e-06 | 0.039877 | 0.039878 | 0.039878 | 0.98172 | -0.35164 | 0.98134 | -0.35909 | 10.9554
71 | 0.021654 | 0.0054373 | -0.021643 | -0.0054305 | 1.1261e-05 | 6.8549e-06 | 0.032825 | 0.032825 | 0.032825 | 0.98172 | -0.35164 | 0.98117 | -0.36255 | 9.0179
72 | 0.022739 | 0.005716 | -0.022727 | -0.0057081 | 1.2932e-05 | 7.91e-06 | 0.034473 | 0.034473 | 0.034473 | 0.98172 | -0.35164 | 0.98111 | -0.36356 | 9.4706
73 | -0.084088 | -0.021188 | 0.084159 | 0.021234 | 7.1775e-05 | 4.5785e-05 | 0.1271 | 0.1271 | 0.1271 | 0.98476 | -0.29239 | 0.98568 | -0.27456 | 34.9176
74 | 0.016112 | 0.0040387 | -0.01611 | -0.0040372 | 2.5362e-06 | 1.4801e-06 | 0.024431 | 0.024431 | 0.024431 | 0.98134 | -0.35909 | 0.98117 | -0.36239 | 6.7119
75 | 0.016806 | 0.0042183 | -0.0168 | -0.0042149 | 5.8615e-06 | 3.4476e-06 | 0.02549 | 0.02549 | 0.02549 | 0.98117 | -0.36255 | 0.98079 | -0.36986 | 7.0029
76 | 0.022727 | 0.0057081 | -0.022702 | -0.005693 | 2.4742e-05 | 1.5135e-05 | 0.034473 | 0.034473 | 0.034473 | 0.98111 | -0.36356 | 0.97995 | -0.3864 | 9.4706
77 | 0.025488 | 0.0063949 | -0.025482 | -0.006391 | 6.408e-06 | 3.9541e-06 | 0.03848 | 0.03848 | 0.03848 | 0.98568 | -0.27456 | 0.98541 | -0.27984 | 10.5715
78 | -0.10965 | -0.027629 | 0.10987 | 0.027773 | 0.00022618 | 0.00014447 | 0.16558 | 0.16558 | 0.16558 | 0.98568 | -0.27456 | 0.9879 | -0.23154 | 45.4891
79 | 0.0059006 | 0.0014786 | -0.0059003 | -0.0014785 | 2.4719e-07 | 5.4239e-08 | 0.0089485 | 0.0089486 | 0.0089486 | 0.98117 | -0.36239 | 0.98113 | -0.36327 | 2.4584
80 | 0.011154 | 0.0027998 | -0.011152 | -0.0027986 | 2.3608e-06 | 1.2336e-06 | 0.016924 | 0.016924 | 0.016924 | 0.98079 | -0.36986 | 0.98057 | -0.3743 | 4.6496
81 | -0.0029575 | -0.00074107 | 0.0029575 | 0.00074099 | 7.643e-08 | -7.9015e-08 | 0.0044855 | 0.0044854 | 0.0044855 | 0.9811 | -0.36382 | 0.98113 | -0.36327 | 1.2323
82 | 0.0029575 | 0.00074107 | -0.0029574 | -0.00074118 | 1.0563e-07 | -1.0918e-07 | 0.0044855 | 0.0044855 | 0.0044855 | 0.9811 | -0.36382 | 0.98106 | -0.36457 | 1.2323
83 | 0.022702 | 0.005693 | -0.022694 | -0.0056884 | 7.4459e-06 | 4.555e-06 | 0.034473 | 0.034473 | 0.034473 | 0.97995 | -0.3864 | 0.9796 | -0.39328 | 9.4706
84 | -0.10987 | -0.027773 | 0.11018 | 0.02797 | 0.0003074 | 0.00019635 | 0.16558 | 0.16558 | 0.16558 | 0.9879 | -0.23154 | 0.99092 | -0.17337 | 45.4891
85 | -0.1208 | -0.03063 | 0.12106 | 0.0308 | 0.00026617 | 0.00017007 | 0.18152 | 0.18152 | 0.18152 | 0.99092 | -0.17337 | 0.9933 | -0.12764 | 49.8678
86 | 0.022603 | 0.0056695 | -0.022598 | -0.0056664 | 5.1209e-06 | 3.1281e-06 | 0.034133 | 0.034133 | 0.034133 | 0.98541 | -0.27984 | 0.98517 | -0.28459 | 9.3772
87 | 0.011152 | 0.0027986 | -0.011146 | -0.0027953 | 6.332e-06 | 3.3093e-06 | 0.016924 | 0.016925 | 0.016925 | 0.98057 | -0.3743 | 0.97996 | -0.38621 | 4.6496
88 | -0.0025392 | -0.00063623 | 0.0025394 | 0.00063595 | 1.745e-07 | -2.8095e-07 | 0.00386 | 0.0038598 | 0.00386 | 0.97885 | -0.40794 | 0.97892 | -0.40649 | 1.0604
89 | 0.0025392 | 0.00063623 | -0.0025391 | -0.00063637 | 8.6895e-08 | -1.3987e-07 | 0.00386 | 0.0038601 | 0.0038601 | 0.97885 | -0.40794 | 0.97881 | -0.40866 | 1.0605
90 | 0.0034799 | 0.00087205 | -0.0034798 | -0.00087212 | 1.3243e-07 | -7.3914e-08 | 0.0052896 | 0.0052897 | 0.0052897 | 0.97892 | -0.40649 | 0.97888 | -0.40729 | 1.4532
91 | -0.0060193 | -0.001508 | 0.0060199 | 0.0015081 | 6.007e-07 | 1.4385e-07 | 0.0091495 | 0.0091494 | 0.0091495 | 0.97892 | -0.40649 | 0.97903 | -0.4044 | 2.5136
92 | 0.0067667 | 0.0016959 | -0.0067661 | -0.0016958 | 5.4729e-07 | 1.6991e-07 | 0.010185 | 0.010185 | 0.010185 | 0.98857 | -0.21978 | 0.98849 | -0.22148 | 2.7982
93 | -0.0067667 | -0.0016959 | 0.0067672 | 0.0016961 | 5.0324e-07 | 1.5621e-07 | 0.010185 | 0.010185 | 0.010185 | 0.98857 | -0.21978 | 0.98865 | -0.21822 | 2.7982
94 | -0.017829 | -0.004469 | 0.017831 | 0.0044701 | 1.9233e-06 | 1.1396e-06 | 0.026835 | 0.026835 | 0.026835 | 0.98865 | -0.21822 | 0.98877 | -0.21595 | 7.3723
95 | 0.010619 | 0.0026622 | -0.010617 | -0.0026609 | 2.532e-06 | 1.2939e-06 | 0.016131 | 0.016131 | 0.016131 | 0.9796 | -0.39328 | 0.97934 | -0.39829 | 4.4317
96 | 0.016469 | 0.0041296 | -0.016462 | -0.0041258 | 6.453e-06 | 3.7666e-06 | 0.024713 | 0.024713 | 0.024713 | 0.99163 | -0.16065 | 0.99121 | -0.16888 | 6.7894
97 | -0.016469 | -0.0041296 | 0.016475 | 0.0041331 | 6.0847e-06 | 3.5514e-06 | 0.024713 | 0.024713 | 0.024713 | 0.99163 | -0.16065 | 0.99203 | -0.1529 | 6.7893
98 | -0.047621 | -0.011939 | 0.047641 | 0.011952 | 2.0189e-05 | 1.2785e-05 | 0.071431 | 0.071431 | 0.071431 | 0.99203 | -0.1529 | 0.99249 | -0.14401 | 19.6238
99 | -0.047641 | -0.011952 | 0.047674 | 0.011973 | 3.3559e-05 | 2.1251e-05 | 0.071431 | 0.071431 | 0.071431 | 0.99249 | -0.14401 | 0.99326 | -0.12925 | 19.6238
100 | -0.047674 | -0.011973 | 0.047685 | 0.01198 | 1.0844e-05 | 6.8665e-06 | 0.071431 | 0.071431 | 0.071431 | 0.99326 | -0.12925 | 0.9935 | -0.12448 | 19.6238
101 | -0.056165 | -0.014105 | 0.056237 | 0.014151 | 7.2211e-05 | 4.5862e-05 | 0.084132 | 0.084131 | 0.084132 | 0.9935 | -0.12448 | 0.9949 | -0.097573 | 23.1131
102 | -0.0045946 | -0.0011515 | 0.0045952 | 0.0011515 | 5.4334e-07 | -4.8954e-08 | 0.0068797 | 0.0068796 | 0.0068797 | 0.99378 | -0.11872 | 0.9939 | -0.11624 | 1.89
103 | -0.0085496 | -0.0021425 | 0.0085508 | 0.0021431 | 1.1966e-06 | 5.1339e-07 | 0.0128 | 0.0128 | 0.0128 | 0.9939 | -0.11624 | 0.99406 | -0.1133 | 3.5164
104 | -0.17343 | -0.044027 | 0.17358 | 0.044123 | 0.00015099 | 9.6324e-05 | 0.26 | 0.26 | 0.26 | 0.9933 | -0.12764 | 0.99425 | -0.10956 | 35.7148
105 | 0.020117 | 0.0050447 | -0.020109 | -0.0050399 | 7.9287e-06 | 4.7829e-06 | 0.030387 | 0.030387 | 0.030387 | 0.98517 | -0.28459 | 0.98474 | -0.29286 | 8.348
106 | 0.011146 | 0.0027953 | -0.011137 | -0.0027909 | 8.3369e-06 | 4.3586e-06 | 0.016925 | 0.016925 | 0.016925 | 0.97996 | -0.38621 | 0.97916 | -0.40192 | 4.6497
107 | 0.0064654 | 0.0016204 | -0.0064645 | -0.0016202 | 8.9819e-07 | 2.5564e-07 | 0.0097697 | 0.0097698 | 0.0097698 | 0.98474 | -0.29286 | 0.98459 | -0.29578 | 2.684
108 | 0.0064645 | 0.0016202 | -0.0064641 | -0.00162 | 4.1653e-07 | 1.1859e-07 | 0.0097698 | 0.0097698 | 0.0097698 | 0.98459 | -0.29578 | 0.98452 | -0.29713 | 2.684
109 | -0.028409 | -0.0071533 | 0.028424 | 0.0071628 | 1.5346e-05 | 9.5341e-06 | 0.042753 | 0.042753 | 0.042753 | 0.98904 | -0.21 | 0.98962 | -0.1987 | 11.7454
110 | -0.036236 | -0.0091207 | 0.036239 | 0.0091227 | 3.1727e-06 | 1.994e-06 | 0.054499 | 0.054499 | 0.054499 | 0.98962 | -0.1987 | 0.98972 | -0.19687 | 14.9724
111 | -0.18753 | -0.04762 | 0.18761 | 0.047673 | 8.3507e-05 | 5.3115e-05 | 0.28088 | 0.28088 | 0.28088 | 0.99425 | -0.10956 | 0.99473 | -0.10031 | 25.7213
112 | 0.013947 | 0.0034962 | -0.013944 | -0.0034948 | 2.4811e-06 | 1.391e-06 | 0.020874 | 0.020874 | 0.020874 | 0.99425 | -0.10956 | 0.99406 | -0.1133 | 5.7345
113 | 0.0092377 | 0.0023148 | -0.0092366 | -0.0023143 | 1.0925e-06 | 5.1331e-07 | 0.014038 | 0.014038 | 0.014038 | 0.97916 | -0.40192 | 0.97903 | -0.4044 | 3.8567
114 | -0.19483 | -0.049482 | 0.19538 | 0.049833 | 0.00055153 | 0.00035096 | 0.29168 | 0.29168 | 0.29168 | 0.99473 | -0.10031 | 0.99781 | -0.041678 | 26.7104
115 | 0.0072203 | 0.0018097 | -0.007219 | -0.0018092 | 1.3454e-06 | 4.619e-07 | 0.010801 | 0.010801 | 0.010801 | 0.99473 | -0.10031 | 0.99453 | -0.10423 | 2.9673
116 | -0.023225 | -0.0058219 | 0.023236 | 0.0058288 | 1.1171e-05 | 6.8363e-06 | 0.034952 | 0.034952 | 0.034952 | 0.98877 | -0.21595 | 0.98929 | -0.20586 | 9.6023
117 | -0.056237 | -0.014151 | 0.056245 | 0.014156 | 7.9012e-06 | 5.0181e-06 | 0.084131 | 0.084131 | 0.084131 | 0.9949 | -0.097573 | 0.99505 | -0.094634 | 23.113
118 | 0.16889 | 0.042725 | -0.16868 | -0.042592 | 0.00020937 | 0.00013354 | 0.25201 | 0.25201 | 0.25201 | 0.99781 | -0.041678 | 0.99646 | -0.067549 | 34.6164
119 | -0.36427 | -0.092559 | 0.36501 | 0.093027 | 0.00073257 | 0.00046806 | 0.54368 | 0.54368 | 0.54368 | 0.99781 | -0.041678 | 1 | 0 | 49.7879
120 | 0.099468 | 0.025153 | -0.099162 | -0.024957 | 0.00030577 | 0.00019521 | 0.14861 | 0.14862 | 0.14862 | 0.99646 | -0.067549 | 0.99311 | -0.13185 | 40.8283
121 | 0.064806 | 0.016334 | -0.064722 | -0.016281 | 8.3862e-05 | 5.3361e-05 | 0.096808 | 0.096808 | 0.096808 | 0.99646 | -0.067549 | 0.99505 | -0.094634 | 26.5956
122 | 0.14854 | 0.037925 | -0.14837 | -0.037812 | 0.00017806 | 0.00011281 | 0.22128 | 0.22128 | 0.22128 | 1 | 0 | 0.99869 | -0.024836 | 20.264
123 | 0.012822 | 0.0032141 | -0.01282 | -0.003213 | 2.0133e-06 | 1.1003e-06 | 0.019212 | 0.019213 | 0.019213 | 0.99311 | -0.13185 | 0.99294 | -0.13515 | 5.2782
124 | 0.08634 | 0.021743 | -0.086181 | -0.021642 | 0.0001586 | 0.00010118 | 0.1294 | 0.1294 | 0.1294 | 0.99311 | -0.13185 | 0.99112 | -0.17035 | 35.5502
125 | 0.14072 | 0.035895 | -0.14067 | -0.035862 | 5.0896e-05 | 3.2211e-05 | 0.20989 | 0.20989 | 0.20989 | 0.99869 | -0.024836 | 0.9983 | -0.032328 | 19.2203
126 | 0.0096262 | 0.0024131 | -0.0096253 | -0.0024126 | 8.6815e-07 | 4.1504e-07 | 0.01451 | 0.01451 | 0.01451 | 0.9872 | -0.24495 | 0.9871 | -0.24684 | 3.9862
127 | -0.031507 | -0.0078964 | 0.031527 | 0.007909 | 2.0185e-05 | 1.2609e-05 | 0.047336 | 0.047336 | 0.047336 | 0.99043 | -0.18379 | 0.99112 | -0.17035 | 13.0044
128 | 0.054654 | 0.013733 | -0.054593 | -0.013695 | 6.0248e-05 | 3.8252e-05 | 0.082067 | 0.082067 | 0.082067 | 0.99112 | -0.17035 | 0.98993 | -0.19347 | 22.5458
129 | 0.021614 | 0.0054183 | -0.021603 | -0.0054118 | 1.0753e-05 | 6.5329e-06 | 0.03249 | 0.03249 | 0.03249 | 0.98993 | -0.19347 | 0.98939 | -0.20392 | 8.9258
130 | 0.028648 | 0.0071912 | -0.028631 | -0.0071807 | 1.6928e-05 | 1.0521e-05 | 0.043066 | 0.043066 | 0.043066 | 0.98993 | -0.19347 | 0.98929 | -0.20586 | 11.8313
131 | 0.0043319 | 0.0010854 | -0.0043312 | -0.0010855 | 7.0947e-07 | -1.1949e-07 | 0.0065114 | 0.0065116 | 0.0065116 | 0.98993 | -0.19347 | 0.98975 | -0.19691 | 1.7889
132 | 0.0082728 | 0.0020732 | -0.0082727 | -0.0020732 | 1.6533e-07 | 6.8708e-08 | 0.012398 | 0.012398 | 0.012398 | 0.99294 | -0.13515 | 0.99292 | -0.13557 | 3.4059
133 | 0.0049367 | 0.0012368 | -0.0049364 | -0.0012368 | 3.5201e-07 | 6.6131e-09 | 0.0074245 | 0.0074246 | 0.0074246 | 0.98939 | -0.20392 | 0.98931 | -0.20541 | 2.0397
134 | 0.016667 | 0.004175 | -0.016663 | -0.004173 | 3.4973e-06 | 2.0477e-06 | 0.025065 | 0.025065 | 0.025065 | 0.98939 | -0.20392 | 0.98916 | -0.20832 | 6.8861
135 | 0.002333 | 0.00058456 | -0.002333 | -0.0005847 | 6.3735e-08 | -1.3903e-07 | 0.0034963 | 0.0034964 | 0.0034964 | 0.99292 | -0.13557 | 0.99289 | -0.13614 | 0.96054
136 | 0.0016342 | 0.00040932 | -0.0016341 | -0.00040955 | 4.5753e-08 | -2.3004e-07 | 0.0024578 | 0.0024579 | 0.0024579 | 0.98931 | -0.20541 | 0.98928 | -0.206 | 0.67525
137 | 0.0033022 | 0.00082744 | -0.003302 | -0.00082757 | 1.7577e-07 | -1.3146e-07 | 0.0049668 | 0.0049668 | 0.0049668 | 0.98931 | -0.20541 | 0.98926 | -0.20653 | 1.3645
138 | 0.0099715 | 0.0024959 | -0.0099697 | -0.0024951 | 1.7823e-06 | 8.6956e-07 | 0.014999 | 0.014999 | 0.014999 | 0.98916 | -0.20832 | 0.98897 | -0.21208 | 4.1207
139 | 0.0081027 | 0.0020271 | -0.0081021 | -0.0020269 | 6.262e-07 | 2.5659e-07 | 0.01219 | 0.01219 | 0.01219 | 0.98897 | -0.21208 | 0.98889 | -0.2137 | 3.349
140 | 0.0061601 | 0.0015436 | -0.0061599 | -0.0015436 | 2.6244e-07 | 6.074e-08 | 0.0092098 | 0.0092098 | 0.0092098 | 0.99528 | -0.089753 | 0.99523 | -0.090648 | 2.5302
141 | 0.0016704 | 0.00041839 | -0.0016704 | -0.00041863 | 4.8623e-08 | -2.39e-07 | 0.0024974 | 0.0024975 | 0.0024975 | 0.99523 | -0.090648 | 0.9952 | -0.091259 | 0.68613
142 | -0.0042799 | -0.0010725 | 0.0042802 | 0.0010724 | 2.9636e-07 | -3.8264e-08 | 0.0065539 | 0.0065538 | 0.0065539 | 0.97171 | -0.54688 | 0.97178 | -0.54542 | 1.8005
143 | 0.0042799 | 0.0010725 | -0.0042794 | -0.0010725 | 4.3329e-07 | -5.5871e-08 | 0.0065539 | 0.006554 | 0.006554 | 0.97171 | -0.54688 | 0.9716 | -0.549 | 1.8005
144 | -0.017387 | -0.0043575 | 0.017391 | 0.0043597 | 3.716e-06 | 2.205e-06 | 0.026623 | 0.026623 | 0.026623 | 0.97178 | -0.54542 | 0.97201 | -0.54094 | 7.3141
145 | 0.0047605 | 0.0011929 | -0.0047603 | -0.0011929 | 2.7417e-07 | 5.0086e-09 | 0.0072894 | 0.0072894 | 0.0072894 | 0.97178 | -0.54542 | 0.97172 | -0.54663 | 2.0026
146 | 0.0083462 | 0.0020922 | -0.008344 | -0.0020912 | 2.202e-06 | 9.6402e-07 | 0.01278 | 0.01278 | 0.01278 | 0.97178 | -0.54542 | 0.9715 | -0.55096 | 3.5111
147 | 0.0047603 | 0.0011929 | -0.0047597 | -0.0011929 | 5.5881e-07 | 1.0284e-08 | 0.0072894 | 0.0072896 | 0.0072896 | 0.97172 | -0.54663 | 0.97159 | -0.5491 | 2.0026
148 | 0.008344 | 0.0020912 | -0.0083419 | -0.0020903 | 2.1137e-06 | 9.2558e-07 | 0.01278 | 0.01278 | 0.01278 | 0.9715 | -0.55096 | 0.97123 | -0.55628 | 3.5111
149 | 0.0018321 | 0.00045882 | -0.0018321 | -0.00045889 | 2.0182e-08 | -7.1619e-08 | 0.0028069 | 0.0028069 | 0.0028069 | 0.97123 | -0.55628 | 0.97122 | -0.55651 | 0.77113
150 | -0.0018321 | -0.00045913 | 0.0018321 | 0.00045889 | 6.913e-08 | -2.4528e-07 | 0.002807 | 0.0028069 | 0.002807 | 0.97118 | -0.5573 | 0.97122 | -0.55651 | 0.77116
151 | 0.0018321 | 0.00045913 | -0.001832 | -0.00045915 | 6.1103e-09 | -2.1678e-08 | 0.002807 | 0.002807 | 0.002807 | 0.97118 | -0.5573 | 0.97118 | -0.55737 | 0.77116

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52223 | 0.13271

## res_load
| p_mw | q_mvar
0 | 0.00055895 | 0.00014009
1 | 0.00030495 | 7.6429e-05
2 | 0.0022293 | 0.00055872
3 | 0.0013894 | 0.00034821
4 | 0.0016613 | 0.00041637
5 | 0.0042938 | 0.0010761
6 | 0.00039841 | 9.9851e-05
7 | 0.0067652 | 0.0016955
8 | 0.0026339 | 0.00066011
9 | 0.0016167 | 0.00040519
10 | 0.0063433 | 0.0015898
11 | 0.007744 | 0.0019408
12 | 0.020225 | 0.0050688
13 | 0.0050238 | 0.0012591
14 | 0.0081294 | 0.0020374
15 | 0.023294 | 0.0058381
16 | 0.001728 | 0.00043308
17 | 0.0015744 | 0.00039459
18 | 0.0045991 | 0.0011526
19 | 0.001485 | 0.00037218
20 | 0.00092052 | 0.0002307
21 | 0.0014789 | 0.00037064
22 | 0.0073935 | 0.001853
23 | 0.0026328 | 0.00065984
24 | 0.0026314 | 0.0006595
25 | 0.0039705 | 0.00099511
26 | 0.0036967 | 0.00092648
27 | 0.0060039 | 0.0015047
28 | 0.0036191 | 0.00090702
29 | 0.0032103 | 0.00080457
30 | 0.0068309 | 0.001712
31 | 0.0011715 | 0.00029359
32 | 0.0045148 | 0.0011315
33 | 0.0060301 | 0.0015113
34 | 0.003866 | 0.00096891
35 | 0.0032765 | 0.00082118
36 | 0.010187 | 0.0025531
37 | 0.0048365 | 0.0012121
38 | 0.010209 | 0.0025586
39 | 0.0056462 | 0.0014151
40 | 0.0029428 | 0.00073754
41 | 0.0029574 | 0.00074118
42 | 0.010614 | 0.0026602
43 | 0.0028788 | 0.0007215
44 | 0.0025391 | 0.00063637
45 | 0.0067661 | 0.0016958
46 | 0.012075 | 0.0030262
47 | 0.016462 | 0.0041258
48 | 0.031146 | 0.0078059
49 | 0.0084801 | 0.0021253
50 | 0.0045946 | 0.0011515
51 | 0.0039544 | 0.00099107
52 | 0.0024804 | 0.00062164
53 | 0.013644 | 0.0034195
54 | 0.0064641 | 0.00162
55 | 0.007812 | 0.0019579
56 | 0.0082969 | 0.0020794
57 | 0.0018995 | 0.00047606
58 | 0.0053937 | 0.0013518
59 | 0.010617 | 0.0026609
60 | 0.0053938 | 0.0013518
61 | 0.007219 | 0.0018092
62 | 0.0044094 | 0.0011051
63 | 0.0070262 | 0.0017609
64 | 0.0084768 | 0.0021245
65 | 0.0076495 | 0.0019172
66 | 0.0034798 | 0.00087212
67 | 0.0032167 | 0.00080618
68 | 0.031507 | 0.0078964
69 | 0.0045476 | 0.0011397
70 | 0.0053942 | 0.0013519
71 | 0.0043312 | 0.0010855
72 | 0.0059396 | 0.0014886
73 | 0.0066916 | 0.0016771
74 | 0.002333 | 0.0005847
75 | 0.0016341 | 0.00040955
76 | 0.003302 | 0.00082757
77 | 0.001867 | 0.00046791
78 | 0.0045759 | 0.0011468
79 | 0.0027395 | 0.00068659
80 | 0.0075547 | 0.0018934
81 | 0.0044895 | 0.0011252
82 | 0.0042794 | 0.0010725
83 | 0.0016704 | 0.00041863
84 | 0.0026314 | 0.00065949
85 | 0.0047597 | 0.0011929
86 | 0.0065097 | 0.0016315
87 | 0.0015558 | 0.00038992
88 | 0.001832 | 0.00045915
89 | 0.0015008 | 0.00037614

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1