## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_192-2_1_3_node_134 | 0.4 | n |  | TRUE
1 | bus_LV_192-2_1_3_node_93 | 0.4 | n |  | TRUE
2 | bus_LV_192-2_1_3_node_135 | 0.4 | n |  | TRUE
3 | bus_LV_192-2_1_3_node_45 | 0.4 | n |  | TRUE
4 | bus_LV_192-2_1_3_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_192-2_1_3_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_192-2_1_3_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_192-2_1_3_node_78 | 0.4 | n |  | TRUE
8 | bus_LV_192-2_1_3_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_192-2_1_3_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_192-2_1_3_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_192-2_1_3_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_192-2_1_3_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_192-2_1_3_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_192-2_1_3_node_57 | 0.4 | n |  | TRUE
15 | bus_LV_192-2_1_3_node_100 | 0.4 | n |  | TRUE
16 | bus_LV_192-2_1_3_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_192-2_1_3_node_83 | 0.4 | n |  | TRUE
18 | bus_LV_192-2_1_3_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_192-2_1_3_node_80 | 0.4 | n |  | TRUE
20 | bus_LV_192-2_1_3_node_56 | 0.4 | n |  | TRUE
21 | bus_LV_192-2_1_3_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_192-2_1_3_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_192-2_1_3_node_99 | 0.4 | n |  | TRUE
24 | bus_LV_192-2_1_3_node_112 | 0.4 | n |  | TRUE
25 | bus_LV_192-2_1_3_node_113 | 0.4 | n |  | TRUE
26 | bus_LV_192-2_1_3_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_192-2_1_3_node_116 | 0.4 | n |  | TRUE
28 | bus_LV_192-2_1_3_node_115 | 0.4 | n |  | TRUE
29 | bus_LV_192-2_1_3_node_82 | 0.4 | n |  | TRUE
30 | bus_LV_192-2_1_3_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_192-2_1_3_node_84 | 0.4 | n |  | TRUE
32 | bus_LV_192-2_1_3_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_192-2_1_3_node_86 | 0.4 | n |  | TRUE
34 | bus_LV_192-2_1_3_node_87 | 0.4 | n |  | TRUE
35 | bus_LV_192-2_1_3_node_89 | 0.4 | n |  | TRUE
36 | bus_LV_192-2_1_3_node_101 | 0.4 | n |  | TRUE
37 | bus_LV_192-2_1_3_node_91 | 0.4 | n |  | TRUE
38 | bus_LV_192-2_1_3_node_92 | 0.4 | n |  | TRUE
39 | bus_LV_192-2_1_3_node_94 | 0.4 | n |  | TRUE
40 | bus_LV_192-2_1_3_node_114 | 0.4 | n |  | TRUE
41 | bus_LV_192-2_1_3_node_105 | 0.4 | n |  | TRUE
42 | bus_LV_192-2_1_3_node_95 | 0.4 | n |  | TRUE
43 | bus_LV_192-2_1_3_node_96 | 0.4 | n |  | TRUE
44 | bus_LV_192-2_1_3_node_97 | 0.4 | n |  | TRUE
45 | bus_LV_192-2_1_3_node_98 | 0.4 | n |  | TRUE
46 | bus_LV_192-2_1_3_node_102 | 0.4 | n |  | TRUE
47 | bus_LV_192-2_1_3_node_103 | 0.4 | n |  | TRUE
48 | bus_LV_192-2_1_3_node_106 | 0.4 | n |  | TRUE
49 | bus_LV_192-2_1_3_node_107 | 0.4 | n |  | TRUE
50 | bus_LV_192-2_1_3_node_108 | 0.4 | n |  | TRUE
51 | bus_LV_192-2_1_3_node_109 | 0.4 | n |  | TRUE
52 | bus_LV_192-2_1_3_node_110 | 0.4 | n |  | TRUE
53 | bus_LV_192-2_1_3_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_192-2_1_3_node_117 | 0.4 | n |  | TRUE
55 | bus_MV_356_0_node_72 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_192-2_1_3_load_134 | 0 | 0.0022518 | 0.00056435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_192-2_1_3_load_135 | 2 | 0.011741 | 0.0029426 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_192-2_1_3_load_17 | 4 | 0.011603 | 0.0029081 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_192-2_1_3_load_25 | 6 | 0.01226 | 0.0030726 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_192-2_1_3_load_55 | 8 | 0.011744 | 0.0029433 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_192-2_1_3_load_43 | 9 | 0.011744 | 0.0029433 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_192-2_1_3_load_100 | 15 | 0.002473 | 0.00061979 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_192-2_1_3_load_81 | 18 | 0.0025629 | 0.00064232 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_192-2_1_3_load_80 | 19 | 0.0020375 | 0.00051064 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_192-2_1_3_load_58 | 22 | 0.0074836 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_192-2_1_3_load_99 | 23 | 0.0053991 | 0.0013531 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_192-2_1_3_load_113 | 25 | 0.0071338 | 0.0017879 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_192-2_1_3_load_115 | 28 | 0.010899 | 0.0027315 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_192-2_1_3_load_82 | 29 | 0.0023832 | 0.00059729 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_192-2_1_3_load_88 | 30 | 0.0023933 | 0.00059981 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_192-2_1_3_load_84 | 31 | 0.0021136 | 0.00052971 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_192-2_1_3_load_85 | 32 | 0.0048847 | 0.0012242 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_192-2_1_3_load_86 | 33 | 0.0024858 | 0.00062299 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_192-2_1_3_load_101 | 36 | 0.0023352 | 0.00058526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_192-2_1_3_load_91 | 37 | 0.005964 | 0.0014947 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_192-2_1_3_load_94 | 39 | 0.013941 | 0.0034938 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_192-2_1_3_load_95 | 42 | 0.0054957 | 0.0013773 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_192-2_1_3_load_96 | 43 | 0.0024215 | 0.00060688 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_192-2_1_3_load_97 | 44 | 0.0025656 | 0.00064301 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_192-2_1_3_load_98 | 45 | 0.0026305 | 0.00065927 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_192-2_1_3_load_103 | 47 | 0.016987 | 0.0042574 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_192-2_1_3_load_106 | 48 | 0.0064634 | 0.0016199 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_192-2_1_3_load_107 | 49 | 0.0083621 | 0.0020957 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_192-2_1_3_load_108 | 50 | 0.0021225 | 0.00053196 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_192-2_1_3_load_110 | 52 | 0.001645 | 0.00041228 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_192-2_1_3_load_117 | 54 | 0.011517 | 0.0028864 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_192-2_1_3_line_0 |  | 0 | 1 | 0.044993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_192-2_1_3_line_1 |  | 1 | 40 | 0.039672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_192-2_1_3_line_2 |  | 1 | 38 | 0.034727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_192-2_1_3_line_3 |  | 2 | 3 | 0.010535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_192-2_1_3_line_4 |  | 3 | 12 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_192-2_1_3_line_5 |  | 3 | 10 | 0.036757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_192-2_1_3_line_6 |  | 4 | 5 | 0.042599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_192-2_1_3_line_7 |  | 5 | 8 | 0.025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_192-2_1_3_line_8 |  | 6 | 7 | 0.019472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_192-2_1_3_line_9 |  | 7 | 26 | 0.026202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_192-2_1_3_line_10 |  | 8 | 13 | 0.018103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_192-2_1_3_line_11 |  | 9 | 10 | 0.016233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_192-2_1_3_line_12 |  | 10 | 11 | 0.024961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_192-2_1_3_line_13 |  | 11 | 14 | 0.032049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_192-2_1_3_line_14 |  | 11 | 15 | 0.017704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_192-2_1_3_line_15 |  | 12 | 19 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_192-2_1_3_line_16 |  | 13 | 14 | 0.02268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_192-2_1_3_line_17 |  | 14 | 23 | 0.022374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_192-2_1_3_line_18 |  | 14 | 20 | 0.028475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_192-2_1_3_line_19 |  | 15 | 17 | 0.0154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_192-2_1_3_line_20 |  | 16 | 17 | 0.025814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_192-2_1_3_line_21 |  | 16 | 18 | 0.0051347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_192-2_1_3_line_22 |  | 17 | 30 | 0.013854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_192-2_1_3_line_23 |  | 18 | 29 | 0.033422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_192-2_1_3_line_24 |  | 20 | 21 | 0.030853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_192-2_1_3_line_25 |  | 20 | 22 | 0.015906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_192-2_1_3_line_26 |  | 21 | 24 | 0.026516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_192-2_1_3_line_27 |  | 21 | 25 | 0.020185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_192-2_1_3_line_28 |  | 23 | 45 | 0.010565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_192-2_1_3_line_29 |  | 24 | 28 | 0.024637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_192-2_1_3_line_30 |  | 24 | 53 | 0.049469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_192-2_1_3_line_31 |  | 25 | 40 | 0.028415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_192-2_1_3_line_32 |  | 26 | 27 | 0.004424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_192-2_1_3_line_33 |  | 26 | 28 | 0.027647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_192-2_1_3_line_34 |  | 27 | 54 | 0.02738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_192-2_1_3_line_35 |  | 30 | 33 | 0.028825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_192-2_1_3_line_36 |  | 31 | 32 | 0.0039882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_192-2_1_3_line_37 |  | 31 | 33 | 0.029244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_192-2_1_3_line_38 |  | 32 | 34 | 0.020363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_192-2_1_3_line_39 |  | 34 | 35 | 0.014361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_192-2_1_3_line_40 |  | 35 | 36 | 0.023981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_192-2_1_3_line_41 |  | 36 | 46 | 0.015123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_192-2_1_3_line_42 |  | 37 | 38 | 0.021483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_192-2_1_3_line_43 |  | 38 | 39 | 0.017996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_192-2_1_3_line_44 |  | 39 | 41 | 0.012465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_192-2_1_3_line_45 |  | 41 | 48 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_192-2_1_3_line_46 |  | 42 | 43 | 0.019012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_192-2_1_3_line_47 |  | 42 | 44 | 0.0077364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_192-2_1_3_line_48 |  | 44 | 45 | 0.027051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_192-2_1_3_line_49 |  | 46 | 47 | 0.033768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_192-2_1_3_line_50 |  | 49 | 50 | 0.0088189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_192-2_1_3_line_51 |  | 49 | 51 | 0.020636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_192-2_1_3_line_52 |  | 51 | 52 | 0.062116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_192-2_1_3_line_53 |  | 52 | 53 | 0.017502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_192-2_1_3_trafo_98 | 0.63 MVA 20/0.4 kV | 55 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2694714.4544 | 1239312.058 | 2694706.5918 | 1239321.7398 | 2694685.4555 | 1239323.7264 | 2694674.7301 | 1239319.8748
1 | 2694697.166 | 1239287.1749 | 2694685.8248 | 1239302.005 | 2694674.7301 | 1239319.8748
2 | 2694656.5795 | 1239349.5074 | 2694674.7301 | 1239319.8748
3 | 2694626.359 | 1239168.836 | 2694628.4502 | 1239170.9932 | 2694627.1971 | 1239178.4232
4 | 2694617.8055 | 1239192.4284 | 2694620.0781 | 1239188.9064 | 2694622.5959 | 1239187.5566 | 2694625.7082 | 1239187.3505 | 2694627.1971 | 1239178.4232
5 | 2694627.1971 | 1239178.4232 | 2694634.85 | 1239185.2168 | 2694649.2726 | 1239194.8872 | 2694655.245 | 1239195.5829 | 2694658.4042 | 1239196.2338
6 | 2694707.2831 | 1239176.9988 | 2694710.3791 | 1239180.1839 | 2694721.7655 | 1239184.8134 | 2694729.3573 | 1239185.9464 | 2694733.1164 | 1239185.5061 | 2694735.3007 | 1239182.3052 | 2694740.9369 | 1239173.4108
7 | 2694707.2831 | 1239176.9988 | 2694706.1439 | 1239184.8642 | 2694700.9081 | 1239188.7281 | 2694693.4766 | 1239196.5042
8 | 2694764.7232 | 1239209.5282 | 2694778.521 | 1239195.7881
9 | 2694764.7232 | 1239209.5282 | 2694783.0548 | 1239228.3014
10 | 2694687.2596 | 1239213.5066 | 2694693.4766 | 1239196.5042
11 | 2694658.4042 | 1239196.2338 | 2694663.3873 | 1239181.6579 | 2694663.8541 | 1239180.973
12 | 2694658.4042 | 1239196.2338 | 2694659.4974 | 1239196.4625 | 2694665.9248 | 1239200.4123 | 2694658.0586 | 1239212.2068 | 2694659.7245 | 1239213.5232
13 | 2694659.7245 | 1239213.5232 | 2694672.1104 | 1239223.3057 | 2694682.7239 | 1239226.1214 | 2694687.8309 | 1239227.4817
14 | 2694659.7245 | 1239213.5232 | 2694649.8536 | 1239228.2206
15 | 2694617.8055 | 1239192.4284 | 2694614.1279 | 1239191.558 | 2694602.5872 | 1239183.423
16 | 2694687.2596 | 1239213.5066 | 2694680.0595 | 1239217.2168 | 2694682.7239 | 1239226.1214 | 2694687.8309 | 1239227.4817
17 | 2694687.8309 | 1239227.4817 | 2694674.8644 | 1239245.715
18 | 2694711.5281 | 1239229.0496 | 2694707.371 | 1239234.9988 | 2694702.0223 | 1239231.2441 | 2694687.8309 | 1239227.4817
19 | 2694641.2675 | 1239241.005 | 2694649.8536 | 1239228.2206
20 | 2694620.0583 | 1239226.2004 | 2694641.2675 | 1239241.005
21 | 2694620.0583 | 1239226.2004 | 2694616.9359 | 1239230.2767
22 | 2694641.2675 | 1239241.005 | 2694633.2639 | 1239252.3126
23 | 2694595.0813 | 1239253.1892 | 2694599.0301 | 1239253.6525 | 2694616.9359 | 1239230.2767
24 | 2694711.5281 | 1239229.0496 | 2694707.371 | 1239234.9988 | 2694712.4278 | 1239238.5599 | 2694726.6785 | 1239248.5613
25 | 2694711.5281 | 1239229.0496 | 2694720.1546 | 1239215.6856
26 | 2694726.6785 | 1239248.5613 | 2694746.7645 | 1239265.9391
27 | 2694726.6785 | 1239248.5613 | 2694714.4211 | 1239264.5986
28 | 2694668.7415 | 1239254.3249 | 2694674.8644 | 1239245.715
29 | 2694746.7645 | 1239265.9391 | 2694763.865 | 1239248.2037
30 | 2694746.7645 | 1239265.9391 | 2694773.9652 | 1239293.0044 | 2694779.2594 | 1239298.2706 | 2694776.6323 | 1239300.775
31 | 2694697.166 | 1239287.1749 | 2694714.4211 | 1239264.5986
32 | 2694783.0548 | 1239228.3014 | 2694786.1315 | 1239225.1148
33 | 2694783.0548 | 1239228.3014 | 2694763.865 | 1239248.2037
34 | 2694786.1315 | 1239225.1148 | 2694803.9923 | 1239206.5861 | 2694802.8999 | 1239205.3567
35 | 2694616.611 | 1239275.8401 | 2694633.2639 | 1239252.3126
36 | 2694599.7156 | 1239299.7103 | 2694597.4115 | 1239302.9655
37 | 2694599.7156 | 1239299.7103 | 2694616.611 | 1239275.8401
38 | 2694585.6491 | 1239319.5883 | 2694590.3465 | 1239312.9471 | 2694597.4115 | 1239302.9655
39 | 2694585.6491 | 1239319.5883 | 2694577.7135 | 1239315.8258 | 2694572.1039 | 1239316.1033
40 | 2694572.1039 | 1239316.1033 | 2694576.2035 | 1239339.7315
41 | 2694579.1233 | 1239354.5659 | 2694577.4938 | 1239347.1678 | 2694576.2035 | 1239339.7315
42 | 2694656.5795 | 1239349.5074 | 2694644.1682 | 1239343.2272 | 2694636.9717 | 1239340.8674
43 | 2694656.5795 | 1239349.5074 | 2694648.5069 | 1239365.5911
44 | 2694642.9152 | 1239376.7321 | 2694648.5069 | 1239365.5911
45 | 2694642.9152 | 1239376.7321 | 2694638.5854 | 1239373.6052 | 2694630.6988 | 1239371.0443
46 | 2694648.5807 | 1239282.6748 | 2694637.5625 | 1239298.1685
47 | 2694648.5807 | 1239282.6748 | 2694653.0643 | 1239276.3701
48 | 2694653.0643 | 1239276.3701 | 2694668.7415 | 1239254.3249
49 | 2694579.1233 | 1239354.5659 | 2694586.639 | 1239387.4866
50 | 2694712.9885 | 1239355.4447 | 2694706.2011 | 1239349.8141
51 | 2694730.9994 | 1239365.4949 | 2694713.4531 | 1239355.8301 | 2694712.9885 | 1239355.4447
52 | 2694730.9994 | 1239365.4949 | 2694732.833 | 1239361.9883 | 2694748.2018 | 1239337.4708 | 2694754.6529 | 1239325.7094 | 2694763.8936 | 1239313.5812 | 2694764.289 | 1239313.1837
53 | 2694776.6323 | 1239300.775 | 2694764.289 | 1239313.1837

## bus_geodata
| x | y | coords
0 | 2694714.4544 | 1239312.058
1 | 2694674.7301 | 1239319.8748
2 | 2694626.359 | 1239168.836
3 | 2694627.1971 | 1239178.4232
4 | 2694740.9368 | 1239173.4108
5 | 2694707.2831 | 1239176.9988
6 | 2694778.521 | 1239195.7881
7 | 2694764.7232 | 1239209.5282
8 | 2694693.4766 | 1239196.5042
9 | 2694663.8541 | 1239180.973
10 | 2694658.4042 | 1239196.2338
11 | 2694659.7245 | 1239213.5232
12 | 2694617.8055 | 1239192.4284
13 | 2694687.2596 | 1239213.5066
14 | 2694687.8309 | 1239227.4817
15 | 2694649.8536 | 1239228.2206
16 | 2694620.0583 | 1239226.2005
17 | 2694641.2675 | 1239241.005
18 | 2694616.9359 | 1239230.2767
19 | 2694602.5872 | 1239183.423
20 | 2694711.5281 | 1239229.0496
21 | 2694726.6785 | 1239248.5613
22 | 2694720.1546 | 1239215.6856
23 | 2694674.8644 | 1239245.715
24 | 2694746.7645 | 1239265.9391
25 | 2694714.4211 | 1239264.5986
26 | 2694783.0548 | 1239228.3014
27 | 2694786.1315 | 1239225.1148
28 | 2694763.865 | 1239248.2037
29 | 2694595.0813 | 1239253.1892
30 | 2694633.2639 | 1239252.3126
31 | 2694599.7156 | 1239299.7103
32 | 2694597.4115 | 1239302.9655
33 | 2694616.611 | 1239275.8401
34 | 2694585.649 | 1239319.5883
35 | 2694572.1039 | 1239316.1033
36 | 2694576.2035 | 1239339.7315
37 | 2694636.9717 | 1239340.8674
38 | 2694656.5795 | 1239349.5074
39 | 2694648.5069 | 1239365.5911
40 | 2694697.166 | 1239287.1749
41 | 2694642.9152 | 1239376.7321
42 | 2694648.5807 | 1239282.6748
43 | 2694637.5625 | 1239298.1685
44 | 2694653.0643 | 1239276.3701
45 | 2694668.7415 | 1239254.3249
46 | 2694579.1233 | 1239354.5659
47 | 2694586.639 | 1239387.4866
48 | 2694630.6988 | 1239371.0443
49 | 2694712.9885 | 1239355.4447
50 | 2694706.2011 | 1239349.8141
51 | 2694730.9994 | 1239365.4949
52 | 2694764.289 | 1239313.1837
53 | 2694776.6323 | 1239300.775
54 | 2694802.8999 | 1239205.3567
55 | 2694687.8309 | 1239227.4817

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99008 | -0.19078 | 0.0022518 | 0.00056435
1 | 0.99017 | -0.18898 | 0 | 0
2 | 0.99427 | -0.11003 | 0.011741 | 0.0029426
3 | 0.99438 | -0.10785 | 0 | 0
4 | 0.99572 | -0.082134 | 0.011603 | 0.0029081
5 | 0.99617 | -0.073448 | 0 | 0
6 | 0.98958 | -0.2004 | 0.01226 | 0.0030726
7 | 0.9898 | -0.19616 | 0 | 0
8 | 0.99643 | -0.068311 | 0.011744 | 0.0029433
9 | 0.99467 | -0.10228 | 0.011744 | 0.0029433
10 | 0.99484 | -0.098922 | 0 | 0
11 | 0.99542 | -0.087707 | 0 | 0
12 | 0.99434 | -0.10854 | 0 | 0
13 | 0.99682 | -0.060893 | 0 | 0
14 | 0.9973 | -0.051608 | 0 | 0
15 | 0.9948 | -0.099745 | 0.002473 | 0.00061979
16 | 0.99417 | -0.11181 | 0 | 0
17 | 0.99429 | -0.10956 | 0 | 0
18 | 0.99415 | -0.11226 | 0.0025629 | 0.00064232
19 | 0.99431 | -0.10918 | 0.0020375 | 0.00051064
20 | 0.99495 | -0.096654 | 0 | 0
21 | 0.99262 | -0.14162 | 0 | 0
22 | 0.99484 | -0.09875 | 0.0074836 | 0.0018756
23 | 0.99912 | -0.016861 | 0.0053991 | 0.0013531
24 | 0.99148 | -0.1636 | 0 | 0
25 | 0.99196 | -0.15439 | 0.0071338 | 0.0017879
26 | 0.9901 | -0.19044 | 0 | 0
27 | 0.99005 | -0.19135 | 0 | 0
28 | 0.9907 | -0.17876 | 0.010899 | 0.0027315
29 | 0.99408 | -0.11366 | 0.0023832 | 0.00059729
30 | 0.99389 | -0.11718 | 0.0023933 | 0.00059981
31 | 0.99243 | -0.14546 | 0.0021136 | 0.00052971
32 | 0.99234 | -0.14717 | 0.0048847 | 0.0012242
33 | 0.99313 | -0.13185 | 0.0024858 | 0.00062299
34 | 0.99198 | -0.15414 | 0 | 0
35 | 0.99173 | -0.15905 | 0 | 0
36 | 0.9913 | -0.16727 | 0.0023352 | 0.00058526
37 | 0.98921 | -0.20756 | 0.005964 | 0.0014947
38 | 0.98933 | -0.20527 | 0 | 0
39 | 0.98899 | -0.21182 | 0.013941 | 0.0034938
40 | 0.99121 | -0.16881 | 0 | 0
41 | 0.98892 | -0.21325 | 0 | 0
42 | 0.99969 | -0.0060127 | 0.0054957 | 0.0013773
43 | 0.99965 | -0.0068157 | 0.0024215 | 0.00060688
44 | 0.99974 | -0.0049444 | 0.0025656 | 0.00064301
45 | 1 | 0 | -0.19638 | -0.0493
46 | 0.99107 | -0.17183 | 0 | 0
47 | 0.99054 | -0.18201 | 0.016987 | 0.0042574
48 | 0.98884 | -0.21482 | 0.0064634 | 0.0016199
49 | 0.98994 | -0.19344 | 0.0083621 | 0.0020957
50 | 0.98993 | -0.19377 | 0.0021225 | 0.00053196
51 | 0.99014 | -0.18959 | 0 | 0
52 | 0.99074 | -0.17802 | 0.001645 | 0.00041228
53 | 0.99093 | -0.17425 | 0 | 0
54 | 0.98976 | -0.19696 | 0.011517 | 0.0028864
55 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022518 | -0.00056435 | 0.002252 | 0.00056389 | 1.9323e-07 | -4.5501e-07 | 0.0033842 | 0.003384 | 0.0033842 | 0.99008 | -0.19078 | 0.99017 | -0.18898 | 0.92974
1 | -0.028648 | -0.0071893 | 0.028676 | 0.0072064 | 2.7579e-05 | 1.714e-05 | 0.043056 | 0.043056 | 0.043056 | 0.99017 | -0.18898 | 0.99121 | -0.16881 | 11.8285
2 | 0.026397 | 0.0066254 | -0.026376 | -0.0066127 | 2.0496e-05 | 1.2671e-05 | 0.039672 | 0.039672 | 0.039672 | 0.99017 | -0.18898 | 0.98933 | -0.20527 | 10.8989
3 | -0.011741 | -0.0029426 | 0.011742 | 0.0029433 | 1.2198e-06 | 6.4405e-07 | 0.017572 | 0.017572 | 0.017572 | 0.99427 | -0.11003 | 0.99438 | -0.10785 | 4.8275
4 | 0.0020376 | 0.00051024 | -0.0020375 | -0.00051044 | 6.6997e-08 | -2.0641e-07 | 0.003049 | 0.003049 | 0.003049 | 0.99438 | -0.10785 | 0.99434 | -0.10854 | 0.83765
5 | -0.01378 | -0.0034535 | 0.013786 | 0.0034568 | 5.8611e-06 | 3.2741e-06 | 0.020621 | 0.020621 | 0.020621 | 0.99438 | -0.10785 | 0.99484 | -0.098922 | 5.6651
6 | -0.011603 | -0.0029081 | 0.011608 | 0.0029106 | 4.8032e-06 | 2.5197e-06 | 0.01734 | 0.01734 | 0.01734 | 0.99572 | -0.082134 | 0.99617 | -0.073448 | 4.7638
7 | -0.011608 | -0.0029106 | 0.011611 | 0.0029121 | 2.8426e-06 | 1.4909e-06 | 0.01734 | 0.01734 | 0.01734 | 0.99617 | -0.073448 | 0.99643 | -0.068311 | 4.7637
8 | -0.01226 | -0.0030726 | 0.012262 | 0.0030739 | 2.4815e-06 | 1.3379e-06 | 0.018435 | 0.018435 | 0.018435 | 0.98958 | -0.2004 | 0.9898 | -0.19616 | 5.0645
9 | -0.012262 | -0.0030739 | 0.012265 | 0.0030757 | 3.3391e-06 | 1.8001e-06 | 0.018435 | 0.018434 | 0.018435 | 0.9898 | -0.19616 | 0.9901 | -0.19044 | 5.0644
10 | -0.023355 | -0.0058554 | 0.023363 | 0.0058604 | 8.2581e-06 | 5.0493e-06 | 0.034878 | 0.034877 | 0.034878 | 0.99643 | -0.068311 | 0.99682 | -0.060893 | 9.5817
11 | -0.011744 | -0.0029433 | 0.011746 | 0.0029443 | 1.8789e-06 | 9.9178e-07 | 0.017569 | 0.017569 | 0.017569 | 0.99467 | -0.10228 | 0.99484 | -0.098922 | 4.8266
12 | -0.025532 | -0.0064011 | 0.025545 | 0.0064095 | 1.3651e-05 | 8.4127e-06 | 0.038189 | 0.038189 | 0.038189 | 0.99484 | -0.098922 | 0.99542 | -0.087707 | 10.4916
13 | -0.064286 | -0.016162 | 0.064397 | 0.016233 | 0.00011103 | 7.064e-05 | 0.096116 | 0.096116 | 0.096116 | 0.99542 | -0.087707 | 0.9973 | -0.051608 | 26.4054
14 | 0.03874 | 0.0097528 | -0.038718 | -0.0097388 | 2.2278e-05 | 1.4028e-05 | 0.057926 | 0.057927 | 0.057927 | 0.99542 | -0.087707 | 0.9948 | -0.099745 | 15.9139
15 | 0.0020375 | 0.00051044 | -0.0020375 | -0.00051064 | 6.2402e-08 | -1.9223e-07 | 0.003049 | 0.0030491 | 0.0030491 | 0.99434 | -0.10854 | 0.99431 | -0.10918 | 0.83767
16 | -0.023363 | -0.0058604 | 0.023373 | 0.0058667 | 1.0346e-05 | 6.3254e-06 | 0.034877 | 0.034877 | 0.034877 | 0.99682 | -0.060893 | 0.9973 | -0.051608 | 9.5817
17 | -0.1784 | -0.045033 | 0.17869 | 0.045223 | 0.00029748 | 0.0001898 | 0.26629 | 0.26629 | 0.26629 | 0.9973 | -0.051608 | 0.99912 | -0.016861 | 36.5784
18 | 0.090627 | 0.022933 | -0.090432 | -0.022809 | 0.00019547 | 0.00012473 | 0.1353 | 0.1353 | 0.1353 | 0.9973 | -0.051608 | 0.99495 | -0.096654 | 37.1698
19 | 0.036245 | 0.009119 | -0.036228 | -0.0091083 | 1.6982e-05 | 1.0669e-05 | 0.054227 | 0.054228 | 0.054228 | 0.9948 | -0.099745 | 0.99429 | -0.10956 | 14.8977
20 | -0.0049464 | -0.0012393 | 0.0049469 | 0.0012393 | 5.3055e-07 | 4.7883e-09 | 0.0074033 | 0.0074032 | 0.0074033 | 0.99417 | -0.11181 | 0.99429 | -0.10956 | 2.0339
21 | 0.0049464 | 0.0012393 | -0.0049463 | -0.0012393 | 1.0553e-07 | 9.6309e-10 | 0.0074033 | 0.0074033 | 0.0074033 | 0.99417 | -0.11181 | 0.99415 | -0.11226 | 2.0339
22 | 0.031281 | 0.007869 | -0.03127 | -0.0078619 | 1.139e-05 | 7.1102e-06 | 0.046824 | 0.046824 | 0.046824 | 0.99429 | -0.10956 | 0.99389 | -0.11718 | 12.8639
23 | 0.0023834 | 0.00059696 | -0.0023832 | -0.00059729 | 1.5949e-07 | -3.3124e-07 | 0.0035672 | 0.0035674 | 0.0035674 | 0.99415 | -0.11226 | 0.99408 | -0.11366 | 0.98005
24 | 0.082948 | 0.020933 | -0.082769 | -0.020819 | 0.0001782 | 0.00011365 | 0.1241 | 0.1241 | 0.1241 | 0.99495 | -0.096654 | 0.99262 | -0.14162 | 34.0947
25 | 0.0074843 | 0.0018758 | -0.0074836 | -0.0018756 | 7.4735e-07 | 2.7175e-07 | 0.011193 | 0.011193 | 0.011193 | 0.99495 | -0.096654 | 0.99484 | -0.09875 | 3.0751
26 | 0.046918 | 0.011799 | -0.046869 | -0.011768 | 4.9209e-05 | 3.1151e-05 | 0.070348 | 0.070348 | 0.070348 | 0.99262 | -0.14162 | 0.99148 | -0.1636 | 19.3264
27 | 0.035851 | 0.0090203 | -0.03583 | -0.0090066 | 2.1874e-05 | 1.3739e-05 | 0.053757 | 0.053757 | 0.053757 | 0.99262 | -0.14162 | 0.99196 | -0.15439 | 14.7684
28 | -0.18409 | -0.046576 | 0.18424 | 0.046671 | 0.00014908 | 9.5135e-05 | 0.27433 | 0.27433 | 0.27433 | 0.99912 | -0.016861 | 1 | 0 | 37.6829
29 | 0.034723 | 0.0087193 | -0.034698 | -0.0087036 | 2.5095e-05 | 1.5744e-05 | 0.052118 | 0.052118 | 0.052118 | 0.99148 | -0.1636 | 0.9907 | -0.17876 | 14.3182
30 | 0.012146 | 0.0030482 | -0.01214 | -0.0030449 | 6.1651e-06 | 3.308e-06 | 0.01823 | 0.01823 | 0.01823 | 0.99148 | -0.1636 | 0.99093 | -0.17425 | 5.0083
31 | 0.028696 | 0.0072187 | -0.028676 | -0.0072064 | 1.9753e-05 | 1.2276e-05 | 0.043056 | 0.043056 | 0.043056 | 0.99196 | -0.15439 | 0.99121 | -0.16881 | 11.8285
32 | 0.01152 | 0.0028883 | -0.01152 | -0.002888 | 4.9735e-07 | 2.6141e-07 | 0.017314 | 0.017314 | 0.017314 | 0.9901 | -0.19044 | 0.99005 | -0.19135 | 4.7567
33 | -0.023786 | -0.005964 | 0.023799 | 0.0059721 | 1.3249e-05 | 8.1239e-06 | 0.035749 | 0.035749 | 0.035749 | 0.9901 | -0.19044 | 0.9907 | -0.17876 | 9.8211
34 | 0.01152 | 0.002888 | -0.011517 | -0.0028864 | 3.0781e-06 | 1.618e-06 | 0.017314 | 0.017315 | 0.017315 | 0.99005 | -0.19135 | 0.98976 | -0.19696 | 4.7567
35 | 0.028876 | 0.0072621 | -0.028856 | -0.0072495 | 2.0211e-05 | 1.2562e-05 | 0.043241 | 0.043242 | 0.043242 | 0.99389 | -0.11718 | 0.99313 | -0.13185 | 11.8795
36 | 0.02424 | 0.0060863 | -0.024238 | -0.006085 | 1.9759e-06 | 1.2131e-06 | 0.036348 | 0.036348 | 0.036348 | 0.99243 | -0.14546 | 0.99234 | -0.14717 | 9.9858
37 | -0.026353 | -0.006616 | 0.02637 | 0.0066265 | 1.7126e-05 | 1.0582e-05 | 0.039517 | 0.039517 | 0.039517 | 0.99243 | -0.14546 | 0.99313 | -0.13185 | 10.8564
38 | 0.019353 | 0.0048608 | -0.019347 | -0.004857 | 6.4327e-06 | 3.8539e-06 | 0.029024 | 0.029024 | 0.029024 | 0.99234 | -0.14717 | 0.99198 | -0.15414 | 7.9736
39 | 0.019347 | 0.004857 | -0.019342 | -0.0048543 | 4.5365e-06 | 2.718e-06 | 0.029024 | 0.029024 | 0.029024 | 0.99198 | -0.15414 | 0.99173 | -0.15905 | 7.9736
40 | 0.019342 | 0.0048543 | -0.019335 | -0.0048497 | 7.5755e-06 | 4.5391e-06 | 0.029024 | 0.029024 | 0.029024 | 0.99173 | -0.15905 | 0.9913 | -0.16727 | 7.9736
41 | 0.016999 | 0.0042645 | -0.016996 | -0.0042623 | 3.693e-06 | 2.1686e-06 | 0.025519 | 0.025519 | 0.025519 | 0.9913 | -0.16727 | 0.99107 | -0.17183 | 7.0106
42 | -0.005964 | -0.0014947 | 0.0059647 | 0.0014949 | 6.484e-07 | 1.3915e-07 | 0.0089714 | 0.0089713 | 0.0089714 | 0.98921 | -0.20756 | 0.98933 | -0.20527 | 2.4647
43 | 0.020411 | 0.0051178 | -0.020405 | -0.005114 | 6.3607e-06 | 3.8398e-06 | 0.030701 | 0.030701 | 0.030701 | 0.98933 | -0.20527 | 0.98899 | -0.21182 | 8.4343
44 | 0.0064643 | 0.0016201 | -0.0064639 | -0.00162 | 4.422e-07 | 1.2306e-07 | 0.0097261 | 0.0097261 | 0.0097261 | 0.98899 | -0.21182 | 0.98892 | -0.21325 | 2.672
45 | 0.0064639 | 0.00162 | -0.0064634 | -0.0016199 | 4.8249e-07 | 1.343e-07 | 0.0097261 | 0.0097262 | 0.0097262 | 0.98892 | -0.21325 | 0.98884 | -0.21482 | 2.672
46 | 0.0024216 | 0.00060669 | -0.0024215 | -0.00060688 | 9.2626e-08 | -1.8998e-07 | 0.0036044 | 0.0036045 | 0.0036045 | 0.99969 | -0.0060127 | 0.99965 | -0.0068157 | 0.99024
47 | -0.0079172 | -0.001984 | 0.0079176 | 0.0019842 | 4.029e-07 | 1.5642e-07 | 0.011785 | 0.011785 | 0.011785 | 0.99969 | -0.0060127 | 0.99974 | -0.0049444 | 3.2375
48 | -0.010483 | -0.0026272 | 0.010486 | 0.0026284 | 2.4697e-06 | 1.2258e-06 | 0.015603 | 0.015603 | 0.015603 | 0.99974 | -0.0049444 | 1 | 0 | 4.2866
49 | 0.016996 | 0.0042623 | -0.016987 | -0.0042574 | 8.2462e-06 | 4.8426e-06 | 0.025519 | 0.025519 | 0.025519 | 0.99107 | -0.17183 | 0.99054 | -0.18201 | 7.0107
50 | 0.0021226 | 0.00053187 | -0.0021225 | -0.00053196 | 3.3664e-08 | -9.1835e-08 | 0.0031905 | 0.0031905 | 0.0031905 | 0.98994 | -0.19344 | 0.98993 | -0.19377 | 0.87652
51 | -0.010485 | -0.0026276 | 0.010487 | 0.0026286 | 1.922e-06 | 9.6472e-07 | 0.01576 | 0.01576 | 0.01576 | 0.98994 | -0.19344 | 0.99014 | -0.18959 | 4.3296
52 | -0.010487 | -0.0026286 | 0.010492 | 0.0026315 | 5.7853e-06 | 2.9032e-06 | 0.01576 | 0.015759 | 0.01576 | 0.99014 | -0.18959 | 0.99074 | -0.17802 | 4.3296
53 | -0.012137 | -0.0030438 | 0.01214 | 0.0030449 | 2.1813e-06 | 1.1706e-06 | 0.01823 | 0.01823 | 0.01823 | 0.99074 | -0.17802 | 0.99093 | -0.17425 | 5.0083

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.19901 | 0.049959

## res_load
| p_mw | q_mvar
0 | 0.0022518 | 0.00056435
1 | 0.011741 | 0.0029426
2 | 0.011603 | 0.0029081
3 | 0.01226 | 0.0030726
4 | 0.011744 | 0.0029433
5 | 0.011744 | 0.0029433
6 | 0.002473 | 0.00061979
7 | 0.0025629 | 0.00064232
8 | 0.0020375 | 0.00051064
9 | 0.0074836 | 0.0018756
10 | 0.0053991 | 0.0013531
11 | 0.0071338 | 0.0017879
12 | 0.010899 | 0.0027315
13 | 0.0023832 | 0.00059729
14 | 0.0023933 | 0.00059981
15 | 0.0021136 | 0.00052971
16 | 0.0048847 | 0.0012242
17 | 0.0024858 | 0.00062299
18 | 0.0023352 | 0.00058526
19 | 0.005964 | 0.0014947
20 | 0.013941 | 0.0034938
21 | 0.0054957 | 0.0013773
22 | 0.0024215 | 0.00060688
23 | 0.0025656 | 0.00064301
24 | 0.0026305 | 0.00065927
25 | 0.016987 | 0.0042574
26 | 0.0064634 | 0.0016199
27 | 0.0083621 | 0.0020957
28 | 0.0021225 | 0.00053196
29 | 0.001645 | 0.00041228
30 | 0.011517 | 0.0028864

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1