## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_192-8_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_192-8_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_192-8_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_192-8_0_6_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_192-8_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_192-8_0_6_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_192-8_0_6_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_192-8_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_192-8_0_6_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_192-8_0_6_node_62 | 0.4 | n |  | TRUE
10 | bus_LV_192-8_0_6_node_101 | 0.4 | n |  | TRUE
11 | bus_LV_192-8_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_192-8_0_6_node_74 | 0.4 | n |  | TRUE
13 | bus_LV_192-8_0_6_node_66 | 0.4 | n |  | TRUE
14 | bus_LV_192-8_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_192-8_0_6_node_73 | 0.4 | n |  | TRUE
16 | bus_LV_192-8_0_6_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_192-8_0_6_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_192-8_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_192-8_0_6_node_108 | 0.4 | n |  | TRUE
20 | bus_LV_192-8_0_6_node_111 | 0.4 | n |  | TRUE
21 | bus_LV_192-8_0_6_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_192-8_0_6_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_192-8_0_6_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_192-8_0_6_node_105 | 0.4 | n |  | TRUE
25 | bus_LV_192-8_0_6_node_106 | 0.4 | n |  | TRUE
26 | bus_LV_192-8_0_6_node_104 | 0.4 | n |  | TRUE
27 | bus_LV_192-8_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_192-8_0_6_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_192-8_0_6_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_192-8_0_6_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_192-8_0_6_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_192-8_0_6_node_103 | 0.4 | n |  | TRUE
33 | bus_LV_192-8_0_6_node_102 | 0.4 | n |  | TRUE
34 | bus_LV_192-8_0_6_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_192-8_0_6_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_192-8_0_6_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_192-8_0_6_node_115 | 0.4 | n |  | TRUE
38 | bus_LV_192-8_0_6_node_116 | 0.4 | n |  | TRUE
39 | bus_LV_192-8_0_6_node_120 | 0.4 | n |  | TRUE
40 | bus_LV_192-8_0_6_node_122 | 0.4 | n |  | TRUE
41 | bus_LV_192-8_0_6_node_123 | 0.4 | n |  | TRUE
42 | bus_LV_192-8_0_6_node_67 | 0.4 | n |  | TRUE
43 | bus_LV_192-8_0_6_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_192-8_0_6_node_118 | 0.4 | n |  | TRUE
45 | bus_LV_192-8_0_6_node_107 | 0.4 | n |  | TRUE
46 | bus_LV_192-8_0_6_node_113 | 0.4 | n |  | TRUE
47 | bus_LV_192-8_0_6_node_109 | 0.4 | n |  | TRUE
48 | bus_LV_192-8_0_6_node_100 | 0.4 | n |  | TRUE
49 | bus_LV_192-8_0_6_node_14 | 0.4 | n |  | TRUE
50 | bus_LV_192-8_0_6_node_16 | 0.4 | n |  | TRUE
51 | bus_LV_192-8_0_6_node_23 | 0.4 | n |  | TRUE
52 | bus_LV_192-8_0_6_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_192-8_0_6_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_192-8_0_6_node_21 | 0.4 | n |  | TRUE
55 | bus_LV_192-8_0_6_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_192-8_0_6_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_192-8_0_6_node_18 | 0.4 | n |  | TRUE
58 | bus_LV_192-8_0_6_node_19 | 0.4 | n |  | TRUE
59 | bus_LV_192-8_0_6_node_20 | 0.4 | n |  | TRUE
60 | bus_LV_192-8_0_6_node_22 | 0.4 | n |  | TRUE
61 | bus_LV_192-8_0_6_node_26 | 0.4 | n |  | TRUE
62 | bus_LV_192-8_0_6_node_27 | 0.4 | n |  | TRUE
63 | bus_LV_192-8_0_6_node_28 | 0.4 | n |  | TRUE
64 | bus_LV_192-8_0_6_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_192-8_0_6_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_192-8_0_6_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_192-8_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_192-8_0_6_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_192-8_0_6_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_192-8_0_6_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_192-8_0_6_node_34 | 0.4 | n |  | TRUE
72 | bus_LV_192-8_0_6_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_192-8_0_6_node_36 | 0.4 | n |  | TRUE
74 | bus_LV_192-8_0_6_node_38 | 0.4 | n |  | TRUE
75 | bus_LV_192-8_0_6_node_39 | 0.4 | n |  | TRUE
76 | bus_LV_192-8_0_6_node_125 | 0.4 | n |  | TRUE
77 | bus_LV_192-8_0_6_node_110 | 0.4 | n |  | TRUE
78 | bus_LV_192-8_0_6_node_112 | 0.4 | n |  | TRUE
79 | bus_LV_192-8_0_6_node_124 | 0.4 | n |  | TRUE
80 | bus_LV_192-8_0_6_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_192-8_0_6_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_192-8_0_6_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_192-8_0_6_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_192-8_0_6_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_192-8_0_6_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_192-8_0_6_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_192-8_0_6_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_192-8_0_6_node_119 | 0.4 | n |  | TRUE
89 | bus_LV_192-8_0_6_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_192-8_0_6_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_192-8_0_6_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_192-8_0_6_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_192-8_0_6_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_192-8_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_192-8_0_6_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_192-8_0_6_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_192-8_0_6_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_192-8_0_6_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_192-8_0_6_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_192-8_0_6_node_86 | 0.4 | n |  | TRUE
101 | bus_LV_192-8_0_6_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_192-8_0_6_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_192-8_0_6_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_192-8_0_6_node_84 | 0.4 | n |  | TRUE
105 | bus_LV_192-8_0_6_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_192-8_0_6_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_192-8_0_6_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_192-8_0_6_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_192-8_0_6_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_192-8_0_6_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_192-8_0_6_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_192-8_0_6_node_117 | 0.4 | n |  | TRUE
113 | bus_LV_192-8_0_6_node_97 | 0.4 | n |  | TRUE
114 | bus_LV_192-8_0_6_node_95 | 0.4 | n |  | TRUE
115 | bus_MV_356_0_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_192-8_0_6_load_0 | 0 | 0.0032435 | 0.0008129 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_192-8_0_6_load_3 | 2 | 0.0069443 | 0.0017404 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_192-8_0_6_load_43 | 6 | 0.0021294 | 0.00053367 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_192-8_0_6_load_62 | 9 | 0.0093412 | 0.0023411 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_192-8_0_6_load_101 | 10 | 0.0085276 | 0.0021372 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_192-8_0_6_load_74 | 12 | 0.019021 | 0.0047672 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_192-8_0_6_load_73 | 15 | 0.027761 | 0.0069575 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_192-8_0_6_load_42 | 16 | 0.0046991 | 0.0011777 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_192-8_0_6_load_40 | 17 | 0.012178 | 0.0030522 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_192-8_0_6_load_108 | 19 | 0.0011245 | 0.00028181 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_192-8_0_6_load_105 | 24 | 0.0058135 | 0.001457 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_192-8_0_6_load_106 | 25 | 0.024559 | 0.0061551 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_192-8_0_6_load_104 | 26 | 0.0047842 | 0.001199 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_192-8_0_6_load_13 | 28 | 0.0044754 | 0.0011217 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_192-8_0_6_load_103 | 32 | 0.0059608 | 0.0014939 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_192-8_0_6_load_102 | 33 | 0.0019146 | 0.00047985 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_192-8_0_6_load_45 | 35 | 0.0035064 | 0.00087879 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_192-8_0_6_load_51 | 36 | 0.0021387 | 0.000536 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_192-8_0_6_load_120 | 39 | 0.0023121 | 0.00057948 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_192-8_0_6_load_122 | 40 | 0.018152 | 0.0045493 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_192-8_0_6_load_123 | 41 | 0.0023722 | 0.00059453 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_192-8_0_6_load_118 | 44 | 0.024562 | 0.0061559 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_192-8_0_6_load_107 | 45 | 0.007242 | 0.001815 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_192-8_0_6_load_109 | 47 | 0.0058868 | 0.0014754 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_192-8_0_6_load_100 | 48 | 0.0028037 | 0.00070267 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_192-8_0_6_load_14 | 49 | 0.0028967 | 0.00072598 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_192-8_0_6_load_50 | 52 | 0.0066844 | 0.0016753 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_192-8_0_6_load_21 | 54 | 0.00066952 | 0.0001678 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_192-8_0_6_load_49 | 55 | 0.0031197 | 0.00078186 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_192-8_0_6_load_59 | 56 | 0.0024393 | 0.00061135 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_192-8_0_6_load_18 | 57 | 0.0016253 | 0.00040735 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_192-8_0_6_load_19 | 58 | 0.001381 | 0.00034612 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_192-8_0_6_load_22 | 60 | 0.0027268 | 0.00068339 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_192-8_0_6_load_26 | 61 | 0.0026692 | 0.00066897 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_192-8_0_6_load_27 | 62 | 0.001793 | 0.00044938 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_192-8_0_6_load_28 | 63 | 0.0012586 | 0.00031542 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_192-8_0_6_load_54 | 66 | 0.0085431 | 0.0021411 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_192-8_0_6_load_121 | 68 | 0.00098574 | 0.00024705 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_192-8_0_6_load_44 | 69 | 0.0014144 | 0.00035449 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_192-8_0_6_load_58 | 70 | 0.0043107 | 0.0010804 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_192-8_0_6_load_34 | 71 | 0.0076485 | 0.0019169 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_192-8_0_6_load_35 | 72 | 0.0039055 | 0.00097882 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_192-8_0_6_load_38 | 74 | 0.0050948 | 0.0012769 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_192-8_0_6_load_125 | 76 | 0.00084473 | 0.00021171 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_192-8_0_6_load_112 | 78 | 0.006466 | 0.0016205 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_192-8_0_6_load_124 | 79 | 0.001214 | 0.00030425 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_192-8_0_6_load_72 | 80 | 0.08665 | 0.021717 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_192-8_0_6_load_46 | 82 | 0.0016503 | 0.00041361 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_192-8_0_6_load_47 | 83 | 0.0029649 | 0.00074307 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_192-8_0_6_load_48 | 84 | 0.0066336 | 0.0016625 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_192-8_0_6_load_55 | 86 | 0.0017842 | 0.00044715 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_192-8_0_6_load_56 | 87 | 0.0014132 | 0.00035418 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_192-8_0_6_load_119 | 88 | 0.0065961 | 0.0016531 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_192-8_0_6_load_68 | 89 | 0.032916 | 0.0082497 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_192-8_0_6_load_75 | 90 | 0.0018519 | 0.00046413 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_192-8_0_6_load_77 | 92 | 0.00074874 | 0.00018765 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_192-8_0_6_load_78 | 93 | 0.00075767 | 0.00018989 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_192-8_0_6_load_79 | 94 | 0.00070015 | 0.00017548 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_192-8_0_6_load_80 | 95 | 0.00095241 | 0.0002387 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_192-8_0_6_load_94 | 98 | 0.0026878 | 0.00067361 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_192-8_0_6_load_89 | 101 | 0.0012361 | 0.00030979 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_192-8_0_6_load_91 | 102 | 0.0010153 | 0.00025445 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_192-8_0_6_load_84 | 104 | 0.0011119 | 0.00027868 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_192-8_0_6_load_90 | 105 | 0.0013269 | 0.00033255 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_192-8_0_6_load_85 | 106 | 0.0010057 | 0.00025205 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_192-8_0_6_load_87 | 107 | 0.0014376 | 0.0003603 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_192-8_0_6_load_92 | 108 | 0.00078037 | 0.00019558 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_192-8_0_6_load_99 | 109 | 0.0011615 | 0.0002911 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_192-8_0_6_load_98 | 110 | 0.0014727 | 0.0003691 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_192-8_0_6_load_93 | 111 | 0.0016414 | 0.00041138 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_192-8_0_6_load_117 | 112 | 0.0038831 | 0.0009732 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_192-8_0_6_load_95 | 114 | 0.0017072 | 0.00042787 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_192-8_0_6_line_0 |  | 0 | 1 | 0.027966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_192-8_0_6_line_1 |  | 1 | 2 | 0.019634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_192-8_0_6_line_2 |  | 2 | 3 | 0.022945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_192-8_0_6_line_3 |  | 3 | 27 | 0.037309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_192-8_0_6_line_4 |  | 3 | 28 | 0.012696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_192-8_0_6_line_5 |  | 4 | 5 | 0.075608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_192-8_0_6_line_6 |  | 4 | 6 | 0.006031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_192-8_0_6_line_7 |  | 5 | 10 | 0.032289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_192-8_0_6_line_8 |  | 7 | 8 | 0.009175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_192-8_0_6_line_9 |  | 7 | 9 | 0.023018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_192-8_0_6_line_10 |  | 8 | 34 | 0.013677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_192-8_0_6_line_11 |  | 8 | 35 | 0.030149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_192-8_0_6_line_12 |  | 9 | 29 | 0.037804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_192-8_0_6_line_13 |  | 10 | 16 | 0.029124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_192-8_0_6_line_14 |  | 11 | 12 | 0.021899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_192-8_0_6_line_15 |  | 11 | 13 | 0.040588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_192-8_0_6_line_16 |  | 11 | 14 | 0.045839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_192-8_0_6_line_17 |  | 11 | 15 | 0.032194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_192-8_0_6_line_18 |  | 13 | 41 | 0.017692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_192-8_0_6_line_19 |  | 13 | 38 | 0.016994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_192-8_0_6_line_20 |  | 14 | 16 | 0.029858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_192-8_0_6_line_21 |  | 14 | 17 | 0.015908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_192-8_0_6_line_22 |  | 15 | 43 | 0.015583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_192-8_0_6_line_23 |  | 17 | 21 | 0.018788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_192-8_0_6_line_24 |  | 18 | 19 | 0.022478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_192-8_0_6_line_25 |  | 18 | 20 | 0.050102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_192-8_0_6_line_26 |  | 19 | 45 | 0.023058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_192-8_0_6_line_27 |  | 20 | 46 | 0.026392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_192-8_0_6_line_28 |  | 20 | 47 | 0.001742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_192-8_0_6_line_29 |  | 21 | 22 | 0.010001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_192-8_0_6_line_30 |  | 22 | 26 | 0.013742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_192-8_0_6_line_31 |  | 23 | 24 | 0.0047207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_192-8_0_6_line_32 |  | 23 | 25 | 0.046104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_192-8_0_6_line_33 |  | 23 | 26 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_192-8_0_6_line_34 |  | 24 | 45 | 0.020806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_192-8_0_6_line_35 |  | 25 | 48 | 0.10416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_192-8_0_6_line_36 |  | 27 | 52 | 0.023057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_192-8_0_6_line_37 |  | 27 | 53 | 0.029214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_192-8_0_6_line_38 |  | 28 | 49 | 0.013436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_192-8_0_6_line_39 |  | 29 | 30 | 0.019349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_192-8_0_6_line_40 |  | 30 | 68 | 0.022396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_192-8_0_6_line_41 |  | 31 | 32 | 0.021747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_192-8_0_6_line_42 |  | 31 | 33 | 0.033499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_192-8_0_6_line_43 |  | 33 | 70 | 0.018588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_192-8_0_6_line_44 |  | 34 | 36 | 0.019089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_192-8_0_6_line_45 |  | 35 | 69 | 0.027219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_192-8_0_6_line_46 |  | 36 | 67 | 0.012029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_192-8_0_6_line_47 |  | 37 | 38 | 0.039397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_192-8_0_6_line_48 |  | 37 | 39 | 0.036343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_192-8_0_6_line_49 |  | 38 | 40 | 0.016956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_192-8_0_6_line_50 |  | 39 | 68 | 0.0088301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_192-8_0_6_line_51 |  | 42 | 43 | 0.019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_192-8_0_6_line_52 |  | 42 | 44 | 0.021815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_192-8_0_6_line_53 |  | 43 | 81 | 0.031769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_192-8_0_6_line_54 |  | 44 | 88 | 0.0006309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_192-8_0_6_line_55 |  | 46 | 79 | 0.011534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_192-8_0_6_line_56 |  | 46 | 75 | 0.007038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_192-8_0_6_line_57 |  | 47 | 77 | 0.02697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_192-8_0_6_line_58 |  | 48 | 113 | 0.023174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_192-8_0_6_line_59 |  | 49 | 50 | 0.033505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_192-8_0_6_line_60 |  | 50 | 51 | 0.01334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_192-8_0_6_line_61 |  | 51 | 54 | 0.1486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_192-8_0_6_line_62 |  | 52 | 55 | 0.019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_192-8_0_6_line_63 |  | 53 | 56 | 0.0099407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_192-8_0_6_line_64 |  | 54 | 58 | 0.03316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_192-8_0_6_line_65 |  | 55 | 83 | 0.042947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_192-8_0_6_line_66 |  | 56 | 65 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_192-8_0_6_line_67 |  | 57 | 58 | 0.017822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_192-8_0_6_line_68 |  | 57 | 59 | 0.16106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_192-8_0_6_line_69 |  | 59 | 60 | 0.015817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_192-8_0_6_line_70 |  | 61 | 62 | 0.019873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_192-8_0_6_line_71 |  | 62 | 63 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_192-8_0_6_line_72 |  | 63 | 64 | 0.040677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_192-8_0_6_line_73 |  | 64 | 65 | 0.02138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_192-8_0_6_line_74 |  | 65 | 87 | 0.007902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_192-8_0_6_line_75 |  | 66 | 67 | 0.029245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_192-8_0_6_line_76 |  | 67 | 85 | 0.008718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_192-8_0_6_line_77 |  | 70 | 85 | 0.067143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_192-8_0_6_line_78 |  | 71 | 72 | 0.011394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_192-8_0_6_line_79 |  | 71 | 73 | 0.0023459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_192-8_0_6_line_80 |  | 73 | 74 | 0.009542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_192-8_0_6_line_81 |  | 73 | 75 | 0.016669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_192-8_0_6_line_82 |  | 75 | 76 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_192-8_0_6_line_83 |  | 77 | 78 | 0.023098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_192-8_0_6_line_84 |  | 80 | 81 | 0.026999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_192-8_0_6_line_85 |  | 81 | 89 | 0.010529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_192-8_0_6_line_86 |  | 82 | 83 | 0.02427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_192-8_0_6_line_87 |  | 82 | 84 | 0.0011047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_192-8_0_6_line_88 |  | 85 | 86 | 0.0098201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_192-8_0_6_line_89 |  | 86 | 87 | 0.023616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_192-8_0_6_line_90 |  | 90 | 91 | 0.026524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_192-8_0_6_line_91 |  | 91 | 92 | 0.015005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_192-8_0_6_line_92 |  | 92 | 93 | 0.014501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_192-8_0_6_line_93 |  | 93 | 94 | 0.0030405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_192-8_0_6_line_94 |  | 94 | 95 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_192-8_0_6_line_95 |  | 95 | 96 | 0.038392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_192-8_0_6_line_96 |  | 96 | 97 | 0.15719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_192-8_0_6_line_97 |  | 97 | 98 | 0.15116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_192-8_0_6_line_98 |  | 98 | 102 | 0.026714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_192-8_0_6_line_99 |  | 99 | 100 | 0.028999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_192-8_0_6_line_100 |  | 99 | 101 | 0.034579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_192-8_0_6_line_101 |  | 100 | 103 | 0.13434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_192-8_0_6_line_102 |  | 100 | 104 | 0.020945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_192-8_0_6_line_103 |  | 101 | 105 | 0.025448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_192-8_0_6_line_104 |  | 102 | 105 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_192-8_0_6_line_105 |  | 103 | 109 | 0.0082042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_192-8_0_6_line_106 |  | 103 | 110 | 0.013151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_192-8_0_6_line_107 |  | 104 | 106 | 0.050228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_192-8_0_6_line_108 |  | 106 | 107 | 0.0069149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_192-8_0_6_line_109 |  | 107 | 108 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_192-8_0_6_line_110 |  | 108 | 111 | 0.011413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_192-8_0_6_line_111 |  | 109 | 112 | 0.053429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_192-8_0_6_line_112 |  | 110 | 113 | 0.02331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_192-8_0_6_line_113 |  | 111 | 114 | 0.014839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_192-8_0_6_trafo_8 | 0.63 MVA 20/0.4 kV | 115 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2696399.9135 | 1238129.1418 | 2696403.2239 | 1238122.3682 | 2696403.9314 | 1238119.8 | 2696404.2469 | 1238117.1476 | 2696404.0553 | 1238113.5752 | 2696403.5223 | 1238110.0528 | 2696402.3399 | 1238103.6622 | 2696401.9764 | 1238102.2557
1 | 2696399.9135 | 1238129.1418 | 2696402.887 | 1238138.4525 | 2696404.1169 | 1238141.9195 | 2696405.0985 | 1238144.3706 | 2696406.4354 | 1238146.8386 | 2696406.8883 | 1238147.4165
2 | 2696426.8833 | 1238157.2561 | 2696423.594 | 1238156.68 | 2696420.4962 | 1238155.9514 | 2696417.2137 | 1238154.9529 | 2696414.7189 | 1238153.9005 | 2696412.3111 | 1238152.6161 | 2696410.2624 | 1238151.115 | 2696408.1476 | 1238149.0236 | 2696406.8883 | 1238147.4165
3 | 2696422.5308 | 1238194.1796 | 2696422.3905 | 1238189.307 | 2696422.4837 | 1238184.5049 | 2696422.8668 | 1238179.5519 | 2696423.554 | 1238174.5038 | 2696426.8833 | 1238157.2561
4 | 2696426.8833 | 1238157.2561 | 2696428.8245 | 1238144.7089
5 | 2696301.5996 | 1238147.9053 | 2696294.4798 | 1238150.7142 | 2696313.2703 | 1238202.2017 | 2696313.2903 | 1238209.8299 | 2696307.7843 | 1238210.1742
6 | 2696301.5996 | 1238147.9053 | 2696303.5476 | 1238153.613
7 | 2696307.7843 | 1238210.1742 | 2696305.106 | 1238208.3071 | 2696298.8248 | 1238208.4054 | 2696276.0965 | 1238209.193
8 | 2696341.7241 | 1238297.8344 | 2696349.2396 | 1238292.5412
9 | 2696341.7241 | 1238297.8344 | 2696339.8378 | 1238299.3827 | 2696331.7345 | 1238305.9339 | 2696324.2397 | 1238312.79
10 | 2696349.2396 | 1238292.5412 | 2696351.8339 | 1238300.0445 | 2696357.2514 | 1238298.1532
11 | 2696349.2396 | 1238292.5412 | 2696343.2817 | 1238276.9218 | 2696339.4413 | 1238264.0507
12 | 2696296.3463 | 1238338.3064 | 2696324.2397 | 1238312.79
13 | 2696246.9902 | 1238210.2016 | 2696276.0965 | 1238209.193
14 | 2696217.2663 | 1238238.1835 | 2696239.1586 | 1238238.7213
15 | 2696217.2663 | 1238238.1835 | 2696216.478 | 1238267.6705 | 2696227.5685 | 1238267.728
16 | 2696217.2663 | 1238238.1835 | 2696218.9085 | 1238235.3525 | 2696225.5184 | 1238223.851 | 2696227.2234 | 1238220.8875 | 2696227.7757 | 1238219.9513 | 2696238.3053 | 1238224.2807 | 2696236.4356 | 1238222.0043 | 2696230.9884 | 1238218.7247 | 2696228.2001 | 1238215.7106
17 | 2696217.2663 | 1238238.1835 | 2696205.2843 | 1238238.0449 | 2696197.9681 | 1238234.3125 | 2696187.4866 | 1238240.1501
18 | 2696227.486 | 1238285.4176 | 2696227.5685 | 1238267.728
19 | 2696227.5685 | 1238267.728 | 2696244.6124 | 1238267.8376
20 | 2696228.2001 | 1238215.7106 | 2696232.3267 | 1238216.9117 | 2696239.4828 | 1238220.7193 | 2696239.6464 | 1238210.6256 | 2696242.435 | 1238210.3595 | 2696246.9902 | 1238210.2016
21 | 2696228.2001 | 1238215.7106 | 2696224.6683 | 1238211.8838 | 2696215.4718 | 1238206.4126
22 | 2696173.8729 | 1238247.7322 | 2696187.4866 | 1238240.1501
23 | 2696199.325 | 1238196.8065 | 2696215.4718 | 1238206.4126
24 | 2696214.6417 | 1238134.9975 | 2696206.5205 | 1238138.9133 | 2696197.6978 | 1238149.0816
25 | 2696216.3237 | 1238085.8437 | 2696215.357 | 1238088.5412 | 2696214.0046 | 1238092.6223 | 2696212.7947 | 1238097.2506 | 2696211.6631 | 1238102.6474 | 2696211.2944 | 1238106.2552 | 2696211.1942 | 1238109.6339 | 2696211.3238 | 1238112.8384 | 2696211.6235 | 1238116.7573 | 2696212.3456 | 1238122.1508 | 2696213.3798 | 1238128.361 | 2696214.6417 | 1238134.9975
26 | 2696181.4504 | 1238165.4233 | 2696194.4852 | 1238152.7843 | 2696197.6978 | 1238149.0816
27 | 2696216.3237 | 1238085.8437 | 2696242.0617 | 1238092.0098
28 | 2696216.3237 | 1238085.8437 | 2696216.9904 | 1238084.2344
29 | 2696199.325 | 1238196.8065 | 2696192.5998 | 1238204.2253
30 | 2696192.5998 | 1238204.2253 | 2696182.2248 | 1238195.2148
31 | 2696169.695 | 1238183.3945 | 2696166.5133 | 1238179.907
32 | 2696169.695 | 1238183.3945 | 2696157.9036 | 1238195.7683 | 2696147.8002 | 1238206.6907 | 2696138.4129 | 1238217.2551
33 | 2696169.695 | 1238183.3945 | 2696173.1866 | 1238187.3651 | 2696182.2248 | 1238195.2148
34 | 2696166.5133 | 1238179.907 | 2696181.4504 | 1238165.4233
35 | 2696138.4129 | 1238217.2551 | 2696137.1346 | 1238218.6936 | 2696126.356 | 1238231.1395 | 2696109.3377 | 1238251.4014 | 2696092.6993 | 1238271.5694 | 2696071.823 | 1238297.334
36 | 2696422.5308 | 1238194.1796 | 2696418.6801 | 1238196.0184 | 2696402.0255 | 1238204.7183
37 | 2696428.5202 | 1238222.7537 | 2696425.2358 | 1238209.3014 | 2696424.0107 | 1238203.2103 | 2696423.1339 | 1238198.5037 | 2696422.5308 | 1238194.1796
38 | 2696428.8245 | 1238144.7089 | 2696430.5607 | 1238133.487 | 2696430.9386 | 1238131.441
39 | 2696296.3463 | 1238338.3064 | 2696277.2287 | 1238334.9829
40 | 2696277.2287 | 1238334.9829 | 2696277.2961 | 1238312.5868
41 | 2696451.9855 | 1238339.8442 | 2696446.7326 | 1238341.8492 | 2696443.4897 | 1238343.0753 | 2696431.541 | 1238347.4178
42 | 2696451.9855 | 1238339.8442 | 2696441.0904 | 1238317.0614 | 2696437.9763 | 1238309.4273
43 | 2696437.9763 | 1238309.4273 | 2696421.1558 | 1238317.3373
44 | 2696357.2514 | 1238298.1532 | 2696358.6833 | 1238297.5648 | 2696369.8302 | 1238291.8192 | 2696373.8788 | 1238288.8845
45 | 2696331.659 | 1238237.9677 | 2696339.4413 | 1238264.0507
46 | 2696383.6184 | 1238281.8244 | 2696373.8788 | 1238288.8845
47 | 2696244.6124 | 1238267.8376 | 2696244.6739 | 1238264.0468 | 2696260.1113 | 1238264.3194 | 2696277.4403 | 1238264.5783 | 2696277.4321 | 1238267.4136
48 | 2696277.4321 | 1238267.4136 | 2696277.3227 | 1238303.7568
49 | 2696244.6124 | 1238267.8376 | 2696244.6408 | 1238284.7937
50 | 2696277.3227 | 1238303.7568 | 2696277.2961 | 1238312.5868
51 | 2696173.8729 | 1238247.7322 | 2696173.7181 | 1238267.5556
52 | 2696173.7181 | 1238267.5556 | 2696173.5531 | 1238289.3699
53 | 2696144.9315 | 1238260.0061 | 2696153.4316 | 1238258.8429 | 2696173.8729 | 1238247.7322
54 | 2696173.5483 | 1238290.0007 | 2696173.5531 | 1238289.3699
55 | 2696242.0617 | 1238092.0098 | 2696238.9309 | 1238103.1118
56 | 2696248.4879 | 1238090.9131 | 2696245.4536 | 1238092.7987 | 2696242.0617 | 1238092.0098
57 | 2696230.25 | 1238060.8174 | 2696224.0985 | 1238070.1691 | 2696220.9745 | 1238075.7227 | 2696218.497 | 1238080.5973 | 2696216.9904 | 1238084.2344
58 | 2696057.2337 | 1238315.3394 | 2696071.823 | 1238297.334
59 | 2696444.1962 | 1238100.7951 | 2696438.5164 | 1238111.8333 | 2696436.0558 | 1238117.0528 | 2696433.33 | 1238123.2354 | 2696431.9749 | 1238127.0051 | 2696431.1995 | 1238130.0281 | 2696430.9386 | 1238131.441
60 | 2696450.3281 | 1238088.9414 | 2696444.1962 | 1238100.7951
61 | 2696450.3281 | 1238088.9414 | 2696496.0626 | 1238111.4121 | 2696502.2615 | 1238114.0593 | 2696506.0815 | 1238115.5002 | 2696508.7622 | 1238116.7558 | 2696510.7785 | 1238117.9228 | 2696512.6966 | 1238119.544 | 2696514.3249 | 1238121.3051 | 2696516.1566 | 1238124.048 | 2696517.2614 | 1238126.3677 | 2696518.0216 | 1238128.4705 | 2696520.3036 | 1238136.0911 | 2696521.2385 | 1238138.6193 | 2696522.3117 | 1238141.0163 | 2696523.7415 | 1238143.8194 | 2696525.2154 | 1238146.234 | 2696526.8754 | 1238148.3737 | 2696529.0917 | 1238150.7337 | 2696550.5085 | 1238170.8746 | 2696554.1433 | 1238174.403 | 2696560.4191 | 1238180.6505
62 | 2696384.8231 | 1238213.7043 | 2696402.0255 | 1238204.7183
63 | 2696428.5202 | 1238222.7537 | 2696426.0488 | 1238232.3822
64 | 2696584.8648 | 1238203.0423 | 2696577.1713 | 1238196.416 | 2696564.0679 | 1238184.2828 | 2696560.4191 | 1238180.6505
65 | 2696357.1014 | 1238184.4938 | 2696362.1729 | 1238194.011 | 2696376.5673 | 1238198.8815 | 2696384.8231 | 1238213.7043 | 2696384.8231 | 1238213.7043
66 | 2696420.3254 | 1238247.9616 | 2696425.2005 | 1238235.6872 | 2696426.0488 | 1238232.3822
67 | 2696599.2317 | 1238213.5427 | 2696596.5299 | 1238211.909 | 2696591.7939 | 1238208.6407 | 2696587.0799 | 1238204.9502 | 2696584.8648 | 1238203.0423
68 | 2696664.5765 | 1238345.7382 | 2696664.8628 | 1238342.0957 | 2696665.3408 | 1238335.9767 | 2696662.2278 | 1238315.2883 | 2696654.6181 | 1238263.1701 | 2696653.6685 | 1238258.2954 | 2696652.3165 | 1238253.5143 | 2696650.641 | 1238250.0066 | 2696648.7163 | 1238246.9397 | 2696646.2805 | 1238243.6643 | 2696643.1873 | 1238240.3337 | 2696639.6589 | 1238237.2518 | 2696635.6985 | 1238234.2073 | 2696630.6213 | 1238230.9889 | 2696610.2531 | 1238219.8938 | 2696602.0292 | 1238215.2343 | 2696599.2317 | 1238213.5427
69 | 2696664.5765 | 1238345.7382 | 2696660.4309 | 1238350.363 | 2696650.8249 | 1238350.2867
70 | 2696475.2742 | 1238297.5978 | 2696488.4294 | 1238312.4928
71 | 2696464.5774 | 1238283.0093 | 2696472.3886 | 1238294.3305 | 2696475.2742 | 1238297.5978
72 | 2696441.4766 | 1238249.5284 | 2696464.5774 | 1238283.0093
73 | 2696441.4766 | 1238249.5284 | 2696430.4694 | 1238247.1368 | 2696420.3254 | 1238247.9616
74 | 2696420.3254 | 1238247.9616 | 2696416.5407 | 1238252.726 | 2696415.2078 | 1238253.9614
75 | 2696383.6184 | 1238281.8244 | 2696389.1499 | 1238294.3457 | 2696393.6721 | 1238309.2301
76 | 2696390.685 | 1238276.6908 | 2696383.6184 | 1238281.8244
77 | 2696390.685 | 1238276.6908 | 2696405.8184 | 1238324.5499 | 2696421.1558 | 1238317.3373
78 | 2696266.8102 | 1238069.6164 | 2696264.6313 | 1238080.8005
79 | 2696262.6439 | 1238082.047 | 2696264.6313 | 1238080.8005
80 | 2696262.6439 | 1238082.047 | 2696258.9058 | 1238075.5483 | 2696256.9087 | 1238075.06
81 | 2696262.6439 | 1238082.047 | 2696248.4879 | 1238090.9131
82 | 2696248.4879 | 1238090.9131 | 2696252.7265 | 1238097.8091 | 2696251.6282 | 1238103.9515
83 | 2696230.25 | 1238060.8174 | 2696226.8456 | 1238058.4605 | 2696228.272 | 1238048.8876 | 2696230.915 | 1238043.1372 | 2696232.1158 | 1238040.4422
84 | 2696144.9315 | 1238260.0061 | 2696162.3447 | 1238239.3726
85 | 2696144.9315 | 1238260.0061 | 2696138.3723 | 1238268.2423
86 | 2696345.6879 | 1238163.0752 | 2696357.1014 | 1238184.4938
87 | 2696345.1683 | 1238162.1003 | 2696345.6879 | 1238163.0752
88 | 2696390.685 | 1238276.6908 | 2696397.8872 | 1238270.0153
89 | 2696397.8872 | 1238270.0153 | 2696415.2078 | 1238253.9614
90 | 2695783.352 | 1238161.3017 | 2695786.3725 | 1238134.9499
91 | 2695783.352 | 1238161.3017 | 2695782.5639 | 1238167.9383 | 2695781.6662 | 1238176.2111
92 | 2695781.6662 | 1238176.2111 | 2695781.3907 | 1238178.7497 | 2695781.2931 | 1238180.5828 | 2695781.2705 | 1238181.9835 | 2695781.3694 | 1238183.3527 | 2695781.7113 | 1238184.6703 | 2695782.1488 | 1238185.6893 | 2695782.8136 | 1238186.6896 | 2695785.1658 | 1238189.5025
93 | 2695787.1163 | 1238191.835 | 2695785.1658 | 1238189.5025
94 | 2695793.3748 | 1238204.2913 | 2695793.1261 | 1238203.0792 | 2695792.4413 | 1238200.5107 | 2695791.6504 | 1238198.4186 | 2695790.7811 | 1238196.4921 | 2695789.4435 | 1238194.5246 | 2695787.5641 | 1238192.3704 | 2695787.1163 | 1238191.835
95 | 2695799.3568 | 1238242.2088 | 2695795.8269 | 1238219.5017 | 2695794.339 | 1238210.9046 | 2695794.0541 | 1238208.3981 | 2695793.6662 | 1238205.7121 | 2695793.3748 | 1238204.2913
96 | 2695799.3568 | 1238242.2088 | 2695807.7325 | 1238297.018 | 2695812.2261 | 1238325.634 | 2695814.5662 | 1238343.763 | 2695816.6146 | 1238361.2201 | 2695818.3997 | 1238381.8643 | 2695818.7483 | 1238387.4518 | 2695818.8038 | 1238391.0443 | 2695818.6004 | 1238394.2656 | 2695818.0409 | 1238397.9927
97 | 2695818.0409 | 1238397.9927 | 2695827.9862 | 1238398.6759 | 2695836.3633 | 1238399.4895 | 2695843.6684 | 1238400.1634 | 2695848.0236 | 1238400.3227 | 2695851.328 | 1238400.4317 | 2695853.5496 | 1238400.601 | 2695855.2788 | 1238400.8068 | 2695856.8947 | 1238400.9997 | 2695858.5432 | 1238401.0486 | 2695860.1256 | 1238400.9741 | 2695861.6803 | 1238400.7434 | 2695863.1624 | 1238400.3226 | 2695864.3968 | 1238399.7754 | 2695865.4685 | 1238399.0033 | 2695866.5506 | 1238398.0534 | 2695867.4155 | 1238396.9665 | 2695868.5235 | 1238395.3499 | 2695870.0865 | 1238392.7287 | 2695873.0725 | 1238388.1957 | 2695881.2656 | 1238376.5193 | 2695883.9563 | 1238370.5917 | 2695886.5146 | 1238366.3076 | 2695900.4566 | 1238342.9931 | 2695908.3687 | 1238327.6428 | 2695912.2379 | 1238319.0211 | 2695916.3765 | 1238309.6476
98 | 2695925.0009 | 1238284.3749 | 2695921.7336 | 1238295.1011 | 2695916.3765 | 1238309.6476
99 | 2695956.2815 | 1238203.68 | 2695960.3061 | 1238200.8986 | 2695964.3526 | 1238198.64 | 2695967.2252 | 1238197.3855 | 2695969.7032 | 1238196.6695 | 2695973.0555 | 1238196.1677 | 2695975.5602 | 1238196.1415 | 2695978.1422 | 1238196.4835 | 2695981.0509 | 1238197.2088 | 2695983.2394 | 1238198.0225
100 | 2695956.2815 | 1238203.68 | 2695952.4428 | 1238207.1317 | 2695949.1328 | 1238210.6364 | 2695946.9599 | 1238213.5368 | 2695945.3889 | 1238216.18 | 2695943.7785 | 1238219.3897 | 2695942.4399 | 1238222.6261 | 2695941.3921 | 1238225.667 | 2695939.443 | 1238232.0402 | 2695939.1854 | 1238232.926
101 | 2696028.553 | 1238292.8367 | 2696025.9239 | 1238290.737 | 2696024.922 | 1238289.5311 | 2696024.1407 | 1238288.2508 | 2696023.5731 | 1238286.8628 | 2696023.1761 | 1238285.2107 | 2696023.0142 | 1238283.5291 | 2696023.1426 | 1238281.6742 | 2696023.4948 | 1238280.012 | 2696030.7482 | 1238256.7675 | 2696031.1218 | 1238255.1835 | 2696031.4476 | 1238253.7544 | 2696031.6204 | 1238251.9558 | 2696031.7405 | 1238250.1453 | 2696031.705 | 1238248.1321 | 2696031.5034 | 1238246.094 | 2696031.1553 | 1238244.2315 | 2696030.626 | 1238242.3437 | 2696030.0167 | 1238240.7216 | 2696029.0782 | 1238238.8717 | 2696027.9782 | 1238237.186 | 2696026.59 | 1238235.5401 | 2696024.9607 | 1238233.8347 | 2696019.4955 | 1238228.3867 | 2696017.5454 | 1238226.3982 | 2696016.1144 | 1238224.5959 | 2696014.185 | 1238221.796 | 2696012.1218 | 1238218.3823 | 2695999.6744 | 1238196.9652 | 2695997.142 | 1238193.088 | 2695993.2596 | 1238188.0104 | 2695983.2394 | 1238198.0225
102 | 2695983.2394 | 1238198.0225 | 2695985.4684 | 1238199.1372 | 2695987.4966 | 1238200.5043 | 2695989.6917 | 1238202.3189 | 2695991.7964 | 1238204.5657 | 2695993.7421 | 1238207.2992 | 2695995.1604 | 1238210.3577 | 2695996.2718 | 1238213.5216
103 | 2695939.1854 | 1238232.926 | 2695935.085 | 1238247.0254 | 2695932.3344 | 1238257.4325
104 | 2695932.3344 | 1238257.4325 | 2695926.6073 | 1238279.1012 | 2695925.0009 | 1238284.3749
105 | 2696028.553 | 1238292.8367 | 2696029.7259 | 1238284.7167
106 | 2696028.553 | 1238292.8367 | 2696035.5698 | 1238298.71 | 2696038.7434 | 1238301.1462
107 | 2695996.2718 | 1238213.5216 | 2695996.7082 | 1238214.7638 | 2695998.0271 | 1238218.8215 | 2695999.1906 | 1238223.5994 | 2696000.2623 | 1238229.3765 | 2696000.8391 | 1238234.4118 | 2696000.9636 | 1238239.8068 | 2696000.717 | 1238244.295 | 2696000.1598 | 1238249.2786 | 2695999.4359 | 1238253.3366 | 2695997.3509 | 1238262.866
108 | 2695997.3509 | 1238262.866 | 2695997.2056 | 1238263.5303 | 2695995.7903 | 1238269.6023
109 | 2695995.7903 | 1238269.6023 | 2695994.7991 | 1238273.8547 | 2695992.4477 | 1238283.5795 | 2695990.7497 | 1238290.2812
110 | 2695990.7497 | 1238290.2812 | 2695990.1526 | 1238292.638 | 2695987.6527 | 1238301.2652
111 | 2696029.7259 | 1238284.7167 | 2696030.1378 | 1238281.8652 | 2696040.0828 | 1238269.4835 | 2696049.565 | 1238263.2655 | 2696054.1699 | 1238257.8249 | 2696063.1324 | 1238252.8661 | 2696066.3486 | 1238247.8524
112 | 2696057.2337 | 1238315.3394 | 2696038.7434 | 1238301.1462
113 | 2695983.2306 | 1238315.429 | 2695983.6607 | 1238314.1824 | 2695987.2759 | 1238302.5655 | 2695987.6527 | 1238301.2652

## bus_geodata
| x | y | coords
0 | 2696401.9764 | 1238102.2557
1 | 2696399.9135 | 1238129.1418
2 | 2696406.8883 | 1238147.4165
3 | 2696426.8833 | 1238157.2561
4 | 2696301.5996 | 1238147.9053
5 | 2696307.7843 | 1238210.1742
6 | 2696303.5476 | 1238153.613
7 | 2696341.7241 | 1238297.8344
8 | 2696349.2396 | 1238292.5412
9 | 2696324.2397 | 1238312.79
10 | 2696276.0965 | 1238209.193
11 | 2696217.2663 | 1238238.1835
12 | 2696239.1586 | 1238238.7213
13 | 2696227.5685 | 1238267.728
14 | 2696228.2001 | 1238215.7106
15 | 2696187.4866 | 1238240.1501
16 | 2696246.9902 | 1238210.2016
17 | 2696215.4718 | 1238206.4126
18 | 2696214.6417 | 1238134.9975
19 | 2696197.6978 | 1238149.0816
20 | 2696216.3237 | 1238085.8437
21 | 2696199.325 | 1238196.8065
22 | 2696192.5998 | 1238204.2253
23 | 2696169.695 | 1238183.3945
24 | 2696166.5133 | 1238179.907
25 | 2696138.4129 | 1238217.2551
26 | 2696182.2248 | 1238195.2148
27 | 2696422.5308 | 1238194.1796
28 | 2696428.8245 | 1238144.7089
29 | 2696296.3463 | 1238338.3064
30 | 2696277.2287 | 1238334.9829
31 | 2696451.9855 | 1238339.8442
32 | 2696431.541 | 1238347.4178
33 | 2696437.9763 | 1238309.4273
34 | 2696357.2514 | 1238298.1532
35 | 2696339.4413 | 1238264.0507
36 | 2696373.8788 | 1238288.8845
37 | 2696277.4321 | 1238267.4136
38 | 2696244.6124 | 1238267.8376
39 | 2696277.3227 | 1238303.7568
40 | 2696244.6408 | 1238284.7937
41 | 2696227.486 | 1238285.4176
42 | 2696173.7181 | 1238267.5556
43 | 2696173.8729 | 1238247.7322
44 | 2696173.5531 | 1238289.3699
45 | 2696181.4504 | 1238165.4233
46 | 2696242.0617 | 1238092.0098
47 | 2696216.9904 | 1238084.2344
48 | 2696071.823 | 1238297.334
49 | 2696430.9386 | 1238131.441
50 | 2696444.1962 | 1238100.7951
51 | 2696450.3281 | 1238088.9414
52 | 2696402.0255 | 1238204.7183
53 | 2696428.5202 | 1238222.7537
54 | 2696560.4191 | 1238180.6505
55 | 2696384.8231 | 1238213.7043
56 | 2696426.0488 | 1238232.3822
57 | 2696599.2317 | 1238213.5427
58 | 2696584.8648 | 1238203.0423
59 | 2696664.5765 | 1238345.7382
60 | 2696650.8249 | 1238350.2867
61 | 2696488.4294 | 1238312.4928
62 | 2696475.2742 | 1238297.5978
63 | 2696464.5774 | 1238283.0093
64 | 2696441.4766 | 1238249.5284
65 | 2696420.3254 | 1238247.9616
66 | 2696393.6721 | 1238309.2301
67 | 2696383.6184 | 1238281.8244
68 | 2696277.2961 | 1238312.5868
69 | 2696331.659 | 1238237.9677
70 | 2696421.1558 | 1238317.3373
71 | 2696264.6313 | 1238080.8005
72 | 2696266.8102 | 1238069.6164
73 | 2696262.6439 | 1238082.047
74 | 2696256.9087 | 1238075.06
75 | 2696248.4879 | 1238090.9131
76 | 2696251.6282 | 1238103.9515
77 | 2696230.25 | 1238060.8174
78 | 2696232.1158 | 1238040.4422
79 | 2696238.9309 | 1238103.1118
80 | 2696162.3447 | 1238239.3726
81 | 2696144.9315 | 1238260.0061
82 | 2696345.6879 | 1238163.0752
83 | 2696357.1014 | 1238184.4938
84 | 2696345.1683 | 1238162.1003
85 | 2696390.685 | 1238276.6908
86 | 2696397.8872 | 1238270.0153
87 | 2696415.2078 | 1238253.9614
88 | 2696173.5483 | 1238290.0007
89 | 2696138.3723 | 1238268.2423
90 | 2695786.3725 | 1238134.9499
91 | 2695783.352 | 1238161.3017
92 | 2695781.6662 | 1238176.2111
93 | 2695785.1658 | 1238189.5025
94 | 2695787.1163 | 1238191.835
95 | 2695793.3748 | 1238204.2913
96 | 2695799.3568 | 1238242.2088
97 | 2695818.0409 | 1238397.9927
98 | 2695916.3765 | 1238309.6476
99 | 2695956.2815 | 1238203.68
100 | 2695983.2394 | 1238198.0225
101 | 2695939.1854 | 1238232.926
102 | 2695925.0009 | 1238284.3749
103 | 2696028.553 | 1238292.8367
104 | 2695996.2718 | 1238213.5216
105 | 2695932.3344 | 1238257.4325
106 | 2695997.3509 | 1238262.866
107 | 2695995.7903 | 1238269.6023
108 | 2695990.7497 | 1238290.2812
109 | 2696029.7259 | 1238284.7167
110 | 2696038.7434 | 1238301.1462
111 | 2695987.6527 | 1238301.2652
112 | 2696066.3486 | 1238247.8524
113 | 2696057.2337 | 1238315.3394
114 | 2695983.2306 | 1238315.429
115 | 2696216.478 | 1238267.6705

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97209 | -0.53781 | 0.0032435 | 0.0008129
1 | 0.97218 | -0.53613 | 0 | 0
2 | 0.97224 | -0.53496 | 0.0069443 | 0.0017404
3 | 0.97245 | -0.53065 | 0 | 0
4 | 0.99358 | -0.12243 | 0 | 0
5 | 0.99373 | -0.11958 | 0 | 0
6 | 0.99357 | -0.12265 | 0.0021294 | 0.00053367
7 | 0.98234 | -0.33712 | 0 | 0
8 | 0.98162 | -0.35108 | 0 | 0
9 | 0.98414 | -0.30217 | 0.0093412 | 0.0023411
10 | 0.99379 | -0.11837 | 0.0085276 | 0.0021372
11 | 1 | 0 | -0.45211 | -0.11489
12 | 0.99962 | -0.007263 | 0.019021 | 0.0047672
13 | 0.99779 | -0.041608 | 0 | 0
14 | 0.99449 | -0.1048 | 0 | 0
15 | 0.99737 | -0.050209 | 0.027761 | 0.0069575
16 | 0.99407 | -0.11289 | 0.0046991 | 0.0011777
17 | 0.9928 | -0.13712 | 0.012178 | 0.0030522
18 | 0.98492 | -0.28944 | 0 | 0
19 | 0.98557 | -0.2769 | 0.0011245 | 0.00028181
20 | 0.98349 | -0.31744 | 0 | 0
21 | 0.99102 | -0.17138 | 0 | 0
22 | 0.99007 | -0.18966 | 0 | 0
23 | 0.9872 | -0.24508 | 0 | 0
24 | 0.98701 | -0.2489 | 0.0058135 | 0.001457
25 | 0.98495 | -0.28877 | 0.024559 | 0.0061551
26 | 0.98877 | -0.21484 | 0.0047842 | 0.001199
27 | 0.97329 | -0.51417 | 0 | 0
28 | 0.97229 | -0.53387 | 0.0044754 | 0.0011217
29 | 0.98743 | -0.23875 | 0 | 0
30 | 0.98911 | -0.20645 | 0 | 0
31 | 0.9767 | -0.44721 | 0 | 0
32 | 0.97658 | -0.44958 | 0.0059608 | 0.0014939
33 | 0.97688 | -0.44356 | 0.0019146 | 0.00047985
34 | 0.98061 | -0.37071 | 0 | 0
35 | 0.98148 | -0.35376 | 0.0035064 | 0.00087879
36 | 0.9792 | -0.39818 | 0.0021387 | 0.000536
37 | 0.99511 | -0.092248 | 0 | 0
38 | 0.99689 | -0.05873 | 0 | 0
39 | 0.99184 | -0.1544 | 0.0023121 | 0.00057948
40 | 0.99661 | -0.06413 | 0.018152 | 0.0045493
41 | 0.99775 | -0.042343 | 0.0023722 | 0.00059453
42 | 0.99574 | -0.081662 | 0 | 0
43 | 0.9963 | -0.070808 | 0 | 0
44 | 0.99512 | -0.093618 | 0.024562 | 0.0061559
45 | 0.98625 | -0.26359 | 0.007242 | 0.001815
46 | 0.98303 | -0.32635 | 0 | 0
47 | 0.98347 | -0.31783 | 0.0058868 | 0.0014754
48 | 0.98222 | -0.3419 | 0.0028037 | 0.00070267
49 | 0.97218 | -0.53618 | 0.0028967 | 0.00072598
50 | 0.97197 | -0.54015 | 0 | 0
51 | 0.97189 | -0.54173 | 0 | 0
52 | 0.97284 | -0.52311 | 0.0066844 | 0.0016753
53 | 0.97452 | -0.48999 | 0 | 0
54 | 0.97101 | -0.55932 | 0.00066952 | 0.0001678
55 | 0.97258 | -0.52825 | 0.0031197 | 0.00078186
56 | 0.97493 | -0.48178 | 0.0024393 | 0.00061135
57 | 0.97076 | -0.56428 | 0.0016253 | 0.00040735
58 | 0.97083 | -0.56284 | 0.001381 | 0.00034612
59 | 0.97035 | -0.57241 | 0 | 0
60 | 0.97031 | -0.57321 | 0.0027268 | 0.00068339
61 | 0.97521 | -0.47628 | 0.0026692 | 0.00066897
62 | 0.97526 | -0.47531 | 0.001793 | 0.00044938
63 | 0.97534 | -0.47383 | 0.0012586 | 0.00031542
64 | 0.97555 | -0.46956 | 0 | 0
65 | 0.97567 | -0.46732 | 0 | 0
66 | 0.9781 | -0.41961 | 0.0085431 | 0.0021411
67 | 0.97834 | -0.41506 | 0 | 0
68 | 0.99106 | -0.1692 | 0.00098574 | 0.00024705
69 | 0.98144 | -0.35446 | 0.0014144 | 0.00035449
70 | 0.97702 | -0.44089 | 0.0043107 | 0.0010804
71 | 0.98264 | -0.33406 | 0.0076485 | 0.0019169
72 | 0.9826 | -0.33487 | 0.0039055 | 0.00097882
73 | 0.98266 | -0.33358 | 0 | 0
74 | 0.98262 | -0.33445 | 0.0050948 | 0.0012769
75 | 0.98292 | -0.32857 | 0 | 0
76 | 0.98291 | -0.32879 | 0.00084473 | 0.00021171
77 | 0.98331 | -0.32098 | 0 | 0
78 | 0.98317 | -0.32367 | 0.006466 | 0.0016205
79 | 0.98302 | -0.3266 | 0.001214 | 0.00030425
80 | 0.99068 | -0.1792 | 0.08665 | 0.021717
81 | 0.99283 | -0.13774 | 0 | 0
82 | 0.97194 | -0.54086 | 0.0016503 | 0.00041361
83 | 0.97213 | -0.53715 | 0.0029649 | 0.00074307
84 | 0.97193 | -0.541 | 0.0066336 | 0.0016625
85 | 0.97778 | -0.42596 | 0 | 0
86 | 0.97726 | -0.43606 | 0.0017842 | 0.00044715
87 | 0.97606 | -0.45963 | 0.0014132 | 0.00035418
88 | 0.99512 | -0.093691 | 0.0065961 | 0.0016531
89 | 0.99251 | -0.14387 | 0.032916 | 0.0082497
90 | 0.97536 | -0.47651 | 0.0018519 | 0.00046413
91 | 0.97541 | -0.47561 | 0 | 0
92 | 0.97544 | -0.4751 | 0.00074874 | 0.00018765
93 | 0.97547 | -0.47441 | 0.00075767 | 0.00018989
94 | 0.97548 | -0.47422 | 0.00070015 | 0.00017548
95 | 0.97553 | -0.47317 | 0.00095241 | 0.0002387
96 | 0.97571 | -0.46964 | 0 | 0
97 | 0.97644 | -0.45522 | 0 | 0
98 | 0.97715 | -0.44135 | 0.0026878 | 0.00067361
99 | 0.97816 | -0.42136 | 0 | 0
100 | 0.97847 | -0.4154 | 0 | 0
101 | 0.9778 | -0.42848 | 0.0012361 | 0.00030979
102 | 0.97734 | -0.43759 | 0.0010153 | 0.00025445
103 | 0.98083 | -0.36907 | 0 | 0
104 | 0.97832 | -0.41833 | 0.0011119 | 0.00027868
105 | 0.97757 | -0.43314 | 0.0013269 | 0.00033255
106 | 0.97801 | -0.42434 | 0.0010057 | 0.00025205
107 | 0.97798 | -0.42504 | 0.0014376 | 0.0003603
108 | 0.9779 | -0.42665 | 0.00078037 | 0.00019558
109 | 0.98079 | -0.36982 | 0.0011615 | 0.0002911
110 | 0.98112 | -0.36335 | 0.0014727 | 0.0003691
111 | 0.97786 | -0.42734 | 0.0016414 | 0.00041138
112 | 0.9806 | -0.37358 | 0.0038831 | 0.0009732
113 | 0.98167 | -0.35259 | 0 | 0
114 | 0.97784 | -0.42781 | 0.0017072 | 0.00042787
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0032435 | -0.0008129 | 0.0032438 | 0.00081272 | 2.5851e-07 | -1.8128e-07 | 0.004965 | 0.0049648 | 0.004965 | 0.97209 | -0.53781 | 0.97218 | -0.53613 | 1.364
1 | -0.0032438 | -0.00081272 | 0.003244 | 0.00081259 | 1.8149e-07 | -1.2731e-07 | 0.0049648 | 0.0049647 | 0.0049648 | 0.97218 | -0.53613 | 0.97224 | -0.53496 | 1.364
2 | -0.010188 | -0.002553 | 0.01019 | 0.0025541 | 2.0921e-06 | 1.0543e-06 | 0.015593 | 0.015593 | 0.015593 | 0.97224 | -0.53496 | 0.97245 | -0.53065 | 4.2838
3 | -0.023978 | -0.0060089 | 0.023997 | 0.0060205 | 1.8834e-05 | 1.159e-05 | 0.03669 | 0.03669 | 0.03669 | 0.97245 | -0.53065 | 0.97329 | -0.51417 | 10.0796
4 | 0.013787 | 0.0034548 | -0.013785 | -0.0034536 | 2.1191e-06 | 1.1987e-06 | 0.021097 | 0.021097 | 0.021097 | 0.97245 | -0.53065 | 0.97229 | -0.53387 | 5.7958
5 | -0.0021294 | -0.00053361 | 0.0021297 | 0.00053281 | 2.8831e-07 | -7.9485e-07 | 0.003189 | 0.0031887 | 0.003189 | 0.99358 | -0.12243 | 0.99373 | -0.11958 | 0.8761
6 | 0.0021294 | 0.00053361 | -0.0021294 | -0.00053367 | 2.3e-08 | -6.3388e-08 | 0.003189 | 0.003189 | 0.003189 | 0.99358 | -0.12243 | 0.99357 | -0.12265 | 0.87611
7 | -0.0021297 | -0.00053281 | 0.0021298 | 0.00053247 | 1.2311e-07 | -3.3955e-07 | 0.0031887 | 0.0031885 | 0.0031887 | 0.99373 | -0.11958 | 0.99379 | -0.11837 | 0.87601
8 | 0.084777 | 0.021472 | -0.08472 | -0.021436 | 5.6812e-05 | 3.6243e-05 | 0.1285 | 0.1285 | 0.1285 | 0.98234 | -0.33712 | 0.98162 | -0.35108 | 35.302
9 | -0.084777 | -0.021472 | 0.08492 | 0.021563 | 0.00014253 | 9.0927e-05 | 0.1285 | 0.1285 | 0.1285 | 0.98234 | -0.33712 | 0.98414 | -0.30217 | 35.302
10 | 0.079799 | 0.020203 | -0.079724 | -0.020155 | 7.5142e-05 | 4.7918e-05 | 0.12104 | 0.12104 | 0.12104 | 0.98162 | -0.35108 | 0.98061 | -0.37071 | 33.2525
11 | 0.0049215 | 0.001233 | -0.0049209 | -0.001233 | 6.2925e-07 | 2.1651e-08 | 0.0074603 | 0.0074605 | 0.0074605 | 0.98162 | -0.35108 | 0.98148 | -0.35376 | 2.0496
12 | -0.094261 | -0.023905 | 0.094549 | 0.024089 | 0.00028837 | 0.00018407 | 0.14262 | 0.14262 | 0.14262 | 0.98414 | -0.30217 | 0.98743 | -0.23875 | 39.1821
13 | -0.010657 | -0.0026697 | 0.01066 | 0.0026711 | 2.7809e-06 | 1.4023e-06 | 0.015957 | 0.015957 | 0.015957 | 0.99379 | -0.11837 | 0.99407 | -0.11289 | 4.3838
14 | 0.019028 | 0.0047711 | -0.019021 | -0.0047672 | 6.5837e-06 | 3.9264e-06 | 0.028314 | 0.028315 | 0.028315 | 1 | 0 | 0.99962 | -0.007263 | 7.7787
15 | 0.11956 | 0.030816 | -0.11932 | -0.030662 | 0.00024169 | 0.00015362 | 0.17821 | 0.17821 | 0.17821 | 1 | 0 | 0.99779 | -0.041608 | 24.4794
16 | 0.1322 | 0.033814 | -0.13154 | -0.033388 | 0.00066685 | 0.00042619 | 0.19696 | 0.19696 | 0.19696 | 1 | 0 | 0.99449 | -0.1048 | 54.1101
17 | 0.17967 | 0.045485 | -0.17923 | -0.04521 | 0.00043196 | 0.00027561 | 0.26751 | 0.26751 | 0.26751 | 1 | 0 | 0.99737 | -0.050209 | 36.7454
18 | 0.0023723 | 0.00059435 | -0.0023722 | -0.00059453 | 8.3038e-08 | -1.7793e-07 | 0.0035378 | 0.0035378 | 0.0035378 | 0.99779 | -0.041608 | 0.99775 | -0.042343 | 0.97193
19 | 0.11695 | 0.030068 | -0.11685 | -0.030006 | 9.7218e-05 | 6.1776e-05 | 0.17467 | 0.17467 | 0.17467 | 0.99779 | -0.041608 | 0.99689 | -0.05873 | 23.9935
20 | 0.015365 | 0.0038522 | -0.015359 | -0.0038488 | 5.9184e-06 | 3.4005e-06 | 0.022991 | 0.022991 | 0.022991 | 0.99449 | -0.1048 | 0.99407 | -0.11289 | 6.3162
21 | 0.11617 | 0.029535 | -0.11599 | -0.02942 | 0.00018055 | 0.00011535 | 0.17397 | 0.17397 | 0.17397 | 0.99449 | -0.1048 | 0.9928 | -0.13712 | 47.794
22 | 0.15147 | 0.038252 | -0.15132 | -0.038157 | 0.00014935 | 9.5178e-05 | 0.22609 | 0.22609 | 0.22609 | 0.99737 | -0.050209 | 0.9963 | -0.070808 | 31.0563
23 | 0.10381 | 0.026368 | -0.10364 | -0.026259 | 0.00017084 | 0.0001091 | 0.15572 | 0.15572 | 0.15572 | 0.9928 | -0.13712 | 0.99102 | -0.17138 | 42.7796
24 | -0.031118 | -0.007819 | 0.031137 | 0.0078307 | 1.8637e-05 | 1.1641e-05 | 0.047021 | 0.047021 | 0.047021 | 0.98492 | -0.28944 | 0.98557 | -0.2769 | 12.9178
25 | 0.031118 | 0.007819 | -0.031077 | -0.0077931 | 4.154e-05 | 2.5949e-05 | 0.047021 | 0.047021 | 0.047021 | 0.98492 | -0.28944 | 0.98349 | -0.31744 | 12.9178
26 | -0.032261 | -0.0081125 | 0.032282 | 0.0081253 | 2.0523e-05 | 1.2841e-05 | 0.048718 | 0.048718 | 0.048718 | 0.98557 | -0.2769 | 0.98625 | -0.26359 | 13.3841
27 | 0.018722 | 0.0046965 | -0.018714 | -0.0046918 | 7.9421e-06 | 4.7482e-06 | 0.028328 | 0.028328 | 0.028328 | 0.98349 | -0.31744 | 0.98303 | -0.32635 | 7.7824
28 | 0.012355 | 0.0030965 | -0.012355 | -0.0030964 | 2.2826e-07 | 1.2398e-07 | 0.018693 | 0.018693 | 0.018693 | 0.98349 | -0.31744 | 0.98347 | -0.31783 | 5.1354
29 | 0.10364 | 0.026259 | -0.10355 | -0.026201 | 9.0939e-05 | 5.8072e-05 | 0.15572 | 0.15572 | 0.15572 | 0.99102 | -0.17138 | 0.99007 | -0.18966 | 42.7796
30 | 0.10355 | 0.026201 | -0.10342 | -0.026121 | 0.00012495 | 7.9793e-05 | 0.15572 | 0.15572 | 0.15572 | 0.99007 | -0.18966 | 0.98877 | -0.21484 | 42.7796
31 | 0.045374 | 0.01142 | -0.045365 | -0.011415 | 8.2845e-06 | 5.2418e-06 | 0.068409 | 0.068409 | 0.068409 | 0.9872 | -0.24508 | 0.98701 | -0.2489 | 18.7937
32 | 0.053124 | 0.013411 | -0.053013 | -0.01334 | 0.00011095 | 7.042e-05 | 0.080109 | 0.080109 | 0.080109 | 0.9872 | -0.24508 | 0.98495 | -0.28877 | 22.008
33 | -0.098498 | -0.024831 | 0.098641 | 0.024922 | 0.00014276 | 9.1142e-05 | 0.14852 | 0.14852 | 0.14852 | 0.9872 | -0.24508 | 0.98877 | -0.21484 | 40.8016
34 | 0.039552 | 0.0099578 | -0.039524 | -0.0099403 | 2.7756e-05 | 1.7498e-05 | 0.059644 | 0.059645 | 0.059645 | 0.98701 | -0.2489 | 0.98625 | -0.26359 | 16.3859
35 | 0.028454 | 0.0071851 | -0.028382 | -0.0071402 | 7.2241e-05 | 4.4912e-05 | 0.043006 | 0.043007 | 0.043007 | 0.98495 | -0.28877 | 0.98222 | -0.3419 | 11.815
36 | 0.021072 | 0.005287 | -0.021063 | -0.0052815 | 8.9748e-06 | 5.4574e-06 | 0.032218 | 0.032218 | 0.032218 | 0.97329 | -0.51417 | 0.97284 | -0.52311 | 8.851
37 | -0.045068 | -0.011307 | 0.04512 | 0.01134 | 5.2018e-05 | 3.2928e-05 | 0.068907 | 0.068907 | 0.068907 | 0.97329 | -0.51417 | 0.97452 | -0.48999 | 18.9305
38 | 0.0093098 | 0.002332 | -0.0093088 | -0.0023315 | 1.0228e-06 | 4.8796e-07 | 0.014248 | 0.014248 | 0.014248 | 0.97229 | -0.53387 | 0.97218 | -0.53618 | 3.9142
39 | -0.094549 | -0.024089 | 0.094697 | 0.024183 | 0.00014759 | 9.4212e-05 | 0.14262 | 0.14262 | 0.14262 | 0.98743 | -0.23875 | 0.98911 | -0.20645 | 39.1821
40 | -0.094697 | -0.024183 | 0.094868 | 0.024292 | 0.00017084 | 0.00010905 | 0.14262 | 0.14262 | 0.14262 | 0.98911 | -0.20645 | 0.99106 | -0.1692 | 39.182
41 | 0.0059615 | 0.0014941 | -0.0059608 | -0.0014939 | 6.7272e-07 | 1.5841e-07 | 0.0090824 | 0.0090825 | 0.0090825 | 0.9767 | -0.44721 | 0.97658 | -0.44958 | 2.4952
42 | -0.0059615 | -0.0014941 | 0.0059625 | 0.0014943 | 1.0362e-06 | 2.4387e-07 | 0.0090824 | 0.0090822 | 0.0090824 | 0.9767 | -0.44721 | 0.97688 | -0.44356 | 2.4952
43 | -0.0078771 | -0.0019742 | 0.0078781 | 0.0019746 | 1.0035e-06 | 4.095e-07 | 0.011999 | 0.011999 | 0.011999 | 0.97688 | -0.44356 | 0.97702 | -0.44089 | 3.2963
44 | 0.079724 | 0.020155 | -0.079619 | -0.020088 | 0.00010487 | 6.6878e-05 | 0.12104 | 0.12104 | 0.12104 | 0.98061 | -0.37071 | 0.9792 | -0.39818 | 33.2525
45 | 0.0014145 | 0.00035418 | -0.0014144 | -0.00035449 | 4.694e-08 | -3.1394e-07 | 0.0021444 | 0.0021445 | 0.0021445 | 0.98148 | -0.35376 | 0.98144 | -0.35446 | 0.58915
46 | 0.07748 | 0.019552 | -0.077418 | -0.019513 | 6.2587e-05 | 3.9905e-05 | 0.11779 | 0.11779 | 0.11779 | 0.9792 | -0.39818 | 0.97834 | -0.41506 | 32.3597
47 | -0.098531 | -0.025352 | 0.098692 | 0.025454 | 0.00016087 | 0.00010193 | 0.14757 | 0.14757 | 0.14757 | 0.99511 | -0.092248 | 0.99689 | -0.05873 | 20.2708
48 | 0.098531 | 0.025352 | -0.098234 | -0.025162 | 0.0002968 | 0.00018948 | 0.14757 | 0.14757 | 0.14757 | 0.99511 | -0.092248 | 0.99184 | -0.1544 | 40.5415
49 | 0.018157 | 0.0045521 | -0.018152 | -0.0045493 | 4.6707e-06 | 2.7682e-06 | 0.027102 | 0.027103 | 0.027103 | 0.99689 | -0.05873 | 0.99661 | -0.06413 | 7.4458
50 | 0.095922 | 0.024583 | -0.095853 | -0.024539 | 6.8761e-05 | 4.3893e-05 | 0.1441 | 0.1441 | 0.1441 | 0.99184 | -0.1544 | 0.99106 | -0.1692 | 39.5886
51 | -0.031176 | -0.0078201 | 0.031192 | 0.0078302 | 1.614e-05 | 1.0072e-05 | 0.046592 | 0.046591 | 0.046592 | 0.99574 | -0.081662 | 0.9963 | -0.070808 | 12.7999
52 | 0.031176 | 0.0078201 | -0.031158 | -0.007809 | 1.7758e-05 | 1.1082e-05 | 0.046592 | 0.046592 | 0.046592 | 0.99574 | -0.081662 | 0.99512 | -0.093618 | 12.7999
53 | 0.12013 | 0.030327 | -0.11975 | -0.030082 | 0.00038385 | 0.00024525 | 0.1795 | 0.1795 | 0.1795 | 0.9963 | -0.070808 | 0.99283 | -0.13774 | 49.3128
54 | 0.0065961 | 0.0016531 | -0.0065961 | -0.0016531 | 2.3016e-08 | 6.5339e-09 | 0.0098633 | 0.0098633 | 0.0098633 | 0.99512 | -0.093618 | 0.99512 | -0.093691 | 2.7097
55 | 0.001214 | 0.00030412 | -0.001214 | -0.00030425 | 1.4606e-08 | -1.3688e-07 | 0.0018376 | 0.0018376 | 0.0018376 | 0.98303 | -0.32635 | 0.98302 | -0.3266 | 0.50484
56 | 0.0175 | 0.0043877 | -0.017498 | -0.0043866 | 1.8521e-06 | 1.0961e-06 | 0.02649 | 0.026491 | 0.026491 | 0.98303 | -0.32635 | 0.98292 | -0.32857 | 7.2776
57 | 0.0064678 | 0.0016211 | -0.0064668 | -0.0016208 | 9.6858e-07 | 2.7772e-07 | 0.009786 | 0.0097862 | 0.0097862 | 0.98347 | -0.31783 | 0.98331 | -0.32098 | 2.6885
58 | 0.025578 | 0.0064375 | -0.025565 | -0.0064294 | 1.3055e-05 | 8.0623e-06 | 0.038759 | 0.038759 | 0.038759 | 0.98222 | -0.3419 | 0.98167 | -0.35259 | 10.6482
59 | 0.0064121 | 0.0016055 | -0.0064109 | -0.0016051 | 1.2101e-06 | 3.5911e-07 | 0.0098139 | 0.009814 | 0.009814 | 0.97218 | -0.53618 | 0.97197 | -0.54015 | 2.6962
60 | 0.0064109 | 0.0016051 | -0.0064104 | -0.001605 | 4.8182e-07 | 1.4304e-07 | 0.009814 | 0.0098141 | 0.0098141 | 0.97197 | -0.54015 | 0.97189 | -0.54173 | 2.6962
61 | 0.0064104 | 0.001605 | -0.0064051 | -0.0016034 | 5.3676e-06 | 1.5955e-06 | 0.0098141 | 0.0098147 | 0.0098147 | 0.97189 | -0.54173 | 0.97101 | -0.55932 | 2.6964
62 | 0.014378 | 0.0036063 | -0.014375 | -0.0036042 | 3.5205e-06 | 2.0122e-06 | 0.021993 | 0.021994 | 0.021994 | 0.97284 | -0.52311 | 0.97258 | -0.52825 | 6.0422
63 | -0.04512 | -0.01134 | 0.045138 | 0.011352 | 1.77e-05 | 1.1204e-05 | 0.068907 | 0.068907 | 0.068907 | 0.97452 | -0.48999 | 0.97493 | -0.48178 | 18.9305
64 | 0.0057355 | 0.0014356 | -0.0057346 | -0.0014354 | 9.6053e-07 | 2.0463e-07 | 0.0087887 | 0.0087889 | 0.0087889 | 0.97101 | -0.55932 | 0.97083 | -0.56284 | 2.4145
65 | 0.011255 | 0.0028224 | -0.01125 | -0.0028199 | 4.776e-06 | 2.5239e-06 | 0.017221 | 0.017221 | 0.017221 | 0.97258 | -0.52825 | 0.97213 | -0.53715 | 4.731
66 | -0.047577 | -0.011963 | 0.04761 | 0.011984 | 3.2876e-05 | 2.0833e-05 | 0.07263 | 0.07263 | 0.07263 | 0.97493 | -0.48178 | 0.97567 | -0.46732 | 19.9533
67 | -0.0043532 | -0.0010893 | 0.0043535 | 0.0010893 | 2.9752e-07 | -2.9938e-08 | 0.0066722 | 0.0066721 | 0.0066722 | 0.97076 | -0.56428 | 0.97083 | -0.56284 | 1.833
68 | 0.0027279 | 0.00068195 | -0.0027269 | -0.00068326 | 1.0559e-06 | -1.3146e-06 | 0.0041808 | 0.0041816 | 0.0041816 | 0.97076 | -0.56428 | 0.97035 | -0.57241 | 1.1488
69 | 0.0027269 | 0.00068326 | -0.0027268 | -0.00068339 | 1.0372e-07 | -1.29e-07 | 0.0041816 | 0.0041816 | 0.0041816 | 0.97035 | -0.57241 | 0.97031 | -0.57321 | 1.1488
70 | -0.0026692 | -0.00066897 | 0.0026694 | 0.0006688 | 1.2361e-07 | -1.6885e-07 | 0.0040728 | 0.0040727 | 0.0040728 | 0.97521 | -0.47628 | 0.97526 | -0.47531 | 1.1189
71 | -0.0044624 | -0.0011182 | 0.0044627 | 0.0011182 | 3.1487e-07 | -2.4528e-08 | 0.0068085 | 0.0068084 | 0.0068085 | 0.97526 | -0.47531 | 0.97534 | -0.47383 | 1.8705
72 | -0.0057213 | -0.0014336 | 0.0057224 | 0.0014338 | 1.1621e-06 | 2.3598e-07 | 0.0087285 | 0.0087283 | 0.0087285 | 0.97534 | -0.47383 | 0.97555 | -0.46956 | 2.3979
73 | -0.0057224 | -0.0014338 | 0.005723 | 0.0014339 | 6.1079e-07 | 1.2393e-07 | 0.0087283 | 0.0087282 | 0.0087283 | 0.97555 | -0.46956 | 0.97567 | -0.46732 | 2.3979
74 | -0.053333 | -0.013418 | 0.053353 | 0.01343 | 1.9614e-05 | 1.2454e-05 | 0.081358 | 0.081358 | 0.081358 | 0.97567 | -0.46732 | 0.97606 | -0.45963 | 22.3512
75 | -0.0085431 | -0.0021411 | 0.0085449 | 0.0021419 | 1.8525e-06 | 8.1843e-07 | 0.012997 | 0.012997 | 0.012997 | 0.9781 | -0.41961 | 0.97834 | -0.41506 | 3.5705
76 | 0.068873 | 0.017371 | -0.068837 | -0.017348 | 3.5901e-05 | 2.2867e-05 | 0.10479 | 0.10479 | 0.10479 | 0.97834 | -0.41506 | 0.97778 | -0.42596 | 28.7892
77 | -0.012189 | -0.0030549 | 0.012198 | 0.0030597 | 8.6769e-06 | 4.7117e-06 | 0.018564 | 0.018564 | 0.018564 | 0.97702 | -0.44089 | 0.97778 | -0.42596 | 5.1
78 | 0.0039057 | 0.00097877 | -0.0039055 | -0.00097882 | 1.4947e-07 | -4.8674e-08 | 0.0059144 | 0.0059145 | 0.0059145 | 0.98264 | -0.33406 | 0.9826 | -0.33487 | 1.6249
79 | -0.011554 | -0.0028957 | 0.011555 | 0.0028958 | 2.6931e-07 | 1.4264e-07 | 0.017497 | 0.017497 | 0.017497 | 0.98264 | -0.33406 | 0.98266 | -0.33358 | 4.8068
80 | 0.005095 | 0.0012769 | -0.0050948 | -0.0012769 | 2.1299e-07 | 1.5439e-08 | 0.0077151 | 0.0077152 | 0.0077152 | 0.98266 | -0.33358 | 0.98262 | -0.33445 | 2.1196
81 | -0.016649 | -0.0041727 | 0.016653 | 0.004175 | 3.9733e-06 | 2.3317e-06 | 0.025212 | 0.025212 | 0.025212 | 0.98266 | -0.33358 | 0.98292 | -0.32857 | 6.9263
82 | 0.00084473 | 0.00021153 | -0.00084473 | -0.00021171 | 8.7865e-09 | -1.7598e-07 | 0.0012788 | 0.0012788 | 0.0012788 | 0.98292 | -0.32857 | 0.98291 | -0.32879 | 0.35133
83 | 0.0064668 | 0.0016208 | -0.006466 | -0.0016205 | 8.2954e-07 | 2.3795e-07 | 0.0097862 | 0.0097863 | 0.0097863 | 0.98331 | -0.32098 | 0.98317 | -0.32367 | 2.6885
84 | -0.08665 | -0.021717 | 0.086821 | 0.021826 | 0.0001715 | 0.00010941 | 0.13015 | 0.13015 | 0.13015 | 0.99068 | -0.1792 | 0.99283 | -0.13774 | 35.7552
85 | 0.032926 | 0.0082557 | -0.032916 | -0.0082497 | 9.6159e-06 | 6.018e-06 | 0.04935 | 0.04935 | 0.04935 | 0.99283 | -0.13774 | 0.99251 | -0.14387 | 13.5577
86 | -0.0082839 | -0.0020762 | 0.0082854 | 0.0020768 | 1.4639e-06 | 6.3604e-07 | 0.012683 | 0.012682 | 0.012683 | 0.97194 | -0.54086 | 0.97213 | -0.53715 | 3.4842
87 | 0.0066336 | 0.0016625 | -0.0066336 | -0.0016625 | 4.273e-08 | 1.3656e-08 | 0.010156 | 0.010156 | 0.010156 | 0.97194 | -0.54086 | 0.97193 | -0.541 | 2.7901
88 | 0.056639 | 0.014288 | -0.056612 | -0.014271 | 2.7381e-05 | 1.7401e-05 | 0.086229 | 0.086229 | 0.086229 | 0.97778 | -0.42596 | 0.97726 | -0.43606 | 23.6893
89 | 0.054828 | 0.013824 | -0.054766 | -0.013784 | 6.1766e-05 | 3.9235e-05 | 0.083512 | 0.083513 | 0.083513 | 0.97726 | -0.43606 | 0.97606 | -0.45963 | 22.943
90 | -0.0018519 | -0.00046413 | 0.001852 | 0.00046385 | 7.9392e-08 | -2.8025e-07 | 0.0028253 | 0.0028252 | 0.0028253 | 0.97536 | -0.47651 | 0.97541 | -0.47561 | 0.77617
91 | -0.001852 | -0.00046385 | 0.001852 | 0.00046369 | 4.4909e-08 | -1.5855e-07 | 0.0028252 | 0.0028251 | 0.0028252 | 0.97541 | -0.47561 | 0.97544 | -0.4751 | 0.77614
92 | -0.0026008 | -0.00065134 | 0.0026009 | 0.00065122 | 8.5586e-08 | -1.2624e-07 | 0.0039673 | 0.0039672 | 0.0039673 | 0.97544 | -0.4751 | 0.97547 | -0.47441 | 1.0899
93 | -0.0033585 | -0.00084111 | 0.0033586 | 0.00084109 | 2.9924e-08 | -1.8805e-08 | 0.005123 | 0.005123 | 0.005123 | 0.97547 | -0.47441 | 0.97548 | -0.47422 | 1.4074
94 | -0.0040587 | -0.0010166 | 0.0040589 | 0.0010165 | 2.0383e-07 | -4.6597e-08 | 0.006191 | 0.0061909 | 0.006191 | 0.97548 | -0.47422 | 0.97553 | -0.47317 | 1.7008
95 | -0.0050113 | -0.0012552 | 0.0050122 | 0.0012553 | 8.4113e-07 | 5.891e-08 | 0.0076437 | 0.0076435 | 0.0076437 | 0.97553 | -0.47317 | 0.97571 | -0.46964 | 2.0999
96 | -0.0050122 | -0.0012553 | 0.0050156 | 0.0012555 | 3.4435e-06 | 2.3911e-07 | 0.0076435 | 0.0076428 | 0.0076435 | 0.97571 | -0.46964 | 0.97644 | -0.45522 | 2.0999
97 | -0.0050156 | -0.0012555 | 0.0050189 | 0.0012557 | 3.3109e-06 | 2.2678e-07 | 0.0076428 | 0.0076421 | 0.0076428 | 0.97644 | -0.45522 | 0.97715 | -0.44135 | 2.0997
98 | -0.0077067 | -0.0019294 | 0.0077081 | 0.0019299 | 1.3796e-06 | 5.4822e-07 | 0.011735 | 0.011735 | 0.011735 | 0.97715 | -0.44135 | 0.97734 | -0.43759 | 3.2239
99 | -0.011294 | -0.0028306 | 0.011297 | 0.0028323 | 3.2101e-06 | 1.6903e-06 | 0.017181 | 0.017181 | 0.017181 | 0.97816 | -0.42136 | 0.97847 | -0.4154 | 4.7201
100 | 0.011294 | 0.0028306 | -0.01129 | -0.0028286 | 3.8278e-06 | 2.0159e-06 | 0.017181 | 0.017181 | 0.017181 | 0.97816 | -0.42136 | 0.9778 | -0.42848 | 4.7201
101 | -0.018985 | -0.0047589 | 0.019027 | 0.0047841 | 4.1995e-05 | 2.5185e-05 | 0.028872 | 0.028872 | 0.028872 | 0.97847 | -0.4154 | 0.98083 | -0.36907 | 7.9319
102 | 0.0076878 | 0.0019266 | -0.0076868 | -0.0019262 | 1.0736e-06 | 4.2406e-07 | 0.011691 | 0.011691 | 0.011691 | 0.97847 | -0.4154 | 0.97832 | -0.41833 | 3.2119
103 | 0.010054 | 0.0025188 | -0.010052 | -0.0025177 | 2.234e-06 | 1.1106e-06 | 0.0153 | 0.0153 | 0.0153 | 0.9778 | -0.42848 | 0.97757 | -0.43314 | 4.2034
104 | -0.0087233 | -0.0021844 | 0.0087252 | 0.0021852 | 1.847e-06 | 8.3207e-07 | 0.013281 | 0.013281 | 0.013281 | 0.97734 | -0.43759 | 0.97757 | -0.43314 | 3.6486
105 | 0.0050455 | 0.0012641 | -0.0050453 | -0.0012641 | 1.8025e-07 | 1.1819e-08 | 0.0076543 | 0.0076544 | 0.0076544 | 0.98083 | -0.36907 | 0.98079 | -0.36982 | 2.1028
106 | -0.024073 | -0.0060482 | 0.024079 | 0.0060522 | 6.5797e-06 | 4.0449e-06 | 0.036526 | 0.036526 | 0.036526 | 0.98083 | -0.36907 | 0.98112 | -0.36335 | 10.0346
107 | 0.0065748 | 0.0016475 | -0.0065729 | -0.0016469 | 1.8836e-06 | 5.7503e-07 | 0.01 | 0.01 | 0.01 | 0.97832 | -0.41833 | 0.97801 | -0.42434 | 2.7474
108 | 0.0055673 | 0.0013949 | -0.0055671 | -0.0013948 | 1.8604e-07 | 3.2297e-08 | 0.0084703 | 0.0084703 | 0.0084703 | 0.97801 | -0.42434 | 0.97798 | -0.42504 | 2.327
109 | 0.0041295 | 0.0010345 | -0.0041292 | -0.0010346 | 3.1509e-07 | -6.5399e-08 | 0.0062829 | 0.006283 | 0.006283 | 0.97798 | -0.42504 | 0.9779 | -0.42665 | 1.7261
110 | 0.0033488 | 0.00083901 | -0.0033487 | -0.00083908 | 1.1113e-07 | -7.206e-08 | 0.0050956 | 0.0050956 | 0.0050956 | 0.9779 | -0.42665 | 0.97786 | -0.42734 | 1.3999
111 | 0.0038838 | 0.00097297 | -0.0038831 | -0.0009732 | 6.9562e-07 | -2.2895e-07 | 0.0058922 | 0.0058924 | 0.0058924 | 0.98079 | -0.36982 | 0.9806 | -0.37358 | 1.6188
112 | -0.025552 | -0.0064213 | 0.025565 | 0.0064294 | 1.3132e-05 | 8.1098e-06 | 0.03876 | 0.038759 | 0.03876 | 0.98112 | -0.36335 | 0.98167 | -0.35259 | 10.6482
113 | 0.0017072 | 0.0004277 | -0.0017072 | -0.00042787 | 3.7556e-08 | -1.6211e-07 | 0.0025979 | 0.0025979 | 0.0025979 | 0.97786 | -0.42734 | 0.97784 | -0.42781 | 0.71372

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45211 | 0.11489

## res_load
| p_mw | q_mvar
0 | 0.0032435 | 0.0008129
1 | 0.0069443 | 0.0017404
2 | 0.0021294 | 0.00053367
3 | 0.0093412 | 0.0023411
4 | 0.0085276 | 0.0021372
5 | 0.019021 | 0.0047672
6 | 0.027761 | 0.0069575
7 | 0.0046991 | 0.0011777
8 | 0.012178 | 0.0030522
9 | 0.0011245 | 0.00028181
10 | 0.0058135 | 0.001457
11 | 0.024559 | 0.0061551
12 | 0.0047842 | 0.001199
13 | 0.0044754 | 0.0011217
14 | 0.0059608 | 0.0014939
15 | 0.0019146 | 0.00047985
16 | 0.0035064 | 0.00087879
17 | 0.0021387 | 0.000536
18 | 0.0023121 | 0.00057948
19 | 0.018152 | 0.0045493
20 | 0.0023722 | 0.00059453
21 | 0.024562 | 0.0061559
22 | 0.007242 | 0.001815
23 | 0.0058868 | 0.0014754
24 | 0.0028037 | 0.00070267
25 | 0.0028967 | 0.00072598
26 | 0.0066844 | 0.0016753
27 | 0.00066952 | 0.0001678
28 | 0.0031197 | 0.00078186
29 | 0.0024393 | 0.00061135
30 | 0.0016253 | 0.00040735
31 | 0.001381 | 0.00034612
32 | 0.0027268 | 0.00068339
33 | 0.0026692 | 0.00066897
34 | 0.001793 | 0.00044938
35 | 0.0012586 | 0.00031542
36 | 0.0085431 | 0.0021411
37 | 0.00098574 | 0.00024705
38 | 0.0014144 | 0.00035449
39 | 0.0043107 | 0.0010804
40 | 0.0076485 | 0.0019169
41 | 0.0039055 | 0.00097882
42 | 0.0050948 | 0.0012769
43 | 0.00084473 | 0.00021171
44 | 0.006466 | 0.0016205
45 | 0.001214 | 0.00030425
46 | 0.08665 | 0.021717
47 | 0.0016503 | 0.00041361
48 | 0.0029649 | 0.00074307
49 | 0.0066336 | 0.0016625
50 | 0.0017842 | 0.00044715
51 | 0.0014132 | 0.00035418
52 | 0.0065961 | 0.0016531
53 | 0.032916 | 0.0082497
54 | 0.0018519 | 0.00046413
55 | 0.00074874 | 0.00018765
56 | 0.00075767 | 0.00018989
57 | 0.00070015 | 0.00017548
58 | 0.00095241 | 0.0002387
59 | 0.0026878 | 0.00067361
60 | 0.0012361 | 0.00030979
61 | 0.0010153 | 0.00025445
62 | 0.0011119 | 0.00027868
63 | 0.0013269 | 0.00033255
64 | 0.0010057 | 0.00025205
65 | 0.0014376 | 0.0003603
66 | 0.00078037 | 0.00019558
67 | 0.0011615 | 0.0002911
68 | 0.0014727 | 0.0003691
69 | 0.0016414 | 0.00041138
70 | 0.0038831 | 0.0009732
71 | 0.0017072 | 0.00042787

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1