## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_193-11_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_193-11_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_193-11_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_193-11_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_193-11_0_5_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_193-11_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_193-11_0_5_node_136 | 0.4 | n |  | TRUE
7 | bus_LV_193-11_0_5_node_137 | 0.4 | n |  | TRUE
8 | bus_LV_193-11_0_5_node_103 | 0.4 | n |  | TRUE
9 | bus_LV_193-11_0_5_node_135 | 0.4 | n |  | TRUE
10 | bus_LV_193-11_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_193-11_0_5_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_193-11_0_5_node_102 | 0.4 | n |  | TRUE
13 | bus_LV_193-11_0_5_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_193-11_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_193-11_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_193-11_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_193-11_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_193-11_0_5_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_193-11_0_5_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_193-11_0_5_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_193-11_0_5_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_193-11_0_5_node_157 | 0.4 | n |  | TRUE
23 | bus_LV_193-11_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_193-11_0_5_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_193-11_0_5_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_193-11_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_193-11_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_193-11_0_5_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_193-11_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_193-11_0_5_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_193-11_0_5_node_106 | 0.4 | n |  | TRUE
32 | bus_LV_193-11_0_5_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_193-11_0_5_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_193-11_0_5_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_193-11_0_5_node_105 | 0.4 | n |  | TRUE
36 | bus_LV_193-11_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_193-11_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_193-11_0_5_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_193-11_0_5_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_193-11_0_5_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_193-11_0_5_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_193-11_0_5_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_193-11_0_5_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_193-11_0_5_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_193-11_0_5_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_193-11_0_5_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_193-11_0_5_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_193-11_0_5_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_193-11_0_5_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_193-11_0_5_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_193-11_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_193-11_0_5_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_193-11_0_5_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_193-11_0_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_193-11_0_5_node_78 | 0.4 | n |  | TRUE
56 | bus_LV_193-11_0_5_node_138 | 0.4 | n |  | TRUE
57 | bus_LV_193-11_0_5_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_193-11_0_5_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_193-11_0_5_node_139 | 0.4 | n |  | TRUE
60 | bus_LV_193-11_0_5_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_193-11_0_5_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_193-11_0_5_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_193-11_0_5_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_193-11_0_5_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_193-11_0_5_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_193-11_0_5_node_82 | 0.4 | n |  | TRUE
67 | bus_LV_193-11_0_5_node_144 | 0.4 | n |  | TRUE
68 | bus_LV_193-11_0_5_node_146 | 0.4 | n |  | TRUE
69 | bus_LV_193-11_0_5_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_193-11_0_5_node_145 | 0.4 | n |  | TRUE
71 | bus_LV_193-11_0_5_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_193-11_0_5_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_193-11_0_5_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_193-11_0_5_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_193-11_0_5_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_193-11_0_5_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_193-11_0_5_node_97 | 0.4 | n |  | TRUE
78 | bus_LV_193-11_0_5_node_122 | 0.4 | n |  | TRUE
79 | bus_LV_193-11_0_5_node_112 | 0.4 | n |  | TRUE
80 | bus_LV_193-11_0_5_node_119 | 0.4 | n |  | TRUE
81 | bus_LV_193-11_0_5_node_156 | 0.4 | n |  | TRUE
82 | bus_LV_193-11_0_5_node_111 | 0.4 | n |  | TRUE
83 | bus_LV_193-11_0_5_node_155 | 0.4 | n |  | TRUE
84 | bus_LV_193-11_0_5_node_154 | 0.4 | n |  | TRUE
85 | bus_LV_193-11_0_5_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_193-11_0_5_node_107 | 0.4 | n |  | TRUE
87 | bus_LV_193-11_0_5_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_193-11_0_5_node_121 | 0.4 | n |  | TRUE
89 | bus_LV_193-11_0_5_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_193-11_0_5_node_66 | 0.4 | n |  | TRUE
91 | bus_LV_193-11_0_5_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_193-11_0_5_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_193-11_0_5_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_193-11_0_5_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_193-11_0_5_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_193-11_0_5_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_193-11_0_5_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_193-11_0_5_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_193-11_0_5_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_193-11_0_5_node_142 | 0.4 | n |  | TRUE
101 | bus_LV_193-11_0_5_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_193-11_0_5_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_193-11_0_5_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_193-11_0_5_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_193-11_0_5_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_193-11_0_5_node_80 | 0.4 | n |  | TRUE
107 | bus_LV_193-11_0_5_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_193-11_0_5_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_193-11_0_5_node_85 | 0.4 | n |  | TRUE
110 | bus_LV_193-11_0_5_node_152 | 0.4 | n |  | TRUE
111 | bus_LV_193-11_0_5_node_149 | 0.4 | n |  | TRUE
112 | bus_LV_193-11_0_5_node_98 | 0.4 | n |  | TRUE
113 | bus_LV_193-11_0_5_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_193-11_0_5_node_93 | 0.4 | n |  | TRUE
115 | bus_LV_193-11_0_5_node_86 | 0.4 | n |  | TRUE
116 | bus_LV_193-11_0_5_node_153 | 0.4 | n |  | TRUE
117 | bus_LV_193-11_0_5_node_151 | 0.4 | n |  | TRUE
118 | bus_LV_193-11_0_5_node_89 | 0.4 | n |  | TRUE
119 | bus_LV_193-11_0_5_node_88 | 0.4 | n |  | TRUE
120 | bus_LV_193-11_0_5_node_158 | 0.4 | n |  | TRUE
121 | bus_LV_193-11_0_5_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_193-11_0_5_node_90 | 0.4 | n |  | TRUE
123 | bus_LV_193-11_0_5_node_101 | 0.4 | n |  | TRUE
124 | bus_LV_193-11_0_5_node_117 | 0.4 | n |  | TRUE
125 | bus_LV_193-11_0_5_node_147 | 0.4 | n |  | TRUE
126 | bus_LV_193-11_0_5_node_143 | 0.4 | n |  | TRUE
127 | bus_LV_193-11_0_5_node_150 | 0.4 | n |  | TRUE
128 | bus_LV_193-11_0_5_node_108 | 0.4 | n |  | TRUE
129 | bus_LV_193-11_0_5_node_109 | 0.4 | n |  | TRUE
130 | bus_LV_193-11_0_5_node_104 | 0.4 | n |  | TRUE
131 | bus_LV_193-11_0_5_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_193-11_0_5_node_148 | 0.4 | n |  | TRUE
133 | bus_LV_193-11_0_5_node_118 | 0.4 | n |  | TRUE
134 | bus_LV_193-11_0_5_node_116 | 0.4 | n |  | TRUE
135 | bus_LV_193-11_0_5_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_193-11_0_5_node_123 | 0.4 | n |  | TRUE
137 | bus_LV_193-11_0_5_node_124 | 0.4 | n |  | TRUE
138 | bus_LV_193-11_0_5_node_125 | 0.4 | n |  | TRUE
139 | bus_LV_193-11_0_5_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_193-11_0_5_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_193-11_0_5_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_193-11_0_5_node_132 | 0.4 | n |  | TRUE
143 | bus_LV_193-11_0_5_node_129 | 0.4 | n |  | TRUE
144 | bus_LV_193-11_0_5_node_130 | 0.4 | n |  | TRUE
145 | bus_LV_193-11_0_5_node_131 | 0.4 | n |  | TRUE
146 | bus_LV_193-11_0_5_node_133 | 0.4 | n |  | TRUE
147 | bus_LV_193-11_0_5_node_134 | 0.4 | n |  | TRUE
148 | bus_LV_193-11_0_5_node_140 | 0.4 | n |  | TRUE
149 | bus_LV_193-11_0_5_node_141 | 0.4 | n |  | TRUE
150 | bus_MV_365_0_node_187 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_193-11_0_5_load_0 | 0 | 0.00085294 | 0.00021377 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_193-11_0_5_load_1 | 1 | 0.00093008 | 0.0002331 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_193-11_0_5_load_4 | 3 | 0.0016011 | 0.00040128 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_193-11_0_5_load_7 | 4 | 0.0021352 | 0.00053513 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_193-11_0_5_load_136 | 6 | 0.0015542 | 0.00038951 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_193-11_0_5_load_137 | 7 | 0.0025904 | 0.00064922 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_193-11_0_5_load_103 | 8 | 0.0017433 | 0.00043691 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_193-11_0_5_load_135 | 9 | 0.0020377 | 0.00051069 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_193-11_0_5_load_8 | 10 | 0.00059058 | 0.00014801 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_193-11_0_5_load_102 | 12 | 0.0017523 | 0.00043917 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_193-11_0_5_load_14 | 13 | 0.0018501 | 0.00046369 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_193-11_0_5_load_9 | 14 | 0.0018093 | 0.00045346 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_193-11_0_5_load_10 | 15 | 0.0032598 | 0.00081698 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_193-11_0_5_load_11 | 16 | 0.0019311 | 0.00048398 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_193-11_0_5_load_12 | 17 | 0.00078344 | 0.00019635 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_193-11_0_5_load_13 | 18 | 0.0013891 | 0.00034815 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_193-11_0_5_load_15 | 20 | 0.0018817 | 0.00047161 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_193-11_0_5_load_17 | 21 | 0.0013974 | 0.00035022 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_193-11_0_5_load_157 | 22 | 0.0017486 | 0.00043824 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_193-11_0_5_load_19 | 23 | 0.001426 | 0.0003574 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_193-11_0_5_load_20 | 25 | 0.0005935 | 0.00014875 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_193-11_0_5_load_21 | 26 | 0.0045986 | 0.0011525 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_193-11_0_5_load_22 | 27 | 0.0045957 | 0.0011518 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_193-11_0_5_load_23 | 29 | 0.0023252 | 0.00058275 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_193-11_0_5_load_63 | 30 | 0.0034424 | 0.00086276 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_193-11_0_5_load_106 | 31 | 0.0037906 | 0.00095001 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_193-11_0_5_load_24 | 33 | 0.002587 | 0.00064836 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_193-11_0_5_load_61 | 34 | 0.0021045 | 0.00052744 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_193-11_0_5_load_105 | 35 | 0.0036432 | 0.00091307 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_193-11_0_5_load_25 | 36 | 0.0016857 | 0.00042248 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_193-11_0_5_load_26 | 37 | 0.0023389 | 0.00058618 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_193-11_0_5_load_45 | 38 | 0.0019458 | 0.00048767 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_193-11_0_5_load_30 | 40 | 0.0014692 | 0.00036821 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_193-11_0_5_load_34 | 42 | 0.0019072 | 0.00047798 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_193-11_0_5_load_32 | 44 | 0.001547 | 0.00038773 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_193-11_0_5_load_33 | 45 | 0.0013027 | 0.00032649 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_193-11_0_5_load_36 | 46 | 0.00097 | 0.00024311 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_193-11_0_5_load_37 | 48 | 0.0012721 | 0.00031883 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_193-11_0_5_load_46 | 49 | 0.0041208 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_193-11_0_5_load_40 | 50 | 0.0010444 | 0.00026174 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_193-11_0_5_load_38 | 51 | 0.0014114 | 0.00035374 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_193-11_0_5_load_43 | 53 | 0.0082655 | 0.0020715 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_193-11_0_5_load_44 | 54 | 0.010902 | 0.0027322 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_193-11_0_5_load_78 | 55 | 0.0027656 | 0.00069313 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_193-11_0_5_load_138 | 56 | 0.010393 | 0.0026048 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_193-11_0_5_load_62 | 57 | 0.0020651 | 0.00051755 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_193-11_0_5_load_139 | 59 | 0.0082526 | 0.0020683 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_193-11_0_5_load_59 | 60 | 0.0013224 | 0.00033141 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_193-11_0_5_load_47 | 61 | 0.0047859 | 0.0011995 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_193-11_0_5_load_52 | 64 | 0.0069824 | 0.0017499 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_193-11_0_5_load_53 | 65 | 0.0089462 | 0.0022421 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_193-11_0_5_load_82 | 66 | 0.021284 | 0.0053343 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_193-11_0_5_load_146 | 68 | 0.0046691 | 0.0011702 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_193-11_0_5_load_145 | 70 | 0.016662 | 0.0041759 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_193-11_0_5_load_55 | 71 | 0.001602 | 0.00040149 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_193-11_0_5_load_56 | 72 | 0.0022586 | 0.00056606 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_193-11_0_5_load_57 | 73 | 0.0012526 | 0.00031392 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_193-11_0_5_load_60 | 75 | 0.0014069 | 0.00035261 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_193-11_0_5_load_122 | 78 | 0.0040682 | 0.0010196 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_193-11_0_5_load_156 | 81 | 0.0018204 | 0.00045624 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_193-11_0_5_load_155 | 83 | 0.0019291 | 0.00048348 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_193-11_0_5_load_110 | 85 | 0.0020296 | 0.00050867 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_193-11_0_5_load_107 | 86 | 0.0021155 | 0.00053019 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_193-11_0_5_load_121 | 88 | 0.0045984 | 0.0011525 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_193-11_0_5_load_65 | 89 | 0.0066881 | 0.0016762 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_193-11_0_5_load_66 | 90 | 0.0091691 | 0.002298 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_193-11_0_5_load_72 | 96 | 0.010375 | 0.0026002 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_193-11_0_5_load_94 | 97 | 0.019084 | 0.0047829 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_193-11_0_5_load_84 | 98 | 0.0088633 | 0.0022214 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_193-11_0_5_load_77 | 99 | 0.019628 | 0.0049194 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_193-11_0_5_load_142 | 100 | 0.01855 | 0.004649 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_193-11_0_5_load_99 | 101 | 0.040064 | 0.010041 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_193-11_0_5_load_75 | 102 | 0.0013143 | 0.00032938 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_193-11_0_5_load_73 | 103 | 0.00046329 | 0.00011611 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_193-11_0_5_load_74 | 104 | 0.0073658 | 0.001846 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_193-11_0_5_load_92 | 107 | 0.00073313 | 0.00018374 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_193-11_0_5_load_85 | 109 | 0.0025761 | 0.00064563 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_193-11_0_5_load_152 | 110 | 0.001392 | 0.00034886 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_193-11_0_5_load_149 | 111 | 0.0014461 | 0.00036243 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_193-11_0_5_load_98 | 112 | 0.0024763 | 0.00062063 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_193-11_0_5_load_93 | 114 | 0.00081747 | 0.00020488 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_193-11_0_5_load_153 | 116 | 0.0014182 | 0.00035544 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_193-11_0_5_load_158 | 120 | 0.0017423 | 0.00043666 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_193-11_0_5_load_100 | 121 | 0.0012872 | 0.0003226 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_193-11_0_5_load_101 | 123 | 0.0018076 | 0.00045303 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_193-11_0_5_load_147 | 125 | 0.012224 | 0.0030636 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_193-11_0_5_load_143 | 126 | 0.0040158 | 0.0010065 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_193-11_0_5_load_108 | 128 | 0.0029775 | 0.00074624 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_193-11_0_5_load_104 | 130 | 0.0017331 | 0.00043435 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_193-11_0_5_load_115 | 131 | 0.0024711 | 0.00061932 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_193-11_0_5_load_148 | 132 | 0.0022427 | 0.00056208 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_193-11_0_5_load_118 | 133 | 0.00058185 | 0.00014582 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_193-11_0_5_load_116 | 134 | 0.006794 | 0.0017027 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_193-11_0_5_load_120 | 135 | 0.0024913 | 0.00062438 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_193-11_0_5_load_123 | 136 | 0.003549 | 0.00088947 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_193-11_0_5_load_124 | 137 | 0.0033053 | 0.00082839 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_193-11_0_5_load_125 | 138 | 0.0032831 | 0.00082281 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_193-11_0_5_load_127 | 140 | 0.012724 | 0.0031889 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_193-11_0_5_load_128 | 141 | 0.0015813 | 0.00039632 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_193-11_0_5_load_132 | 142 | 0.00094515 | 0.00023688 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_193-11_0_5_load_129 | 143 | 0.0034649 | 0.00086838 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_193-11_0_5_load_130 | 144 | 0.0011641 | 0.00029175 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_193-11_0_5_load_131 | 145 | 0.0016177 | 0.00040543 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_193-11_0_5_load_133 | 146 | 0.0017343 | 0.00043465 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_193-11_0_5_load_134 | 147 | 0.0021468 | 0.00053803 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_193-11_0_5_load_140 | 148 | 0.0019099 | 0.00047866 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_193-11_0_5_load_141 | 149 | 0.0020632 | 0.0005171 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_193-11_0_5_line_0 |  | 0 | 1 | 0.022513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_193-11_0_5_line_1 |  | 0 | 2 | 0.020576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_193-11_0_5_line_2 |  | 2 | 3 | 0.017308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_193-11_0_5_line_3 |  | 3 | 4 | 0.038636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_193-11_0_5_line_4 |  | 4 | 8 | 0.0072736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_193-11_0_5_line_5 |  | 5 | 6 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_193-11_0_5_line_6 |  | 5 | 7 | 0.0060541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_193-11_0_5_line_7 |  | 6 | 9 | 0.019717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_193-11_0_5_line_8 |  | 8 | 12 | 0.022214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_193-11_0_5_line_9 |  | 9 | 147 | 0.010242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_193-11_0_5_line_10 |  | 10 | 11 | 0.015782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_193-11_0_5_line_11 |  | 11 | 13 | 0.025069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_193-11_0_5_line_12 |  | 12 | 130 | 0.0079847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_193-11_0_5_line_13 |  | 13 | 16 | 0.032308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_193-11_0_5_line_14 |  | 14 | 15 | 0.015237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_193-11_0_5_line_15 |  | 14 | 16 | 0.0044574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_193-11_0_5_line_16 |  | 15 | 17 | 0.029401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_193-11_0_5_line_17 |  | 17 | 18 | 0.0080283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_193-11_0_5_line_18 |  | 18 | 19 | 0.025235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_193-11_0_5_line_19 |  | 18 | 20 | 0.045148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_193-11_0_5_line_20 |  | 19 | 22 | 0.024547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_193-11_0_5_line_21 |  | 20 | 21 | 0.031376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_193-11_0_5_line_22 |  | 21 | 23 | 0.0055485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_193-11_0_5_line_23 |  | 23 | 28 | 0.032519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_193-11_0_5_line_24 |  | 24 | 25 | 0.022738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_193-11_0_5_line_25 |  | 24 | 26 | 0.032184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_193-11_0_5_line_26 |  | 24 | 27 | 0.021839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_193-11_0_5_line_27 |  | 25 | 29 | 0.020643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_193-11_0_5_line_28 |  | 26 | 30 | 0.0081865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_193-11_0_5_line_29 |  | 27 | 31 | 0.029323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_193-11_0_5_line_30 |  | 28 | 32 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_193-11_0_5_line_31 |  | 29 | 33 | 0.0087373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_193-11_0_5_line_32 |  | 30 | 34 | 0.0037404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_193-11_0_5_line_33 |  | 31 | 35 | 0.022863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_193-11_0_5_line_34 |  | 32 | 40 | 0.016161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_193-11_0_5_line_35 |  | 33 | 36 | 0.015587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_193-11_0_5_line_36 |  | 35 | 130 | 0.020949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_193-11_0_5_line_37 |  | 36 | 37 | 0.026282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_193-11_0_5_line_38 |  | 37 | 38 | 0.012789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_193-11_0_5_line_39 |  | 38 | 39 | 0.017194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_193-11_0_5_line_40 |  | 39 | 47 | 0.028208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_193-11_0_5_line_41 |  | 39 | 44 | 0.039647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_193-11_0_5_line_42 |  | 40 | 41 | 0.019332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_193-11_0_5_line_43 |  | 41 | 44 | 0.023277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_193-11_0_5_line_44 |  | 41 | 45 | 0.024298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_193-11_0_5_line_45 |  | 42 | 43 | 0.052704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_193-11_0_5_line_46 |  | 43 | 48 | 0.027814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_193-11_0_5_line_47 |  | 45 | 46 | 0.0035066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_193-11_0_5_line_48 |  | 47 | 49 | 0.0035769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_193-11_0_5_line_49 |  | 47 | 50 | 0.018393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_193-11_0_5_line_50 |  | 48 | 51 | 0.026634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_193-11_0_5_line_51 |  | 49 | 57 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_193-11_0_5_line_52 |  | 50 | 51 | 0.0051433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_193-11_0_5_line_53 |  | 52 | 53 | 0.015556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_193-11_0_5_line_54 |  | 52 | 54 | 0.013752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_193-11_0_5_line_55 |  | 53 | 55 | 0.035071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_193-11_0_5_line_56 |  | 54 | 56 | 0.026493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_193-11_0_5_line_57 |  | 55 | 58 | 0.061971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_193-11_0_5_line_58 |  | 56 | 59 | 0.020299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_193-11_0_5_line_59 |  | 57 | 60 | 0.0087699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_193-11_0_5_line_60 |  | 58 | 87 | 0.037853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_193-11_0_5_line_61 |  | 58 | 104 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_193-11_0_5_line_62 |  | 59 | 148 | 0.03535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_193-11_0_5_line_63 |  | 60 | 73 | 0.013934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_193-11_0_5_line_64 |  | 61 | 62 | 0.01687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_193-11_0_5_line_65 |  | 62 | 63 | 0.033091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_193-11_0_5_line_66 |  | 63 | 64 | 0.042036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_193-11_0_5_line_67 |  | 63 | 65 | 0.0090063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_193-11_0_5_line_68 |  | 64 | 66 | 0.0074212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_193-11_0_5_line_69 |  | 65 | 67 | 0.024571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_193-11_0_5_line_70 |  | 66 | 69 | 0.018601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_193-11_0_5_line_71 |  | 67 | 70 | 0.019637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_193-11_0_5_line_72 |  | 67 | 68 | 0.017953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_193-11_0_5_line_73 |  | 69 | 95 | 0.012412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_193-11_0_5_line_74 |  | 70 | 125 | 0.009221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_193-11_0_5_line_75 |  | 71 | 72 | 0.016805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_193-11_0_5_line_76 |  | 71 | 73 | 0.011258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_193-11_0_5_line_77 |  | 72 | 74 | 0.026758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_193-11_0_5_line_78 |  | 74 | 75 | 0.014933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_193-11_0_5_line_79 |  | 75 | 76 | 0.018647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_193-11_0_5_line_80 |  | 76 | 77 | 0.033829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_193-11_0_5_line_81 |  | 76 | 78 | 0.025948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_193-11_0_5_line_82 |  | 77 | 85 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_193-11_0_5_line_83 |  | 77 | 86 | 0.015392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_193-11_0_5_line_84 |  | 77 | 87 | 0.025878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_193-11_0_5_line_85 |  | 78 | 88 | 0.0081367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_193-11_0_5_line_86 |  | 79 | 80 | 0.061099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_193-11_0_5_line_87 |  | 79 | 81 | 0.036619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_193-11_0_5_line_88 |  | 80 | 124 | 0.044316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_193-11_0_5_line_89 |  | 81 | 82 | 0.0011462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_193-11_0_5_line_90 |  | 82 | 83 | 0.024898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_193-11_0_5_line_91 |  | 82 | 84 | 0.019918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_193-11_0_5_line_92 |  | 83 | 127 | 0.020925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_193-11_0_5_line_93 |  | 84 | 116 | 0.019965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_193-11_0_5_line_94 |  | 86 | 128 | 0.0045078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_193-11_0_5_line_95 |  | 87 | 105 | 0.006999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_193-11_0_5_line_96 |  | 88 | 136 | 0.032308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_193-11_0_5_line_97 |  | 89 | 90 | 0.0051404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_193-11_0_5_line_98 |  | 89 | 91 | 0.030247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_193-11_0_5_line_99 |  | 90 | 92 | 0.01257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_193-11_0_5_line_100 |  | 91 | 93 | 0.022988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_193-11_0_5_line_101 |  | 92 | 94 | 0.028839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_193-11_0_5_line_102 |  | 93 | 95 | 0.011797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_193-11_0_5_line_103 |  | 93 | 96 | 0.014496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_193-11_0_5_line_104 |  | 94 | 97 | 0.014133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_193-11_0_5_line_105 |  | 95 | 98 | 0.013352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_193-11_0_5_line_106 |  | 96 | 99 | 0.014217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_193-11_0_5_line_107 |  | 97 | 100 | 0.035955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_193-11_0_5_line_108 |  | 98 | 101 | 0.017623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_193-11_0_5_line_109 |  | 99 | 102 | 0.017361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
110 | LV_193-11_0_5_line_110 |  | 100 | 126 | 0.029735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_193-11_0_5_line_111 |  | 101 | 118 | 0.0034125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_193-11_0_5_line_112 |  | 102 | 103 | 0.022851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_193-11_0_5_line_113 |  | 103 | 104 | 0.0060847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_193-11_0_5_line_114 |  | 105 | 111 | 0.0064429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_193-11_0_5_line_115 |  | 106 | 107 | 0.014775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_193-11_0_5_line_116 |  | 106 | 108 | 0.046529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_193-11_0_5_line_117 |  | 106 | 109 | 0.069094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_193-11_0_5_line_118 |  | 107 | 114 | 0.012519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_193-11_0_5_line_119 |  | 108 | 110 | 0.022445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_193-11_0_5_line_120 |  | 109 | 115 | 0.035334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_193-11_0_5_line_121 |  | 110 | 117 | 0.012579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_193-11_0_5_line_122 |  | 111 | 117 | 0.028057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_193-11_0_5_line_123 |  | 112 | 113 | 0.00038903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_193-11_0_5_line_124 |  | 113 | 129 | 0.023566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_193-11_0_5_line_125 |  | 114 | 122 | 0.020366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_193-11_0_5_line_126 |  | 115 | 119 | 0.063599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_193-11_0_5_line_127 |  | 117 | 127 | 0.0027359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_193-11_0_5_line_128 |  | 118 | 121 | 0.025743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_193-11_0_5_line_129 |  | 119 | 120 | 0.064249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_193-11_0_5_line_130 |  | 122 | 123 | 0.000966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_193-11_0_5_line_131 |  | 124 | 133 | 0.0034629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_193-11_0_5_line_132 |  | 124 | 134 | 0.025997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_193-11_0_5_line_133 |  | 128 | 129 | 0.01361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_193-11_0_5_line_134 |  | 129 | 131 | 0.023281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_193-11_0_5_line_135 |  | 131 | 132 | 0.0023461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_193-11_0_5_line_136 |  | 133 | 135 | 0.0099276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_193-11_0_5_line_137 |  | 136 | 137 | 0.0062631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_193-11_0_5_line_138 |  | 137 | 138 | 0.021897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_193-11_0_5_line_139 |  | 138 | 139 | 0.0020612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_193-11_0_5_line_140 |  | 139 | 140 | 0.046609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_193-11_0_5_line_141 |  | 139 | 141 | 0.01646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_193-11_0_5_line_142 |  | 140 | 142 | 0.0033109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_193-11_0_5_line_143 |  | 141 | 143 | 0.0065383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_193-11_0_5_line_144 |  | 143 | 144 | 0.019448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_193-11_0_5_line_145 |  | 144 | 145 | 0.0087361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_193-11_0_5_line_146 |  | 145 | 146 | 0.016829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_193-11_0_5_line_147 |  | 146 | 147 | 0.015334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_193-11_0_5_line_148 |  | 148 | 149 | 0.033674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_193-11_0_5_trafo_76 | 0.63 MVA 20/0.4 kV | 150 | 58 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2690320.9624 | 1247092.0447 | 2690305.4127 | 1247087.7196 | 2690299.0652 | 1247088.2846
1 | 2690340.3235 | 1247098.9597 | 2690325.7984 | 1247093.3898 | 2690320.9624 | 1247092.0447
2 | 2690340.3235 | 1247098.9597 | 2690333.9 | 1247115.0317
3 | 2690333.3617 | 1247151.7286 | 2690327.6946 | 1247130.5578 | 2690333.9 | 1247115.0317
4 | 2690333.3617 | 1247151.7286 | 2690335.2426 | 1247158.7548
5 | 2690381.3203 | 1247106.4122 | 2690383.8917 | 1247112.6561 | 2690385.9249 | 1247119.2777
6 | 2690381.3203 | 1247106.4122 | 2690387.3245 | 1247107.1872
7 | 2690390.546 | 1247138.4263 | 2690389.3486 | 1247133.7773 | 2690387.4901 | 1247124.3753 | 2690385.9249 | 1247119.2777
8 | 2690334.7231 | 1247180.45 | 2690337.3362 | 1247166.5762 | 2690335.2426 | 1247158.7548
9 | 2690392.6995 | 1247148.4387 | 2690390.6252 | 1247138.7339 | 2690390.546 | 1247138.4263
10 | 2690234.2771 | 1247246.2673 | 2690234.1525 | 1247233.1221 | 2690233.7517 | 1247230.5164
11 | 2690234.2771 | 1247246.2673 | 2690232.3551 | 1247257.8912 | 2690228.815 | 1247270.6977
12 | 2690334.7231 | 1247180.45 | 2690333.2452 | 1247188.2968
13 | 2690228.815 | 1247270.6977 | 2690197.2041 | 1247277.3712
14 | 2690187.1134 | 1247293.0753 | 2690193.0767 | 1247279.0541
15 | 2690197.2041 | 1247277.3712 | 2690193.0767 | 1247279.0541
16 | 2690187.1134 | 1247293.0753 | 2690185.2345 | 1247297.4932 | 2690173.1984 | 1247318.9478
17 | 2690169.2704 | 1247325.9496 | 2690173.1984 | 1247318.9478
18 | 2690144.0552 | 1247326.9448 | 2690169.2704 | 1247325.9496 | 2690169.2704 | 1247325.9496
19 | 2690206.4691 | 1247351.5342 | 2690169.2704 | 1247325.9496
20 | 2690157.0404 | 1247306.0932 | 2690144.0552 | 1247326.9448
21 | 2690198.2219 | 1247381.7953 | 2690198.2597 | 1247381.2321 | 2690206.4691 | 1247351.5342
22 | 2690198.2219 | 1247381.7953 | 2690197.8512 | 1247387.3314
23 | 2690195.6787 | 1247419.7774 | 2690197.8512 | 1247387.3314
24 | 2690295.153 | 1247274.693 | 2690282.9091 | 1247293.8532
25 | 2690295.153 | 1247274.693 | 2690300.7128 | 1247277.6688 | 2690306.3699 | 1247284.1709 | 2690317.5257 | 1247297.34
26 | 2690295.153 | 1247274.693 | 2690305.9211 | 1247255.6928
27 | 2690282.9091 | 1247293.8532 | 2690274.4215 | 1247307.1351 | 2690272.0774 | 1247311.4166
28 | 2690317.5257 | 1247297.34 | 2690322.8172 | 1247303.5864
29 | 2690305.9211 | 1247255.6928 | 2690308.5671 | 1247251.0239 | 2690319.3057 | 1247229.6097
30 | 2690195.6787 | 1247419.7774 | 2690196.0371 | 1247433.9491
31 | 2690267.8815 | 1247319.0805 | 2690272.0774 | 1247311.4166
32 | 2690325.2349 | 1247306.4404 | 2690322.8172 | 1247303.5864
33 | 2690319.3057 | 1247229.6097 | 2690324.593 | 1247219.0661 | 2690327.9958 | 1247208.5345
34 | 2690196.0371 | 1247433.9491 | 2690212.1719 | 1247433.0353
35 | 2690260.3963 | 1247332.7521 | 2690260.3963 | 1247332.7521 | 2690267.8815 | 1247319.0805
36 | 2690327.9958 | 1247208.5345 | 2690331.4429 | 1247197.8656 | 2690333.2452 | 1247188.2968
37 | 2690260.3963 | 1247332.7521 | 2690258.0922 | 1247345.1597 | 2690258.3615 | 1247355.7495 | 2690259.0171 | 1247358.7475
38 | 2690263.3075 | 1247370.7472 | 2690259.8375 | 1247362.4993 | 2690259.0171 | 1247358.7475
39 | 2690273.0026 | 1247384.9054 | 2690266.9512 | 1247377.0185 | 2690263.3075 | 1247370.7472 | 2690263.3075 | 1247370.7472
40 | 2690294.6934 | 1247403.016 | 2690273.0026 | 1247384.9054
41 | 2690273.0026 | 1247384.9054 | 2690268.1691 | 1247389.3019 | 2690246.265 | 1247414.1356
42 | 2690231.4726 | 1247431.9422 | 2690212.1719 | 1247433.0353
43 | 2690231.4726 | 1247431.9422 | 2690232.0421 | 1247430.2607 | 2690246.265 | 1247414.1356
44 | 2690231.4726 | 1247431.9422 | 2690223.6962 | 1247454.9626
45 | 2690258.579 | 1247468.927 | 2690238.1314 | 1247487.7411 | 2690220.1595 | 1247505.0005
46 | 2690258.579 | 1247468.927 | 2690257.1117 | 1247464.0899 | 2690257.7718 | 1247455.4712 | 2690264.9497 | 1247443.3168
47 | 2690222.574 | 1247458.2847 | 2690223.6962 | 1247454.9626
48 | 2690294.6934 | 1247403.016 | 2690297.3248 | 1247400.5931
49 | 2690294.6934 | 1247403.016 | 2690283.0529 | 1247417.2563
50 | 2690279.7978 | 1247421.2384 | 2690276.8818 | 1247424.8057 | 2690266.6034 | 1247440.5166 | 2690264.9497 | 1247443.3168
51 | 2690297.3248 | 1247400.5931 | 2690307.4247 | 1247391.2937
52 | 2690279.7978 | 1247421.2384 | 2690283.0529 | 1247417.2563
53 | 2690357.8998 | 1247429.5765 | 2690372.5048 | 1247424.2203
54 | 2690357.8998 | 1247429.5765 | 2690359.8964 | 1247435.3668 | 2690361.4925 | 1247442.6522 | 2690361.4543 | 1247442.8169
55 | 2690404.0439 | 1247408.8942 | 2690392.1247 | 1247414.8314 | 2690373.328 | 1247423.9184 | 2690372.5048 | 1247424.2203
56 | 2690347.9011 | 1247464.613 | 2690353.8978 | 1247459.6938 | 2690358.4251 | 1247453.0911 | 2690360.2067 | 1247448.2034 | 2690361.4543 | 1247442.8169
57 | 2690457.3362 | 1247377.2974 | 2690408.9542 | 1247406.4483 | 2690404.0439 | 1247408.8942
58 | 2690347.9011 | 1247464.613 | 2690347.7629 | 1247464.7263 | 2690335.5276 | 1247469.0654 | 2690328.7805 | 1247471.3977
59 | 2690314.0536 | 1247385.5588 | 2690310.7671 | 1247388.2163 | 2690307.4247 | 1247391.2937
60 | 2690433.4004 | 1247347.9213 | 2690437.0877 | 1247352.3142 | 2690444.3951 | 1247361.0433 | 2690447.057 | 1247364.3197 | 2690450.0747 | 1247368.0352 | 2690452.5659 | 1247371.1089 | 2690457.3362 | 1247377.2974
61 | 2690457.3362 | 1247377.2974 | 2690459.9674 | 1247380.1063 | 2690470.1185 | 1247385.1428 | 2690474.9277 | 1247386.6899
62 | 2690328.7805 | 1247471.3977 | 2690322.0334 | 1247473.73 | 2690301.8077 | 1247480.9386 | 2690295.4522 | 1247483.1819
63 | 2690324.8888 | 1247376.7974 | 2690314.0536 | 1247385.5588
64 | 2690609.4005 | 1247513.9108 | 2690622.0569 | 1247502.7574
65 | 2690609.4005 | 1247513.9108 | 2690593.1668 | 1247494.6816 | 2690591.215 | 1247486.9682
66 | 2690591.215 | 1247486.9682 | 2690587.8797 | 1247485.7496 | 2690565.168 | 1247454.6809
67 | 2690591.215 | 1247486.9682 | 2690598.1829 | 1247481.2618
68 | 2690560.7884 | 1247448.6898 | 2690565.168 | 1247454.6809
69 | 2690617.193 | 1247465.6934 | 2690598.1829 | 1247481.2618
70 | 2690549.8112 | 1247433.6734 | 2690560.7884 | 1247448.6898
71 | 2690617.193 | 1247465.6934 | 2690605.9185 | 1247449.6151
72 | 2690617.193 | 1247465.6934 | 2690632.5036 | 1247456.319
73 | 2690549.8112 | 1247433.6734 | 2690542.9672 | 1247423.3055
74 | 2690605.9185 | 1247449.6151 | 2690604.6847 | 1247447.8555 | 2690609.8985 | 1247443.0776
75 | 2690333.6378 | 1247369.7128 | 2690346.6958 | 1247359.1341
76 | 2690333.6378 | 1247369.7128 | 2690327.0041 | 1247375.087 | 2690324.8888 | 1247376.7974
77 | 2690367.4872 | 1247342.2901 | 2690346.6958 | 1247359.1341
78 | 2690367.4872 | 1247342.2901 | 2690379.053 | 1247332.8437
79 | 2690393.4948 | 1247321.0483 | 2690379.053 | 1247332.8437
80 | 2690393.4948 | 1247321.0483 | 2690403.9307 | 1247312.3786 | 2690416.8899 | 1247327.9545
81 | 2690393.4948 | 1247321.0483 | 2690387.0965 | 1247313.6229 | 2690382.0885 | 1247305.6739 | 2690379.6097 | 1247299.394
82 | 2690416.8899 | 1247327.9545 | 2690425.8673 | 1247316.0956
83 | 2690416.8899 | 1247327.9545 | 2690407.3991 | 1247340.0729
84 | 2690433.4004 | 1247347.9213 | 2690431.0046 | 1247345.0271 | 2690429.6176 | 1247343.3491 | 2690428.1936 | 1247341.6261 | 2690425.6272 | 1247338.5291 | 2690424.2178 | 1247336.8285 | 2690421.8222 | 1247333.9231 | 2690416.8899 | 1247327.9545
85 | 2690377.3406 | 1247291.61 | 2690378.2557 | 1247295.9638 | 2690379.6097 | 1247299.394
86 | 2690476.1028 | 1247263.8204 | 2690481.3654 | 1247257.5626 | 2690484.9381 | 1247251.1568 | 2690492.5756 | 1247225.4094 | 2690494.6874 | 1247220.6826 | 2690503.3973 | 1247210.2965
87 | 2690476.1028 | 1247263.8204 | 2690482.7025 | 1247268.936 | 2690473.3164 | 1247280.5794 | 2690483.6737 | 1247288.9437
88 | 2690503.3973 | 1247210.2965 | 2690494.6874 | 1247220.6826 | 2690505.3094 | 1247246.8421 | 2690505.7624 | 1247249.3287
89 | 2690482.9799 | 1247289.856 | 2690483.6737 | 1247288.9437
90 | 2690482.9799 | 1247289.856 | 2690467.7864 | 1247309.581
91 | 2690478.1086 | 1247304.6262 | 2690477.4084 | 1247303.9817 | 2690486.453 | 1247292.4443 | 2690482.9799 | 1247289.856
92 | 2690462.0683 | 1247325.1192 | 2690458.0408 | 1247322.2333 | 2690467.7864 | 1247309.581
93 | 2690478.1086 | 1247304.6262 | 2690493.9836 | 1247316.7331
94 | 2690407.3991 | 1247340.0729 | 2690404.6197 | 1247343.6218
95 | 2690433.4004 | 1247347.9213 | 2690437.9163 | 1247342.5639
96 | 2690377.3406 | 1247291.61 | 2690376.4527 | 1247287.3854 | 2690375.6362 | 1247276.0311 | 2690377.1336 | 1247266.5134 | 2690379.0357 | 1247259.8053
97 | 2690494.16 | 1247466.325 | 2690490.4012 | 1247469.8314
98 | 2690516.2773 | 1247445.6927 | 2690494.16 | 1247466.325
99 | 2690481.2931 | 1247478.4947 | 2690490.2767 | 1247469.9476 | 2690490.4012 | 1247469.8314
100 | 2690533.7072 | 1247430.6475 | 2690516.2773 | 1247445.6927
101 | 2690481.2931 | 1247478.4947 | 2690460.7541 | 1247498.7967
102 | 2690542.9672 | 1247423.3055 | 2690539.2661 | 1247426.2512 | 2690533.7072 | 1247430.6475
103 | 2690533.7072 | 1247430.6475 | 2690523.8257 | 1247420.0416
104 | 2690460.7541 | 1247498.7967 | 2690450.7926 | 1247488.7705
105 | 2690542.9672 | 1247423.3055 | 2690553.1734 | 1247414.6972
106 | 2690523.8257 | 1247420.0416 | 2690514.134 | 1247409.6394
107 | 2690424.7597 | 1247513.2697 | 2690430.1307 | 1247510.2049 | 2690450.7926 | 1247488.7705
108 | 2690553.1734 | 1247414.6972 | 2690566.645 | 1247403.3348
109 | 2690500.9568 | 1247398.3939 | 2690511.1956 | 1247406.4856 | 2690514.134 | 1247409.6394
110 | 2690424.7597 | 1247513.2697 | 2690421.9696 | 1247514.8618 | 2690404.5827 | 1247534.8903
111 | 2690569.2536 | 1247401.1346 | 2690566.645 | 1247403.3348
112 | 2690480.72 | 1247388.5533 | 2690493.8497 | 1247392.7772 | 2690500.9568 | 1247398.3939
113 | 2690480.72 | 1247388.5533 | 2690474.9277 | 1247386.6899
114 | 2690437.9163 | 1247342.5639 | 2690439.2387 | 1247343.5293 | 2690442.1201 | 1247339.6832
115 | 2690507.628 | 1247347.2754 | 2690517.4502 | 1247358.3124
116 | 2690485.8535 | 1247349.0223 | 2690480.3232 | 1247355.9987 | 2690481.4026 | 1247362.976 | 2690507.628 | 1247347.2754
117 | 2690507.628 | 1247347.2754 | 2690560.7307 | 1247315.262 | 2690566.9373 | 1247311.8399
118 | 2690525.7731 | 1247367.6647 | 2690517.4502 | 1247358.3124
119 | 2690485.8535 | 1247349.0223 | 2690482.6667 | 1247346.4828 | 2690469.3418 | 1247336.0717 | 2690470.3177 | 1247334.9858
120 | 2690598.7053 | 1247296.45 | 2690589.1618 | 1247300.5851 | 2690579.7458 | 1247304.7778 | 2690566.9373 | 1247311.8399
121 | 2690460.3811 | 1247327.2728 | 2690470.3177 | 1247334.9858
122 | 2690460.3811 | 1247327.2728 | 2690458.9326 | 1247329.1299 | 2690453.2574 | 1247324.8179 | 2690442.1201 | 1247339.6832
123 | 2690415.0923 | 1247368.5355 | 2690415.3305 | 1247368.2279
124 | 2690415.0923 | 1247368.5355 | 2690396.2276 | 1247354.3372
125 | 2690540.5422 | 1247364.4797 | 2690536.9729 | 1247367.205 | 2690530.561 | 1247373.0449 | 2690525.7731 | 1247367.6647
126 | 2690585.7906 | 1247248.3387 | 2690596.1651 | 1247265.4545 | 2690608.0164 | 1247285.2838 | 2690610.348 | 1247293.3589 | 2690606.3423 | 1247293.9871 | 2690598.7053 | 1247296.45
127 | 2690460.3811 | 1247327.2728 | 2690461.0282 | 1247326.4487 | 2690462.0683 | 1247325.1192
128 | 2690569.2536 | 1247401.1346 | 2690591.3153 | 1247387.8692
129 | 2690585.7906 | 1247248.3387 | 2690577.6563 | 1247253.674 | 2690572.7951 | 1247259.3707 | 2690547.6239 | 1247278.2228 | 2690543.5483 | 1247278.9723 | 2690539.9069 | 1247278.0048 | 2690534.6437 | 1247272.4217
130 | 2690539.8116 | 1247363.8458 | 2690540.5422 | 1247364.4797
131 | 2690505.7624 | 1247249.3287 | 2690504.99 | 1247252.7044
132 | 2690505.7624 | 1247249.3287 | 2690513.899 | 1247256.6918 | 2690523.7066 | 1247251.5932 | 2690523.5551 | 1247248.1549 | 2690524.0796 | 1247248.2206
133 | 2690396.2276 | 1247354.3372 | 2690404.6197 | 1247343.6218
134 | 2690396.2276 | 1247354.3372 | 2690381.8703 | 1247372.6637
135 | 2690380.4234 | 1247374.5106 | 2690381.8703 | 1247372.6637
136 | 2690502.7756 | 1247262.3818 | 2690504.99 | 1247252.7044
137 | 2690380.7444 | 1247253.7798 | 2690379.0357 | 1247259.8053
138 | 2690380.7444 | 1247253.7798 | 2690386.7182 | 1247232.713
139 | 2690387.2806 | 1247230.7299 | 2690386.7182 | 1247232.713
140 | 2690387.2806 | 1247230.7299 | 2690412.3082 | 1247238.1059 | 2690415.7509 | 1247237.7359 | 2690419.4274 | 1247235.9128 | 2690423.629 | 1247231.8516 | 2690427.9258 | 1247226.1899
141 | 2690387.2806 | 1247230.7299 | 2690391.7694 | 1247214.8936
142 | 2690429.9273 | 1247223.5525 | 2690427.9258 | 1247226.1899
143 | 2690391.7694 | 1247214.8936 | 2690392.2704 | 1247213.1261 | 2690392.791 | 1247208.4538
144 | 2690392.791 | 1247208.4538 | 2690394.5635 | 1247192.5455 | 2690394.6877 | 1247189.1069
145 | 2690395.0029 | 1247180.3765 | 2690394.6877 | 1247189.1069
146 | 2690395.0029 | 1247180.3765 | 2690395.2044 | 1247174.7975 | 2690394.8874 | 1247163.5558
147 | 2690392.6995 | 1247148.4387 | 2690394.7289 | 1247157.9331 | 2690394.8874 | 1247163.5558
148 | 2690267.92 | 1247500.6048 | 2690272.837 | 1247494.9525 | 2690277.7944 | 1247489.3571 | 2690289.0639 | 1247485.4368 | 2690295.4522 | 1247483.1819

## bus_geodata
| x | y | coords
0 | 2690320.9624 | 1247092.0447
1 | 2690299.0652 | 1247088.2846
2 | 2690340.3235 | 1247098.9597
3 | 2690333.9 | 1247115.0317
4 | 2690333.3617 | 1247151.7286
5 | 2690381.3203 | 1247106.4122
6 | 2690385.9249 | 1247119.2777
7 | 2690387.3245 | 1247107.1872
8 | 2690335.2426 | 1247158.7548
9 | 2690390.546 | 1247138.4263
10 | 2690233.7517 | 1247230.5164
11 | 2690234.2771 | 1247246.2673
12 | 2690334.7231 | 1247180.45
13 | 2690228.815 | 1247270.6977
14 | 2690193.0767 | 1247279.0541
15 | 2690187.1134 | 1247293.0753
16 | 2690197.2041 | 1247277.3712
17 | 2690173.1984 | 1247318.9478
18 | 2690169.2704 | 1247325.9496
19 | 2690144.0552 | 1247326.9448
20 | 2690206.4691 | 1247351.5342
21 | 2690198.2219 | 1247381.7953
22 | 2690157.0404 | 1247306.0932
23 | 2690197.8512 | 1247387.3314
24 | 2690295.153 | 1247274.693
25 | 2690282.9091 | 1247293.8532
26 | 2690317.5257 | 1247297.34
27 | 2690305.9211 | 1247255.6928
28 | 2690195.6787 | 1247419.7774
29 | 2690272.0774 | 1247311.4166
30 | 2690322.8172 | 1247303.5864
31 | 2690319.3057 | 1247229.6097
32 | 2690196.0371 | 1247433.9491
33 | 2690267.8815 | 1247319.0805
34 | 2690325.2349 | 1247306.4404
35 | 2690327.9958 | 1247208.5345
36 | 2690260.3963 | 1247332.7521
37 | 2690259.0171 | 1247358.7475
38 | 2690263.3075 | 1247370.7472
39 | 2690273.0026 | 1247384.9054
40 | 2690212.1719 | 1247433.0353
41 | 2690231.4726 | 1247431.9422
42 | 2690220.1595 | 1247505.0005
43 | 2690258.579 | 1247468.927
44 | 2690246.265 | 1247414.1356
45 | 2690223.6962 | 1247454.9626
46 | 2690222.574 | 1247458.2847
47 | 2690294.6934 | 1247403.016
48 | 2690264.9497 | 1247443.3168
49 | 2690297.3248 | 1247400.5931
50 | 2690283.0529 | 1247417.2563
51 | 2690279.7978 | 1247421.2384
52 | 2690357.8998 | 1247429.5765
53 | 2690372.5048 | 1247424.2203
54 | 2690361.4543 | 1247442.8169
55 | 2690404.0439 | 1247408.8942
56 | 2690347.9011 | 1247464.613
57 | 2690307.4247 | 1247391.2937
58 | 2690457.3362 | 1247377.2974
59 | 2690328.7805 | 1247471.3977
60 | 2690314.0536 | 1247385.5588
61 | 2690622.0569 | 1247502.7574
62 | 2690609.4005 | 1247513.9108
63 | 2690591.215 | 1247486.9682
64 | 2690565.168 | 1247454.6809
65 | 2690598.1829 | 1247481.2618
66 | 2690560.7884 | 1247448.6898
67 | 2690617.193 | 1247465.6934
68 | 2690632.5036 | 1247456.319
69 | 2690549.8112 | 1247433.6734
70 | 2690605.9185 | 1247449.6151
71 | 2690333.6378 | 1247369.7128
72 | 2690346.6958 | 1247359.1341
73 | 2690324.8888 | 1247376.7974
74 | 2690367.4872 | 1247342.2901
75 | 2690379.053 | 1247332.8437
76 | 2690393.4948 | 1247321.0483
77 | 2690416.8899 | 1247327.9545
78 | 2690379.6097 | 1247299.394
79 | 2690476.1028 | 1247263.8204
80 | 2690503.3973 | 1247210.2965
81 | 2690483.6737 | 1247288.9437
82 | 2690482.9799 | 1247289.856
83 | 2690467.7864 | 1247309.581
84 | 2690478.1086 | 1247304.6262
85 | 2690425.8673 | 1247316.0956
86 | 2690407.3991 | 1247340.0729
87 | 2690433.4004 | 1247347.9213
88 | 2690377.3406 | 1247291.61
89 | 2690494.16 | 1247466.325
90 | 2690490.4012 | 1247469.8314
91 | 2690516.2773 | 1247445.6927
92 | 2690481.2931 | 1247478.4947
93 | 2690533.7072 | 1247430.6475
94 | 2690460.7541 | 1247498.7967
95 | 2690542.9672 | 1247423.3055
96 | 2690523.8257 | 1247420.0416
97 | 2690450.7926 | 1247488.7705
98 | 2690553.1734 | 1247414.6972
99 | 2690514.134 | 1247409.6394
100 | 2690424.7597 | 1247513.2697
101 | 2690566.645 | 1247403.3348
102 | 2690500.9568 | 1247398.3939
103 | 2690480.72 | 1247388.5533
104 | 2690474.9277 | 1247386.6899
105 | 2690437.9163 | 1247342.5639
106 | 2690507.628 | 1247347.2754
107 | 2690517.4502 | 1247358.3124
108 | 2690485.8535 | 1247349.0223
109 | 2690566.9373 | 1247311.8399
110 | 2690470.3177 | 1247334.9858
111 | 2690442.1201 | 1247339.6832
112 | 2690415.3305 | 1247368.2279
113 | 2690415.0923 | 1247368.5355
114 | 2690525.7731 | 1247367.6647
115 | 2690598.7053 | 1247296.45
116 | 2690493.9836 | 1247316.7331
117 | 2690460.3811 | 1247327.2728
118 | 2690569.2536 | 1247401.1346
119 | 2690585.7906 | 1247248.3387
120 | 2690534.6437 | 1247272.4217
121 | 2690591.3153 | 1247387.8692
122 | 2690540.5422 | 1247364.4797
123 | 2690539.8116 | 1247363.8458
124 | 2690505.7624 | 1247249.3287
125 | 2690609.8985 | 1247443.0776
126 | 2690404.5827 | 1247534.8903
127 | 2690462.0683 | 1247325.1192
128 | 2690404.6197 | 1247343.6218
129 | 2690396.2276 | 1247354.3372
130 | 2690333.2452 | 1247188.2968
131 | 2690381.8703 | 1247372.6637
132 | 2690380.4234 | 1247374.5106
133 | 2690504.99 | 1247252.7044
134 | 2690524.0796 | 1247248.2206
135 | 2690502.7756 | 1247262.3818
136 | 2690379.0357 | 1247259.8053
137 | 2690380.7444 | 1247253.7798
138 | 2690386.7182 | 1247232.713
139 | 2690387.2806 | 1247230.7299
140 | 2690427.9258 | 1247226.1899
141 | 2690391.7694 | 1247214.8936
142 | 2690429.9273 | 1247223.5524
143 | 2690392.791 | 1247208.4538
144 | 2690394.6877 | 1247189.1069
145 | 2690395.0029 | 1247180.3765
146 | 2690394.8874 | 1247163.5558
147 | 2690392.6995 | 1247148.4387
148 | 2690295.4522 | 1247483.1819
149 | 2690267.92 | 1247500.6048
150 | 2690481.4026 | 1247362.976

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97273 | -0.52647 | 0.00085294 | 0.00021377
1 | 0.97271 | -0.52685 | 0.00093008 | 0.0002331
2 | 0.97277 | -0.52579 | 0 | 0
3 | 0.9728 | -0.52522 | 0.0016011 | 0.00040128
4 | 0.97292 | -0.52281 | 0.0021352 | 0.00053513
5 | 0.98586 | -0.27092 | 0 | 0
6 | 0.9859 | -0.27029 | 0.0015542 | 0.00038951
7 | 0.98585 | -0.27121 | 0.0025904 | 0.00064922
8 | 0.97296 | -0.52207 | 0.0017433 | 0.00043691
9 | 0.98597 | -0.26882 | 0.0020377 | 0.00051069
10 | 0.97467 | -0.48837 | 0.00059058 | 0.00014801
11 | 0.97468 | -0.4882 | 0 | 0
12 | 0.97311 | -0.5191 | 0.0017523 | 0.00043917
13 | 0.97469 | -0.48793 | 0.0018501 | 0.00046369
14 | 0.97478 | -0.48612 | 0.0018093 | 0.00045346
15 | 0.97487 | -0.48439 | 0.0032598 | 0.00081698
16 | 0.97477 | -0.48648 | 0.0019311 | 0.00048398
17 | 0.97513 | -0.4793 | 0.00078344 | 0.00019635
18 | 0.97521 | -0.4778 | 0.0013891 | 0.00034815
19 | 0.97516 | -0.47861 | 0 | 0
20 | 0.97577 | -0.46674 | 0.0018817 | 0.00047161
21 | 0.97621 | -0.45799 | 0.0013974 | 0.00035022
22 | 0.97512 | -0.47939 | 0.0017486 | 0.00043824
23 | 0.9763 | -0.4563 | 0.001426 | 0.0003574
24 | 0.97465 | -0.48865 | 0 | 0
25 | 0.97535 | -0.47492 | 0.0005935 | 0.00014875
26 | 0.97434 | -0.49464 | 0.0045986 | 0.0011525
27 | 0.97419 | -0.49778 | 0.0045957 | 0.0011518
28 | 0.97684 | -0.44555 | 0 | 0
29 | 0.97599 | -0.46224 | 0.0023252 | 0.00058275
30 | 0.9743 | -0.49547 | 0.0034424 | 0.00086276
31 | 0.97369 | -0.50758 | 0.0037906 | 0.00095001
32 | 0.97708 | -0.44087 | 0 | 0
33 | 0.97628 | -0.45651 | 0.002587 | 0.00064836
34 | 0.9743 | -0.49562 | 0.0021045 | 0.00052744
35 | 0.97338 | -0.51363 | 0.0036432 | 0.00091307
36 | 0.97684 | -0.44556 | 0.0016857 | 0.00042248
37 | 0.97782 | -0.42632 | 0.0023389 | 0.00058618
38 | 0.97833 | -0.41643 | 0.0019458 | 0.00048767
39 | 0.97904 | -0.40253 | 0 | 0
40 | 0.97735 | -0.43554 | 0.0014692 | 0.00036821
41 | 0.9777 | -0.42865 | 0 | 0
42 | 0.98048 | -0.37446 | 0.0019072 | 0.00047798
43 | 0.98057 | -0.37263 | 0 | 0
44 | 0.97818 | -0.41939 | 0.001547 | 0.00038773
45 | 0.97765 | -0.42966 | 0.0013027 | 0.00032649
46 | 0.97765 | -0.42972 | 0.00097 | 0.00024311
47 | 0.98081 | -0.36783 | 0 | 0
48 | 0.98062 | -0.37167 | 0.0012721 | 0.00031883
49 | 0.98106 | -0.36307 | 0.0041208 | 0.0010328
50 | 0.98072 | -0.36971 | 0.0010444 | 0.00026174
51 | 0.9807 | -0.37013 | 0.0014114 | 0.00035374
52 | 0.99567 | -0.083124 | 0 | 0
53 | 0.99615 | -0.073959 | 0.0082655 | 0.0020715
54 | 0.99525 | -0.091233 | 0.010902 | 0.0027322
55 | 0.99748 | -0.04825 | 0.0027656 | 0.00069313
56 | 0.99471 | -0.10178 | 0.010393 | 0.0026048
57 | 0.98205 | -0.34381 | 0.0020651 | 0.00051755
58 | 1 | 0 | -0.45171 | -0.11487
59 | 0.99448 | -0.10616 | 0.0082526 | 0.0020683
60 | 0.9827 | -0.3312 | 0.0013224 | 0.00033141
61 | 0.98494 | -0.28968 | 0.0047859 | 0.0011995
62 | 0.98502 | -0.28823 | 0 | 0
63 | 0.98516 | -0.28539 | 0 | 0
64 | 0.987 | -0.24975 | 0.0069824 | 0.0017499
65 | 0.98481 | -0.29227 | 0.0089462 | 0.0022421
66 | 0.98737 | -0.24255 | 0.021284 | 0.0053343
67 | 0.98405 | -0.30709 | 0 | 0
68 | 0.98397 | -0.3086 | 0.0046691 | 0.0011702
69 | 0.98866 | -0.21746 | 0 | 0
70 | 0.98353 | -0.31731 | 0.016662 | 0.0041759
71 | 0.9846 | -0.29422 | 0.001602 | 0.00040149
72 | 0.98591 | -0.26894 | 0.0022586 | 0.00056606
73 | 0.98374 | -0.31087 | 0.0012526 | 0.00031392
74 | 0.98805 | -0.22774 | 0 | 0
75 | 0.98925 | -0.20483 | 0.0014069 | 0.00035261
76 | 0.99076 | -0.17583 | 0 | 0
77 | 0.99508 | -0.093398 | 0 | 0
78 | 0.98956 | -0.19907 | 0.0040682 | 0.0010196
79 | 0.995 | -0.095322 | 0 | 0
80 | 0.99445 | -0.10595 | 0 | 0
81 | 0.99533 | -0.088959 | 0.0018204 | 0.00045624
82 | 0.99535 | -0.088724 | 0 | 0
83 | 0.99564 | -0.082981 | 0.0019291 | 0.00048348
84 | 0.99532 | -0.089221 | 0 | 0
85 | 0.99505 | -0.093929 | 0.0020296 | 0.00050867
86 | 0.9949 | -0.096727 | 0.0021155 | 0.00053019
87 | 0.9969 | -0.058809 | 0 | 0
88 | 0.98921 | -0.20577 | 0.0045984 | 0.0011525
89 | 0.98807 | -0.22888 | 0.0066881 | 0.0016762
90 | 0.98783 | -0.23354 | 0.0091691 | 0.002298
91 | 0.98967 | -0.19787 | 0 | 0
92 | 0.98735 | -0.2429 | 0 | 0
93 | 0.99089 | -0.17437 | 0 | 0
94 | 0.98625 | -0.2644 | 0 | 0
95 | 0.98952 | -0.20075 | 0 | 0
96 | 0.99211 | -0.15082 | 0.010375 | 0.0026002
97 | 0.9857 | -0.27495 | 0.019084 | 0.0047829
98 | 0.98891 | -0.21269 | 0.0088633 | 0.0022214
99 | 0.99338 | -0.12647 | 0.019628 | 0.0049194
100 | 0.98496 | -0.28952 | 0.01855 | 0.004649
101 | 0.98824 | -0.22569 | 0.040064 | 0.010041
102 | 0.99508 | -0.093825 | 0.0013143 | 0.00032938
103 | 0.99733 | -0.050761 | 0.00046329 | 0.00011611
104 | 0.99793 | -0.039302 | 0.0073658 | 0.001846
105 | 0.99673 | -0.061948 | 0 | 0
106 | 0.99538 | -0.088055 | 0 | 0
107 | 0.99534 | -0.088928 | 0.00073313 | 0.00018374
108 | 0.99571 | -0.081765 | 0 | 0
109 | 0.99511 | -0.093313 | 0.0025761 | 0.00064563
110 | 0.99586 | -0.078732 | 0.001392 | 0.00034886
111 | 0.99658 | -0.064839 | 0.0014461 | 0.00036243
112 | 0.99472 | -0.1003 | 0.0024763 | 0.00062063
113 | 0.99472 | -0.10029 | 0 | 0
114 | 0.99531 | -0.089506 | 0.00081747 | 0.00020488
115 | 0.99505 | -0.0944 | 0 | 0
116 | 0.99529 | -0.089719 | 0.0014182 | 0.00035544
117 | 0.99597 | -0.076725 | 0 | 0
118 | 0.98824 | -0.22577 | 0 | 0
119 | 0.99495 | -0.096354 | 0 | 0
120 | 0.99485 | -0.098326 | 0.0017423 | 0.00043666
121 | 0.98821 | -0.22636 | 0.0012872 | 0.0003226
122 | 0.99527 | -0.090154 | 0 | 0
123 | 0.99527 | -0.090185 | 0.0018076 | 0.00045303
124 | 0.99405 | -0.11366 | 0 | 0
125 | 0.98342 | -0.31934 | 0.012224 | 0.0030636
126 | 0.98485 | -0.29166 | 0.0040158 | 0.0010065
127 | 0.99593 | -0.077448 | 0 | 0
128 | 0.99486 | -0.097534 | 0.0029775 | 0.00074624
129 | 0.99477 | -0.099258 | 0 | 0
130 | 0.97317 | -0.51778 | 0.0017331 | 0.00043435
131 | 0.99467 | -0.10119 | 0.0024711 | 0.00061932
132 | 0.99467 | -0.10128 | 0.0022427 | 0.00056208
133 | 0.99405 | -0.11384 | 0.00058185 | 0.00014582
134 | 0.99389 | -0.11677 | 0.006794 | 0.0017027
135 | 0.99402 | -0.11428 | 0.0024913 | 0.00062438
136 | 0.98798 | -0.2298 | 0.003549 | 0.00088947
137 | 0.98776 | -0.23407 | 0.0033053 | 0.00082839
138 | 0.98706 | -0.24771 | 0.0032831 | 0.00082281
139 | 0.987 | -0.24888 | 0 | 0
140 | 0.98641 | -0.26028 | 0.012724 | 0.0031889
141 | 0.98672 | -0.25415 | 0.0015813 | 0.00039632
142 | 0.98641 | -0.26034 | 0.00094515 | 0.00023688
143 | 0.98663 | -0.25606 | 0.0034649 | 0.00086838
144 | 0.9864 | -0.26053 | 0.0011641 | 0.00029175
145 | 0.9863 | -0.26236 | 0.0016177 | 0.00040543
146 | 0.98615 | -0.2654 | 0.0017343 | 0.00043465
147 | 0.98603 | -0.26769 | 0.0021468 | 0.00053803
148 | 0.99435 | -0.10864 | 0.0019099 | 0.00047866
149 | 0.99429 | -0.10986 | 0.0020632 | 0.0005171
150 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0009301 | 0.00023283 | -0.00093008 | -0.0002331 | 1.7089e-08 | -2.6852e-07 | 0.0014227 | 0.0014228 | 0.0014228 | 0.97273 | -0.52647 | 0.97271 | -0.52685 | 0.39088
1 | -0.001783 | -0.0004466 | 0.0017831 | 0.00044638 | 5.7398e-08 | -2.187e-07 | 0.0027275 | 0.0027274 | 0.0027275 | 0.97273 | -0.52647 | 0.97277 | -0.52579 | 0.7493
2 | -0.0017831 | -0.00044638 | 0.0017831 | 0.00044619 | 4.8279e-08 | -1.8398e-07 | 0.0027274 | 0.0027273 | 0.0027274 | 0.97277 | -0.52579 | 0.9728 | -0.52522 | 0.74928
3 | -0.0033843 | -0.00084747 | 0.0033847 | 0.00084724 | 3.8821e-07 | -2.3128e-07 | 0.0051764 | 0.0051762 | 0.0051764 | 0.9728 | -0.52522 | 0.97292 | -0.52281 | 1.4221
4 | -0.0055199 | -0.0013824 | 0.0055201 | 0.0013824 | 1.9438e-07 | 3.4077e-08 | 0.0084419 | 0.0084419 | 0.0084419 | 0.97292 | -0.52281 | 0.97296 | -0.52207 | 2.3192
5 | -0.0025905 | -0.00064917 | 0.0025905 | 0.00064904 | 7.8419e-08 | -1.2424e-07 | 0.0039099 | 0.0039098 | 0.0039099 | 0.98586 | -0.27092 | 0.9859 | -0.27029 | 1.0741
6 | 0.0025905 | 0.00064917 | -0.0025904 | -0.00064922 | 3.4707e-08 | -5.4982e-08 | 0.0039099 | 0.0039099 | 0.0039099 | 0.98586 | -0.27092 | 0.98585 | -0.27121 | 1.0742
7 | -0.0041447 | -0.0010386 | 0.004145 | 0.0010385 | 2.8933e-07 | -6.6276e-08 | 0.0062555 | 0.0062555 | 0.0062555 | 0.9859 | -0.27029 | 0.98597 | -0.26882 | 1.7186
8 | -0.0072634 | -0.0018193 | 0.0072644 | 0.0018197 | 1.0279e-06 | 3.8191e-07 | 0.011108 | 0.011108 | 0.011108 | 0.97296 | -0.52207 | 0.97311 | -0.5191 | 3.0517
9 | -0.0061827 | -0.0015492 | 0.006183 | 0.0015493 | 3.3437e-07 | 8.3368e-08 | 0.0093307 | 0.0093306 | 0.0093307 | 0.98597 | -0.26882 | 0.98603 | -0.26769 | 2.5634
10 | -0.00059058 | -0.00014801 | 0.00059058 | 0.00014782 | 4.8108e-09 | -1.9362e-07 | 0.00090162 | 0.00090155 | 0.00090162 | 0.97467 | -0.48837 | 0.97468 | -0.4882 | 0.2477
11 | -0.00059058 | -0.00014782 | 0.00059059 | 0.00014751 | 7.6399e-09 | -3.0755e-07 | 0.00090155 | 0.00090144 | 0.00090155 | 0.97468 | -0.4882 | 0.97469 | -0.48793 | 0.24768
12 | -0.0090167 | -0.0022589 | 0.0090173 | 0.0022591 | 5.692e-07 | 2.6508e-07 | 0.013788 | 0.013787 | 0.013788 | 0.97311 | -0.5191 | 0.97317 | -0.51778 | 3.7878
13 | -0.0024407 | -0.0006112 | 0.0024409 | 0.0006109 | 1.6819e-07 | -2.9506e-07 | 0.0037259 | 0.0037258 | 0.0037259 | 0.97469 | -0.48793 | 0.97477 | -0.48648 | 1.0236
14 | -0.0061814 | -0.0015483 | 0.0061819 | 0.0015485 | 5.087e-07 | 1.3561e-07 | 0.0094357 | 0.0094356 | 0.0094357 | 0.97478 | -0.48612 | 0.97487 | -0.48439 | 2.5922
15 | 0.0043721 | 0.0010949 | -0.004372 | -0.0010949 | 7.4447e-08 | -7.9187e-09 | 0.0066737 | 0.0066737 | 0.0066737 | 0.97478 | -0.48612 | 0.97477 | -0.48648 | 1.8334
16 | -0.0094417 | -0.0023655 | 0.009444 | 0.0023666 | 2.2898e-06 | 1.0988e-06 | 0.014411 | 0.014411 | 0.014411 | 0.97487 | -0.48439 | 0.97513 | -0.4793 | 3.9591
17 | -0.010227 | -0.0025629 | 0.010228 | 0.0025633 | 7.3329e-07 | 3.6914e-07 | 0.015607 | 0.015607 | 0.015607 | 0.97513 | -0.4793 | 0.97521 | -0.4778 | 4.2875
18 | 0.0017487 | 0.00043771 | -0.0017487 | -0.00043798 | 6.7369e-08 | -2.7172e-07 | 0.0026681 | 0.0026682 | 0.0026682 | 0.97521 | -0.4778 | 0.97516 | -0.47861 | 0.73303
19 | -0.013366 | -0.0033491 | 0.013373 | 0.0033531 | 7.0418e-06 | 3.9431e-06 | 0.020394 | 0.020394 | 0.020394 | 0.97521 | -0.4778 | 0.97577 | -0.46674 | 5.6028
20 | 0.0017487 | 0.00043798 | -0.0017486 | -0.00043824 | 6.5538e-08 | -2.6429e-07 | 0.0026682 | 0.0026683 | 0.0026683 | 0.97516 | -0.47861 | 0.97512 | -0.47939 | 0.73306
21 | -0.015255 | -0.0038247 | 0.015261 | 0.0038284 | 6.3678e-06 | 3.6833e-06 | 0.023264 | 0.023264 | 0.023264 | 0.97577 | -0.46674 | 0.97621 | -0.45799 | 6.3911
22 | -0.016659 | -0.0041786 | 0.01666 | 0.0041794 | 1.3417e-06 | 7.8931e-07 | 0.025394 | 0.025394 | 0.025394 | 0.97621 | -0.45799 | 0.9763 | -0.4563 | 6.9763
23 | -0.018086 | -0.0045368 | 0.018095 | 0.0045423 | 9.2671e-06 | 5.524e-06 | 0.027567 | 0.027567 | 0.027567 | 0.9763 | -0.4563 | 0.97684 | -0.44555 | 7.5734
24 | -0.032953 | -0.0082672 | 0.032975 | 0.0082807 | 2.1585e-05 | 1.3531e-05 | 0.050313 | 0.050313 | 0.050313 | 0.97465 | -0.48865 | 0.97535 | -0.47492 | 13.8224
25 | 0.010149 | 0.0025442 | -0.010146 | -0.0025427 | 2.8975e-06 | 1.4534e-06 | 0.015494 | 0.015495 | 0.015495 | 0.97465 | -0.48865 | 0.97434 | -0.49464 | 4.2568
26 | 0.022805 | 0.005723 | -0.022795 | -0.0057169 | 9.9289e-06 | 6.0825e-06 | 0.034819 | 0.034819 | 0.034819 | 0.97465 | -0.48865 | 0.97419 | -0.49778 | 9.5657
27 | -0.033568 | -0.0084294 | 0.033589 | 0.0084422 | 2.0308e-05 | 1.2739e-05 | 0.051219 | 0.051219 | 0.051219 | 0.97535 | -0.47492 | 0.97599 | -0.46224 | 14.0711
28 | 0.0055472 | 0.0013902 | -0.005547 | -0.0013902 | 2.2033e-07 | 3.9053e-08 | 0.0084717 | 0.0084717 | 0.0084717 | 0.97434 | -0.49464 | 0.9743 | -0.49547 | 2.3274
29 | 0.018199 | 0.0045651 | -0.01819 | -0.00456 | 8.4977e-06 | 5.0736e-06 | 0.027799 | 0.027799 | 0.027799 | 0.97419 | -0.49778 | 0.97369 | -0.50758 | 7.6372
30 | -0.018095 | -0.0045423 | 0.018099 | 0.0045447 | 4.0404e-06 | 2.4083e-06 | 0.027567 | 0.027567 | 0.027567 | 0.97684 | -0.44555 | 0.97708 | -0.44087 | 7.5733
31 | -0.035914 | -0.0090249 | 0.035924 | 0.0090311 | 9.8264e-06 | 6.1797e-06 | 0.054764 | 0.054764 | 0.054764 | 0.97599 | -0.46224 | 0.97628 | -0.45651 | 15.045
32 | 0.0021045 | 0.00052741 | -0.0021045 | -0.00052744 | 1.4491e-08 | -3.7307e-08 | 0.0032142 | 0.0032142 | 0.0032142 | 0.9743 | -0.49547 | 0.9743 | -0.49562 | 0.88302
33 | 0.0144 | 0.00361 | -0.014396 | -0.0036077 | 4.1521e-06 | 2.3731e-06 | 0.022007 | 0.022007 | 0.022007 | 0.97369 | -0.50758 | 0.97338 | -0.51363 | 6.0458
34 | -0.018099 | -0.0045447 | 0.018104 | 0.0045475 | 4.6054e-06 | 2.745e-06 | 0.027567 | 0.027567 | 0.027567 | 0.97708 | -0.44087 | 0.97735 | -0.43554 | 7.5733
35 | -0.038511 | -0.0096795 | 0.038531 | 0.0096922 | 2.0144e-05 | 1.2697e-05 | 0.058707 | 0.058707 | 0.058707 | 0.97628 | -0.45651 | 0.97684 | -0.44556 | 16.1282
36 | 0.010752 | 0.0026946 | -0.01075 | -0.0026935 | 2.1226e-06 | 1.0981e-06 | 0.016437 | 0.016437 | 0.016437 | 0.97338 | -0.51363 | 0.97317 | -0.51778 | 4.5158
37 | -0.040216 | -0.010115 | 0.040253 | 0.010138 | 3.7003e-05 | 2.3353e-05 | 0.061274 | 0.061274 | 0.061274 | 0.97684 | -0.44556 | 0.97782 | -0.42632 | 16.8336
38 | -0.042592 | -0.010724 | 0.042613 | 0.010737 | 2.0158e-05 | 1.2741e-05 | 0.064834 | 0.064833 | 0.064834 | 0.97782 | -0.42632 | 0.97833 | -0.41643 | 17.8114
39 | -0.044558 | -0.011225 | 0.044588 | 0.011243 | 2.9633e-05 | 1.8749e-05 | 0.067793 | 0.067793 | 0.067793 | 0.97833 | -0.41643 | 0.97904 | -0.40253 | 18.6245
40 | -0.068016 | -0.017137 | 0.068129 | 0.017209 | 0.00011311 | 7.2038e-05 | 0.10341 | 0.10341 | 0.10341 | 0.97904 | -0.40253 | 0.98081 | -0.36783 | 28.409
41 | 0.023428 | 0.0058941 | -0.023409 | -0.0058825 | 1.8859e-05 | 1.1572e-05 | 0.035616 | 0.035616 | 0.035616 | 0.97904 | -0.40253 | 0.97818 | -0.41939 | 9.7846
42 | -0.019573 | -0.0049157 | 0.01958 | 0.0049195 | 6.4393e-06 | 3.8788e-06 | 0.029804 | 0.029804 | 0.029804 | 0.97735 | -0.43554 | 0.9777 | -0.42865 | 8.1878
43 | -0.021852 | -0.0054889 | 0.021862 | 0.0054948 | 9.6575e-06 | 5.8887e-06 | 0.033263 | 0.033262 | 0.033263 | 0.9777 | -0.42865 | 0.97818 | -0.41939 | 9.1381
44 | 0.0022728 | 0.00056932 | -0.0022727 | -0.00056956 | 1.0903e-07 | -2.3493e-07 | 0.003459 | 0.0034591 | 0.0034591 | 0.9777 | -0.42865 | 0.97765 | -0.42966 | 0.95031
45 | -0.0019072 | -0.00047798 | 0.0019073 | 0.00047742 | 1.6556e-07 | -5.588e-07 | 0.0028944 | 0.0028942 | 0.0028944 | 0.98048 | -0.37446 | 0.98057 | -0.37263 | 0.79517
46 | -0.0019073 | -0.00047742 | 0.0019074 | 0.00047713 | 8.7364e-08 | -2.9497e-07 | 0.0028942 | 0.0028941 | 0.0028942 | 0.98057 | -0.37263 | 0.98062 | -0.37167 | 0.7951
47 | 0.00097001 | 0.00024306 | -0.00097 | -0.00024311 | 2.8662e-09 | -4.2136e-08 | 0.0014764 | 0.0014764 | 0.0014764 | 0.97765 | -0.42966 | 0.97765 | -0.42972 | 0.4056
48 | -0.073765 | -0.018621 | 0.073782 | 0.018631 | 1.6813e-05 | 1.0715e-05 | 0.11196 | 0.11196 | 0.11196 | 0.98081 | -0.36783 | 0.98106 | -0.36307 | 30.7579
49 | 0.0056362 | 0.0014113 | -0.0056357 | -0.0014112 | 5.0425e-07 | 9.0614e-08 | 0.0085503 | 0.0085504 | 0.0085504 | 0.98081 | -0.36783 | 0.98072 | -0.36971 | 2.349
50 | -0.0031796 | -0.00079596 | 0.0031798 | 0.00079577 | 2.3246e-07 | -1.8726e-07 | 0.0048244 | 0.0048243 | 0.0048244 | 0.98062 | -0.37167 | 0.9807 | -0.37013 | 1.3254
51 | -0.077903 | -0.019664 | 0.077975 | 0.01971 | 7.1941e-05 | 4.5868e-05 | 0.11821 | 0.11821 | 0.11821 | 0.98106 | -0.36307 | 0.98205 | -0.34381 | 32.475
52 | 0.0045913 | 0.0011495 | -0.0045912 | -0.0011495 | 9.3588e-08 | -5.0013e-09 | 0.0069659 | 0.0069659 | 0.0069659 | 0.98072 | -0.36971 | 0.9807 | -0.37013 | 1.9137
53 | -0.033548 | -0.008417 | 0.033563 | 0.0084262 | 1.4666e-05 | 9.1837e-06 | 0.05014 | 0.05014 | 0.05014 | 0.99567 | -0.083124 | 0.99615 | -0.073959 | 13.7748
54 | 0.033548 | 0.008417 | -0.033535 | -0.0084089 | 1.2965e-05 | 8.1189e-06 | 0.05014 | 0.05014 | 0.05014 | 0.99567 | -0.083124 | 0.99525 | -0.091233 | 13.7748
55 | -0.041828 | -0.010498 | 0.04188 | 0.01053 | 5.1352e-05 | 3.2408e-05 | 0.062487 | 0.062487 | 0.062487 | 0.99615 | -0.073959 | 0.99748 | -0.04825 | 17.1668
56 | 0.022633 | 0.0056766 | -0.022622 | -0.0056697 | 1.1378e-05 | 6.9376e-06 | 0.033841 | 0.033841 | 0.033841 | 0.99525 | -0.091233 | 0.99471 | -0.10178 | 9.297
57 | -0.044645 | -0.011223 | 0.044748 | 0.011288 | 0.00010312 | 6.5184e-05 | 0.066613 | 0.066612 | 0.066613 | 0.99748 | -0.04825 | 1 | 0 | 18.3001
58 | 0.012229 | 0.0030649 | -0.012226 | -0.0030635 | 2.5475e-06 | 1.367e-06 | 0.018294 | 0.018294 | 0.018294 | 0.99471 | -0.10178 | 0.99448 | -0.10616 | 5.0257
59 | -0.08004 | -0.020228 | 0.080088 | 0.020259 | 4.8419e-05 | 3.0877e-05 | 0.12134 | 0.12134 | 0.12134 | 0.98205 | -0.34381 | 0.9827 | -0.3312 | 33.3346
60 | 0.18035 | 0.046221 | -0.17983 | -0.045894 | 0.00051251 | 0.00032702 | 0.26872 | 0.26872 | 0.26872 | 1 | 0 | 0.9969 | -0.058809 | 36.9122
61 | 0.22497 | 0.057364 | -0.22454 | -0.057092 | 0.00042599 | 0.0002721 | 0.3351 | 0.3351 | 0.3351 | 1 | 0 | 0.99793 | -0.039302 | 46.0302
62 | 0.0039737 | 0.00099524 | -0.0039732 | -0.0009954 | 4.6862e-07 | -1.5869e-07 | 0.0059455 | 0.0059457 | 0.0059457 | 0.99448 | -0.10616 | 0.99435 | -0.10864 | 1.6334
63 | -0.081411 | -0.02059 | 0.08149 | 0.020641 | 7.9492e-05 | 5.0698e-05 | 0.12334 | 0.12334 | 0.12334 | 0.9827 | -0.3312 | 0.98374 | -0.31087 | 33.8847
64 | -0.0047859 | -0.0011995 | 0.0047862 | 0.0011994 | 3.3071e-07 | -3.0663e-09 | 0.0072303 | 0.0072302 | 0.0072303 | 0.98494 | -0.28968 | 0.98502 | -0.28823 | 1.9863
65 | -0.0047862 | -0.0011994 | 0.0047868 | 0.0011994 | 6.4869e-07 | -6.1219e-09 | 0.0072302 | 0.0072301 | 0.0072302 | 0.98502 | -0.28823 | 0.98516 | -0.28539 | 1.9863
66 | -0.047341 | -0.011884 | 0.047422 | 0.011935 | 8.0614e-05 | 5.1057e-05 | 0.071512 | 0.071512 | 0.071512 | 0.98516 | -0.28539 | 0.987 | -0.24975 | 19.6462
67 | 0.042554 | 0.010685 | -0.04254 | -0.010676 | 1.3956e-05 | 8.8172e-06 | 0.064282 | 0.064282 | 0.064282 | 0.98516 | -0.28539 | 0.98481 | -0.29227 | 17.66
68 | -0.054404 | -0.013685 | 0.054423 | 0.013697 | 1.873e-05 | 1.1892e-05 | 0.082039 | 0.082039 | 0.082039 | 0.987 | -0.24975 | 0.98737 | -0.24255 | 22.5382
69 | 0.033594 | 0.0084339 | -0.03357 | -0.008419 | 2.3746e-05 | 1.4885e-05 | 0.050765 | 0.050765 | 0.050765 | 0.98481 | -0.29227 | 0.98405 | -0.30709 | 13.9464
70 | -0.075707 | -0.019031 | 0.075798 | 0.019089 | 9.0834e-05 | 5.7896e-05 | 0.11411 | 0.11411 | 0.11411 | 0.98737 | -0.24255 | 0.98866 | -0.21746 | 31.3503
71 | 0.028901 | 0.0072489 | -0.028887 | -0.0072401 | 1.4066e-05 | 8.7527e-06 | 0.043704 | 0.043704 | 0.043704 | 0.98405 | -0.30709 | 0.98353 | -0.31731 | 12.0067
72 | 0.0046694 | 0.0011702 | -0.0046691 | -0.0011702 | 3.3563e-07 | -1.3249e-08 | 0.0070608 | 0.0070608 | 0.0070608 | 0.98405 | -0.30709 | 0.98397 | -0.3086 | 1.9398
73 | -0.075798 | -0.019089 | 0.075858 | 0.019128 | 6.0612e-05 | 3.8632e-05 | 0.11411 | 0.11411 | 0.11411 | 0.98866 | -0.21746 | 0.98952 | -0.20075 | 31.3502
74 | 0.012225 | 0.0030642 | -0.012224 | -0.0030636 | 1.1829e-06 | 6.4005e-07 | 0.018496 | 0.018496 | 0.018496 | 0.98353 | -0.31731 | 0.98342 | -0.31934 | 5.0812
75 | -0.084411 | -0.021398 | 0.084514 | 0.021464 | 0.0001027 | 6.5512e-05 | 0.12766 | 0.12766 | 0.12766 | 0.9846 | -0.29422 | 0.98591 | -0.26894 | 35.0703
76 | 0.082809 | 0.020997 | -0.082743 | -0.020955 | 6.6211e-05 | 4.2232e-05 | 0.12523 | 0.12523 | 0.12523 | 0.9846 | -0.29422 | 0.98374 | -0.31087 | 34.4052
77 | -0.086772 | -0.02203 | 0.086945 | 0.02214 | 0.00017237 | 0.00010997 | 0.13106 | 0.13106 | 0.13106 | 0.98591 | -0.26894 | 0.98805 | -0.22774 | 36.0067
78 | -0.086945 | -0.02214 | 0.087041 | 0.022201 | 9.6196e-05 | 6.1374e-05 | 0.13106 | 0.13106 | 0.13106 | 0.98805 | -0.22774 | 0.98925 | -0.20483 | 36.0067
79 | -0.088448 | -0.022554 | 0.088572 | 0.022633 | 0.00012403 | 7.9137e-05 | 0.13318 | 0.13318 | 0.13318 | 0.98925 | -0.20483 | 0.99076 | -0.17583 | 36.5881
80 | -0.13911 | -0.035362 | 0.13966 | 0.035716 | 0.00055468 | 0.00035456 | 0.2091 | 0.2091 | 0.2091 | 0.99076 | -0.17583 | 0.99508 | -0.093398 | 57.4455
81 | 0.050536 | 0.012729 | -0.050479 | -0.012693 | 5.6088e-05 | 3.5562e-05 | 0.075921 | 0.075921 | 0.075921 | 0.99076 | -0.17583 | 0.98956 | -0.19907 | 20.8575
82 | 0.0020297 | 0.00050851 | -0.0020296 | -0.00050867 | 5.1379e-08 | -1.6033e-07 | 0.003035 | 0.0030351 | 0.0030351 | 0.99508 | -0.093398 | 0.99505 | -0.093929 | 0.83382
83 | 0.012287 | 0.0030796 | -0.012285 | -0.0030786 | 1.9486e-06 | 1.0472e-06 | 0.018373 | 0.018373 | 0.018373 | 0.99508 | -0.093398 | 0.9949 | -0.096727 | 5.0476
84 | -0.15398 | -0.039304 | 0.15424 | 0.039469 | 0.00025782 | 0.00016433 | 0.23051 | 0.23051 | 0.23051 | 0.99508 | -0.093398 | 0.9969 | -0.058809 | 31.6634
85 | 0.046411 | 0.011673 | -0.046396 | -0.011664 | 1.4868e-05 | 9.4107e-06 | 0.069804 | 0.069804 | 0.069804 | 0.98956 | -0.19907 | 0.98921 | -0.20577 | 19.1769
86 | 0.0098769 | 0.0024773 | -0.0098719 | -0.0024749 | 4.9995e-06 | 2.4065e-06 | 0.014771 | 0.014772 | 0.014772 | 0.995 | -0.095322 | 0.99445 | -0.10595 | 4.0582
87 | -0.0098769 | -0.0024773 | 0.0098799 | 0.0024787 | 2.9962e-06 | 1.4418e-06 | 0.014771 | 0.014771 | 0.014771 | 0.995 | -0.095322 | 0.99533 | -0.088959 | 4.0581
88 | 0.0098719 | 0.0024749 | -0.0098683 | -0.0024731 | 3.6263e-06 | 1.7461e-06 | 0.014772 | 0.014772 | 0.014772 | 0.99445 | -0.10595 | 0.99405 | -0.11366 | 4.0582
89 | -0.0117 | -0.002935 | 0.0117 | 0.002935 | 1.3152e-07 | 6.9277e-08 | 0.017493 | 0.017493 | 0.017493 | 0.99533 | -0.088959 | 0.99535 | -0.088724 | 4.8057
90 | -0.013119 | -0.00329 | 0.013122 | 0.003292 | 3.5915e-06 | 1.9749e-06 | 0.019613 | 0.019613 | 0.019613 | 0.99535 | -0.088724 | 0.99564 | -0.082981 | 5.3882
91 | 0.0014183 | 0.00035496 | -0.0014182 | -0.0003552 | 3.3575e-08 | -2.3739e-07 | 0.0021201 | 0.0021202 | 0.0021202 | 0.99535 | -0.088724 | 0.99532 | -0.089221 | 0.58248
92 | -0.015051 | -0.0037755 | 0.015055 | 0.0037777 | 3.9711e-06 | 2.2693e-06 | 0.022496 | 0.022496 | 0.022496 | 0.99564 | -0.082981 | 0.99593 | -0.077448 | 6.1802
93 | 0.0014182 | 0.0003552 | -0.0014182 | -0.00035544 | 3.3657e-08 | -2.3793e-07 | 0.0021202 | 0.0021203 | 0.0021203 | 0.99532 | -0.089221 | 0.99529 | -0.089719 | 0.5825
94 | 0.010169 | 0.0025484 | -0.010169 | -0.0025482 | 3.9104e-07 | 1.9173e-07 | 0.015209 | 0.015209 | 0.015209 | 0.9949 | -0.096727 | 0.99486 | -0.097534 | 4.1784
95 | 0.025598 | 0.0064253 | -0.025594 | -0.006423 | 3.8323e-06 | 2.3614e-06 | 0.038212 | 0.038212 | 0.038212 | 0.9969 | -0.058809 | 0.99673 | -0.061948 | 10.4977
96 | 0.041798 | 0.010512 | -0.04175 | -0.010481 | 4.7914e-05 | 3.0251e-05 | 0.062887 | 0.062887 | 0.062887 | 0.98921 | -0.20577 | 0.98798 | -0.2298 | 17.2767
97 | 0.050929 | 0.012805 | -0.050917 | -0.012798 | 1.1344e-05 | 7.1942e-06 | 0.076712 | 0.076712 | 0.076712 | 0.98807 | -0.22888 | 0.98783 | -0.23354 | 21.0747
98 | -0.057617 | -0.014481 | 0.057702 | 0.014536 | 8.5426e-05 | 5.4285e-05 | 0.086784 | 0.086784 | 0.086784 | 0.98807 | -0.22888 | 0.98967 | -0.19787 | 23.8418
99 | 0.041748 | 0.0105 | -0.04173 | -0.010488 | 1.865e-05 | 1.1775e-05 | 0.0629 | 0.0629 | 0.0629 | 0.98783 | -0.23354 | 0.98735 | -0.2429 | 17.2803
100 | -0.057702 | -0.014536 | 0.057767 | 0.014577 | 6.4925e-05 | 4.1256e-05 | 0.086784 | 0.086784 | 0.086784 | 0.98967 | -0.19787 | 0.99089 | -0.17437 | 23.8418
101 | 0.04173 | 0.010488 | -0.041687 | -0.010461 | 4.2788e-05 | 2.7016e-05 | 0.0629 | 0.0629 | 0.0629 | 0.98735 | -0.2429 | 0.98625 | -0.2644 | 17.2803
102 | 0.12629 | 0.031849 | -0.12613 | -0.031747 | 0.00015922 | 0.00010175 | 0.18971 | 0.18971 | 0.18971 | 0.99089 | -0.17437 | 0.98952 | -0.20075 | 52.1193
103 | -0.18405 | -0.046425 | 0.18426 | 0.046558 | 0.00020779 | 0.00013261 | 0.2765 | 0.2765 | 0.2765 | 0.99089 | -0.17437 | 0.99211 | -0.15082 | 37.9805
104 | 0.041687 | 0.010461 | -0.041666 | -0.010448 | 2.0969e-05 | 1.324e-05 | 0.0629 | 0.0629 | 0.0629 | 0.98625 | -0.2644 | 0.9857 | -0.27495 | 17.2804
105 | 0.050269 | 0.012619 | -0.05024 | -0.012601 | 2.8616e-05 | 1.8143e-05 | 0.0756 | 0.0756 | 0.0756 | 0.98952 | -0.20075 | 0.98891 | -0.21269 | 20.7691
106 | -0.19464 | -0.049158 | 0.19486 | 0.049303 | 0.00022739 | 0.00014516 | 0.29206 | 0.29206 | 0.29206 | 0.99211 | -0.15082 | 0.99338 | -0.12647 | 40.118
107 | 0.022582 | 0.0056649 | -0.022566 | -0.0056554 | 1.5671e-05 | 9.5712e-06 | 0.034091 | 0.034091 | 0.034091 | 0.9857 | -0.27495 | 0.98496 | -0.28952 | 9.3658
108 | 0.041377 | 0.010379 | -0.041351 | -0.010363 | 2.562e-05 | 1.6171e-05 | 0.062263 | 0.062263 | 0.062263 | 0.98891 | -0.21269 | 0.98824 | -0.22569 | 17.1052
109 | -0.21449 | -0.054223 | 0.21483 | 0.054438 | 0.00033638 | 0.00021483 | 0.32146 | 0.32146 | 0.32146 | 0.99338 | -0.12647 | 0.99508 | -0.093825 | 44.1567
110 | 0.0040163 | 0.0010063 | -0.0040158 | -0.0010065 | 4.1051e-07 | -1.1569e-07 | 0.0060674 | 0.0060676 | 0.0060676 | 0.98496 | -0.28952 | 0.98485 | -0.29166 | 1.6669
111 | 0.0012872 | 0.00032225 | -0.0012872 | -0.0003223 | 4.8068e-09 | -4.0647e-08 | 0.0019381 | 0.0019381 | 0.0019381 | 0.98824 | -0.22569 | 0.98824 | -0.22577 | 0.53245
112 | -0.21614 | -0.054767 | 0.21659 | 0.055053 | 0.00044818 | 0.00028624 | 0.32343 | 0.32343 | 0.32343 | 0.99508 | -0.093825 | 0.99733 | -0.050761 | 44.4266
113 | -0.21705 | -0.055169 | 0.21717 | 0.055246 | 0.00011985 | 7.6546e-05 | 0.32412 | 0.32412 | 0.32412 | 0.99733 | -0.050761 | 0.99793 | -0.039302 | 44.5216
114 | 0.025594 | 0.006423 | -0.02559 | -0.0064208 | 3.5278e-06 | 2.1739e-06 | 0.038212 | 0.038212 | 0.038212 | 0.99673 | -0.061948 | 0.99658 | -0.064839 | 10.4978
115 | 0.0033585 | 0.00084119 | -0.0033583 | -0.00084129 | 1.3965e-07 | -1.0266e-07 | 0.0050205 | 0.0050205 | 0.0050205 | 0.99538 | -0.088055 | 0.99534 | -0.088928 | 1.3793
116 | -0.0076783 | -0.0019214 | 0.0076806 | 0.0019223 | 2.2985e-06 | 8.6602e-07 | 0.011477 | 0.011477 | 0.011477 | 0.99538 | -0.088055 | 0.99571 | -0.081765 | 3.1532
117 | 0.0043199 | 0.0010802 | -0.0043188 | -0.0010804 | 1.0803e-06 | -2.0646e-07 | 0.006457 | 0.0064573 | 0.0064573 | 0.99538 | -0.088055 | 0.99511 | -0.093313 | 1.774
118 | 0.0026252 | 0.00065755 | -0.0026251 | -0.00065767 | 7.231e-08 | -1.1643e-07 | 0.0039245 | 0.0039246 | 0.0039246 | 0.99534 | -0.088928 | 0.99531 | -0.089506 | 1.0782
119 | -0.0076806 | -0.0019223 | 0.0076817 | 0.0019227 | 1.1087e-06 | 4.1759e-07 | 0.011477 | 0.011477 | 0.011477 | 0.99571 | -0.081765 | 0.99586 | -0.078732 | 3.1531
120 | 0.0017427 | 0.00043481 | -0.0017426 | -0.00043521 | 8.9939e-08 | -4.0145e-07 | 0.0026052 | 0.0026054 | 0.0026054 | 0.99511 | -0.093313 | 0.99505 | -0.0944 | 0.71577
121 | -0.0090737 | -0.0022716 | 0.0090746 | 0.0022719 | 8.6696e-07 | 3.9117e-07 | 0.013557 | 0.013557 | 0.013557 | 0.99586 | -0.078732 | 0.99597 | -0.076725 | 3.7245
122 | 0.024144 | 0.0060584 | -0.02413 | -0.00605 | 1.3676e-05 | 8.3872e-06 | 0.036053 | 0.036053 | 0.036053 | 0.99658 | -0.064839 | 0.99597 | -0.076725 | 9.9046
123 | -0.0024763 | -0.00062063 | 0.0024763 | 0.00062062 | 2.0021e-09 | -3.7685e-09 | 0.0037044 | 0.0037044 | 0.0037044 | 0.99472 | -0.1003 | 0.99472 | -0.10029 | 1.0177
124 | -0.0024763 | -0.00062062 | 0.0024765 | 0.0006204 | 1.2127e-07 | -2.2832e-07 | 0.0037044 | 0.0037043 | 0.0037044 | 0.99472 | -0.10029 | 0.99477 | -0.099258 | 1.0177
125 | 0.0018077 | 0.00045279 | -0.0018076 | -0.00045302 | 5.5777e-08 | -2.2897e-07 | 0.0027024 | 0.0027025 | 0.0027025 | 0.99531 | -0.089506 | 0.99527 | -0.090154 | 0.74245
126 | 0.0017426 | 0.00043521 | -0.0017425 | -0.00043593 | 1.6191e-07 | -7.2244e-07 | 0.0026054 | 0.0026057 | 0.0026057 | 0.99505 | -0.0944 | 0.99495 | -0.096354 | 0.71585
127 | 0.015056 | 0.003778 | -0.015055 | -0.0037777 | 5.1919e-07 | 2.9668e-07 | 0.022496 | 0.022496 | 0.022496 | 0.99597 | -0.076725 | 0.99593 | -0.077448 | 6.1802
128 | 0.0012872 | 0.0003223 | -0.0012872 | -0.0003226 | 3.6264e-08 | -3.0661e-07 | 0.0019381 | 0.0019382 | 0.0019382 | 0.98824 | -0.22577 | 0.98821 | -0.22636 | 0.53248
129 | 0.0017425 | 0.00043593 | -0.0017423 | -0.00043666 | 1.636e-07 | -7.2963e-07 | 0.0026057 | 0.002606 | 0.002606 | 0.99495 | -0.096354 | 0.99485 | -0.098326 | 0.71593
130 | 0.0018076 | 0.00045302 | -0.0018076 | -0.00045303 | 2.6459e-09 | -1.086e-08 | 0.0027025 | 0.0027025 | 0.0027025 | 0.99527 | -0.090154 | 0.99527 | -0.090185 | 0.74246
131 | 0.0030732 | 0.00077009 | -0.0030732 | -0.00077011 | 2.7482e-08 | -2.7303e-08 | 0.0046003 | 0.0046004 | 0.0046004 | 0.99405 | -0.11366 | 0.99405 | -0.11384 | 1.2638
132 | 0.006795 | 0.001703 | -0.006794 | -0.0017027 | 1.0087e-06 | 3.0857e-07 | 0.010172 | 0.010172 | 0.010172 | 0.99405 | -0.11366 | 0.99389 | -0.11677 | 2.7944
133 | 0.0071913 | 0.0018019 | -0.0071907 | -0.0018017 | 5.9048e-07 | 2.0119e-07 | 0.010756 | 0.010756 | 0.010756 | 0.99486 | -0.097534 | 0.99477 | -0.099258 | 2.9549
134 | 0.0047143 | 0.0011814 | -0.0047139 | -0.0011814 | 4.3414e-07 | -2.4364e-08 | 0.0070517 | 0.0070518 | 0.0070518 | 0.99477 | -0.099258 | 0.99467 | -0.10119 | 1.9373
135 | 0.0022427 | 0.00056206 | -0.0022427 | -0.00056208 | 9.9035e-09 | -2.4114e-08 | 0.0033551 | 0.0033551 | 0.0033551 | 0.99467 | -0.10119 | 0.99467 | -0.10128 | 0.92173
136 | 0.0024914 | 0.00062429 | -0.0024913 | -0.00062438 | 5.1779e-08 | -9.5555e-08 | 0.0037294 | 0.0037294 | 0.0037294 | 0.99405 | -0.11384 | 0.99402 | -0.11428 | 1.0246
137 | 0.038201 | 0.0095918 | -0.038193 | -0.0095869 | 7.7766e-06 | 4.8969e-06 | 0.057542 | 0.057542 | 0.057542 | 0.98798 | -0.2298 | 0.98776 | -0.23407 | 15.8082
138 | 0.034888 | 0.0087585 | -0.034865 | -0.0087443 | 2.2687e-05 | 1.424e-05 | 0.052563 | 0.052563 | 0.052563 | 0.98776 | -0.23407 | 0.98706 | -0.24771 | 14.4403
139 | 0.031582 | 0.0079215 | -0.03158 | -0.0079204 | 1.7523e-06 | 1.0952e-06 | 0.047613 | 0.047613 | 0.047613 | 0.98706 | -0.24771 | 0.987 | -0.24888 | 13.0806
140 | 0.013676 | 0.0034299 | -0.013669 | -0.0034257 | 7.4312e-06 | 4.1607e-06 | 0.020619 | 0.02062 | 0.02062 | 0.987 | -0.24888 | 0.98641 | -0.26028 | 5.6647
141 | 0.017904 | 0.0044905 | -0.0179 | -0.0044878 | 4.4978e-06 | 2.6683e-06 | 0.026994 | 0.026994 | 0.026994 | 0.987 | -0.24888 | 0.98672 | -0.25415 | 7.4159
142 | 0.00094516 | 0.00023684 | -0.00094515 | -0.00023688 | 2.524e-09 | -4.0649e-08 | 0.0014258 | 0.0014258 | 0.0014258 | 0.98641 | -0.26028 | 0.98641 | -0.26034 | 0.3917
143 | 0.016318 | 0.0040915 | -0.016317 | -0.0040907 | 1.4849e-06 | 8.6682e-07 | 0.024609 | 0.024609 | 0.024609 | 0.98672 | -0.25415 | 0.98663 | -0.25606 | 6.7608
144 | 0.012852 | 0.0032223 | -0.012849 | -0.0032208 | 2.7401e-06 | 1.5054e-06 | 0.019384 | 0.019384 | 0.019384 | 0.98663 | -0.25606 | 0.9864 | -0.26053 | 5.3252
145 | 0.011685 | 0.002929 | -0.011684 | -0.0029285 | 1.018e-06 | 5.4e-07 | 0.017628 | 0.017628 | 0.017628 | 0.9864 | -0.26053 | 0.9863 | -0.26236 | 4.8428
146 | 0.010066 | 0.002523 | -0.010065 | -0.0025223 | 1.4556e-06 | 7.1682e-07 | 0.015187 | 0.015187 | 0.015187 | 0.9863 | -0.26236 | 0.98615 | -0.2654 | 4.1723
147 | 0.0083307 | 0.0020877 | -0.0083298 | -0.0020873 | 9.0859e-07 | 3.8589e-07 | 0.01257 | 0.01257 | 0.01257 | 0.98615 | -0.2654 | 0.98603 | -0.26769 | 3.4534
148 | 0.0020634 | 0.00051674 | -0.0020632 | -0.0005171 | 1.2039e-07 | -3.5972e-07 | 0.0030876 | 0.0030878 | 0.0030878 | 0.99435 | -0.10864 | 0.99429 | -0.10986 | 0.84829

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45171 | 0.11487

## res_load
| p_mw | q_mvar
0 | 0.00085294 | 0.00021377
1 | 0.00093008 | 0.0002331
2 | 0.0016011 | 0.00040128
3 | 0.0021352 | 0.00053513
4 | 0.0015542 | 0.00038951
5 | 0.0025904 | 0.00064922
6 | 0.0017433 | 0.00043691
7 | 0.0020377 | 0.00051069
8 | 0.00059058 | 0.00014801
9 | 0.0017523 | 0.00043917
10 | 0.0018501 | 0.00046369
11 | 0.0018093 | 0.00045346
12 | 0.0032598 | 0.00081698
13 | 0.0019311 | 0.00048398
14 | 0.00078344 | 0.00019635
15 | 0.0013891 | 0.00034815
16 | 0.0018817 | 0.00047161
17 | 0.0013974 | 0.00035022
18 | 0.0017486 | 0.00043824
19 | 0.001426 | 0.0003574
20 | 0.0005935 | 0.00014875
21 | 0.0045986 | 0.0011525
22 | 0.0045957 | 0.0011518
23 | 0.0023252 | 0.00058275
24 | 0.0034424 | 0.00086276
25 | 0.0037906 | 0.00095001
26 | 0.002587 | 0.00064836
27 | 0.0021045 | 0.00052744
28 | 0.0036432 | 0.00091307
29 | 0.0016857 | 0.00042248
30 | 0.0023389 | 0.00058618
31 | 0.0019458 | 0.00048767
32 | 0.0014692 | 0.00036821
33 | 0.0019072 | 0.00047798
34 | 0.001547 | 0.00038773
35 | 0.0013027 | 0.00032649
36 | 0.00097 | 0.00024311
37 | 0.0012721 | 0.00031883
38 | 0.0041208 | 0.0010328
39 | 0.0010444 | 0.00026174
40 | 0.0014114 | 0.00035374
41 | 0.0082655 | 0.0020715
42 | 0.010902 | 0.0027322
43 | 0.0027656 | 0.00069313
44 | 0.010393 | 0.0026048
45 | 0.0020651 | 0.00051755
46 | 0.0082526 | 0.0020683
47 | 0.0013224 | 0.00033141
48 | 0.0047859 | 0.0011995
49 | 0.0069824 | 0.0017499
50 | 0.0089462 | 0.0022421
51 | 0.021284 | 0.0053343
52 | 0.0046691 | 0.0011702
53 | 0.016662 | 0.0041759
54 | 0.001602 | 0.00040149
55 | 0.0022586 | 0.00056606
56 | 0.0012526 | 0.00031392
57 | 0.0014069 | 0.00035261
58 | 0.0040682 | 0.0010196
59 | 0.0018204 | 0.00045624
60 | 0.0019291 | 0.00048348
61 | 0.0020296 | 0.00050867
62 | 0.0021155 | 0.00053019
63 | 0.0045984 | 0.0011525
64 | 0.0066881 | 0.0016762
65 | 0.0091691 | 0.002298
66 | 0.010375 | 0.0026002
67 | 0.019084 | 0.0047829
68 | 0.0088633 | 0.0022214
69 | 0.019628 | 0.0049194
70 | 0.01855 | 0.004649
71 | 0.040064 | 0.010041
72 | 0.0013143 | 0.00032938
73 | 0.00046329 | 0.00011611
74 | 0.0073658 | 0.001846
75 | 0.00073313 | 0.00018374
76 | 0.0025761 | 0.00064563
77 | 0.001392 | 0.00034886
78 | 0.0014461 | 0.00036243
79 | 0.0024763 | 0.00062063
80 | 0.00081747 | 0.00020488
81 | 0.0014182 | 0.00035544
82 | 0.0017423 | 0.00043666
83 | 0.0012872 | 0.0003226
84 | 0.0018076 | 0.00045303
85 | 0.012224 | 0.0030636
86 | 0.0040158 | 0.0010065
87 | 0.0029775 | 0.00074624
88 | 0.0017331 | 0.00043435
89 | 0.0024711 | 0.00061932
90 | 0.0022427 | 0.00056208
91 | 0.00058185 | 0.00014582
92 | 0.006794 | 0.0017027
93 | 0.0024913 | 0.00062438
94 | 0.003549 | 0.00088947
95 | 0.0033053 | 0.00082839
96 | 0.0032831 | 0.00082281
97 | 0.012724 | 0.0031889
98 | 0.0015813 | 0.00039632
99 | 0.00094515 | 0.00023688
100 | 0.0034649 | 0.00086838
101 | 0.0011641 | 0.00029175
102 | 0.0016177 | 0.00040543
103 | 0.0017343 | 0.00043465
104 | 0.0021468 | 0.00053803
105 | 0.0019099 | 0.00047866
106 | 0.0020632 | 0.0005171

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1