## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_193-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_193-13_0_3_node_46 | 0.4 | n |  | TRUE
2 | bus_LV_193-13_0_3_node_47 | 0.4 | n |  | TRUE
3 | bus_LV_193-13_0_3_node_48 | 0.4 | n |  | TRUE
4 | bus_LV_193-13_0_3_node_1 | 0.4 | n |  | TRUE
5 | bus_LV_193-13_0_3_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_193-13_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_193-13_0_3_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_193-13_0_3_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_193-13_0_3_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_193-13_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_193-13_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_193-13_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_193-13_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_193-13_0_3_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_193-13_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_193-13_0_3_node_36 | 0.4 | n |  | TRUE
17 | bus_LV_193-13_0_3_node_150 | 0.4 | n |  | TRUE
18 | bus_LV_193-13_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_193-13_0_3_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_193-13_0_3_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_193-13_0_3_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_193-13_0_3_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_193-13_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_193-13_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_193-13_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_193-13_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_193-13_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_193-13_0_3_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_193-13_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_193-13_0_3_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_193-13_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_193-13_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_193-13_0_3_node_56 | 0.4 | n |  | TRUE
34 | bus_LV_193-13_0_3_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_193-13_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_193-13_0_3_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_193-13_0_3_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_193-13_0_3_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_193-13_0_3_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_193-13_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_193-13_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_193-13_0_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_193-13_0_3_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_193-13_0_3_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_193-13_0_3_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_193-13_0_3_node_83 | 0.4 | n |  | TRUE
47 | bus_LV_193-13_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_193-13_0_3_node_89 | 0.4 | n |  | TRUE
49 | bus_LV_193-13_0_3_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_193-13_0_3_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_193-13_0_3_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_193-13_0_3_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_193-13_0_3_node_77 | 0.4 | n |  | TRUE
54 | bus_LV_193-13_0_3_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_193-13_0_3_node_91 | 0.4 | n |  | TRUE
56 | bus_LV_193-13_0_3_node_133 | 0.4 | n |  | TRUE
57 | bus_LV_193-13_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_193-13_0_3_node_134 | 0.4 | n |  | TRUE
59 | bus_LV_193-13_0_3_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_193-13_0_3_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_193-13_0_3_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_193-13_0_3_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_193-13_0_3_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_193-13_0_3_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_193-13_0_3_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_193-13_0_3_node_68 | 0.4 | n |  | TRUE
67 | bus_LV_193-13_0_3_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_193-13_0_3_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_193-13_0_3_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_193-13_0_3_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_193-13_0_3_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_193-13_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_193-13_0_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_193-13_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_193-13_0_3_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_193-13_0_3_node_78 | 0.4 | n |  | TRUE
77 | bus_LV_193-13_0_3_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_193-13_0_3_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_193-13_0_3_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_193-13_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_193-13_0_3_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_193-13_0_3_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_193-13_0_3_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_193-13_0_3_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_193-13_0_3_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_193-13_0_3_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_193-13_0_3_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_193-13_0_3_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_193-13_0_3_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_193-13_0_3_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_193-13_0_3_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_193-13_0_3_node_97 | 0.4 | n |  | TRUE
93 | bus_LV_193-13_0_3_node_98 | 0.4 | n |  | TRUE
94 | bus_LV_193-13_0_3_node_101 | 0.4 | n |  | TRUE
95 | bus_LV_193-13_0_3_node_127 | 0.4 | n |  | TRUE
96 | bus_LV_193-13_0_3_node_102 | 0.4 | n |  | TRUE
97 | bus_LV_193-13_0_3_node_125 | 0.4 | n |  | TRUE
98 | bus_LV_193-13_0_3_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_193-13_0_3_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_193-13_0_3_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_193-13_0_3_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_193-13_0_3_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_193-13_0_3_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_193-13_0_3_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_193-13_0_3_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_193-13_0_3_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_193-13_0_3_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_193-13_0_3_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_193-13_0_3_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_193-13_0_3_node_135 | 0.4 | n |  | TRUE
111 | bus_LV_193-13_0_3_node_111 | 0.4 | n |  | TRUE
112 | bus_LV_193-13_0_3_node_136 | 0.4 | n |  | TRUE
113 | bus_LV_193-13_0_3_node_137 | 0.4 | n |  | TRUE
114 | bus_LV_193-13_0_3_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_193-13_0_3_node_123 | 0.4 | n |  | TRUE
116 | bus_LV_193-13_0_3_node_108 | 0.4 | n |  | TRUE
117 | bus_LV_193-13_0_3_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_193-13_0_3_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_193-13_0_3_node_143 | 0.4 | n |  | TRUE
120 | bus_LV_193-13_0_3_node_144 | 0.4 | n |  | TRUE
121 | bus_LV_193-13_0_3_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_193-13_0_3_node_114 | 0.4 | n |  | TRUE
123 | bus_LV_193-13_0_3_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_193-13_0_3_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_193-13_0_3_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_193-13_0_3_node_118 | 0.4 | n |  | TRUE
127 | bus_LV_193-13_0_3_node_126 | 0.4 | n |  | TRUE
128 | bus_LV_193-13_0_3_node_141 | 0.4 | n |  | TRUE
129 | bus_LV_193-13_0_3_node_124 | 0.4 | n |  | TRUE
130 | bus_LV_193-13_0_3_node_142 | 0.4 | n |  | TRUE
131 | bus_LV_193-13_0_3_node_119 | 0.4 | n |  | TRUE
132 | bus_LV_193-13_0_3_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_193-13_0_3_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_193-13_0_3_node_145 | 0.4 | n |  | TRUE
135 | bus_LV_193-13_0_3_node_140 | 0.4 | n |  | TRUE
136 | bus_LV_193-13_0_3_node_128 | 0.4 | n |  | TRUE
137 | bus_LV_193-13_0_3_node_129 | 0.4 | n |  | TRUE
138 | bus_LV_193-13_0_3_node_130 | 0.4 | n |  | TRUE
139 | bus_LV_193-13_0_3_node_131 | 0.4 | n |  | TRUE
140 | bus_LV_193-13_0_3_node_132 | 0.4 | n |  | TRUE
141 | bus_LV_193-13_0_3_node_138 | 0.4 | n |  | TRUE
142 | bus_LV_193-13_0_3_node_139 | 0.4 | n |  | TRUE
143 | bus_LV_193-13_0_3_node_153 | 0.4 | n |  | TRUE
144 | bus_LV_193-13_0_3_node_146 | 0.4 | n |  | TRUE
145 | bus_LV_193-13_0_3_node_147 | 0.4 | n |  | TRUE
146 | bus_LV_193-13_0_3_node_148 | 0.4 | n |  | TRUE
147 | bus_LV_193-13_0_3_node_152 | 0.4 | n |  | TRUE
148 | bus_LV_193-13_0_3_node_155 | 0.4 | n |  | TRUE
149 | bus_MV_364_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_193-13_0_3_load_0 | 0 | 0.00085331 | 0.00021386 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_193-13_0_3_load_46 | 1 | 0.0017518 | 0.00043904 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_193-13_0_3_load_47 | 2 | 0.0017259 | 0.00043254 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_193-13_0_3_load_48 | 3 | 0.0010785 | 0.0002703 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_193-13_0_3_load_1 | 4 | 0.0035026 | 0.00087784 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_193-13_0_3_load_4 | 6 | 0.0034375 | 0.00086151 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_193-13_0_3_load_20 | 8 | 0.0026897 | 0.00067411 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_193-13_0_3_load_21 | 9 | 0.0026397 | 0.00066157 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_193-13_0_3_load_5 | 10 | 0.0044866 | 0.0011245 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_193-13_0_3_load_6 | 11 | 0.0064133 | 0.0016073 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_193-13_0_3_load_18 | 13 | 0.0030594 | 0.00076676 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_193-13_0_3_load_150 | 17 | 0.0040551 | 0.0010163 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_193-13_0_3_load_16 | 18 | 0.0047356 | 0.0011868 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_193-13_0_3_load_34 | 19 | 0.0056886 | 0.0014257 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_193-13_0_3_load_43 | 20 | 0.0050269 | 0.0012599 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_193-13_0_3_load_40 | 21 | 0.004839 | 0.0012128 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_193-13_0_3_load_9 | 22 | 0.005366 | 0.0013448 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_193-13_0_3_load_10 | 23 | 0.0054503 | 0.001366 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_193-13_0_3_load_13 | 26 | 0.003157 | 0.00079122 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_193-13_0_3_load_14 | 27 | 0.0050878 | 0.0012751 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_193-13_0_3_load_15 | 30 | 0.003291 | 0.0008248 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_193-13_0_3_load_30 | 31 | 0.0045171 | 0.0011321 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_193-13_0_3_load_31 | 32 | 0.0055011 | 0.0013787 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_193-13_0_3_load_56 | 33 | 0.0037433 | 0.00093816 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_193-13_0_3_load_57 | 34 | 0.0011274 | 0.00028256 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_193-13_0_3_load_22 | 35 | 0.0060132 | 0.0015071 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_193-13_0_3_load_23 | 36 | 0.0031612 | 0.00079226 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_193-13_0_3_load_26 | 39 | 0.0049259 | 0.0012346 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_193-13_0_3_load_37 | 40 | 0.0020438 | 0.00051223 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_193-13_0_3_load_38 | 41 | 0.0017893 | 0.00044845 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_193-13_0_3_load_44 | 42 | 0.005663 | 0.0014193 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_193-13_0_3_load_41 | 44 | 0.0055983 | 0.0014031 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_193-13_0_3_load_32 | 45 | 0.0020025 | 0.00050188 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_193-13_0_3_load_83 | 46 | 0.0018201 | 0.00045616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_193-13_0_3_load_39 | 47 | 0.0033047 | 0.00082825 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_193-13_0_3_load_54 | 50 | 0.0043601 | 0.0010928 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_193-13_0_3_load_52 | 51 | 0.0029194 | 0.00073168 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_193-13_0_3_load_33 | 52 | 0.004926 | 0.0012346 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_193-13_0_3_load_77 | 53 | 0.0018975 | 0.00047556 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_193-13_0_3_load_91 | 55 | 0.0015262 | 0.00038249 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_193-13_0_3_load_133 | 56 | 0.0030269 | 0.00075861 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_193-13_0_3_load_134 | 58 | 0.0017858 | 0.00044757 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_193-13_0_3_load_50 | 60 | 0.00096987 | 0.00024307 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_193-13_0_3_load_67 | 61 | 0.00070038 | 0.00017553 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_193-13_0_3_load_51 | 63 | 0.0022245 | 0.00055751 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_193-13_0_3_load_53 | 64 | 0.003517 | 0.00088145 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_193-13_0_3_load_55 | 65 | 0.0018013 | 0.00045144 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_193-13_0_3_load_68 | 66 | 0.0019716 | 0.00049414 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_193-13_0_3_load_61 | 67 | 0.0015474 | 0.00038781 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_193-13_0_3_load_58 | 68 | 0.0021955 | 0.00055024 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_193-13_0_3_load_59 | 69 | 0.0022602 | 0.00056647 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_193-13_0_3_load_60 | 70 | 0.0017098 | 0.00042851 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_193-13_0_3_load_62 | 71 | 0.001748 | 0.0004381 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_193-13_0_3_load_64 | 73 | 0.0024629 | 0.00061726 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_193-13_0_3_load_63 | 74 | 0.00068172 | 0.00017085 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_193-13_0_3_load_80 | 75 | 0.0024535 | 0.0006149 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_193-13_0_3_load_78 | 76 | 0.0022178 | 0.00055583 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_193-13_0_3_load_70 | 77 | 0.0014765 | 0.00037005 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_193-13_0_3_load_71 | 78 | 0.0010707 | 0.00026834 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_193-13_0_3_load_72 | 79 | 0.0024449 | 0.00061276 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_193-13_0_3_load_73 | 80 | 0.0013042 | 0.00032688 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_193-13_0_3_load_74 | 81 | 0.0022052 | 0.00055267 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_193-13_0_3_load_82 | 82 | 0.0013539 | 0.00033932 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_193-13_0_3_load_75 | 83 | 0.0019344 | 0.00048481 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_193-13_0_3_load_81 | 84 | 0.0011984 | 0.00030035 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_193-13_0_3_load_76 | 85 | 0.003723 | 0.00093306 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_193-13_0_3_load_79 | 86 | 0.0019977 | 0.00050067 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_193-13_0_3_load_84 | 87 | 0.0050504 | 0.0012657 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_193-13_0_3_load_85 | 88 | 0.0018378 | 0.0004606 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_193-13_0_3_load_86 | 89 | 0.0020475 | 0.00051316 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_193-13_0_3_load_87 | 90 | 0.0043731 | 0.001096 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_193-13_0_3_load_88 | 91 | 0.0028992 | 0.00072662 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_193-13_0_3_load_97 | 92 | 0.0014182 | 0.00035543 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_193-13_0_3_load_98 | 93 | 0.0026545 | 0.00066528 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_193-13_0_3_load_101 | 94 | 0.0026592 | 0.00066645 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_193-13_0_3_load_127 | 95 | 0.0016061 | 0.00040254 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_193-13_0_3_load_102 | 96 | 0.0014753 | 0.00036974 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_193-13_0_3_load_96 | 98 | 0.003226 | 0.00080851 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_193-13_0_3_load_92 | 99 | 0.0049413 | 0.0012384 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_193-13_0_3_load_93 | 100 | 0.0028227 | 0.00070743 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_193-13_0_3_load_94 | 101 | 0.002144 | 0.00053734 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_193-13_0_3_load_95 | 102 | 0.0073382 | 0.0018391 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_193-13_0_3_load_100 | 103 | 0.0022533 | 0.00056473 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_193-13_0_3_load_99 | 104 | 0.0044464 | 0.0011144 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_193-13_0_3_load_103 | 105 | 0.0046689 | 0.0011701 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_193-13_0_3_load_104 | 106 | 0.0061242 | 0.0015349 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_193-13_0_3_load_106 | 108 | 0.0038785 | 0.00097204 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_193-13_0_3_load_111 | 111 | 0.0033231 | 0.00083284 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_193-13_0_3_load_109 | 114 | 0.0015813 | 0.0003963 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_193-13_0_3_load_123 | 115 | 0.0033486 | 0.00083924 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_193-13_0_3_load_108 | 116 | 0.0024992 | 0.00062635 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_193-13_0_3_load_110 | 117 | 0.0015684 | 0.00039308 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_193-13_0_3_load_112 | 118 | 0.0010249 | 0.00025686 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_193-13_0_3_load_143 | 119 | 0.00097676 | 0.0002448 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_193-13_0_3_load_144 | 120 | 0.0016596 | 0.00041594 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_193-13_0_3_load_113 | 121 | 0.0010843 | 0.00027175 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_193-13_0_3_load_114 | 122 | 0.00064382 | 0.00016136 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_193-13_0_3_load_115 | 123 | 0.0032437 | 0.00081296 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_193-13_0_3_load_116 | 124 | 0.0028332 | 0.00071006 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_193-13_0_3_load_117 | 125 | 0.0020445 | 0.00051241 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_193-13_0_3_load_118 | 126 | 0.00083883 | 0.00021023 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_193-13_0_3_load_126 | 127 | 0.001682 | 0.00042154 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_193-13_0_3_load_141 | 128 | 0.0022004 | 0.00055147 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_193-13_0_3_load_124 | 129 | 0.0012417 | 0.00031119 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_193-13_0_3_load_142 | 130 | 0.0021128 | 0.00052951 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_193-13_0_3_load_119 | 131 | 0.001373 | 0.0003441 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_193-13_0_3_load_120 | 132 | 0.0015356 | 0.00038487 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_193-13_0_3_load_122 | 133 | 0.0012746 | 0.00031945 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_193-13_0_3_load_145 | 134 | 0.0013999 | 0.00035085 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_193-13_0_3_load_140 | 135 | 0.0010277 | 0.00025758 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_193-13_0_3_load_128 | 136 | 0.0054284 | 0.0013605 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_193-13_0_3_load_129 | 137 | 0.001133 | 0.00028397 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_193-13_0_3_load_130 | 138 | 0.0010987 | 0.00027535 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_193-13_0_3_load_131 | 139 | 0.0012089 | 0.00030298 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_193-13_0_3_load_132 | 140 | 0.0011039 | 0.00027665 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_193-13_0_3_load_139 | 142 | 0.0020471 | 0.00051304 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_193-13_0_3_load_153 | 143 | 0.0042177 | 0.0010571 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_193-13_0_3_load_146 | 144 | 0.0023321 | 0.00058447 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_193-13_0_3_load_147 | 145 | 0.0022668 | 0.00056812 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_193-13_0_3_load_155 | 148 | 0.0063307 | 0.0015866 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_193-13_0_3_line_0 |  | 0 | 1 | 0.085015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_193-13_0_3_line_1 |  | 1 | 2 | 0.033825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_193-13_0_3_line_2 |  | 1 | 3 | 0.028499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_193-13_0_3_line_3 |  | 2 | 59 | 0.031223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_193-13_0_3_line_4 |  | 3 | 60 | 0.00018787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_193-13_0_3_line_5 |  | 4 | 5 | 0.051257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_193-13_0_3_line_6 |  | 5 | 6 | 0.023983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_193-13_0_3_line_7 |  | 6 | 7 | 0.03247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_193-13_0_3_line_8 |  | 7 | 8 | 0.022775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_193-13_0_3_line_9 |  | 7 | 9 | 0.032585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_193-13_0_3_line_10 |  | 8 | 33 | 0.024287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_193-13_0_3_line_11 |  | 9 | 31 | 0.0022185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_193-13_0_3_line_12 |  | 10 | 11 | 0.017868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_193-13_0_3_line_13 |  | 11 | 12 | 0.018371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_193-13_0_3_line_14 |  | 12 | 13 | 0.0309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_193-13_0_3_line_15 |  | 12 | 14 | 0.021194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_193-13_0_3_line_16 |  | 13 | 18 | 0.0055731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_193-13_0_3_line_17 |  | 14 | 19 | 0.040082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_193-13_0_3_line_18 |  | 15 | 16 | 0.024061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_193-13_0_3_line_19 |  | 15 | 17 | 0.018789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_193-13_0_3_line_20 |  | 16 | 20 | 0.011479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_193-13_0_3_line_21 |  | 16 | 21 | 0.018937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_193-13_0_3_line_22 |  | 17 | 25 | 0.017975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_193-13_0_3_line_23 |  | 18 | 30 | 0.010225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_193-13_0_3_line_24 |  | 19 | 52 | 0.0087493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_193-13_0_3_line_25 |  | 21 | 44 | 0.021706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_193-13_0_3_line_26 |  | 22 | 23 | 0.017795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_193-13_0_3_line_27 |  | 22 | 24 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_193-13_0_3_line_28 |  | 23 | 25 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_193-13_0_3_line_29 |  | 24 | 26 | 0.031238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_193-13_0_3_line_30 |  | 24 | 27 | 0.027186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_193-13_0_3_line_31 |  | 25 | 28 | 0.030405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_193-13_0_3_line_32 |  | 26 | 29 | 0.017301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_193-13_0_3_line_33 |  | 28 | 30 | 0.011148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_193-13_0_3_line_34 |  | 29 | 31 | 0.019003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_193-13_0_3_line_35 |  | 29 | 32 | 0.019924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_193-13_0_3_line_36 |  | 32 | 50 | 0.021303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_193-13_0_3_line_37 |  | 33 | 34 | 0.030187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_193-13_0_3_line_38 |  | 34 | 60 | 0.026629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_193-13_0_3_line_39 |  | 35 | 36 | 0.0058538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_193-13_0_3_line_40 |  | 35 | 37 | 0.0098493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_193-13_0_3_line_41 |  | 36 | 38 | 0.018491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_193-13_0_3_line_42 |  | 37 | 39 | 0.0242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_193-13_0_3_line_43 |  | 38 | 40 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_193-13_0_3_line_44 |  | 38 | 41 | 0.017685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_193-13_0_3_line_45 |  | 39 | 42 | 0.020148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_193-13_0_3_line_46 |  | 40 | 45 | 0.012263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_193-13_0_3_line_47 |  | 41 | 46 | 0.026067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_193-13_0_3_line_48 |  | 42 | 43 | 0.025737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_193-13_0_3_line_49 |  | 43 | 44 | 0.020701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_193-13_0_3_line_50 |  | 44 | 49 | 0.036073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_193-13_0_3_line_51 |  | 46 | 53 | 0.0014754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_193-13_0_3_line_52 |  | 47 | 48 | 0.029585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_193-13_0_3_line_53 |  | 48 | 54 | 0.003639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_193-13_0_3_line_54 |  | 48 | 55 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_193-13_0_3_line_55 |  | 49 | 56 | 0.017349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_193-13_0_3_line_56 |  | 50 | 51 | 0.0021122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_193-13_0_3_line_57 |  | 51 | 63 | 0.025061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_193-13_0_3_line_58 |  | 53 | 85 | 0.012636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_193-13_0_3_line_59 |  | 54 | 95 | 0.022957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_193-13_0_3_line_60 |  | 54 | 58 | 0.017443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_193-13_0_3_line_61 |  | 55 | 96 | 0.024175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_193-13_0_3_line_62 |  | 56 | 57 | 0.01983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_193-13_0_3_line_63 |  | 57 | 58 | 0.008659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_193-13_0_3_line_64 |  | 59 | 61 | 0.0053271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_193-13_0_3_line_65 |  | 61 | 62 | 0.032072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_193-13_0_3_line_66 |  | 62 | 74 | 0.004021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_193-13_0_3_line_67 |  | 63 | 64 | 0.0034643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_193-13_0_3_line_68 |  | 64 | 65 | 0.019974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_193-13_0_3_line_69 |  | 65 | 66 | 0.0054856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_193-13_0_3_line_70 |  | 66 | 67 | 0.021615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_193-13_0_3_line_71 |  | 67 | 69 | 0.0035502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_193-13_0_3_line_72 |  | 68 | 69 | 0.027819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_193-13_0_3_line_73 |  | 68 | 70 | 0.0091971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_193-13_0_3_line_74 |  | 70 | 71 | 0.03098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_193-13_0_3_line_75 |  | 71 | 72 | 0.019253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_193-13_0_3_line_76 |  | 72 | 73 | 0.029155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_193-13_0_3_line_77 |  | 75 | 76 | 0.0083699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_193-13_0_3_line_78 |  | 76 | 86 | 0.023618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_193-13_0_3_line_79 |  | 77 | 78 | 0.0018232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_193-13_0_3_line_80 |  | 77 | 79 | 0.0010572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_193-13_0_3_line_81 |  | 78 | 80 | 0.025489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_193-13_0_3_line_82 |  | 79 | 81 | 0.018867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_193-13_0_3_line_83 |  | 80 | 82 | 0.0033808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_193-13_0_3_line_84 |  | 81 | 83 | 0.010278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_193-13_0_3_line_85 |  | 82 | 84 | 0.019692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_193-13_0_3_line_86 |  | 83 | 85 | 0.013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_193-13_0_3_line_87 |  | 84 | 86 | 0.0051636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_193-13_0_3_line_88 |  | 87 | 88 | 0.022701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_193-13_0_3_line_89 |  | 87 | 89 | 0.0035476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_193-13_0_3_line_90 |  | 88 | 90 | 0.0019572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_193-13_0_3_line_91 |  | 89 | 91 | 0.020455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_193-13_0_3_line_92 |  | 91 | 92 | 0.031715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_193-13_0_3_line_93 |  | 91 | 93 | 0.024554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_193-13_0_3_line_94 |  | 93 | 94 | 0.008724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_193-13_0_3_line_95 |  | 94 | 104 | 0.0041569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_193-13_0_3_line_96 |  | 95 | 97 | 0.0075624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_193-13_0_3_line_97 |  | 96 | 98 | 0.010196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_193-13_0_3_line_98 |  | 97 | 115 | 0.01466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_193-13_0_3_line_99 |  | 97 | 109 | 0.049965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_193-13_0_3_line_100 |  | 98 | 101 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_193-13_0_3_line_101 |  | 99 | 100 | 0.01438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_193-13_0_3_line_102 |  | 99 | 101 | 0.010532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_193-13_0_3_line_103 |  | 100 | 102 | 0.014359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_193-13_0_3_line_104 |  | 102 | 103 | 0.0076936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_193-13_0_3_line_105 |  | 103 | 104 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_193-13_0_3_line_106 |  | 105 | 106 | 0.021752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_193-13_0_3_line_107 |  | 105 | 107 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_193-13_0_3_line_108 |  | 107 | 108 | 0.017222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_193-13_0_3_line_109 |  | 107 | 109 | 0.014176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_193-13_0_3_line_110 |  | 108 | 110 | 0.019554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_193-13_0_3_line_111 |  | 109 | 111 | 0.015443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_193-13_0_3_line_112 |  | 110 | 112 | 0.02178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_193-13_0_3_line_113 |  | 110 | 113 | 0.009963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_193-13_0_3_line_114 |  | 111 | 114 | 0.0099167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_193-13_0_3_line_115 |  | 112 | 143 | 0.024351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_193-13_0_3_line_116 |  | 113 | 144 | 0.004476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_193-13_0_3_line_117 |  | 114 | 116 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_193-13_0_3_line_118 |  | 115 | 129 | 0.0038734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_193-13_0_3_line_119 |  | 116 | 117 | 0.0092361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_193-13_0_3_line_120 |  | 117 | 118 | 0.018495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_193-13_0_3_line_121 |  | 118 | 119 | 0.013854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_193-13_0_3_line_122 |  | 119 | 120 | 0.010928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_193-13_0_3_line_123 |  | 121 | 122 | 0.0026337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_193-13_0_3_line_124 |  | 121 | 123 | 0.004733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_193-13_0_3_line_125 |  | 122 | 124 | 0.017934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_193-13_0_3_line_126 |  | 123 | 125 | 0.023704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_193-13_0_3_line_127 |  | 124 | 126 | 0.0053747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_193-13_0_3_line_128 |  | 125 | 127 | 0.00066816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_193-13_0_3_line_129 |  | 126 | 128 | 0.016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_193-13_0_3_line_130 |  | 127 | 129 | 0.024806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_193-13_0_3_line_131 |  | 128 | 130 | 0.020766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_193-13_0_3_line_132 |  | 130 | 142 | 0.0084353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_193-13_0_3_line_133 |  | 131 | 132 | 0.015217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_193-13_0_3_line_134 |  | 132 | 133 | 0.020144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_193-13_0_3_line_135 |  | 133 | 134 | 0.0050594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_193-13_0_3_line_136 |  | 134 | 135 | 0.017334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_193-13_0_3_line_137 |  | 135 | 141 | 0.01302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_193-13_0_3_line_138 |  | 136 | 137 | 0.010864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_193-13_0_3_line_139 |  | 136 | 138 | 0.024129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_193-13_0_3_line_140 |  | 137 | 139 | 0.016185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_193-13_0_3_line_141 |  | 138 | 140 | 0.0092557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_193-13_0_3_line_142 |  | 140 | 141 | 0.012403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_193-13_0_3_line_143 |  | 141 | 142 | 0.0058036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_193-13_0_3_line_144 |  | 144 | 145 | 0.0085537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_193-13_0_3_line_145 |  | 145 | 146 | 0.015412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_193-13_0_3_line_146 |  | 146 | 147 | 0.031804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_193-13_0_3_line_147 |  | 147 | 148 | 0.017626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_193-13_0_3_trafo_39 | 0.63 MVA 20/0.4 kV | 149 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2689319.7993 | 1246962.6775 | 2689256.2126 | 1247019.1069
1 | 2689319.7993 | 1246962.6775 | 2689345.2334 | 1246984.9765
2 | 2689298.3699 | 1246943.8896 | 2689319.7993 | 1246962.6775
3 | 2689368.7124 | 1247005.5579 | 2689362.785 | 1247000.3647 | 2689345.2334 | 1246984.9765
4 | 2689298.3699 | 1246943.8896 | 2689298.2287 | 1246943.7658
5 | 2689202.0506 | 1246820.6882 | 2689189.9656 | 1246829.0683 | 2689180.9189 | 1246835.8484 | 2689173.7011 | 1246840.0764 | 2689172.9597 | 1246841.6553 | 2689172.8589 | 1246843.8332 | 2689173.7858 | 1246856.7563
6 | 2689202.0506 | 1246820.6882 | 2689207.2631 | 1246831.2411 | 2689212.8885 | 1246842.0809
7 | 2689228.9091 | 1246870.2404 | 2689224.1121 | 1246863.7078 | 2689212.8885 | 1246842.0809
8 | 2689228.9091 | 1246870.2404 | 2689228.5334 | 1246877.1288 | 2689231.2359 | 1246883.2852 | 2689237.9598 | 1246889.4957
9 | 2689228.9091 | 1246870.2404 | 2689231.2609 | 1246868.0742 | 2689252.5693 | 1246847.8368
10 | 2689237.9598 | 1246889.4957 | 2689241.7118 | 1246892.9612 | 2689255.9594 | 1246905.8006
11 | 2689254.1779 | 1246846.309 | 2689252.5693 | 1246847.8368
12 | 2689187.2266 | 1246707.6334 | 2689169.372 | 1246708.3247
13 | 2689205.5836 | 1246706.9228 | 2689187.2266 | 1246707.6334
14 | 2689205.5836 | 1246706.9228 | 2689194.1375 | 1246718.0145 | 2689193.7667 | 1246732.9709
15 | 2689205.5836 | 1246706.9228 | 2689215.8753 | 1246698.2489 | 2689211.7355 | 1246691.715
16 | 2689193.7667 | 1246732.9709 | 2689193.6286 | 1246738.5423
17 | 2689211.7355 | 1246691.715 | 2689231.2733 | 1246680.0891 | 2689231.2878 | 1246662.7427
18 | 2689240.9829 | 1246716.607 | 2689236.7133 | 1246722.7029 | 2689249.0564 | 1246733.8303
19 | 2689249.0564 | 1246733.8303 | 2689237.0373 | 1246748.2726
20 | 2689240.9829 | 1246716.607 | 2689252.3561 | 1246718.3906
21 | 2689240.9829 | 1246716.607 | 2689246.0231 | 1246710.0001 | 2689245.3669 | 1246699.3934
22 | 2689223.5934 | 1246760.1669 | 2689235.8228 | 1246749.7319 | 2689237.0373 | 1246748.2726
23 | 2689193.3753 | 1246748.7637 | 2689193.6286 | 1246738.5423
24 | 2689231.2951 | 1246653.9934 | 2689231.2878 | 1246662.7427
25 | 2689266.9679 | 1246697.2613 | 2689245.3669 | 1246699.3934
26 | 2689222.9489 | 1246778.824 | 2689222.3346 | 1246796.6086
27 | 2689236.1522 | 1246796.5942 | 2689222.3346 | 1246796.6086 | 2689222.3346 | 1246796.6086
28 | 2689223.5934 | 1246760.1669 | 2689222.9489 | 1246778.824
29 | 2689236.1522 | 1246796.5942 | 2689237.697 | 1246798.8636 | 2689240.1739 | 1246801.4361 | 2689252.703 | 1246815.2461 | 2689256.763 | 1246820.0306
30 | 2689247.6538 | 1246775.2958 | 2689236.2983 | 1246785.8884 | 2689234.2009 | 1246788.7145 | 2689234.7519 | 1246792.7592 | 2689236.1522 | 1246796.5942
31 | 2689223.5934 | 1246760.1669 | 2689193.099 | 1246759.908
32 | 2689267.957 | 1246833.2225 | 2689256.763 | 1246820.0306
33 | 2689193.099 | 1246759.908 | 2689193.3753 | 1246748.7637
34 | 2689267.957 | 1246833.2225 | 2689254.1779 | 1246846.309
35 | 2689267.957 | 1246833.2225 | 2689283.0862 | 1246846.1865
36 | 2689299.2626 | 1246860.0478 | 2689283.0862 | 1246846.1865
37 | 2689278.3843 | 1246926.0093 | 2689255.9594 | 1246905.8006
38 | 2689298.2287 | 1246943.7658 | 2689293.5646 | 1246939.6766 | 2689291.0154 | 1246937.3921 | 2689278.3843 | 1246926.0093
39 | 2689298.3609 | 1246765.005 | 2689293.1763 | 1246762.2872
40 | 2689284.453 | 1246757.7142 | 2689293.1763 | 1246762.2872
41 | 2689313.0584 | 1246776.0364 | 2689303.6714 | 1246767.7889 | 2689298.3609 | 1246765.005
42 | 2689284.453 | 1246757.7142 | 2689290.8813 | 1246745.2239 | 2689291.4805 | 1246735.0889
43 | 2689313.0584 | 1246776.0364 | 2689307.5291 | 1246786.5166 | 2689303.6332 | 1246792.0947
44 | 2689313.0584 | 1246776.0364 | 2689323.9303 | 1246783.5057 | 2689327.8679 | 1246785.6734
45 | 2689294.3653 | 1246715.5541 | 2689294.7355 | 1246724.0772 | 2689291.6924 | 1246731.5036 | 2689291.4805 | 1246735.0889
46 | 2689296.6114 | 1246802.1482 | 2689303.6332 | 1246792.0947
47 | 2689350.7033 | 1246798.2447 | 2689327.8679 | 1246785.6734
48 | 2689268.6592 | 1246717.8911 | 2689294.3653 | 1246715.5541
49 | 2689266.9679 | 1246697.2613 | 2689268.6592 | 1246717.8911
50 | 2689287.9044 | 1246675.5491 | 2689281.8955 | 1246695.796 | 2689266.9679 | 1246697.2613
51 | 2689351.9958 | 1246798.9562 | 2689350.7033 | 1246798.2447
52 | 2689346.8682 | 1246707.2052 | 2689334.6371 | 1246734.144
53 | 2689346.8682 | 1246707.2052 | 2689343.6376 | 1246705.5108
54 | 2689346.8682 | 1246707.2052 | 2689359.5065 | 1246713.639
55 | 2689287.9044 | 1246675.5491 | 2689303.0091 | 1246684.0842
56 | 2689299.2626 | 1246860.0478 | 2689300.8665 | 1246861.4221
57 | 2689321.5047 | 1246875.5483 | 2689305.8003 | 1246865.6498 | 2689300.8665 | 1246861.4221
58 | 2689351.9958 | 1246798.9562 | 2689363.0657 | 1246805.0504
59 | 2689343.6376 | 1246705.5108 | 2689353.9895 | 1246685.0207
60 | 2689343.6376 | 1246705.5108 | 2689335.1383 | 1246701.0127 | 2689328.2097 | 1246697.3712
61 | 2689381.0508 | 1246724.6067 | 2689359.5065 | 1246713.639
62 | 2689320.5448 | 1246693.3428 | 2689304.0175 | 1246684.6541 | 2689303.0091 | 1246684.0842
63 | 2689320.5448 | 1246693.3428 | 2689328.2097 | 1246697.3712
64 | 2689368.7124 | 1247005.5579 | 2689373.7338 | 1247007.3368
65 | 2689402.6694 | 1246999.543 | 2689397.5031 | 1247004.491 | 2689389.9999 | 1247008.114 | 2689384.0405 | 1247009.0471 | 2689377.6619 | 1247008.7285 | 2689373.7338 | 1247007.3368
66 | 2689402.6694 | 1246999.543 | 2689405.2654 | 1246996.4723
67 | 2689321.5047 | 1246875.5483 | 2689324.4354 | 1246877.3955
68 | 2689341.333 | 1246888.046 | 2689324.4354 | 1246877.3955
69 | 2689341.333 | 1246888.046 | 2689345.9737 | 1246890.9711
70 | 2689364.7674 | 1246901.617 | 2689353.2078 | 1246895.5307 | 2689345.9737 | 1246890.9711
71 | 2689364.7674 | 1246901.617 | 2689367.9088 | 1246903.271
72 | 2689392.5243 | 1246916.2314 | 2689367.9088 | 1246903.271
73 | 2689392.5243 | 1246916.2314 | 2689400.6623 | 1246920.5161
74 | 2689400.6623 | 1246920.5161 | 2689428.075 | 1246934.9493
75 | 2689445.1109 | 1246943.9189 | 2689428.075 | 1246934.9493
76 | 2689445.1109 | 1246943.9189 | 2689427.6946 | 1246967.3007
77 | 2689462.5124 | 1246876.9158 | 2689469.9851 | 1246880.6857
78 | 2689462.5124 | 1246876.9158 | 2689456.0002 | 1246873.6305 | 2689443.6308 | 1246862.9784
79 | 2689400.8189 | 1246827.6658 | 2689402.3227 | 1246828.6966
80 | 2689399.9469 | 1246827.068 | 2689400.8189 | 1246827.6658
81 | 2689422.2344 | 1246844.5525 | 2689409.6732 | 1246833.7353 | 2689402.3227 | 1246828.6966
82 | 2689399.9469 | 1246827.068 | 2689387.2489 | 1246818.3636 | 2689384.2071 | 1246816.689
83 | 2689424.7962 | 1246846.7587 | 2689422.2344 | 1246844.5525
84 | 2689375.2033 | 1246811.7323 | 2689384.2071 | 1246816.689
85 | 2689424.7962 | 1246846.7587 | 2689439.718 | 1246859.6089
86 | 2689375.2033 | 1246811.7323 | 2689363.0657 | 1246805.0504
87 | 2689443.6308 | 1246862.9784 | 2689439.718 | 1246859.6089
88 | 2689482.7762 | 1246803.2997 | 2689471.5948 | 1246823.0556
89 | 2689482.7762 | 1246803.2997 | 2689484.5237 | 1246800.2123
90 | 2689470.6307 | 1246824.759 | 2689471.5948 | 1246823.0556
91 | 2689494.5988 | 1246782.411 | 2689484.5237 | 1246800.2123
92 | 2689494.5988 | 1246782.411 | 2689522.4864 | 1246797.5142
93 | 2689494.5988 | 1246782.411 | 2689472.7167 | 1246771.2714
94 | 2689472.7167 | 1246771.2714 | 2689464.9421 | 1246767.3136
95 | 2689461.2376 | 1246765.4277 | 2689464.9421 | 1246767.3136
96 | 2689358.4662 | 1246679.0477 | 2689355.5519 | 1246681.9282 | 2689353.9895 | 1246685.0207
97 | 2689390.1371 | 1246729.2323 | 2689381.0508 | 1246724.6067
98 | 2689358.4662 | 1246679.0477 | 2689363.0282 | 1246676.6146 | 2689367.8431 | 1246675.4418 | 2689372.3731 | 1246675.6325
99 | 2689358.4662 | 1246679.0477 | 2689355.5195 | 1246655.0186 | 2689345.9454 | 1246631.101
100 | 2689390.1371 | 1246729.2323 | 2689403.0333 | 1246735.7974
101 | 2689412.4193 | 1246740.5755 | 2689425.2343 | 1246747.0994
102 | 2689412.4193 | 1246740.5755 | 2689403.0333 | 1246735.7974
103 | 2689438.0307 | 1246753.6137 | 2689425.2343 | 1246747.0994
104 | 2689438.0307 | 1246753.6137 | 2689444.887 | 1246757.104
105 | 2689461.2376 | 1246765.4277 | 2689444.887 | 1246757.104
106 | 2689321.2389 | 1246631.1658 | 2689303.1786 | 1246643.2891
107 | 2689335.9548 | 1246621.2876 | 2689321.2389 | 1246631.1658
108 | 2689335.9548 | 1246621.2876 | 2689330.4374 | 1246604.9736
109 | 2689345.9454 | 1246631.101 | 2689340.7846 | 1246627.654 | 2689335.9548 | 1246621.2876
110 | 2689324.1729 | 1246586.4507 | 2689330.4374 | 1246604.9736
111 | 2689345.9454 | 1246631.101 | 2689351.1774 | 1246632.3362 | 2689358.065 | 1246630.9946 | 2689360.931 | 1246629.9509
112 | 2689324.1729 | 1246586.4507 | 2689303.4373 | 1246593.2991
113 | 2689324.1729 | 1246586.4507 | 2689333.5259 | 1246582.9445
114 | 2689370.2491 | 1246626.5577 | 2689360.931 | 1246629.9509
115 | 2689303.4373 | 1246593.2991 | 2689300.6199 | 1246594.2686 | 2689290.9159 | 1246594.5004 | 2689282.7938 | 1246592.5322 | 2689279.7449 | 1246591.2514
116 | 2689333.5259 | 1246582.9445 | 2689337.6576 | 1246581.2229
117 | 2689386.6526 | 1246620.5844 | 2689370.2491 | 1246626.5577
118 | 2689376.0076 | 1246676.972 | 2689372.3731 | 1246675.6325 | 2689372.3731 | 1246675.6325
119 | 2689386.6526 | 1246620.5844 | 2689389.6439 | 1246619.4951 | 2689395.4247 | 1246617.7018
120 | 2689413.3953 | 1246613.7591 | 2689405.8798 | 1246614.4583 | 2689395.4247 | 1246617.7018
121 | 2689427.1897 | 1246612.4759 | 2689413.3953 | 1246613.7591
122 | 2689438.0709 | 1246611.4636 | 2689427.1897 | 1246612.4759
123 | 2689426.5921 | 1246695.616 | 2689428.2398 | 1246696.2233 | 2689429.0618 | 1246696.5307
124 | 2689422.1511 | 1246693.9792 | 2689426.5921 | 1246695.616
125 | 2689445.8601 | 1246702.8127 | 2689429.0618 | 1246696.5307
126 | 2689422.1511 | 1246693.9792 | 2689399.9102 | 1246685.7818
127 | 2689445.8601 | 1246702.8127 | 2689450.8943 | 1246704.6953
128 | 2689399.9102 | 1246685.7818 | 2689399.2833 | 1246685.5507
129 | 2689450.8943 | 1246704.6953 | 2689456.3736 | 1246706.7443 | 2689467.1143 | 1246709.7332
130 | 2689376.0076 | 1246676.972 | 2689399.2833 | 1246685.5507
131 | 2689487.126 | 1246715.279 | 2689476.4002 | 1246712.3173 | 2689467.1143 | 1246709.7332
132 | 2689495.2569 | 1246717.5243 | 2689487.126 | 1246715.279
133 | 2689567.5477 | 1246742.173 | 2689562.2582 | 1246740.9235 | 2689552.8056 | 1246738.4058
134 | 2689533.9824 | 1246731.3607 | 2689546.5021 | 1246736.7269 | 2689552.8056 | 1246738.4058
135 | 2689533.9824 | 1246731.3607 | 2689529.3321 | 1246729.3675
136 | 2689513.4001 | 1246722.5388 | 2689513.4001 | 1246722.5388 | 2689529.3321 | 1246729.3675
137 | 2689500.8512 | 1246719.069 | 2689513.4001 | 1246722.5388
138 | 2689496.8668 | 1246673.4551 | 2689495.9214 | 1246662.6319
139 | 2689496.8668 | 1246673.4551 | 2689498.9665 | 1246697.4923
140 | 2689494.513 | 1246646.5079 | 2689495.9214 | 1246662.6319
141 | 2689499.7719 | 1246706.7129 | 2689498.9665 | 1246697.4923
142 | 2689500.8512 | 1246719.069 | 2689499.7719 | 1246706.7129
143 | 2689500.8512 | 1246719.069 | 2689495.2569 | 1246717.5243
144 | 2689345.5533 | 1246577.933 | 2689337.6576 | 1246581.2229
145 | 2689358.5295 | 1246569.6223 | 2689356.4678 | 1246571.0701 | 2689345.5533 | 1246577.933 | 2689345.5533 | 1246577.933
146 | 2689358.5295 | 1246569.6223 | 2689364.6599 | 1246563.8881 | 2689373.3189 | 1246554.8007 | 2689380.8333 | 1246546.9636
147 | 2689380.8333 | 1246546.9636 | 2689376.5807 | 1246544.9091 | 2689370.4377 | 1246543.9603 | 2689365.8424 | 1246539.1025

## bus_geodata
| x | y | coords
0 | 2689256.2126 | 1247019.1069
1 | 2689319.7993 | 1246962.6775
2 | 2689345.2334 | 1246984.9765
3 | 2689298.3699 | 1246943.8896
4 | 2689173.7858 | 1246856.7563
5 | 2689202.0506 | 1246820.6882
6 | 2689212.8885 | 1246842.0809
7 | 2689228.9091 | 1246870.2404
8 | 2689237.9598 | 1246889.4957
9 | 2689252.5693 | 1246847.8368
10 | 2689169.372 | 1246708.3247
11 | 2689187.2266 | 1246707.6334
12 | 2689205.5836 | 1246706.9228
13 | 2689193.7667 | 1246732.9709
14 | 2689211.7355 | 1246691.715
15 | 2689249.0564 | 1246733.8303
16 | 2689240.9829 | 1246716.607
17 | 2689237.0373 | 1246748.2726
18 | 2689193.6286 | 1246738.5423
19 | 2689231.2878 | 1246662.7427
20 | 2689252.3561 | 1246718.3906
21 | 2689245.3669 | 1246699.3934
22 | 2689222.3346 | 1246796.6086
23 | 2689222.9489 | 1246778.824
24 | 2689236.1522 | 1246796.5942
25 | 2689223.5934 | 1246760.1669
26 | 2689256.763 | 1246820.0306
27 | 2689247.6538 | 1246775.2958
28 | 2689193.099 | 1246759.908
29 | 2689267.957 | 1246833.2225
30 | 2689193.3753 | 1246748.7637
31 | 2689254.1779 | 1246846.309
32 | 2689283.0862 | 1246846.1865
33 | 2689255.9594 | 1246905.8006
34 | 2689278.3843 | 1246926.0093
35 | 2689293.1763 | 1246762.2872
36 | 2689298.3609 | 1246765.005
37 | 2689284.453 | 1246757.7142
38 | 2689313.0584 | 1246776.0364
39 | 2689291.4805 | 1246735.0889
40 | 2689303.6332 | 1246792.0947
41 | 2689327.8679 | 1246785.6734
42 | 2689294.3653 | 1246715.5541
43 | 2689268.6592 | 1246717.8911
44 | 2689266.9679 | 1246697.2613
45 | 2689296.6114 | 1246802.1482
46 | 2689350.7033 | 1246798.2447
47 | 2689334.6371 | 1246734.144
48 | 2689346.8682 | 1246707.2052
49 | 2689287.9044 | 1246675.5491
50 | 2689299.2626 | 1246860.0478
51 | 2689300.8665 | 1246861.4221
52 | 2689231.2951 | 1246653.9934
53 | 2689351.9958 | 1246798.9562
54 | 2689343.6376 | 1246705.5108
55 | 2689359.5065 | 1246713.639
56 | 2689303.0091 | 1246684.0842
57 | 2689320.5448 | 1246693.3428
58 | 2689328.2097 | 1246697.3712
59 | 2689368.7124 | 1247005.5579
60 | 2689298.2287 | 1246943.7658
61 | 2689373.7338 | 1247007.3368
62 | 2689402.6694 | 1246999.543
63 | 2689321.5047 | 1246875.5483
64 | 2689324.4354 | 1246877.3955
65 | 2689341.333 | 1246888.046
66 | 2689345.9737 | 1246890.9711
67 | 2689364.7674 | 1246901.617
68 | 2689392.5243 | 1246916.2314
69 | 2689367.9088 | 1246903.271
70 | 2689400.6623 | 1246920.5161
71 | 2689428.075 | 1246934.9493
72 | 2689445.1109 | 1246943.9189
73 | 2689427.6946 | 1246967.3007
74 | 2689405.2654 | 1246996.4723
75 | 2689469.9851 | 1246880.6857
76 | 2689462.5124 | 1246876.9158
77 | 2689400.8189 | 1246827.6658
78 | 2689402.3227 | 1246828.6966
79 | 2689399.9469 | 1246827.068
80 | 2689422.2344 | 1246844.5525
81 | 2689384.2071 | 1246816.689
82 | 2689424.7962 | 1246846.7587
83 | 2689375.2033 | 1246811.7323
84 | 2689439.718 | 1246859.6089
85 | 2689363.0657 | 1246805.0504
86 | 2689443.6308 | 1246862.9784
87 | 2689482.7762 | 1246803.2997
88 | 2689471.5948 | 1246823.0556
89 | 2689484.5237 | 1246800.2123
90 | 2689470.6307 | 1246824.759
91 | 2689494.5988 | 1246782.411
92 | 2689522.4864 | 1246797.5142
93 | 2689472.7167 | 1246771.2714
94 | 2689464.9421 | 1246767.3136
95 | 2689353.9895 | 1246685.0207
96 | 2689381.0508 | 1246724.6067
97 | 2689358.4662 | 1246679.0477
98 | 2689390.1371 | 1246729.2323
99 | 2689412.4193 | 1246740.5755
100 | 2689425.2343 | 1246747.0994
101 | 2689403.0333 | 1246735.7974
102 | 2689438.0307 | 1246753.6137
103 | 2689444.887 | 1246757.104
104 | 2689461.2376 | 1246765.4277
105 | 2689321.2389 | 1246631.1658
106 | 2689303.1786 | 1246643.2891
107 | 2689335.9548 | 1246621.2876
108 | 2689330.4374 | 1246604.9736
109 | 2689345.9454 | 1246631.101
110 | 2689324.1729 | 1246586.4507
111 | 2689360.931 | 1246629.9509
112 | 2689303.4373 | 1246593.2991
113 | 2689333.5259 | 1246582.9445
114 | 2689370.2491 | 1246626.5577
115 | 2689372.3731 | 1246675.6325
116 | 2689386.6526 | 1246620.5844
117 | 2689395.4247 | 1246617.7018
118 | 2689413.3953 | 1246613.7591
119 | 2689427.1897 | 1246612.4759
120 | 2689438.0709 | 1246611.4636
121 | 2689426.5921 | 1246695.616
122 | 2689429.0618 | 1246696.5307
123 | 2689422.1511 | 1246693.9792
124 | 2689445.8601 | 1246702.8127
125 | 2689399.9102 | 1246685.7818
126 | 2689450.8943 | 1246704.6953
127 | 2689399.2833 | 1246685.5508
128 | 2689467.1143 | 1246709.7332
129 | 2689376.0076 | 1246676.972
130 | 2689487.126 | 1246715.279
131 | 2689567.5477 | 1246742.173
132 | 2689552.8056 | 1246738.4058
133 | 2689533.9824 | 1246731.3607
134 | 2689529.3321 | 1246729.3675
135 | 2689513.4001 | 1246722.5388
136 | 2689496.8668 | 1246673.4551
137 | 2689495.9214 | 1246662.6319
138 | 2689498.9665 | 1246697.4923
139 | 2689494.513 | 1246646.5079
140 | 2689499.7719 | 1246706.7129
141 | 2689500.8512 | 1246719.069
142 | 2689495.2569 | 1246717.5243
143 | 2689279.7449 | 1246591.2514
144 | 2689337.6576 | 1246581.2229
145 | 2689345.5533 | 1246577.933
146 | 2689358.5295 | 1246569.6223
147 | 2689380.8333 | 1246546.9636
148 | 2689365.8424 | 1246539.1025
149 | 2689346.8682 | 1246707.2052

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97156 | -0.54914 | 0.00085331 | 0.00021386
1 | 0.97163 | -0.5478 | 0.0017518 | 0.00043904
2 | 0.97153 | -0.54974 | 0.0017259 | 0.00043254
3 | 0.97178 | -0.54479 | 0.0010785 | 0.0002703
4 | 0.97238 | -0.53291 | 0.0035026 | 0.00087784
5 | 0.97254 | -0.52961 | 0 | 0
6 | 0.97262 | -0.52806 | 0.0034375 | 0.00086151
7 | 0.97283 | -0.5239 | 0 | 0
8 | 0.97251 | -0.53034 | 0.0026897 | 0.00067411
9 | 0.97351 | -0.51055 | 0.0026397 | 0.00066157
10 | 0.97816 | -0.4194 | 0.0044866 | 0.0011245
11 | 0.97824 | -0.41794 | 0.0064133 | 0.0016073
12 | 0.97842 | -0.4143 | 0 | 0
13 | 0.97904 | -0.4022 | 0.0030594 | 0.00076676
14 | 0.97822 | -0.41839 | 0 | 0
15 | 0.98472 | -0.29177 | 0 | 0
16 | 0.98739 | -0.24028 | 0 | 0
17 | 0.98263 | -0.33218 | 0.0040551 | 0.0010163
18 | 0.97917 | -0.39971 | 0.0047356 | 0.0011868
19 | 0.97782 | -0.42615 | 0.0056886 | 0.0014257
20 | 0.98734 | -0.24131 | 0.0050269 | 0.0012599
21 | 0.98958 | -0.19825 | 0.004839 | 0.0012128
22 | 0.97798 | -0.42273 | 0.005366 | 0.0013448
23 | 0.97926 | -0.3977 | 0.0054503 | 0.001366
24 | 0.97705 | -0.44085 | 0 | 0
25 | 0.9807 | -0.36968 | 0 | 0
26 | 0.97511 | -0.47904 | 0.003157 | 0.00079122
27 | 0.97693 | -0.44338 | 0.0050878 | 0.0012751
28 | 0.97978 | -0.38766 | 0 | 0
29 | 0.97408 | -0.49925 | 0 | 0
30 | 0.97945 | -0.39426 | 0.003291 | 0.0008248
31 | 0.97356 | -0.50953 | 0.0045171 | 0.0011321
32 | 0.97345 | -0.51178 | 0.0055011 | 0.0013787
33 | 0.97222 | -0.536 | 0.0037433 | 0.00093816
34 | 0.97197 | -0.54095 | 0.0011274 | 0.00028256
35 | 0.98644 | -0.25943 | 0.0060132 | 0.0015071
36 | 0.98624 | -0.26322 | 0.0031612 | 0.00079226
37 | 0.98682 | -0.25201 | 0 | 0
38 | 0.98568 | -0.27414 | 0 | 0
39 | 0.98776 | -0.23378 | 0.0049259 | 0.0012346
40 | 0.98561 | -0.2755 | 0.0020438 | 0.00051223
41 | 0.98521 | -0.28331 | 0.0017893 | 0.00044845
42 | 0.98863 | -0.21686 | 0.005663 | 0.0014193
43 | 0.98988 | -0.1927 | 0 | 0
44 | 0.99088 | -0.17332 | 0.0055983 | 0.0014031
45 | 0.98559 | -0.27594 | 0.0020025 | 0.00050188
46 | 0.98456 | -0.29601 | 0.0018201 | 0.00045616
47 | 1 | 0 | -0.33576 | -0.08553
48 | 0.997 | -0.056806 | 0 | 0
49 | 0.99297 | -0.13336 | 0 | 0
50 | 0.97288 | -0.52304 | 0.0043601 | 0.0010928
51 | 0.97283 | -0.52399 | 0.0029194 | 0.00073168
52 | 0.97778 | -0.42693 | 0.004926 | 0.0012346
53 | 0.98453 | -0.29668 | 0.0018975 | 0.00047556
54 | 0.9967 | -0.062686 | 0 | 0
55 | 0.99632 | -0.070024 | 0.0015262 | 0.00038249
56 | 0.99398 | -0.11421 | 0.0030269 | 0.00075861
57 | 0.99515 | -0.09201 | 0 | 0
58 | 0.99566 | -0.082333 | 0.0017858 | 0.00044757
59 | 0.97149 | -0.55054 | 0 | 0
60 | 0.97178 | -0.54477 | 0.00096987 | 0.00024307
61 | 0.97148 | -0.55068 | 0.00070038 | 0.00017553
62 | 0.97146 | -0.55108 | 0 | 0
63 | 0.97233 | -0.53389 | 0.0022245 | 0.00055751
64 | 0.97226 | -0.53512 | 0.003517 | 0.00088145
65 | 0.97197 | -0.54091 | 0.0018013 | 0.00045144
66 | 0.9719 | -0.54231 | 0.0019716 | 0.00049414
67 | 0.97166 | -0.54707 | 0.0015474 | 0.00038781
68 | 0.97141 | -0.55192 | 0.0021955 | 0.00055024
69 | 0.97163 | -0.54775 | 0.0022602 | 0.00056647
70 | 0.97136 | -0.55293 | 0.0017098 | 0.00042851
71 | 0.97124 | -0.55534 | 0.001748 | 0.0004381
72 | 0.9712 | -0.55622 | 0 | 0
73 | 0.97113 | -0.55754 | 0.0024629 | 0.00061726
74 | 0.97146 | -0.55113 | 0.00068172 | 0.00017085
75 | 0.98296 | -0.32725 | 0.0024535 | 0.0006149
76 | 0.98298 | -0.32688 | 0.0022178 | 0.00055583
77 | 0.98355 | -0.3157 | 0.0014765 | 0.00037005
78 | 0.98353 | -0.31608 | 0.0010707 | 0.00026834
79 | 0.98357 | -0.31545 | 0.0024449 | 0.00061276
80 | 0.98329 | -0.32092 | 0.0013042 | 0.00032688
81 | 0.98383 | -0.31018 | 0.0022052 | 0.00055267
82 | 0.98326 | -0.32148 | 0.0013539 | 0.00033932
83 | 0.984 | -0.3069 | 0.0019344 | 0.00048481
84 | 0.98311 | -0.32427 | 0.0011984 | 0.00030035
85 | 0.98425 | -0.30199 | 0.003723 | 0.00093306
86 | 0.98308 | -0.32489 | 0.0019977 | 0.00050067
87 | 0.99105 | -0.17169 | 0.0050504 | 0.0012657
88 | 0.99092 | -0.1742 | 0.0018378 | 0.0004606
89 | 0.99109 | -0.17098 | 0.0020475 | 0.00051316
90 | 0.99091 | -0.17435 | 0.0043731 | 0.001096
91 | 0.99134 | -0.16615 | 0.0028992 | 0.00072662
92 | 0.9913 | -0.16695 | 0.0014182 | 0.00035543
93 | 0.99173 | -0.15848 | 0.0026545 | 0.00066528
94 | 0.99189 | -0.15534 | 0.0026592 | 0.00066645
95 | 0.99493 | -0.096573 | 0.0016061 | 0.00040254
96 | 0.99518 | -0.09195 | 0.0014753 | 0.00036974
97 | 0.99436 | -0.10755 | 0 | 0
98 | 0.99471 | -0.10095 | 0.003226 | 0.00080851
99 | 0.99366 | -0.12122 | 0.0049413 | 0.0012384
100 | 0.99314 | -0.13133 | 0.0028227 | 0.00070743
101 | 0.99409 | -0.11291 | 0.002144 | 0.00053734
102 | 0.99265 | -0.14072 | 0.0073382 | 0.0018391
103 | 0.99244 | -0.14476 | 0.0022533 | 0.00056473
104 | 0.99198 | -0.15365 | 0.0044464 | 0.0011144
105 | 0.99186 | -0.1559 | 0.0046689 | 0.0011701
106 | 0.99174 | -0.15826 | 0.0061242 | 0.0015349
107 | 0.99204 | -0.15251 | 0 | 0
108 | 0.99174 | -0.15831 | 0.0038785 | 0.00097204
109 | 0.99242 | -0.14502 | 0 | 0
110 | 0.99147 | -0.16357 | 0 | 0
111 | 0.99224 | -0.14848 | 0.0033231 | 0.00083284
112 | 0.99138 | -0.16519 | 0 | 0
113 | 0.99137 | -0.1655 | 0 | 0
114 | 0.99216 | -0.15011 | 0.0015813 | 0.0003963
115 | 0.99383 | -0.11787 | 0.0033486 | 0.00083924
116 | 0.99204 | -0.1525 | 0.0024992 | 0.00062635
117 | 0.99199 | -0.15336 | 0.0015684 | 0.00039308
118 | 0.99193 | -0.15456 | 0.0010249 | 0.00025686
119 | 0.9919 | -0.1552 | 0.00097676 | 0.0002448
120 | 0.99188 | -0.15552 | 0.0016596 | 0.00041594
121 | 0.99207 | -0.15187 | 0.0010843 | 0.00027175
122 | 0.992 | -0.15314 | 0.00064382 | 0.00016136
123 | 0.99219 | -0.1495 | 0.0032437 | 0.00081296
124 | 0.99157 | -0.1616 | 0.0028332 | 0.00071006
125 | 0.99288 | -0.13624 | 0.0020445 | 0.00051241
126 | 0.99145 | -0.16387 | 0.00083883 | 0.00021023
127 | 0.9929 | -0.13585 | 0.001682 | 0.00042154
128 | 0.99109 | -0.17079 | 0.0022004 | 0.00055147
129 | 0.9937 | -0.12037 | 0.0012417 | 0.00031119
130 | 0.9907 | -0.17844 | 0.0021128 | 0.00052951
131 | 0.99021 | -0.18798 | 0.001373 | 0.0003441
132 | 0.99022 | -0.18761 | 0.0015356 | 0.00038487
133 | 0.99028 | -0.18657 | 0.0012746 | 0.00031945
134 | 0.9903 | -0.18619 | 0.0013999 | 0.00035085
135 | 0.99039 | -0.18447 | 0.0010277 | 0.00025758
136 | 0.9901 | -0.18993 | 0.0054284 | 0.0013605
137 | 0.99008 | -0.19038 | 0.001133 | 0.00028397
138 | 0.99028 | -0.1866 | 0.0010987 | 0.00027535
139 | 0.99006 | -0.19073 | 0.0012089 | 0.00030298
140 | 0.99035 | -0.18514 | 0.0011039 | 0.00027665
141 | 0.99046 | -0.18294 | 0 | 0
142 | 0.99055 | -0.18123 | 0.0020471 | 0.00051304
143 | 0.99129 | -0.16702 | 0.0042177 | 0.0010571
144 | 0.99132 | -0.16636 | 0.0023321 | 0.00058447
145 | 0.99125 | -0.16767 | 0.0022668 | 0.00056812
146 | 0.99116 | -0.1694 | 0 | 0
147 | 0.99098 | -0.17297 | 0 | 0
148 | 0.99088 | -0.17495 | 0.0063307 | 0.0015866
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00085331 | -0.00021386 | 0.00085336 | 0.00021284 | 5.4436e-08 | -1.018e-06 | 0.0013069 | 0.0013065 | 0.0013069 | 0.97156 | -0.54914 | 0.97163 | -0.5478 | 0.35904
1 | 0.0031083 | 0.00077784 | -0.003108 | -0.00077808 | 2.8739e-07 | -2.3496e-07 | 0.0047599 | 0.00476 | 0.00476 | 0.97163 | -0.5478 | 0.97153 | -0.54974 | 1.3077
2 | -0.0057135 | -0.0014297 | 0.0057143 | 0.0014299 | 8.1808e-07 | 1.7054e-07 | 0.0087492 | 0.0087491 | 0.0087492 | 0.97163 | -0.5478 | 0.97178 | -0.54479 | 2.4036
3 | 0.0013822 | 0.00034553 | -0.0013821 | -0.00034589 | 5.246e-08 | -3.5304e-07 | 0.0021167 | 0.0021168 | 0.0021168 | 0.97153 | -0.54974 | 0.97149 | -0.55054 | 0.58154
4 | -0.0067928 | -0.0017002 | 0.0067928 | 0.0017002 | 7.6218e-09 | 2.5493e-09 | 0.010401 | 0.010401 | 0.010401 | 0.97178 | -0.54479 | 0.97178 | -0.54477 | 2.8573
5 | -0.0035026 | -0.00087784 | 0.0035032 | 0.00087756 | 5.5221e-07 | -2.8252e-07 | 0.00536 | 0.0053598 | 0.00536 | 0.97238 | -0.53291 | 0.97254 | -0.52961 | 1.4725
6 | -0.0035032 | -0.00087756 | 0.0035034 | 0.00087743 | 2.5836e-07 | -1.3227e-07 | 0.0053598 | 0.0053597 | 0.0053598 | 0.97254 | -0.52961 | 0.97262 | -0.52806 | 1.4725
7 | -0.0069409 | -0.0017389 | 0.0069423 | 0.0017394 | 1.373e-06 | 4.7562e-07 | 0.010619 | 0.010619 | 0.010619 | 0.97262 | -0.52806 | 0.97283 | -0.5239 | 2.9172
8 | 0.015335 | 0.0038442 | -0.01533 | -0.0038415 | 4.699e-06 | 2.7247e-06 | 0.023456 | 0.023456 | 0.023456 | 0.97283 | -0.5239 | 0.97251 | -0.53034 | 6.444
9 | -0.022277 | -0.0055837 | 0.022291 | 0.0055923 | 1.4187e-05 | 8.675e-06 | 0.034074 | 0.034074 | 0.034074 | 0.97283 | -0.5239 | 0.97351 | -0.51055 | 9.3611
10 | 0.01264 | 0.0031674 | -0.012637 | -0.0031655 | 3.4067e-06 | 1.8791e-06 | 0.01934 | 0.019341 | 0.019341 | 0.97251 | -0.53034 | 0.97222 | -0.536 | 5.3134
11 | -0.024931 | -0.0062539 | 0.024932 | 0.0062546 | 1.2082e-06 | 7.4568e-07 | 0.038109 | 0.038109 | 0.038109 | 0.97351 | -0.51055 | 0.97356 | -0.50953 | 10.4695
12 | -0.0044866 | -0.0011245 | 0.0044869 | 0.0011244 | 3.1213e-07 | -2.4545e-08 | 0.0068252 | 0.0068251 | 0.0068252 | 0.97816 | -0.4194 | 0.97824 | -0.41794 | 1.8751
13 | -0.0109 | -0.0027317 | 0.010902 | 0.0027327 | 1.8939e-06 | 9.8139e-07 | 0.01658 | 0.01658 | 0.01658 | 0.97824 | -0.41794 | 0.97842 | -0.4143 | 4.5551
14 | -0.021523 | -0.0053961 | 0.021535 | 0.0054036 | 1.2415e-05 | 7.5576e-06 | 0.032733 | 0.032733 | 0.032733 | 0.97842 | -0.4143 | 0.97904 | -0.4022 | 8.9927
15 | 0.010621 | 0.0026633 | -0.010619 | -0.0026623 | 2.0737e-06 | 1.0611e-06 | 0.016153 | 0.016153 | 0.016153 | 0.97842 | -0.4143 | 0.97822 | -0.41839 | 4.4376
16 | -0.024595 | -0.0061704 | 0.024598 | 0.0061722 | 2.9206e-06 | 1.7991e-06 | 0.037383 | 0.037383 | 0.037383 | 0.97904 | -0.4022 | 0.97917 | -0.39971 | 10.2701
17 | 0.010619 | 0.0026623 | -0.010615 | -0.0026603 | 3.9218e-06 | 2.007e-06 | 0.016153 | 0.016153 | 0.016153 | 0.97822 | -0.41839 | 0.97782 | -0.42615 | 4.4377
18 | -0.12042 | -0.030583 | 0.12072 | 0.030774 | 0.00029925 | 0.00019121 | 0.18212 | 0.18212 | 0.18212 | 0.98472 | -0.29177 | 0.98739 | -0.24028 | 50.0319
19 | 0.12042 | 0.030583 | -0.12019 | -0.030434 | 0.00023369 | 0.00014932 | 0.18212 | 0.18212 | 0.18212 | 0.98472 | -0.29177 | 0.98263 | -0.33218 | 50.032
20 | 0.0050272 | 0.0012599 | -0.0050269 | -0.0012599 | 2.4707e-07 | 1.1312e-08 | 0.007576 | 0.0075761 | 0.0075761 | 0.98739 | -0.24028 | 0.98734 | -0.24131 | 2.0813
21 | -0.12575 | -0.032034 | 0.126 | 0.032198 | 0.00025553 | 0.0001633 | 0.18969 | 0.18969 | 0.18969 | 0.98739 | -0.24028 | 0.98958 | -0.19825 | 52.1132
22 | 0.11613 | 0.029418 | -0.11592 | -0.029284 | 0.00020874 | 0.00013337 | 0.17598 | 0.17598 | 0.17598 | 0.98263 | -0.33218 | 0.9807 | -0.36968 | 48.345
23 | -0.029333 | -0.007359 | 0.029341 | 0.0073638 | 7.6198e-06 | 4.748e-06 | 0.04458 | 0.04458 | 0.04458 | 0.97917 | -0.39971 | 0.97945 | -0.39426 | 12.2471
24 | 0.0049262 | 0.0012346 | -0.004926 | -0.0012346 | 1.8438e-07 | 8.2591e-09 | 0.0074964 | 0.0074965 | 0.0074965 | 0.97782 | -0.42615 | 0.97778 | -0.42693 | 2.0595
25 | -0.13084 | -0.03341 | 0.131 | 0.033511 | 0.0001579 | 0.0001005 | 0.19697 | 0.19697 | 0.19697 | 0.98958 | -0.19825 | 0.99088 | -0.17332 | 27.0561
26 | -0.0776 | -0.019575 | 0.077693 | 0.019634 | 9.3099e-05 | 5.936e-05 | 0.11812 | 0.11811 | 0.11812 | 0.97798 | -0.42273 | 0.97926 | -0.3977 | 32.4492
27 | 0.072234 | 0.01823 | -0.072171 | -0.01819 | 6.2641e-05 | 3.9917e-05 | 0.10995 | 0.10995 | 0.10995 | 0.97798 | -0.42273 | 0.97705 | -0.44085 | 30.2062
28 | -0.083143 | -0.021 | 0.083255 | 0.021072 | 0.00011184 | 7.1344e-05 | 0.1264 | 0.1264 | 0.1264 | 0.97926 | -0.3977 | 0.9807 | -0.36968 | 34.7244
29 | 0.067083 | 0.016915 | -0.06696 | -0.016837 | 0.00012236 | 7.7918e-05 | 0.1022 | 0.1022 | 0.1022 | 0.97705 | -0.44085 | 0.97511 | -0.47904 | 28.0773
30 | 0.0050884 | 0.0012752 | -0.0050878 | -0.0012751 | 6.1223e-07 | 5.1391e-08 | 0.0077494 | 0.0077495 | 0.0077495 | 0.97705 | -0.44085 | 0.97693 | -0.44338 | 2.129
31 | 0.03267 | 0.0082126 | -0.032642 | -0.008195 | 2.8027e-05 | 1.7554e-05 | 0.049579 | 0.049579 | 0.049579 | 0.9807 | -0.36968 | 0.97978 | -0.38766 | 13.6207
32 | 0.063803 | 0.016046 | -0.063742 | -0.016007 | 6.1529e-05 | 3.9163e-05 | 0.097384 | 0.097384 | 0.097384 | 0.97511 | -0.47904 | 0.97408 | -0.49925 | 26.7538
33 | 0.032642 | 0.008195 | -0.032632 | -0.0081886 | 1.0276e-05 | 6.4362e-06 | 0.049579 | 0.049579 | 0.049579 | 0.97978 | -0.38766 | 0.97945 | -0.39426 | 13.6207
34 | 0.029464 | 0.0073958 | -0.029449 | -0.0073867 | 1.4439e-05 | 9.0045e-06 | 0.045013 | 0.045013 | 0.045013 | 0.97408 | -0.49925 | 0.97356 | -0.50953 | 12.3663
35 | 0.034278 | 0.008611 | -0.034258 | -0.0085981 | 2.0492e-05 | 1.2867e-05 | 0.052371 | 0.052371 | 0.052371 | 0.97408 | -0.49925 | 0.97345 | -0.51178 | 14.3876
36 | 0.028756 | 0.0072194 | -0.028741 | -0.0072098 | 1.5439e-05 | 9.6163e-06 | 0.043962 | 0.043962 | 0.043962 | 0.97345 | -0.51178 | 0.97288 | -0.52304 | 12.0774
37 | 0.0088936 | 0.0022274 | -0.0088915 | -0.0022264 | 2.0973e-06 | 9.6804e-07 | 0.013611 | 0.013612 | 0.013612 | 0.97222 | -0.536 | 0.97197 | -0.54095 | 3.7394
38 | 0.0077641 | 0.0019438 | -0.0077627 | -0.0019433 | 1.4107e-06 | 5.7286e-07 | 0.011886 | 0.011886 | 0.011886 | 0.97197 | -0.54095 | 0.97178 | -0.54477 | 3.2653
39 | 0.036171 | 0.0090916 | -0.036164 | -0.0090875 | 6.5374e-06 | 4.1092e-06 | 0.054572 | 0.054572 | 0.054572 | 0.98644 | -0.25943 | 0.98624 | -0.26322 | 14.9922
40 | -0.042184 | -0.010599 | 0.042199 | 0.010608 | 1.496e-05 | 9.4486e-06 | 0.063643 | 0.063642 | 0.063643 | 0.98644 | -0.25943 | 0.98682 | -0.25201 | 17.4842
41 | 0.033003 | 0.0082953 | -0.032986 | -0.0082845 | 1.7199e-05 | 1.0771e-05 | 0.049802 | 0.049802 | 0.049802 | 0.98624 | -0.26322 | 0.98568 | -0.27414 | 13.682
42 | -0.042199 | -0.010608 | 0.042236 | 0.010631 | 3.6757e-05 | 2.3215e-05 | 0.063642 | 0.063642 | 0.063642 | 0.98682 | -0.25201 | 0.98776 | -0.23378 | 17.4842
43 | 0.0040466 | 0.0010139 | -0.0040464 | -0.001014 | 2.6104e-07 | -7.0679e-08 | 0.0061088 | 0.0061089 | 0.0061089 | 0.98568 | -0.27414 | 0.98561 | -0.2755 | 1.6783
44 | 0.028939 | 0.0072706 | -0.028926 | -0.0072627 | 1.2661e-05 | 7.878e-06 | 0.043694 | 0.043694 | 0.043694 | 0.98568 | -0.27414 | 0.98521 | -0.28331 | 12.0038
45 | -0.047161 | -0.011866 | 0.0472 | 0.01189 | 3.8156e-05 | 2.4162e-05 | 0.071063 | 0.071063 | 0.071063 | 0.98776 | -0.23378 | 0.98863 | -0.21686 | 19.5228
46 | 0.0020025 | 0.00050175 | -0.0020025 | -0.00050188 | 4.2033e-08 | -1.2938e-07 | 0.0030233 | 0.0030233 | 0.0030233 | 0.98561 | -0.2755 | 0.98559 | -0.27594 | 0.83058
47 | 0.027137 | 0.0068143 | -0.027121 | -0.0068041 | 1.6425e-05 | 1.018e-05 | 0.040991 | 0.040991 | 0.040991 | 0.98521 | -0.28331 | 0.98456 | -0.29601 | 11.2613
48 | -0.052863 | -0.013309 | 0.052924 | 0.013348 | 6.1132e-05 | 3.8794e-05 | 0.079586 | 0.079586 | 0.079586 | 0.98863 | -0.21686 | 0.98988 | -0.1927 | 21.8644
49 | -0.052924 | -0.013348 | 0.052973 | 0.013379 | 4.917e-05 | 3.1202e-05 | 0.079586 | 0.079586 | 0.079586 | 0.98988 | -0.1927 | 0.99088 | -0.17332 | 21.8644
50 | -0.18957 | -0.048293 | 0.18994 | 0.048526 | 0.00036615 | 0.00023294 | 0.28496 | 0.28496 | 0.28496 | 0.99088 | -0.17332 | 0.99297 | -0.13336 | 26.0953
51 | 0.025301 | 0.0063479 | -0.0253 | -0.0063474 | 8.0907e-07 | 4.9904e-07 | 0.03824 | 0.03824 | 0.03824 | 0.98456 | -0.29601 | 0.98453 | -0.29668 | 10.5056
52 | 0.33411 | 0.08553 | -0.33319 | -0.084944 | 0.0009164 | 0.00058533 | 0.49779 | 0.49779 | 0.49779 | 1 | 0 | 0.997 | -0.056806 | 45.5854
53 | 0.27985 | 0.071493 | -0.27977 | -0.071443 | 7.9538e-05 | 5.0762e-05 | 0.41816 | 0.41816 | 0.41816 | 0.997 | -0.056806 | 0.9967 | -0.062686 | 38.293
54 | 0.053336 | 0.013451 | -0.053302 | -0.01343 | 3.3725e-05 | 2.1399e-05 | 0.079633 | 0.079633 | 0.079633 | 0.997 | -0.056806 | 0.99632 | -0.070024 | 21.8772
55 | -0.18994 | -0.048526 | 0.19011 | 0.048638 | 0.0001761 | 0.00011203 | 0.28496 | 0.28496 | 0.28496 | 0.99297 | -0.13336 | 0.99398 | -0.11421 | 26.0953
56 | 0.024381 | 0.0061171 | -0.02438 | -0.0061164 | 1.1016e-06 | 6.7878e-07 | 0.037293 | 0.037293 | 0.037293 | 0.97288 | -0.52304 | 0.97283 | -0.52399 | 10.2454
57 | 0.02146 | 0.0053847 | -0.02145 | -0.0053785 | 1.0128e-05 | 6.1707e-06 | 0.032828 | 0.032828 | 0.032828 | 0.97283 | -0.52399 | 0.97233 | -0.53389 | 9.0186
58 | 0.023402 | 0.0058719 | -0.023396 | -0.0058682 | 5.9291e-06 | 3.634e-06 | 0.035373 | 0.035373 | 0.035373 | 0.98453 | -0.29668 | 0.98425 | -0.30199 | 9.7178
59 | 0.084362 | 0.02129 | -0.084226 | -0.021203 | 0.00013667 | 8.7172e-05 | 0.126 | 0.126 | 0.126 | 0.9967 | -0.062686 | 0.99493 | -0.096573 | 34.6155
60 | 0.19541 | 0.050153 | -0.19523 | -0.050034 | 0.00018612 | 0.00011843 | 0.29216 | 0.29216 | 0.29216 | 0.9967 | -0.062686 | 0.99566 | -0.082333 | 26.7546
61 | 0.051776 | 0.013047 | -0.051722 | -0.013013 | 5.4246e-05 | 3.4403e-05 | 0.077354 | 0.077354 | 0.077354 | 0.99632 | -0.070024 | 0.99518 | -0.09195 | 21.251
62 | -0.19314 | -0.049397 | 0.19335 | 0.049529 | 0.00020774 | 0.00013218 | 0.28949 | 0.28949 | 0.28949 | 0.99398 | -0.11421 | 0.99515 | -0.09201 | 26.5102
63 | -0.19335 | -0.049529 | 0.19344 | 0.049587 | 9.0708e-05 | 5.7716e-05 | 0.28949 | 0.28949 | 0.28949 | 0.99515 | -0.09201 | 0.99566 | -0.082333 | 26.5102
64 | 0.0013821 | 0.00034589 | -0.0013821 | -0.00034595 | 8.9512e-09 | -6.023e-08 | 0.0021168 | 0.0021168 | 0.0021168 | 0.97149 | -0.55054 | 0.97148 | -0.55068 | 0.58154
65 | 0.00068173 | 0.00017042 | -0.00068172 | -0.00017081 | 1.3112e-08 | -3.887e-07 | 0.001044 | 0.0010442 | 0.0010442 | 0.97148 | -0.55068 | 0.97146 | -0.55108 | 0.28687
66 | 0.00068172 | 0.00017081 | -0.00068172 | -0.00017085 | 1.6441e-09 | -4.8732e-08 | 0.0010442 | 0.0010442 | 0.0010442 | 0.97146 | -0.55108 | 0.97146 | -0.55113 | 0.28687
67 | 0.019226 | 0.004821 | -0.019225 | -0.0048203 | 1.1247e-06 | 6.7683e-07 | 0.029423 | 0.029423 | 0.029423 | 0.97233 | -0.53389 | 0.97226 | -0.53512 | 8.0833
68 | 0.015708 | 0.0039389 | -0.015703 | -0.0039364 | 4.3291e-06 | 2.523e-06 | 0.024041 | 0.024041 | 0.024041 | 0.97226 | -0.53512 | 0.97197 | -0.54091 | 6.6046
69 | 0.013902 | 0.0034849 | -0.013901 | -0.0034844 | 9.3181e-07 | 5.2838e-07 | 0.021283 | 0.021283 | 0.021283 | 0.97197 | -0.54091 | 0.9719 | -0.54231 | 5.847
70 | 0.011929 | 0.0029903 | -0.011927 | -0.0029888 | 2.704e-06 | 1.4628e-06 | 0.018265 | 0.018265 | 0.018265 | 0.9719 | -0.54231 | 0.97166 | -0.54707 | 5.0178
71 | 0.010379 | 0.002601 | -0.010379 | -0.0026008 | 3.3636e-07 | 1.713e-07 | 0.015895 | 0.015895 | 0.015895 | 0.97166 | -0.54707 | 0.97163 | -0.54775 | 4.3668
72 | -0.0081172 | -0.0020337 | 0.0081188 | 0.0020343 | 1.6127e-06 | 6.8768e-07 | 0.012434 | 0.012434 | 0.012434 | 0.97141 | -0.55192 | 0.97163 | -0.54775 | 3.4158
73 | 0.0059217 | 0.0014834 | -0.0059214 | -0.0014834 | 2.8376e-07 | 6.7755e-08 | 0.0090706 | 0.0090707 | 0.0090707 | 0.97141 | -0.55192 | 0.97136 | -0.55293 | 2.4919
74 | 0.0042117 | 0.0010548 | -0.0042112 | -0.0010549 | 4.8356e-07 | -7.397e-08 | 0.0064515 | 0.0064516 | 0.0064516 | 0.97136 | -0.55293 | 0.97124 | -0.55534 | 1.7724
75 | 0.0024631 | 0.00061682 | -0.002463 | -0.000617 | 1.0281e-07 | -1.7246e-07 | 0.0037735 | 0.0037736 | 0.0037736 | 0.97124 | -0.55534 | 0.9712 | -0.55622 | 1.0367
76 | 0.002463 | 0.000617 | -0.0024629 | -0.00061726 | 1.557e-07 | -2.6111e-07 | 0.0037736 | 0.0037738 | 0.0037738 | 0.9712 | -0.55622 | 0.97113 | -0.55754 | 1.0367
77 | -0.0024535 | -0.0006149 | 0.0024535 | 0.00061483 | 4.3297e-08 | -7.8389e-08 | 0.0037141 | 0.0037141 | 0.0037141 | 0.98296 | -0.32725 | 0.98298 | -0.32688 | 1.0204
78 | -0.0046713 | -0.0011707 | 0.0046718 | 0.0011706 | 4.4286e-07 | -1.5992e-08 | 0.0070713 | 0.0070712 | 0.0070713 | 0.98298 | -0.32688 | 0.98308 | -0.32489 | 1.9427
79 | 0.011601 | 0.0029081 | -0.011601 | -0.002908 | 2.1061e-07 | 1.1165e-07 | 0.017551 | 0.017551 | 0.017551 | 0.98355 | -0.3157 | 0.98353 | -0.31608 | 4.8217
80 | -0.013077 | -0.0032782 | 0.013077 | 0.0032783 | 1.5519e-07 | 8.5906e-08 | 0.019785 | 0.019785 | 0.019785 | 0.98355 | -0.3157 | 0.98357 | -0.31545 | 5.4354
81 | 0.01053 | 0.0026397 | -0.010528 | -0.0026384 | 2.426e-06 | 1.2292e-06 | 0.015931 | 0.015931 | 0.015931 | 0.98353 | -0.31608 | 0.98329 | -0.32092 | 4.3768
82 | -0.015522 | -0.003891 | 0.015526 | 0.0038933 | 3.9019e-06 | 2.2577e-06 | 0.023484 | 0.023484 | 0.023484 | 0.98357 | -0.31545 | 0.98383 | -0.31018 | 6.4516
83 | 0.0092233 | 0.0023116 | -0.009223 | -0.0023115 | 2.4699e-07 | 1.1519e-07 | 0.013958 | 0.013958 | 0.013958 | 0.98329 | -0.32092 | 0.98326 | -0.32148 | 3.8345
84 | -0.017732 | -0.004446 | 0.017734 | 0.0044476 | 2.7722e-06 | 1.6437e-06 | 0.026819 | 0.026819 | 0.026819 | 0.98383 | -0.31018 | 0.984 | -0.3069 | 7.3679
85 | 0.0078691 | 0.0019721 | -0.0078681 | -0.0019717 | 1.0473e-06 | 4.2053e-07 | 0.011909 | 0.011909 | 0.011909 | 0.98326 | -0.32148 | 0.98311 | -0.32427 | 3.2717
86 | -0.019669 | -0.0049324 | 0.019673 | 0.0049352 | 4.5968e-06 | 2.7659e-06 | 0.029744 | 0.029744 | 0.029744 | 0.984 | -0.3069 | 0.98425 | -0.30199 | 8.1715
87 | 0.0066697 | 0.0016714 | -0.0066695 | -0.0016713 | 1.9733e-07 | 6.0819e-08 | 0.010095 | 0.010095 | 0.010095 | 0.98311 | -0.32427 | 0.98308 | -0.32489 | 2.7733
88 | 0.0062117 | 0.0015568 | -0.0062109 | -0.0015566 | 7.4048e-07 | 1.8144e-07 | 0.0093265 | 0.0093266 | 0.0093266 | 0.99105 | -0.17169 | 0.99092 | -0.1742 | 2.5623
89 | -0.011262 | -0.0028225 | 0.011262 | 0.0028227 | 3.8039e-07 | 1.9773e-07 | 0.016909 | 0.016909 | 0.016909 | 0.99105 | -0.17169 | 0.99109 | -0.17098 | 4.6455
90 | 0.0043731 | 0.001096 | -0.0043731 | -0.001096 | 3.1651e-08 | -4.9564e-09 | 0.0065669 | 0.0065669 | 0.0065669 | 0.99092 | -0.1742 | 0.99091 | -0.17435 | 1.8041
91 | -0.01331 | -0.0033359 | 0.013313 | 0.0033376 | 3.0632e-06 | 1.6968e-06 | 0.019984 | 0.019984 | 0.019984 | 0.99109 | -0.17098 | 0.99134 | -0.16615 | 5.49
92 | 0.0014182 | 0.00035506 | -0.0014182 | -0.00035543 | 5.3893e-08 | -3.7439e-07 | 0.0021287 | 0.0021288 | 0.0021288 | 0.99134 | -0.16615 | 0.9913 | -0.16695 | 0.58484
93 | -0.017631 | -0.0044193 | 0.017637 | 0.0044231 | 6.4486e-06 | 3.8104e-06 | 0.026464 | 0.026464 | 0.026464 | 0.99134 | -0.16615 | 0.99173 | -0.15848 | 7.2703
94 | -0.020291 | -0.0050883 | 0.020295 | 0.0050902 | 3.0327e-06 | 1.8283e-06 | 0.030447 | 0.030447 | 0.030447 | 0.99173 | -0.15848 | 0.99189 | -0.15534 | 8.3645
95 | -0.022954 | -0.0057566 | 0.022956 | 0.0057578 | 1.8485e-06 | 1.1294e-06 | 0.034436 | 0.034436 | 0.034436 | 0.99189 | -0.15534 | 0.99198 | -0.15365 | 9.4604
96 | 0.082619 | 0.0208 | -0.082576 | -0.020772 | 4.3323e-05 | 2.7628e-05 | 0.1236 | 0.1236 | 0.1236 | 0.99493 | -0.096573 | 0.99436 | -0.10755 | 33.9556
97 | 0.050247 | 0.012643 | -0.050225 | -0.012629 | 2.1592e-05 | 1.3686e-05 | 0.075148 | 0.075148 | 0.075148 | 0.99518 | -0.09195 | 0.99471 | -0.10095 | 20.645
98 | 0.040017 | 0.010069 | -0.039997 | -0.010057 | 1.9723e-05 | 1.2433e-05 | 0.059897 | 0.059897 | 0.059897 | 0.99436 | -0.10755 | 0.99383 | -0.11787 | 16.4553
99 | 0.042559 | 0.010703 | -0.042483 | -0.010655 | 7.6031e-05 | 4.8013e-05 | 0.063701 | 0.063701 | 0.063701 | 0.99436 | -0.10755 | 0.99242 | -0.14502 | 17.5004
100 | 0.046999 | 0.011821 | -0.046972 | -0.011804 | 2.6836e-05 | 1.6987e-05 | 0.070322 | 0.070322 | 0.070322 | 0.99471 | -0.10095 | 0.99409 | -0.11291 | 19.3193
101 | 0.039869 | 0.010017 | -0.03985 | -0.010005 | 1.9228e-05 | 1.212e-05 | 0.059713 | 0.059713 | 0.059713 | 0.99366 | -0.12122 | 0.99314 | -0.13133 | 16.4048
102 | -0.04481 | -0.011255 | 0.044828 | 0.011266 | 1.7789e-05 | 1.1249e-05 | 0.067113 | 0.067113 | 0.067113 | 0.99366 | -0.12122 | 0.99409 | -0.11291 | 18.4376
103 | 0.037027 | 0.0092972 | -0.037011 | -0.0092867 | 1.6577e-05 | 1.0423e-05 | 0.055484 | 0.055484 | 0.055484 | 0.99314 | -0.13133 | 0.99265 | -0.14072 | 15.2429
104 | 0.029673 | 0.0074476 | -0.029667 | -0.0074441 | 5.7091e-06 | 3.5544e-06 | 0.044484 | 0.044484 | 0.044484 | 0.99265 | -0.14072 | 0.99244 | -0.14476 | 12.2209
105 | 0.027414 | 0.0068793 | -0.027402 | -0.0068721 | 1.1625e-05 | 7.2033e-06 | 0.041106 | 0.041106 | 0.041106 | 0.99244 | -0.14476 | 0.99198 | -0.15365 | 11.2928
106 | 0.0061249 | 0.001535 | -0.0061242 | -0.0015349 | 6.8873e-07 | 1.6008e-07 | 0.0091888 | 0.0091889 | 0.0091889 | 0.99186 | -0.1559 | 0.99174 | -0.15826 | 2.5244
107 | -0.010794 | -0.0027052 | 0.010796 | 0.0027061 | 1.7428e-06 | 8.8661e-07 | 0.016193 | 0.016193 | 0.016193 | 0.99186 | -0.1559 | 0.99204 | -0.15251 | 4.4487
108 | 0.01904 | 0.004775 | -0.019034 | -0.0047719 | 5.2678e-06 | 3.1491e-06 | 0.02856 | 0.02856 | 0.02856 | 0.99204 | -0.15251 | 0.99174 | -0.15831 | 7.8462
109 | -0.029835 | -0.0074811 | 0.029846 | 0.0074877 | 1.0647e-05 | 6.631e-06 | 0.044753 | 0.044753 | 0.044753 | 0.99204 | -0.15251 | 0.99242 | -0.14502 | 12.2948
110 | 0.015156 | 0.0037998 | -0.015152 | -0.0037977 | 3.792e-06 | 2.1746e-06 | 0.022741 | 0.022741 | 0.022741 | 0.99174 | -0.15831 | 0.99147 | -0.16357 | 6.2475
111 | 0.012637 | 0.0031676 | -0.012635 | -0.0031665 | 2.0792e-06 | 1.1312e-06 | 0.018948 | 0.018948 | 0.018948 | 0.99242 | -0.14502 | 0.99224 | -0.14848 | 5.2056
112 | 0.0042184 | 0.0010569 | -0.0042181 | -0.001057 | 3.2737e-07 | -7.1344e-08 | 0.0063309 | 0.006331 | 0.006331 | 0.99147 | -0.16357 | 0.99138 | -0.16519 | 1.7393
113 | 0.010934 | 0.0027408 | -0.010933 | -0.0027403 | 1.0061e-06 | 5.1542e-07 | 0.01641 | 0.01641 | 0.01641 | 0.99147 | -0.16357 | 0.99137 | -0.1655 | 4.5082
114 | 0.0093122 | 0.0023337 | -0.0093115 | -0.0023333 | 7.2523e-07 | 3.3607e-07 | 0.013965 | 0.013965 | 0.013965 | 0.99224 | -0.14848 | 0.99216 | -0.15011 | 3.8365
115 | 0.0042181 | 0.001057 | -0.0042177 | -0.0010571 | 3.6601e-07 | -7.97e-08 | 0.006331 | 0.0063312 | 0.0063312 | 0.99138 | -0.16519 | 0.99129 | -0.16702 | 1.7393
116 | 0.010933 | 0.0027403 | -0.010932 | -0.00274 | 4.52e-07 | 2.3157e-07 | 0.01641 | 0.01641 | 0.01641 | 0.99137 | -0.1655 | 0.99132 | -0.16636 | 4.5082
117 | 0.0077302 | 0.001937 | -0.0077294 | -0.0019367 | 8.7991e-07 | 3.3772e-07 | 0.011593 | 0.011594 | 0.011594 | 0.99216 | -0.15011 | 0.99204 | -0.1525 | 3.185
118 | 0.036648 | 0.0092174 | -0.036644 | -0.0092146 | 4.3753e-06 | 2.75e-06 | 0.054884 | 0.054884 | 0.054884 | 0.99383 | -0.11787 | 0.9937 | -0.12037 | 15.0779
119 | 0.0052302 | 0.0013103 | -0.00523 | -0.0013103 | 2.1316e-07 | 1.7176e-08 | 0.0078449 | 0.0078449 | 0.0078449 | 0.99204 | -0.1525 | 0.99199 | -0.15336 | 2.1552
120 | 0.0036616 | 0.00091724 | -0.0036614 | -0.00091735 | 2.0921e-07 | -1.0485e-07 | 0.0054923 | 0.0054924 | 0.0054924 | 0.99199 | -0.15336 | 0.99193 | -0.15456 | 1.5089
121 | 0.0026365 | 0.00066049 | -0.0026364 | -0.00066061 | 8.1263e-08 | -1.2682e-07 | 0.0039549 | 0.003955 | 0.003955 | 0.99193 | -0.15456 | 0.9919 | -0.1552 | 1.0865
122 | 0.0016596 | 0.00041581 | -0.0016596 | -0.00041594 | 2.5403e-08 | -1.248e-07 | 0.0024897 | 0.0024897 | 0.0024897 | 0.9919 | -0.1552 | 0.99188 | -0.15552 | 0.684
123 | 0.027298 | 0.0068535 | -0.027296 | -0.0068524 | 1.6561e-06 | 1.0259e-06 | 0.040949 | 0.040949 | 0.040949 | 0.99207 | -0.15187 | 0.992 | -0.15314 | 11.2496
124 | -0.028382 | -0.0071252 | 0.028385 | 0.0071272 | 3.2172e-06 | 1.9979e-06 | 0.042575 | 0.042575 | 0.042575 | 0.99207 | -0.15187 | 0.99219 | -0.1495 | 11.6964
125 | 0.026652 | 0.0066911 | -0.026642 | -0.0066844 | 1.0752e-05 | 6.6495e-06 | 0.039983 | 0.039983 | 0.039983 | 0.992 | -0.15314 | 0.99157 | -0.1616 | 10.9843
126 | -0.031629 | -0.0079402 | 0.031649 | 0.0079527 | 2.0004e-05 | 1.2496e-05 | 0.04744 | 0.04744 | 0.04744 | 0.99219 | -0.1495 | 0.99288 | -0.13624 | 13.0329
127 | 0.023808 | 0.0059744 | -0.023806 | -0.0059728 | 2.5732e-06 | 1.5776e-06 | 0.035731 | 0.035731 | 0.035731 | 0.99157 | -0.1616 | 0.99145 | -0.16387 | 9.8163
128 | -0.033694 | -0.0084651 | 0.033694 | 0.0084655 | 6.3908e-07 | 4.0037e-07 | 0.050504 | 0.050504 | 0.050504 | 0.99288 | -0.13624 | 0.9929 | -0.13585 | 13.8746
129 | 0.022967 | 0.0057626 | -0.022959 | -0.0057579 | 7.5752e-06 | 4.629e-06 | 0.034472 | 0.034472 | 0.034472 | 0.99145 | -0.16387 | 0.99109 | -0.17079 | 9.4705
130 | -0.035376 | -0.008887 | 0.035402 | 0.0089034 | 2.6154e-05 | 1.6418e-05 | 0.053024 | 0.053024 | 0.053024 | 0.9929 | -0.13585 | 0.9937 | -0.12037 | 14.5671
131 | 0.020759 | 0.0052065 | -0.020752 | -0.0052019 | 7.5653e-06 | 4.5743e-06 | 0.031169 | 0.031169 | 0.031169 | 0.99109 | -0.17079 | 0.9907 | -0.17844 | 8.5629
132 | 0.018639 | 0.0046724 | -0.018636 | -0.0046709 | 2.4792e-06 | 1.4781e-06 | 0.027996 | 0.027996 | 0.027996 | 0.9907 | -0.17844 | 0.99055 | -0.18123 | 7.6911
133 | -0.001373 | -0.0003441 | 0.001373 | 0.00034392 | 2.429e-08 | -1.8021e-07 | 0.0020632 | 0.0020631 | 0.0020632 | 0.99021 | -0.18798 | 0.99022 | -0.18761 | 0.56681
134 | -0.0029086 | -0.00072879 | 0.0029088 | 0.00072862 | 1.4431e-07 | -1.668e-07 | 0.0043708 | 0.0043707 | 0.0043708 | 0.99022 | -0.18761 | 0.99028 | -0.18657 | 1.2008
135 | -0.0041834 | -0.0010481 | 0.0041835 | 0.0010481 | 7.4968e-08 | -1.7114e-08 | 0.006286 | 0.0062859 | 0.006286 | 0.99028 | -0.18657 | 0.9903 | -0.18619 | 1.7269
136 | -0.0055834 | -0.0013989 | 0.0055838 | 0.001399 | 4.5749e-07 | 6.976e-08 | 0.0083894 | 0.0083893 | 0.0083894 | 0.9903 | -0.18619 | 0.99039 | -0.18447 | 2.3048
137 | -0.0066116 | -0.0016566 | 0.0066121 | 0.0016567 | 4.8177e-07 | 1.4077e-07 | 0.0099335 | 0.0099334 | 0.0099335 | 0.99039 | -0.18447 | 0.99046 | -0.18294 | 2.729
138 | 0.002342 | 0.00058664 | -0.002342 | -0.00058675 | 5.0472e-08 | -1.0742e-07 | 0.0035197 | 0.0035197 | 0.0035197 | 0.9901 | -0.18993 | 0.99008 | -0.19038 | 0.96696
139 | -0.0077704 | -0.0019471 | 0.0077716 | 0.0019476 | 1.2339e-06 | 4.7934e-07 | 0.011678 | 0.011678 | 0.011678 | 0.9901 | -0.18993 | 0.99028 | -0.1866 | 3.2082
140 | 0.0012089 | 0.00030278 | -0.0012089 | -0.00030298 | 2.0036e-08 | -1.9532e-07 | 0.0018168 | 0.0018169 | 0.0018169 | 0.99008 | -0.19038 | 0.99006 | -0.19073 | 0.49915
141 | -0.0088703 | -0.0022229 | 0.0088709 | 0.0022232 | 6.1661e-07 | 2.7554e-07 | 0.013329 | 0.013329 | 0.013329 | 0.99028 | -0.1866 | 0.99035 | -0.18514 | 3.6617
142 | -0.0099747 | -0.0024999 | 0.0099758 | 0.0025004 | 1.0447e-06 | 5.0901e-07 | 0.014987 | 0.014987 | 0.014987 | 0.99035 | -0.18514 | 0.99046 | -0.18294 | 4.1174
143 | -0.016588 | -0.0041571 | 0.016589 | 0.0041579 | 1.3516e-06 | 7.9032e-07 | 0.024921 | 0.024921 | 0.024921 | 0.99046 | -0.18294 | 0.99055 | -0.18123 | 6.8463
144 | 0.0086003 | 0.0021556 | -0.0085997 | -0.0021553 | 5.3456e-07 | 2.3185e-07 | 0.012909 | 0.012909 | 0.012909 | 0.99132 | -0.16636 | 0.99125 | -0.16767 | 3.5466
145 | 0.0063329 | 0.0015872 | -0.0063324 | -0.0015871 | 5.2234e-07 | 1.3564e-07 | 0.0095066 | 0.0095067 | 0.0095067 | 0.99125 | -0.16767 | 0.99116 | -0.1694 | 2.6117
146 | 0.0063324 | 0.0015871 | -0.0063313 | -0.0015868 | 1.0779e-06 | 2.8003e-07 | 0.0095067 | 0.0095068 | 0.0095068 | 0.99116 | -0.1694 | 0.99098 | -0.17297 | 2.6118
147 | 0.0063313 | 0.0015868 | -0.0063307 | -0.0015866 | 5.9738e-07 | 1.5526e-07 | 0.0095068 | 0.0095069 | 0.0095069 | 0.99098 | -0.17297 | 0.99088 | -0.17495 | 2.6118

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33906 | 0.086358

## res_load
| p_mw | q_mvar
0 | 0.00085331 | 0.00021386
1 | 0.0017518 | 0.00043904
2 | 0.0017259 | 0.00043254
3 | 0.0010785 | 0.0002703
4 | 0.0035026 | 0.00087784
5 | 0.0034375 | 0.00086151
6 | 0.0026897 | 0.00067411
7 | 0.0026397 | 0.00066157
8 | 0.0044866 | 0.0011245
9 | 0.0064133 | 0.0016073
10 | 0.0030594 | 0.00076676
11 | 0.0040551 | 0.0010163
12 | 0.0047356 | 0.0011868
13 | 0.0056886 | 0.0014257
14 | 0.0050269 | 0.0012599
15 | 0.004839 | 0.0012128
16 | 0.005366 | 0.0013448
17 | 0.0054503 | 0.001366
18 | 0.003157 | 0.00079122
19 | 0.0050878 | 0.0012751
20 | 0.003291 | 0.0008248
21 | 0.0045171 | 0.0011321
22 | 0.0055011 | 0.0013787
23 | 0.0037433 | 0.00093816
24 | 0.0011274 | 0.00028256
25 | 0.0060132 | 0.0015071
26 | 0.0031612 | 0.00079226
27 | 0.0049259 | 0.0012346
28 | 0.0020438 | 0.00051223
29 | 0.0017893 | 0.00044845
30 | 0.005663 | 0.0014193
31 | 0.0055983 | 0.0014031
32 | 0.0020025 | 0.00050188
33 | 0.0018201 | 0.00045616
34 | 0.0033047 | 0.00082825
35 | 0.0043601 | 0.0010928
36 | 0.0029194 | 0.00073168
37 | 0.004926 | 0.0012346
38 | 0.0018975 | 0.00047556
39 | 0.0015262 | 0.00038249
40 | 0.0030269 | 0.00075861
41 | 0.0017858 | 0.00044757
42 | 0.00096987 | 0.00024307
43 | 0.00070038 | 0.00017553
44 | 0.0022245 | 0.00055751
45 | 0.003517 | 0.00088145
46 | 0.0018013 | 0.00045144
47 | 0.0019716 | 0.00049414
48 | 0.0015474 | 0.00038781
49 | 0.0021955 | 0.00055024
50 | 0.0022602 | 0.00056647
51 | 0.0017098 | 0.00042851
52 | 0.001748 | 0.0004381
53 | 0.0024629 | 0.00061726
54 | 0.00068172 | 0.00017085
55 | 0.0024535 | 0.0006149
56 | 0.0022178 | 0.00055583
57 | 0.0014765 | 0.00037005
58 | 0.0010707 | 0.00026834
59 | 0.0024449 | 0.00061276
60 | 0.0013042 | 0.00032688
61 | 0.0022052 | 0.00055267
62 | 0.0013539 | 0.00033932
63 | 0.0019344 | 0.00048481
64 | 0.0011984 | 0.00030035
65 | 0.003723 | 0.00093306
66 | 0.0019977 | 0.00050067
67 | 0.0050504 | 0.0012657
68 | 0.0018378 | 0.0004606
69 | 0.0020475 | 0.00051316
70 | 0.0043731 | 0.001096
71 | 0.0028992 | 0.00072662
72 | 0.0014182 | 0.00035543
73 | 0.0026545 | 0.00066528
74 | 0.0026592 | 0.00066645
75 | 0.0016061 | 0.00040254
76 | 0.0014753 | 0.00036974
77 | 0.003226 | 0.00080851
78 | 0.0049413 | 0.0012384
79 | 0.0028227 | 0.00070743
80 | 0.002144 | 0.00053734
81 | 0.0073382 | 0.0018391
82 | 0.0022533 | 0.00056473
83 | 0.0044464 | 0.0011144
84 | 0.0046689 | 0.0011701
85 | 0.0061242 | 0.0015349
86 | 0.0038785 | 0.00097204
87 | 0.0033231 | 0.00083284
88 | 0.0015813 | 0.0003963
89 | 0.0033486 | 0.00083924
90 | 0.0024992 | 0.00062635
91 | 0.0015684 | 0.00039308
92 | 0.0010249 | 0.00025686
93 | 0.00097676 | 0.0002448
94 | 0.0016596 | 0.00041594
95 | 0.0010843 | 0.00027175
96 | 0.00064382 | 0.00016136
97 | 0.0032437 | 0.00081296
98 | 0.0028332 | 0.00071006
99 | 0.0020445 | 0.00051241
100 | 0.00083883 | 0.00021023
101 | 0.001682 | 0.00042154
102 | 0.0022004 | 0.00055147
103 | 0.0012417 | 0.00031119
104 | 0.0021128 | 0.00052951
105 | 0.001373 | 0.0003441
106 | 0.0015356 | 0.00038487
107 | 0.0012746 | 0.00031945
108 | 0.0013999 | 0.00035085
109 | 0.0010277 | 0.00025758
110 | 0.0054284 | 0.0013605
111 | 0.001133 | 0.00028397
112 | 0.0010987 | 0.00027535
113 | 0.0012089 | 0.00030298
114 | 0.0011039 | 0.00027665
115 | 0.0020471 | 0.00051304
116 | 0.0042177 | 0.0010571
117 | 0.0023321 | 0.00058447
118 | 0.0022668 | 0.00056812
119 | 0.0063307 | 0.0015866

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1