## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_193-16_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_193-16_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_193-16_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_193-16_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_193-16_0_3_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_193-16_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_193-16_0_3_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_193-16_0_3_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_193-16_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_193-16_0_3_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_193-16_0_3_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_193-16_0_3_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_193-16_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_193-16_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_193-16_0_3_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_193-16_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_193-16_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_193-16_0_3_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_193-16_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_193-16_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_193-16_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_193-16_0_3_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_193-16_0_3_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_193-16_0_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_193-16_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_193-16_0_3_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_193-16_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_193-16_0_3_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_193-16_0_3_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_193-16_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_193-16_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_193-16_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_193-16_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_193-16_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_193-16_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_193-16_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_193-16_0_3_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_193-16_0_3_node_56 | 0.4 | n |  | TRUE
38 | bus_LV_193-16_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_193-16_0_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_193-16_0_3_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_193-16_0_3_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_193-16_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_193-16_0_3_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_193-16_0_3_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_193-16_0_3_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_193-16_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_193-16_0_3_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_193-16_0_3_node_59 | 0.4 | n |  | TRUE
49 | bus_LV_193-16_0_3_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_193-16_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_193-16_0_3_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_193-16_0_3_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_193-16_0_3_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_193-16_0_3_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_193-16_0_3_node_53 | 0.4 | n |  | TRUE
56 | bus_MV_364_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_193-16_0_3_load_0 | 0 | 0.0076019 | 0.0019052 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_193-16_0_3_load_1 | 1 | 0.0073533 | 0.0018429 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_193-16_0_3_load_2 | 2 | 0.007075 | 0.0017732 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_193-16_0_3_load_3 | 3 | 0.0071829 | 0.0018002 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_193-16_0_3_load_43 | 6 | 0.010957 | 0.0027462 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_193-16_0_3_load_32 | 8 | 0.0059636 | 0.0014946 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_193-16_0_3_load_44 | 9 | 0.01048 | 0.0026266 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_193-16_0_3_load_40 | 11 | 0.0031268 | 0.00078365 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_193-16_0_3_load_5 | 12 | 0.015306 | 0.0038361 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_193-16_0_3_load_26 | 17 | 0.014424 | 0.0036149 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_193-16_0_3_load_41 | 21 | 0.0015516 | 0.00038886 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_193-16_0_3_load_34 | 22 | 0.0092956 | 0.0023297 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_193-16_0_3_load_36 | 23 | 0.012998 | 0.0032575 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_193-16_0_3_load_50 | 28 | 0.0087384 | 0.0021901 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_193-16_0_3_load_37 | 32 | 0.013759 | 0.0034483 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_193-16_0_3_load_27 | 34 | 0.015946 | 0.0039963 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_193-16_0_3_load_49 | 36 | 0.0059699 | 0.0014962 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_193-16_0_3_load_56 | 37 | 0.0077881 | 0.0019519 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_193-16_0_3_load_35 | 39 | 0.015521 | 0.00389 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_193-16_0_3_load_58 | 41 | 0.0086262 | 0.0021619 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_193-16_0_3_load_28 | 42 | 0.016813 | 0.0042137 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_193-16_0_3_load_33 | 44 | 0.0092918 | 0.0023287 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_193-16_0_3_load_48 | 47 | 0.0080677 | 0.002022 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_193-16_0_3_load_59 | 48 | 0.0097316 | 0.002439 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_193-16_0_3_load_51 | 49 | 0.0086833 | 0.0021762 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_193-16_0_3_load_47 | 50 | 0.0098739 | 0.0024746 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_193-16_0_3_load_38 | 51 | 0.010313 | 0.0025848 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_193-16_0_3_load_57 | 52 | 0.0096253 | 0.0024123 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_193-16_0_3_load_60 | 53 | 0.0087974 | 0.0022048 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_193-16_0_3_load_53 | 55 | 0.0085691 | 0.0021476 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_193-16_0_3_line_0 |  | 0 | 1 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_193-16_0_3_line_1 |  | 0 | 2 | 0.018481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_193-16_0_3_line_2 |  | 1 | 3 | 0.024745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_193-16_0_3_line_3 |  | 3 | 4 | 0.015079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_193-16_0_3_line_4 |  | 4 | 8 | 0.020773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_193-16_0_3_line_5 |  | 5 | 6 | 0.026195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_193-16_0_3_line_6 |  | 5 | 7 | 0.005197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_193-16_0_3_line_7 |  | 6 | 9 | 0.015679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_193-16_0_3_line_8 |  | 7 | 10 | 0.008768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_193-16_0_3_line_9 |  | 7 | 11 | 0.0093702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_193-16_0_3_line_10 |  | 8 | 44 | 0.015159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_193-16_0_3_line_11 |  | 9 | 24 | 0.01388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_193-16_0_3_line_12 |  | 10 | 50 | 0.015773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_193-16_0_3_line_13 |  | 10 | 31 | 0.021805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_193-16_0_3_line_14 |  | 11 | 21 | 0.016468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_193-16_0_3_line_15 |  | 12 | 13 | 0.013876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_193-16_0_3_line_16 |  | 13 | 14 | 0.021627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_193-16_0_3_line_17 |  | 14 | 38 | 0.019138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_193-16_0_3_line_18 |  | 14 | 39 | 0.014464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_193-16_0_3_line_19 |  | 15 | 16 | 0.05407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_193-16_0_3_line_20 |  | 15 | 17 | 0.0064986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_193-16_0_3_line_21 |  | 16 | 24 | 0.029127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_193-16_0_3_line_22 |  | 17 | 29 | 0.017537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_193-16_0_3_line_23 |  | 18 | 19 | 0.007392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_193-16_0_3_line_24 |  | 18 | 20 | 0.067931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_193-16_0_3_line_25 |  | 18 | 21 | 0.035435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_193-16_0_3_line_26 |  | 19 | 22 | 0.012171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_193-16_0_3_line_27 |  | 20 | 23 | 0.047739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_193-16_0_3_line_28 |  | 22 | 44 | 0.020614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_193-16_0_3_line_29 |  | 24 | 25 | 0.047721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_193-16_0_3_line_30 |  | 25 | 45 | 0.013492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_193-16_0_3_line_31 |  | 25 | 46 | 0.051049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_193-16_0_3_line_32 |  | 26 | 27 | 0.008529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_193-16_0_3_line_33 |  | 26 | 28 | 0.033354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_193-16_0_3_line_34 |  | 27 | 48 | 0.01473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_193-16_0_3_line_35 |  | 27 | 40 | 0.013586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_193-16_0_3_line_36 |  | 28 | 49 | 0.02407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_193-16_0_3_line_37 |  | 29 | 30 | 0.030255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_193-16_0_3_line_38 |  | 30 | 33 | 0.022465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_193-16_0_3_line_39 |  | 30 | 34 | 0.042679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_193-16_0_3_line_40 |  | 31 | 32 | 0.050694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_193-16_0_3_line_41 |  | 32 | 51 | 0.00077629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_193-16_0_3_line_42 |  | 33 | 39 | 0.0092967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_193-16_0_3_line_43 |  | 35 | 36 | 0.028386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_193-16_0_3_line_44 |  | 35 | 37 | 0.039776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_193-16_0_3_line_45 |  | 36 | 47 | 0.018726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_193-16_0_3_line_46 |  | 37 | 52 | 0.020706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_193-16_0_3_line_47 |  | 38 | 49 | 0.022888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_193-16_0_3_line_48 |  | 38 | 43 | 0.042794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_193-16_0_3_line_49 |  | 40 | 41 | 0.003314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_193-16_0_3_line_50 |  | 42 | 43 | 0.0032169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_193-16_0_3_line_51 |  | 45 | 53 | 0.013074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_193-16_0_3_line_52 |  | 45 | 54 | 0.013848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_193-16_0_3_line_53 |  | 46 | 47 | 0.00098771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_193-16_0_3_line_54 |  | 54 | 55 | 0.0098174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_193-16_0_3_trafo_21 | 0.63 MVA 20/0.4 kV | 56 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2690654.5545 | 1246148.9845 | 2690647.9054 | 1246157.4004 | 2690641.4652 | 1246157.591 | 2690641.0525 | 1246158.0833
1 | 2690654.5545 | 1246148.9845 | 2690654.5545 | 1246148.9845 | 2690669.7619 | 1246159.4867
2 | 2690641.0525 | 1246158.0833 | 2690630.9372 | 1246170.1506 | 2690623.6355 | 1246170.8507 | 2690622.4588 | 1246172.0274
3 | 2690611.7964 | 1246182.6898 | 2690622.4588 | 1246172.0274
4 | 2690611.7964 | 1246182.6898 | 2690614.6932 | 1246198.8018 | 2690618.1912 | 1246201.4756
5 | 2690701.537 | 1246179.9371 | 2690715.01 | 1246164.5316 | 2690716.5834 | 1246159.0227
6 | 2690701.537 | 1246179.9371 | 2690698.2193 | 1246183.945
7 | 2690716.5834 | 1246159.0227 | 2690717.4289 | 1246156.0622 | 2690725.8128 | 1246146.6564
8 | 2690705.3949 | 1246189.0141 | 2690698.2193 | 1246183.945
9 | 2690698.2193 | 1246183.945 | 2690691.8322 | 1246190.801
10 | 2690630.2344 | 1246210.6814 | 2690618.1912 | 1246201.4756
11 | 2690735.0487 | 1246136.2947 | 2690725.8128 | 1246146.6564
12 | 2690705.3949 | 1246189.0141 | 2690715.0142 | 1246176.5135
13 | 2690705.3949 | 1246189.0141 | 2690691.3207 | 1246205.7003
14 | 2690691.8322 | 1246190.801 | 2690680.6071 | 1246202.8504
15 | 2690855.6069 | 1246153.8977 | 2690862.1458 | 1246159.1018 | 2690866.4844 | 1246162.5129
16 | 2690839.9218 | 1246139.5912 | 2690845.5528 | 1246142.4129 | 2690853.8455 | 1246151.0019 | 2690855.6069 | 1246153.8977
17 | 2690845.6172 | 1246122.4322 | 2690846.4202 | 1246129.6944 | 2690839.9218 | 1246139.5912
18 | 2690839.9218 | 1246139.5912 | 2690830.4543 | 1246150.5268
19 | 2690734.3261 | 1246151.4172 | 2690753.4526 | 1246165.4981 | 2690759.9848 | 1246158.8042 | 2690775.9992 | 1246172.3372
20 | 2690775.9992 | 1246172.3372 | 2690780.275 | 1246167.4434
21 | 2690734.3261 | 1246151.4172 | 2690744.2892 | 1246140.239 | 2690736.1549 | 1246133.1314 | 2690735.0487 | 1246136.2947
22 | 2690793.1657 | 1246179.2162 | 2690791.8138 | 1246177.2051 | 2690780.275 | 1246167.4434
23 | 2690654.8823 | 1246229.3165 | 2690661.5262 | 1246232.5983
24 | 2690638.3446 | 1246290.5098 | 2690638.8293 | 1246289.939 | 2690634.5784 | 1246280.8672 | 2690655.7738 | 1246253.0258 | 2690654.872 | 1246244.8058 | 2690661.5262 | 1246232.5983
25 | 2690661.5262 | 1246232.5983 | 2690664.4025 | 1246227.3161 | 2690677.4251 | 1246206.266 | 2690680.6071 | 1246202.8504
26 | 2690654.8823 | 1246229.3165 | 2690645.2264 | 1246221.9079
27 | 2690638.3446 | 1246290.5098 | 2690649.0236 | 1246302.1484 | 2690657.1147 | 1246303.1728 | 2690671.026 | 1246314.405 | 2690676.8935 | 1246315.0952
28 | 2690630.2344 | 1246210.6814 | 2690633.3561 | 1246213.0643 | 2690636.545 | 1246215.5037 | 2690638.061 | 1246216.6611 | 2690638.2466 | 1246219.8441 | 2690639.0084 | 1246220.4228 | 2690639.7853 | 1246221.0018 | 2690640.562 | 1246221.5919 | 2690645.2264 | 1246221.9079
29 | 2690740.6646 | 1246099.1416 | 2690733.6382 | 1246113.4337 | 2690740.5712 | 1246119.5555 | 2690730.2879 | 1246131.9074 | 2690735.0487 | 1246136.2947
30 | 2690740.6646 | 1246099.1416 | 2690748.5467 | 1246088.1761
31 | 2690704.9255 | 1246118.4761 | 2690713.2091 | 1246125.7082 | 2690731.3569 | 1246116.3677 | 2690733.6382 | 1246113.4337 | 2690740.6646 | 1246099.1416
32 | 2690789.0396 | 1246068.2808 | 2690789.0721 | 1246059.7527
33 | 2690789.0396 | 1246068.2808 | 2690793.6844 | 1246076.7916 | 2690808.3813 | 1246095.3308
34 | 2690789.0721 | 1246059.7527 | 2690803.8251 | 1246058.9668
35 | 2690784.9561 | 1246046.8022 | 2690789.0721 | 1246059.7527
36 | 2690808.3813 | 1246095.3308 | 2690809.9694 | 1246097.3341 | 2690826.491 | 1246111.1133
37 | 2690793.1657 | 1246179.2162 | 2690803.252 | 1246176.7688 | 2690814.1083 | 1246169.4294 | 2690817.9212 | 1246175.0254
38 | 2690817.9212 | 1246175.0254 | 2690814.1083 | 1246169.4294 | 2690824.3693 | 1246157.5554
39 | 2690817.9212 | 1246175.0254 | 2690822.5065 | 1246179.5212 | 2690816.1895 | 1246187.4526 | 2690826.0078 | 1246195.5868 | 2690829.4526 | 1246195.6174 | 2690832.3777 | 1246198.0084 | 2690837.0788 | 1246201.85 | 2690837.1358 | 1246201.8966
40 | 2690691.3207 | 1246205.7003 | 2690709.4163 | 1246221.967 | 2690700.1988 | 1246233.8127 | 2690703.7728 | 1246244.5874
41 | 2690704.0172 | 1246245.3243 | 2690703.7728 | 1246244.5874
42 | 2690824.3693 | 1246157.5554 | 2690830.4543 | 1246150.5268
43 | 2690672.6845 | 1246084.9914 | 2690680.0243 | 1246101.0712 | 2690689.3727 | 1246106.3626
44 | 2690672.6845 | 1246084.9914 | 2690692.1806 | 1246082.343 | 2690701.8914 | 1246083.7036 | 2690708.5754 | 1246075.8729
45 | 2690689.3727 | 1246106.3626 | 2690704.1463 | 1246117.8692
46 | 2690708.5754 | 1246075.8729 | 2690722.0184 | 1246060.1238
47 | 2690845.6172 | 1246122.4322 | 2690838.5868 | 1246121.2014 | 2690826.491 | 1246111.1133
48 | 2690881.1526 | 1246109.022 | 2690871.576 | 1246107.7855 | 2690859.4359 | 1246106.6876 | 2690845.6172 | 1246122.4322
49 | 2690784.9561 | 1246046.8022 | 2690787.5493 | 1246044.7292
50 | 2690881.1526 | 1246109.022 | 2690883.6876 | 1246111.0024
51 | 2690748.5467 | 1246088.1761 | 2690753.4981 | 1246086.0392 | 2690757.9688 | 1246079.7695
52 | 2690748.5467 | 1246088.1761 | 2690745.8079 | 1246074.6018
53 | 2690704.1463 | 1246117.8692 | 2690704.9255 | 1246118.4761
54 | 2690745.8079 | 1246074.6018 | 2690745.6328 | 1246071.2299 | 2690740.5916 | 1246067.2209

## bus_geodata
| x | y | coords
0 | 2690654.5545 | 1246148.9845
1 | 2690641.0525 | 1246158.0833
2 | 2690669.7619 | 1246159.4867
3 | 2690622.4588 | 1246172.0274
4 | 2690611.7964 | 1246182.6898
5 | 2690701.537 | 1246179.9371
6 | 2690716.5834 | 1246159.0227
7 | 2690698.2193 | 1246183.945
8 | 2690618.1912 | 1246201.4756
9 | 2690725.8128 | 1246146.6564
10 | 2690705.3949 | 1246189.0141
11 | 2690691.8322 | 1246190.801
12 | 2690866.4844 | 1246162.5129
13 | 2690855.6069 | 1246153.8977
14 | 2690839.9218 | 1246139.5912
15 | 2690775.9992 | 1246172.3372
16 | 2690734.3261 | 1246151.4172
17 | 2690780.275 | 1246167.4434
18 | 2690661.5262 | 1246232.5983
19 | 2690654.8823 | 1246229.3165
20 | 2690638.3446 | 1246290.5098
21 | 2690680.6071 | 1246202.8504
22 | 2690645.2264 | 1246221.9079
23 | 2690676.8935 | 1246315.0952
24 | 2690735.0487 | 1246136.2947
25 | 2690740.6646 | 1246099.1416
26 | 2690789.0396 | 1246068.2808
27 | 2690789.0721 | 1246059.7527
28 | 2690808.3813 | 1246095.3308
29 | 2690793.1657 | 1246179.2162
30 | 2690817.9212 | 1246175.0254
31 | 2690691.3207 | 1246205.7003
32 | 2690703.7728 | 1246244.5874
33 | 2690824.3693 | 1246157.5554
34 | 2690837.1358 | 1246201.8966
35 | 2690672.6845 | 1246084.9914
36 | 2690689.3727 | 1246106.3626
37 | 2690708.5754 | 1246075.8729
38 | 2690845.6172 | 1246122.4322
39 | 2690830.4543 | 1246150.5268
40 | 2690784.9561 | 1246046.8022
41 | 2690787.5493 | 1246044.7292
42 | 2690883.6876 | 1246111.0024
43 | 2690881.1526 | 1246109.022
44 | 2690630.2344 | 1246210.6814
45 | 2690748.5467 | 1246088.1761
46 | 2690704.9255 | 1246118.4761
47 | 2690704.1463 | 1246117.8692
48 | 2690803.8251 | 1246058.9668
49 | 2690826.491 | 1246111.1133
50 | 2690715.0142 | 1246176.5135
51 | 2690704.0172 | 1246245.3242
52 | 2690722.0184 | 1246060.1238
53 | 2690757.9688 | 1246079.7695
54 | 2690745.8079 | 1246074.6018
55 | 2690740.5916 | 1246067.2209
56 | 2690744.2892 | 1246140.239

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98348 | -0.31844 | 0.0076019 | 0.0019052
1 | 0.98372 | -0.31373 | 0.0073533 | 0.0018429
2 | 0.98336 | -0.3208 | 0.007075 | 0.0017732
3 | 0.98422 | -0.30392 | 0.0071829 | 0.0018002
4 | 0.98463 | -0.29599 | 0 | 0
5 | 0.99182 | -0.15647 | 0 | 0
6 | 0.99436 | -0.10768 | 0.010957 | 0.0027462
7 | 0.99132 | -0.16618 | 0 | 0
8 | 0.98519 | -0.28509 | 0.0059636 | 0.0014946
9 | 0.99604 | -0.075575 | 0.01048 | 0.0026266
10 | 0.99105 | -0.17147 | 0 | 0
11 | 0.9907 | -0.17807 | 0.0031268 | 0.00078365
12 | 0.98544 | -0.27977 | 0.015306 | 0.0038361
13 | 0.98564 | -0.27596 | 0 | 0
14 | 0.98594 | -0.27002 | 0 | 0
15 | 0.99434 | -0.10786 | 0 | 0
16 | 1 | 0 | -0.29419 | -0.074514
17 | 0.99366 | -0.12091 | 0.014424 | 0.0036149
18 | 0.98749 | -0.24027 | 0 | 0
19 | 0.98712 | -0.24737 | 0 | 0
20 | 0.98668 | -0.25606 | 0 | 0
21 | 0.98967 | -0.19807 | 0.0015516 | 0.00038886
22 | 0.98652 | -0.25908 | 0.0092956 | 0.0023297
23 | 0.98611 | -0.26718 | 0.012998 | 0.0032575
24 | 0.99765 | -0.044695 | 0 | 0
25 | 0.99553 | -0.085584 | 0 | 0
26 | 0.98309 | -0.32559 | 0 | 0
27 | 0.98295 | -0.32841 | 0 | 0
28 | 0.98366 | -0.31455 | 0.0087384 | 0.0021901
29 | 0.99205 | -0.15172 | 0 | 0
30 | 0.98929 | -0.20512 | 0 | 0
31 | 0.99057 | -0.18079 | 0 | 0
32 | 0.98945 | -0.20249 | 0.013759 | 0.0034483
33 | 0.98756 | -0.23855 | 0 | 0
34 | 0.98866 | -0.21724 | 0.015946 | 0.0039963
35 | 0.99318 | -0.13087 | 0 | 0
36 | 0.99363 | -0.12214 | 0.0059699 | 0.0014962
37 | 0.99255 | -0.14312 | 0.0077881 | 0.0019519
38 | 0.98501 | -0.28808 | 0 | 0
39 | 0.98684 | -0.25242 | 0.015521 | 0.00389
40 | 0.98284 | -0.33053 | 0 | 0
41 | 0.98281 | -0.33104 | 0.0086262 | 0.0021619
42 | 0.9843 | -0.30199 | 0.016813 | 0.0042137
43 | 0.98435 | -0.30102 | 0 | 0
44 | 0.98568 | -0.27552 | 0.0092918 | 0.0023287
45 | 0.99532 | -0.089705 | 0 | 0
46 | 0.99406 | -0.11386 | 0 | 0
47 | 0.99403 | -0.11441 | 0.0080677 | 0.002022
48 | 0.98281 | -0.331 | 0.0097316 | 0.002439
49 | 0.98426 | -0.30281 | 0.0086833 | 0.0021762
50 | 0.99091 | -0.17423 | 0.0098739 | 0.0024746
51 | 0.98944 | -0.20263 | 0.010313 | 0.0025848
52 | 0.99237 | -0.14665 | 0.0096253 | 0.0024123
53 | 0.99521 | -0.091729 | 0.0087974 | 0.0022048
54 | 0.99521 | -0.091794 | 0 | 0
55 | 0.99513 | -0.093274 | 0.0085691 | 0.0021476
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014678 | -0.0036786 | 0.014681 | 0.0036805 | 3.294e-06 | 1.8821e-06 | 0.022208 | 0.022207 | 0.022208 | 0.98348 | -0.31844 | 0.98372 | -0.31373 | 6.101
1 | 0.0070758 | 0.0017734 | -0.007075 | -0.0017732 | 7.9433e-07 | 2.7389e-07 | 0.010706 | 0.010706 | 0.010706 | 0.98348 | -0.31844 | 0.98336 | -0.3208 | 2.9412
2 | -0.022034 | -0.0055234 | 0.022045 | 0.0055297 | 1.0309e-05 | 6.2833e-06 | 0.03333 | 0.03333 | 0.03333 | 0.98372 | -0.31373 | 0.98422 | -0.30392 | 9.1567
3 | -0.029228 | -0.0073299 | 0.029239 | 0.0073368 | 1.1042e-05 | 6.8752e-06 | 0.04419 | 0.04419 | 0.04419 | 0.98422 | -0.30392 | 0.98463 | -0.29599 | 12.1401
4 | -0.029239 | -0.0073368 | 0.029254 | 0.0073463 | 1.5212e-05 | 9.4712e-06 | 0.04419 | 0.04419 | 0.04419 | 0.98463 | -0.29599 | 0.98519 | -0.28509 | 12.1401
5 | -0.10588 | -0.026723 | 0.10613 | 0.026881 | 0.00024808 | 0.00015843 | 0.15892 | 0.15892 | 0.15892 | 0.99182 | -0.15647 | 0.99436 | -0.10768 | 43.6582
6 | 0.10588 | 0.026723 | -0.10583 | -0.026691 | 4.9217e-05 | 3.1432e-05 | 0.15892 | 0.15892 | 0.15892 | 0.99182 | -0.15647 | 0.99132 | -0.16618 | 43.6582
7 | -0.11709 | -0.029627 | 0.11727 | 0.029743 | 0.00018071 | 0.00011545 | 0.17531 | 0.17531 | 0.17531 | 0.99436 | -0.10768 | 0.99604 | -0.075575 | 48.1629
8 | 0.033992 | 0.0085356 | -0.033983 | -0.0085303 | 8.5618e-06 | 5.3666e-06 | 0.051029 | 0.051029 | 0.051029 | 0.99132 | -0.16618 | 0.99105 | -0.17147 | 14.019
9 | 0.071839 | 0.018156 | -0.071798 | -0.018129 | 4.0899e-05 | 2.6055e-05 | 0.10789 | 0.10789 | 0.10789 | 0.99132 | -0.16618 | 0.9907 | -0.17807 | 29.6392
10 | -0.035217 | -0.0088409 | 0.035233 | 0.008851 | 1.6087e-05 | 1.0102e-05 | 0.053197 | 0.053197 | 0.053197 | 0.98519 | -0.28509 | 0.98568 | -0.27552 | 14.6146
11 | -0.12775 | -0.032369 | 0.12794 | 0.032491 | 0.00018983 | 0.00012131 | 0.19097 | 0.19097 | 0.19097 | 0.99604 | -0.075575 | 0.99765 | -0.044695 | 52.4642
12 | 0.0098752 | 0.0024753 | -0.0098739 | -0.0024746 | 1.3004e-06 | 6.2904e-07 | 0.014827 | 0.014827 | 0.014827 | 0.99105 | -0.17147 | 0.99091 | -0.17423 | 4.0734
13 | 0.024108 | 0.006055 | -0.024097 | -0.0060484 | 1.0716e-05 | 6.5777e-06 | 0.036202 | 0.036202 | 0.036202 | 0.99105 | -0.17147 | 0.99057 | -0.18079 | 9.9456
14 | 0.068671 | 0.017346 | -0.068605 | -0.017304 | 6.5758e-05 | 4.1873e-05 | 0.10319 | 0.10319 | 0.10319 | 0.9907 | -0.17807 | 0.98967 | -0.19807 | 28.3491
15 | -0.015306 | -0.0038361 | 0.015309 | 0.0038377 | 2.7796e-06 | 1.6021e-06 | 0.023112 | 0.023112 | 0.023112 | 0.98544 | -0.27977 | 0.98564 | -0.27596 | 6.3496
16 | -0.015309 | -0.0038377 | 0.015313 | 0.0038402 | 4.3323e-06 | 2.4969e-06 | 0.023112 | 0.023112 | 0.023112 | 0.98564 | -0.27596 | 0.98594 | -0.27002 | 6.3496
17 | 0.052704 | 0.01325 | -0.052658 | -0.013221 | 4.5424e-05 | 2.8828e-05 | 0.079557 | 0.079557 | 0.079557 | 0.98594 | -0.27002 | 0.98501 | -0.28808 | 21.8564
18 | -0.068017 | -0.01709 | 0.068074 | 0.017126 | 5.7176e-05 | 3.6408e-05 | 0.10267 | 0.10267 | 0.10267 | 0.98594 | -0.27002 | 0.98684 | -0.25242 | 28.2059
19 | -0.11464 | -0.029057 | 0.11524 | 0.029439 | 0.00059757 | 0.00038174 | 0.17167 | 0.17167 | 0.17167 | 0.99434 | -0.10786 | 1 | 0 | 47.1625
20 | 0.11464 | 0.029057 | -0.11457 | -0.029011 | 7.182e-05 | 4.5881e-05 | 0.17167 | 0.17167 | 0.17167 | 0.99434 | -0.10786 | 0.99366 | -0.12091 | 47.1625
21 | 0.17731 | 0.045075 | -0.17693 | -0.044832 | 0.00038081 | 0.00024295 | 0.26406 | 0.26406 | 0.26406 | 1 | 0 | 0.99765 | -0.044695 | 36.2721
22 | 0.10014 | 0.025397 | -0.099995 | -0.025302 | 0.00014811 | 9.4565e-05 | 0.15007 | 0.15007 | 0.15007 | 0.99366 | -0.12091 | 0.99205 | -0.15172 | 41.2286
23 | 0.053904 | 0.013562 | -0.053886 | -0.013551 | 1.8297e-05 | 1.1616e-05 | 0.081245 | 0.081245 | 0.081245 | 0.98749 | -0.24027 | 0.98712 | -0.24737 | 22.3201
24 | 0.013014 | 0.0032667 | -0.013005 | -0.0032613 | 9.7991e-06 | 5.4031e-06 | 0.019613 | 0.019613 | 0.019613 | 0.98749 | -0.24027 | 0.98668 | -0.25606 | 5.3882
25 | -0.066919 | -0.016829 | 0.067054 | 0.016915 | 0.00013517 | 8.6056e-05 | 0.10086 | 0.10086 | 0.10086 | 0.98749 | -0.24027 | 0.98967 | -0.19807 | 27.7082
26 | 0.053886 | 0.013551 | -0.053856 | -0.013532 | 3.0126e-05 | 1.9125e-05 | 0.081245 | 0.081245 | 0.081245 | 0.98712 | -0.24737 | 0.98652 | -0.25908 | 22.3201
27 | 0.013005 | 0.0032613 | -0.012998 | -0.0032575 | 6.8865e-06 | 3.798e-06 | 0.019613 | 0.019613 | 0.019613 | 0.98668 | -0.25606 | 0.98611 | -0.26718 | 5.3883
28 | 0.04456 | 0.011202 | -0.044525 | -0.01118 | 3.4934e-05 | 2.2095e-05 | 0.067224 | 0.067224 | 0.067224 | 0.98652 | -0.25908 | 0.98568 | -0.27552 | 18.4682
29 | 0.04899 | 0.012342 | -0.048894 | -0.012281 | 9.5604e-05 | 6.0565e-05 | 0.073092 | 0.073092 | 0.073092 | 0.99765 | -0.044695 | 0.99553 | -0.085584 | 20.0801
30 | 0.017372 | 0.0043555 | -0.017369 | -0.0043534 | 3.4115e-06 | 2.008e-06 | 0.025967 | 0.025967 | 0.025967 | 0.99553 | -0.085584 | 0.99532 | -0.089705 | 7.1337
31 | 0.031522 | 0.0079257 | -0.03148 | -0.0078992 | 4.2513e-05 | 2.6546e-05 | 0.047125 | 0.047125 | 0.047125 | 0.99553 | -0.085584 | 0.99406 | -0.11386 | 12.9465
32 | 0.018363 | 0.0046034 | -0.01836 | -0.0046019 | 2.4708e-06 | 1.4732e-06 | 0.027794 | 0.027794 | 0.027794 | 0.98309 | -0.32559 | 0.98295 | -0.32841 | 7.6358
33 | -0.018363 | -0.0046034 | 0.018372 | 0.0046092 | 9.6623e-06 | 5.7607e-06 | 0.027794 | 0.027794 | 0.027794 | 0.98309 | -0.32559 | 0.98366 | -0.31455 | 7.6358
34 | 0.0097328 | 0.0024395 | -0.0097316 | -0.002439 | 1.1991e-06 | 5.8077e-07 | 0.014734 | 0.014734 | 0.014734 | 0.98295 | -0.32841 | 0.98281 | -0.331 | 4.0478
35 | 0.0086273 | 0.0021624 | -0.0086264 | -0.002162 | 8.6903e-07 | 3.8398e-07 | 0.01306 | 0.01306 | 0.01306 | 0.98295 | -0.32841 | 0.98284 | -0.33053 | 3.588
36 | -0.027111 | -0.0067992 | 0.027126 | 0.0068086 | 1.5183e-05 | 9.4112e-06 | 0.041013 | 0.041013 | 0.041013 | 0.98366 | -0.31455 | 0.98426 | -0.30281 | 11.2673
37 | 0.099995 | 0.025302 | -0.09974 | -0.025139 | 0.00025552 | 0.00016314 | 0.15007 | 0.15007 | 0.15007 | 0.99205 | -0.15172 | 0.98929 | -0.20512 | 41.2286
38 | 0.083785 | 0.021137 | -0.083651 | -0.021052 | 0.0001339 | 8.5407e-05 | 0.12607 | 0.12607 | 0.12607 | 0.98929 | -0.20512 | 0.98756 | -0.23855 | 34.6354
39 | 0.015955 | 0.0040017 | -0.015946 | -0.0039963 | 9.2181e-06 | 5.352e-06 | 0.023999 | 0.023999 | 0.023999 | 0.98929 | -0.20512 | 0.98866 | -0.21724 | 6.5932
40 | 0.024097 | 0.0060484 | -0.024072 | -0.0060331 | 2.4914e-05 | 1.5293e-05 | 0.036202 | 0.036202 | 0.036202 | 0.99057 | -0.18079 | 0.98945 | -0.20249 | 9.9456
41 | 0.010313 | 0.0025848 | -0.010313 | -0.0025848 | 7.0032e-08 | 3.485e-08 | 0.01551 | 0.01551 | 0.01551 | 0.98945 | -0.20249 | 0.98944 | -0.20263 | 4.2611
42 | 0.083651 | 0.021052 | -0.083596 | -0.021016 | 5.5412e-05 | 3.5345e-05 | 0.12607 | 0.12607 | 0.12607 | 0.98756 | -0.23855 | 0.98684 | -0.25242 | 34.6355
43 | -0.017425 | -0.004371 | 0.017432 | 0.0043752 | 7.2558e-06 | 4.2762e-06 | 0.026108 | 0.026108 | 0.026108 | 0.99318 | -0.13087 | 0.99363 | -0.12214 | 7.1726
44 | 0.017425 | 0.004371 | -0.017415 | -0.004365 | 1.0167e-05 | 5.9928e-06 | 0.026108 | 0.026108 | 0.026108 | 0.99318 | -0.13087 | 0.99255 | -0.14312 | 7.1726
45 | -0.023402 | -0.0058714 | 0.023411 | 0.0058767 | 8.626e-06 | 5.278e-06 | 0.035048 | 0.035048 | 0.035048 | 0.99363 | -0.12214 | 0.99403 | -0.11441 | 9.6287
46 | 0.0096269 | 0.0024131 | -0.0096253 | -0.0024123 | 1.6174e-06 | 7.6759e-07 | 0.014433 | 0.014433 | 0.014433 | 0.99255 | -0.14312 | 0.99237 | -0.14665 | 3.965
47 | 0.035834 | 0.0090007 | -0.035809 | -0.0089849 | 2.5158e-05 | 1.581e-05 | 0.05414 | 0.05414 | 0.05414 | 0.98501 | -0.28808 | 0.98426 | -0.30281 | 14.8737
48 | 0.016824 | 0.0042203 | -0.016814 | -0.0042142 | 1.0367e-05 | 6.0907e-06 | 0.025417 | 0.025417 | 0.025417 | 0.98501 | -0.28808 | 0.98435 | -0.30102 | 6.9827
49 | 0.0086264 | 0.002162 | -0.0086262 | -0.0021619 | 2.1198e-07 | 9.3671e-08 | 0.01306 | 0.01306 | 0.01306 | 0.98284 | -0.33053 | 0.98281 | -0.33104 | 3.588
50 | -0.016813 | -0.0042137 | 0.016814 | 0.0042142 | 7.7933e-07 | 4.5788e-07 | 0.025417 | 0.025417 | 0.025417 | 0.9843 | -0.30199 | 0.98435 | -0.30102 | 6.9827
51 | 0.0087982 | 0.0022052 | -0.0087974 | -0.0022048 | 8.4826e-07 | 3.7298e-07 | 0.013154 | 0.013154 | 0.013154 | 0.99532 | -0.089705 | 0.99521 | -0.091729 | 3.6136
52 | 0.0085706 | 0.0021482 | -0.0085697 | -0.0021479 | 8.5259e-07 | 3.657e-07 | 0.012813 | 0.012813 | 0.012813 | 0.99532 | -0.089705 | 0.99521 | -0.091794 | 3.5201
53 | 0.03148 | 0.0078992 | -0.031479 | -0.0078987 | 8.2256e-07 | 5.1364e-07 | 0.047125 | 0.047125 | 0.047125 | 0.99406 | -0.11386 | 0.99403 | -0.11441 | 12.9465
54 | 0.0085697 | 0.0021479 | -0.0085691 | -0.0021476 | 6.0444e-07 | 2.5929e-07 | 0.012813 | 0.012813 | 0.012813 | 0.99521 | -0.091794 | 0.99513 | -0.093274 | 3.5202

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29419 | 0.074514

## res_load
| p_mw | q_mvar
0 | 0.0076019 | 0.0019052
1 | 0.0073533 | 0.0018429
2 | 0.007075 | 0.0017732
3 | 0.0071829 | 0.0018002
4 | 0.010957 | 0.0027462
5 | 0.0059636 | 0.0014946
6 | 0.01048 | 0.0026266
7 | 0.0031268 | 0.00078365
8 | 0.015306 | 0.0038361
9 | 0.014424 | 0.0036149
10 | 0.0015516 | 0.00038886
11 | 0.0092956 | 0.0023297
12 | 0.012998 | 0.0032575
13 | 0.0087384 | 0.0021901
14 | 0.013759 | 0.0034483
15 | 0.015946 | 0.0039963
16 | 0.0059699 | 0.0014962
17 | 0.0077881 | 0.0019519
18 | 0.015521 | 0.00389
19 | 0.0086262 | 0.0021619
20 | 0.016813 | 0.0042137
21 | 0.0092918 | 0.0023287
22 | 0.0080677 | 0.002022
23 | 0.0097316 | 0.002439
24 | 0.0086833 | 0.0021762
25 | 0.0098739 | 0.0024746
26 | 0.010313 | 0.0025848
27 | 0.0096253 | 0.0024123
28 | 0.0087974 | 0.0022048
29 | 0.0085691 | 0.0021476

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1