## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_193-5_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_193-5_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_193-5_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_193-5_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_193-5_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_193-5_0_5_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_193-5_0_5_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_193-5_0_5_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_193-5_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_193-5_0_5_node_52 | 0.4 | n |  | TRUE
10 | bus_LV_193-5_0_5_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_193-5_0_5_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_193-5_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_193-5_0_5_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_193-5_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_193-5_0_5_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_193-5_0_5_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_193-5_0_5_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_193-5_0_5_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_193-5_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_193-5_0_5_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_193-5_0_5_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_193-5_0_5_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_193-5_0_5_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_193-5_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_193-5_0_5_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_193-5_0_5_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_193-5_0_5_node_5 | 0.4 | n |  | TRUE
28 | bus_LV_193-5_0_5_node_6 | 0.4 | n |  | TRUE
29 | bus_LV_193-5_0_5_node_8 | 0.4 | n |  | TRUE
30 | bus_LV_193-5_0_5_node_10 | 0.4 | n |  | TRUE
31 | bus_LV_193-5_0_5_node_12 | 0.4 | n |  | TRUE
32 | bus_LV_193-5_0_5_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_193-5_0_5_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_193-5_0_5_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_193-5_0_5_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_193-5_0_5_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_193-5_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_193-5_0_5_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_193-5_0_5_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_193-5_0_5_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_193-5_0_5_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_193-5_0_5_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_193-5_0_5_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_193-5_0_5_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_193-5_0_5_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_193-5_0_5_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_193-5_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_MV_365_0_node_196 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_193-5_0_5_load_0 | 0 | 0.0076786 | 0.0019244 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_193-5_0_5_load_1 | 1 | 0.0048257 | 0.0012094 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_193-5_0_5_load_2 | 2 | 0.018617 | 0.0046658 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_193-5_0_5_load_52 | 9 | 0.0081133 | 0.0020334 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_193-5_0_5_load_49 | 10 | 0.022138 | 0.0055482 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_193-5_0_5_load_47 | 11 | 0.012109 | 0.0030349 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_193-5_0_5_load_36 | 14 | 0.015442 | 0.0038701 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_193-5_0_5_load_35 | 15 | 0.014933 | 0.0037426 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_193-5_0_5_load_28 | 16 | 0.0049844 | 0.0012492 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_193-5_0_5_load_45 | 18 | 0.013721 | 0.0034387 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_193-5_0_5_load_40 | 20 | 0.0068764 | 0.0017234 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_193-5_0_5_load_39 | 21 | 0.0084417 | 0.0021157 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_193-5_0_5_load_44 | 23 | 0.012902 | 0.0032336 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_193-5_0_5_load_24 | 25 | 0.012424 | 0.0031138 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_193-5_0_5_load_46 | 26 | 0.011867 | 0.002974 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_193-5_0_5_load_5 | 27 | 0.010098 | 0.0025307 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_193-5_0_5_load_8 | 29 | 0.0093928 | 0.0023541 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_193-5_0_5_load_10 | 30 | 0.042622 | 0.010682 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_193-5_0_5_load_13 | 32 | 0.0062567 | 0.0015681 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_193-5_0_5_load_48 | 33 | 0.0028445 | 0.0007129 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_193-5_0_5_load_37 | 34 | 0.017492 | 0.0043838 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_193-5_0_5_load_33 | 35 | 0.0091015 | 0.002281 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_193-5_0_5_load_51 | 38 | 0.015916 | 0.0039889 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_193-5_0_5_load_21 | 40 | 0.013513 | 0.0033866 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_193-5_0_5_load_22 | 41 | 0.013002 | 0.0032585 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_193-5_0_5_load_41 | 42 | 0.0081245 | 0.0020362 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_193-5_0_5_load_27 | 43 | 0.005965 | 0.001495 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_193-5_0_5_load_42 | 44 | 0.0078122 | 0.0019579 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_193-5_0_5_load_43 | 45 | 0.0062821 | 0.0015744 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_193-5_0_5_load_32 | 46 | 0.0087677 | 0.0021974 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_193-5_0_5_load_34 | 47 | 0.029669 | 0.0074357 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_193-5_0_5_line_0 |  | 0 | 1 | 0.0052547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_193-5_0_5_line_1 |  | 0 | 2 | 0.11072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_193-5_0_5_line_2 |  | 1 | 3 | 0.050907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_193-5_0_5_line_3 |  | 2 | 4 | 0.046937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_193-5_0_5_line_4 |  | 3 | 5 | 0.084511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_193-5_0_5_line_5 |  | 4 | 6 | 0.036531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_193-5_0_5_line_6 |  | 4 | 7 | 0.055306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_193-5_0_5_line_7 |  | 4 | 8 | 0.10953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_193-5_0_5_line_8 |  | 5 | 9 | 0.024521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_193-5_0_5_line_9 |  | 5 | 10 | 0.01182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_193-5_0_5_line_10 |  | 6 | 16 | 0.036525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_193-5_0_5_line_11 |  | 7 | 17 | 0.007209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_193-5_0_5_line_12 |  | 7 | 18 | 0.026036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_193-5_0_5_line_13 |  | 8 | 11 | 0.074269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_193-5_0_5_line_14 |  | 8 | 12 | 0.025162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_193-5_0_5_line_15 |  | 10 | 39 | 0.012917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_193-5_0_5_line_16 |  | 11 | 33 | 0.030078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_193-5_0_5_line_17 |  | 12 | 30 | 0.017006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_193-5_0_5_line_18 |  | 12 | 27 | 0.02984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_193-5_0_5_line_19 |  | 13 | 14 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_193-5_0_5_line_20 |  | 13 | 15 | 0.020555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_193-5_0_5_line_21 |  | 14 | 34 | 0.0046598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_193-5_0_5_line_22 |  | 15 | 35 | 0.0073767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_193-5_0_5_line_23 |  | 16 | 43 | 0.0051877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_193-5_0_5_line_24 |  | 17 | 34 | 0.025137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_193-5_0_5_line_25 |  | 18 | 45 | 0.0001628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_193-5_0_5_line_26 |  | 19 | 20 | 0.02403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_193-5_0_5_line_27 |  | 19 | 21 | 0.059429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_193-5_0_5_line_28 |  | 20 | 22 | 0.0094412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_193-5_0_5_line_29 |  | 22 | 23 | 0.023054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_193-5_0_5_line_30 |  | 23 | 36 | 0.014032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_193-5_0_5_line_31 |  | 24 | 25 | 0.020871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_193-5_0_5_line_32 |  | 24 | 26 | 0.02613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_193-5_0_5_line_33 |  | 25 | 37 | 0.049938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_193-5_0_5_line_34 |  | 27 | 28 | 0.031923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_193-5_0_5_line_35 |  | 28 | 29 | 0.03365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_193-5_0_5_line_36 |  | 29 | 31 | 0.0074994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_193-5_0_5_line_37 |  | 31 | 32 | 0.05356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_193-5_0_5_line_38 |  | 35 | 46 | 0.015009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_193-5_0_5_line_39 |  | 36 | 42 | 0.016973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_193-5_0_5_line_40 |  | 36 | 37 | 0.037119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_193-5_0_5_line_41 |  | 37 | 41 | 0.033137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_193-5_0_5_line_42 |  | 38 | 39 | 0.026624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_193-5_0_5_line_43 |  | 40 | 41 | 0.0013385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_193-5_0_5_line_44 |  | 42 | 44 | 0.00043987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_193-5_0_5_line_45 |  | 44 | 45 | 0.036963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_193-5_0_5_line_46 |  | 46 | 47 | 0.012304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_193-5_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 48 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2690735.0929 | 1247787.1664 | 2690736.7952 | 1247792.1378
1 | 2690735.0929 | 1247787.1664 | 2690727.6196 | 1247765.3414 | 2690762.4514 | 1247760.2261 | 2690769.1836 | 1247753.6798 | 2690782.8705 | 1247740.3681 | 2690776.0307 | 1247717.4025
2 | 2690748.7627 | 1247841.2334 | 2690747.3433 | 1247822.9423 | 2690736.7952 | 1247792.1378
3 | 2690762.6331 | 1247672.4181 | 2690776.0307 | 1247717.4025
4 | 2690748.7627 | 1247841.2334 | 2690737.3229 | 1247833.1078 | 2690727.1935 | 1247834.6095 | 2690718.5201 | 1247839.1913 | 2690700.6709 | 1247849.1036 | 2690691.4549 | 1247820.541
5 | 2690762.6331 | 1247672.4181 | 2690757.3249 | 1247677.7187 | 2690729.4517 | 1247686.143
6 | 2690762.6331 | 1247672.4181 | 2690724.7511 | 1247632.0191
7 | 2690762.6331 | 1247672.4181 | 2690771.956 | 1247672.3052 | 2690780.9809 | 1247668.4627 | 2690816.5472 | 1247652.4285 | 2690834.4693 | 1247644.219 | 2690833.9639 | 1247641.7093 | 2690834.2802 | 1247638.3227 | 2690835.5481 | 1247635.44 | 2690837.6386 | 1247633.0924 | 2690840.4438 | 1247631.4342 | 2690843.6117 | 1247630.7488 | 2690846.0491 | 1247630.9085 | 2690848.5672 | 1247631.7144 | 2690850.4457 | 1247632.8551 | 2690853.8756 | 1247628.3821
8 | 2690691.4549 | 1247820.541 | 2690679.7293 | 1247826.6441 | 2690671.3832 | 1247828.0954 | 2690669.1453 | 1247829.8288
9 | 2690691.4549 | 1247820.541 | 2690687.8302 | 1247809.2908
10 | 2690729.4517 | 1247686.143 | 2690739.6929 | 1247721.2025
11 | 2690719.8162 | 1247626.7507 | 2690724.7511 | 1247632.0191
12 | 2690724.7511 | 1247632.0191 | 2690704.2468 | 1247648.0645
13 | 2690853.8756 | 1247628.3821 | 2690857.0096 | 1247631.3879 | 2690859.2591 | 1247634.9362 | 2690860.0969 | 1247640.3976 | 2690861.0172 | 1247647.3725 | 2690862.8144 | 1247656.2734 | 2690874.8353 | 1247672.8146 | 2690879.5403 | 1247679.2804 | 2690888.682 | 1247691.9707
14 | 2690875.5478 | 1247627.836 | 2690858.5333 | 1247622.6602 | 2690853.8756 | 1247628.3821
15 | 2690683.869 | 1247796.9961 | 2690687.8302 | 1247809.2908
16 | 2690888.682 | 1247691.9707 | 2690906.2629 | 1247716.3759
17 | 2690875.5478 | 1247627.836 | 2690891.7148 | 1247633.1107
18 | 2690875.5478 | 1247627.836 | 2690885.0666 | 1247599.5546
19 | 2690760.9011 | 1247597.6018 | 2690744.118 | 1247609.5091
20 | 2690760.9011 | 1247597.6018 | 2690772.7677 | 1247614.385 | 2690772.7677 | 1247614.385
21 | 2690744.118 | 1247609.5091 | 2690740.3176 | 1247612.2054
22 | 2690772.7677 | 1247614.385 | 2690779.3012 | 1247610.9602 | 2690779.3012 | 1247610.9602
23 | 2690741.1475 | 1247726.1821 | 2690739.6929 | 1247721.2025
24 | 2690719.8162 | 1247626.7507 | 2690740.3176 | 1247612.2054
25 | 2690704.2468 | 1247648.0645 | 2690704.1186 | 1247648.1649
26 | 2690615.2898 | 1247628.187 | 2690630.7294 | 1247646.6005
27 | 2690615.2898 | 1247628.187 | 2690661.5181 | 1247590.8411
28 | 2690636.7955 | 1247653.835 | 2690630.7294 | 1247646.6005
29 | 2690636.7955 | 1247653.835 | 2690652.0258 | 1247671.1411
30 | 2690661.2964 | 1247681.675 | 2690652.0258 | 1247671.1411
31 | 2690594.1372 | 1247729.14 | 2690613.9333 | 1247722.5272
32 | 2690594.1372 | 1247729.14 | 2690601.8654 | 1247754.1013
33 | 2690661.2986 | 1247706.705 | 2690613.9333 | 1247722.5272
34 | 2690907.5106 | 1247592.6548 | 2690889.1604 | 1247587.3918 | 2690885.0666 | 1247599.5546
35 | 2690907.5106 | 1247592.6548 | 2690909.6879 | 1247593.5222 | 2690905.7966 | 1247609.3523 | 2690920.1275 | 1247613.7981
36 | 2690927.2902 | 1247616.0202 | 2690920.1275 | 1247613.7981
37 | 2690927.2902 | 1247616.0202 | 2690944.1934 | 1247602.3579 | 2690952.5341 | 1247603.7425 | 2690958.6571 | 1247602.958 | 2690963.4709 | 1247586.4472
38 | 2690787.1203 | 1247623.7714 | 2690779.3012 | 1247610.9602
39 | 2690661.2964 | 1247681.675 | 2690674.663 | 1247671.2151
40 | 2690661.2964 | 1247681.675 | 2690673.5072 | 1247702.6219 | 2690661.2986 | 1247706.705
41 | 2690661.2986 | 1247706.705 | 2690670.8242 | 1247738.4429
42 | 2690683.869 | 1247796.9961 | 2690659.1256 | 1247800.8429 | 2690657.793 | 1247801.6988
43 | 2690671.209 | 1247739.7249 | 2690670.8242 | 1247738.4429
44 | 2690675.0094 | 1247670.944 | 2690674.663 | 1247671.2151
45 | 2690675.0094 | 1247670.944 | 2690704.1186 | 1247648.1649
46 | 2690793.5301 | 1247634.2734 | 2690787.1203 | 1247623.7714

## bus_geodata
| x | y | coords
0 | 2690735.0929 | 1247787.1664
1 | 2690736.7952 | 1247792.1378
2 | 2690776.0307 | 1247717.4025
3 | 2690748.7627 | 1247841.2334
4 | 2690762.6331 | 1247672.4181
5 | 2690691.4549 | 1247820.541
6 | 2690729.4517 | 1247686.143
7 | 2690724.7511 | 1247632.0191
8 | 2690853.8756 | 1247628.3821
9 | 2690669.1453 | 1247829.8288
10 | 2690687.8302 | 1247809.2908
11 | 2690888.682 | 1247691.9707
12 | 2690875.5478 | 1247627.836
13 | 2690760.9011 | 1247597.6018
14 | 2690744.118 | 1247609.5091
15 | 2690772.7677 | 1247614.385
16 | 2690739.6929 | 1247721.2025
17 | 2690719.8162 | 1247626.7507
18 | 2690704.2468 | 1247648.0645
19 | 2690615.2898 | 1247628.187
20 | 2690630.7294 | 1247646.6005
21 | 2690661.5181 | 1247590.8411
22 | 2690636.7955 | 1247653.835
23 | 2690652.0258 | 1247671.1411
24 | 2690594.1372 | 1247729.14
25 | 2690613.9333 | 1247722.5272
26 | 2690601.8654 | 1247754.1013
27 | 2690885.0666 | 1247599.5546
28 | 2690907.5106 | 1247592.6548
29 | 2690920.1275 | 1247613.7981
30 | 2690891.7148 | 1247633.1107
31 | 2690927.2902 | 1247616.0202
32 | 2690963.4709 | 1247586.4472
33 | 2690906.2629 | 1247716.3759
34 | 2690740.3176 | 1247612.2054
35 | 2690779.3012 | 1247610.9602
36 | 2690661.2964 | 1247681.675
37 | 2690661.2986 | 1247706.705
38 | 2690657.793 | 1247801.6988
39 | 2690683.869 | 1247796.9961
40 | 2690671.209 | 1247739.7249
41 | 2690670.8242 | 1247738.4429
42 | 2690674.663 | 1247671.2151
43 | 2690741.1475 | 1247726.1821
44 | 2690675.0094 | 1247670.944
45 | 2690704.1186 | 1247648.1649
46 | 2690787.1203 | 1247623.7714
47 | 2690793.5301 | 1247634.2734
48 | 2690729.4517 | 1247686.143

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99069 | -0.17814 | 0.0076786 | 0.0019244
1 | 0.99044 | -0.1829 | 0.0048257 | 0.0012094
2 | 0.99667 | -0.063449 | 0.018617 | 0.0046658
3 | 0.98827 | -0.22475 | 0 | 0
4 | 1 | 0 | -0.38757 | -0.098258
5 | 0.98468 | -0.29464 | 0 | 0
6 | 0.99964 | -0.0069755 | 0 | 0
7 | 0.99466 | -0.10195 | 0 | 0
8 | 0.99163 | -0.16044 | 0 | 0
9 | 0.9845 | -0.29821 | 0.0081133 | 0.0020334
10 | 0.98426 | -0.30272 | 0.022138 | 0.0055482
11 | 0.99062 | -0.18015 | 0.012109 | 0.0030349
12 | 0.99005 | -0.19098 | 0 | 0
13 | 0.99032 | -0.18572 | 0 | 0
14 | 0.9915 | -0.1629 | 0.015442 | 0.0038701
15 | 0.98914 | -0.20857 | 0.014933 | 0.0037426
16 | 0.99927 | -0.013954 | 0.0049844 | 0.0012492
17 | 0.99403 | -0.11407 | 0 | 0
18 | 0.99191 | -0.15483 | 0.013721 | 0.0034387
19 | 0.98638 | -0.26178 | 0 | 0
20 | 0.98657 | -0.25815 | 0.0068764 | 0.0017234
21 | 0.98592 | -0.27077 | 0.0084417 | 0.0021157
22 | 0.9867 | -0.25556 | 0 | 0
23 | 0.98703 | -0.24923 | 0.012902 | 0.0032336
24 | 0.98431 | -0.30217 | 0 | 0
25 | 0.98454 | -0.29772 | 0.012424 | 0.0031138
26 | 0.98402 | -0.30775 | 0.011867 | 0.002974
27 | 0.98935 | -0.20466 | 0.010098 | 0.0025307
28 | 0.98889 | -0.21356 | 0 | 0
29 | 0.98841 | -0.22295 | 0.0093928 | 0.0023541
30 | 0.98939 | -0.20388 | 0.042622 | 0.010682
31 | 0.98837 | -0.22379 | 0 | 0
32 | 0.98806 | -0.22977 | 0.0062567 | 0.0015681
33 | 0.99054 | -0.18167 | 0.0028445 | 0.0007129
34 | 0.99183 | -0.15647 | 0.017492 | 0.0043838
35 | 0.98882 | -0.21482 | 0.0091015 | 0.002281
36 | 0.98739 | -0.24215 | 0 | 0
37 | 0.98565 | -0.27593 | 0 | 0
38 | 0.98368 | -0.31405 | 0.015916 | 0.0039889
39 | 0.98407 | -0.30642 | 0 | 0
40 | 0.98483 | -0.29203 | 0.013513 | 0.0033866
41 | 0.98485 | -0.2917 | 0.013002 | 0.0032585
42 | 0.98863 | -0.2182 | 0.0081245 | 0.0020362
43 | 0.99925 | -0.014494 | 0.005965 | 0.001495
44 | 0.98866 | -0.21752 | 0.0078122 | 0.0019579
45 | 0.99189 | -0.15512 | 0.0062821 | 0.0015744
46 | 0.98829 | -0.22511 | 0.0087677 | 0.0021974
47 | 0.98795 | -0.23163 | 0.029669 | 0.0074357
48 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.051276 | 0.012959 | -0.051265 | -0.012951 | 1.17e-05 | 7.4203e-06 | 0.077056 | 0.077056 | 0.077056 | 0.99069 | -0.17814 | 0.99044 | -0.1829 | 21.1691
1 | -0.058955 | -0.014883 | 0.059281 | 0.01509 | 0.00032585 | 0.00020711 | 0.088589 | 0.088588 | 0.088589 | 0.99069 | -0.17814 | 0.99667 | -0.063449 | 24.3376
2 | 0.046439 | 0.011742 | -0.046346 | -0.011683 | 9.3022e-05 | 5.8881e-05 | 0.069806 | 0.069806 | 0.069806 | 0.99044 | -0.1829 | 0.98827 | -0.22475 | 19.1774
3 | -0.077898 | -0.019756 | 0.078136 | 0.019908 | 0.00023841 | 0.00015197 | 0.11638 | 0.11638 | 0.11638 | 0.99667 | -0.063449 | 1 | 0 | 31.9733
4 | 0.046346 | 0.011683 | -0.046191 | -0.011585 | 0.00015443 | 9.7756e-05 | 0.069806 | 0.069806 | 0.069806 | 0.98827 | -0.22475 | 0.98468 | -0.29464 | 19.1775
5 | 0.010957 | 0.0027479 | -0.010953 | -0.0027461 | 3.6418e-06 | 1.8517e-06 | 0.016305 | 0.016305 | 0.016305 | 1 | 0 | 0.99964 | -0.0069755 | 4.4793
6 | 0.21269 | 0.054201 | -0.21165 | -0.053536 | 0.0010408 | 0.00066465 | 0.3168 | 0.3168 | 0.3168 | 1 | 0 | 0.99466 | -0.10195 | 43.517
7 | 0.084141 | 0.021401 | -0.083496 | -0.020989 | 0.00064503 | 0.00041139 | 0.12531 | 0.12531 | 0.12531 | 1 | 0 | 0.99163 | -0.16044 | 34.427
8 | 0.0081147 | 0.002034 | -0.0081133 | -0.0020334 | 1.3828e-06 | 5.7311e-07 | 0.012263 | 0.012263 | 0.012263 | 0.98468 | -0.29464 | 0.9845 | -0.29821 | 3.3689
9 | 0.038077 | 0.0095514 | -0.038062 | -0.0095421 | 1.4677e-05 | 9.2429e-06 | 0.057544 | 0.057544 | 0.057544 | 0.98468 | -0.29464 | 0.98426 | -0.30272 | 15.8087
10 | 0.010953 | 0.0027461 | -0.01095 | -0.0027442 | 3.6413e-06 | 1.8518e-06 | 0.016305 | 0.016305 | 0.016305 | 0.99964 | -0.0069755 | 0.99927 | -0.013954 | 4.4794
11 | 0.095857 | 0.024199 | -0.095802 | -0.024163 | 5.5641e-05 | 3.5517e-05 | 0.14347 | 0.14347 | 0.14347 | 0.99466 | -0.10195 | 0.99403 | -0.11407 | 39.4135
12 | 0.11579 | 0.029338 | -0.1155 | -0.02915 | 0.00029336 | 0.00018741 | 0.17334 | 0.17334 | 0.17334 | 0.99466 | -0.10195 | 0.99191 | -0.15483 | 47.6206
13 | 0.014968 | 0.0037556 | -0.014954 | -0.0037475 | 1.4053e-05 | 8.0365e-06 | 0.022462 | 0.022463 | 0.022463 | 0.99163 | -0.16044 | 0.99062 | -0.18015 | 6.1711
14 | 0.068528 | 0.017234 | -0.068428 | -0.01717 | 9.9817e-05 | 6.3559e-05 | 0.10285 | 0.10285 | 0.10285 | 0.99163 | -0.16044 | 0.99005 | -0.19098 | 28.2561
15 | 0.015924 | 0.0039939 | -0.015922 | -0.0039923 | 2.8077e-06 | 1.6328e-06 | 0.024076 | 0.024076 | 0.024076 | 0.98426 | -0.30272 | 0.98407 | -0.30642 | 6.6142
16 | 0.0028447 | 0.00071265 | -0.0028445 | -0.0007129 | 2.0595e-07 | -2.554e-07 | 0.004273 | 0.0042731 | 0.0042731 | 0.99062 | -0.18015 | 0.99054 | -0.18167 | 1.1739
17 | 0.042648 | 0.010699 | -0.042622 | -0.010682 | 2.6205e-05 | 1.6552e-05 | 0.064103 | 0.064103 | 0.064103 | 0.99005 | -0.19098 | 0.98939 | -0.20388 | 17.6106
18 | 0.02578 | 0.0064716 | -0.025763 | -0.0064612 | 1.6802e-05 | 1.037e-05 | 0.038749 | 0.03875 | 0.03875 | 0.99005 | -0.19098 | 0.98935 | -0.20466 | 10.6455
19 | -0.062582 | -0.015727 | 0.06265 | 0.01577 | 6.8255e-05 | 4.3418e-05 | 0.094048 | 0.094048 | 0.094048 | 0.99032 | -0.18572 | 0.9915 | -0.1629 | 25.8374
20 | 0.062582 | 0.015727 | -0.062513 | -0.015683 | 6.8177e-05 | 4.3369e-05 | 0.094048 | 0.094048 | 0.094048 | 0.99032 | -0.18572 | 0.98914 | -0.20857 | 25.8374
21 | -0.078092 | -0.01964 | 0.078116 | 0.019656 | 2.4012e-05 | 1.5307e-05 | 0.11722 | 0.11722 | 0.11722 | 0.9915 | -0.1629 | 0.99183 | -0.15647 | 32.2041
22 | 0.04758 | 0.011941 | -0.047566 | -0.011932 | 1.4175e-05 | 8.9772e-06 | 0.071583 | 0.071583 | 0.071583 | 0.98914 | -0.20857 | 0.98882 | -0.21482 | 19.6657
23 | 0.0059651 | 0.001495 | -0.005965 | -0.001495 | 1.535e-07 | 3.0279e-08 | 0.0088827 | 0.0088827 | 0.0088827 | 0.99927 | -0.013954 | 0.99925 | -0.014494 | 2.4403
24 | 0.095802 | 0.024163 | -0.095608 | -0.024039 | 0.00019402 | 0.00012385 | 0.14347 | 0.14347 | 0.14347 | 0.99403 | -0.11407 | 0.99183 | -0.15647 | 39.4135
25 | 0.10178 | 0.025711 | -0.10178 | -0.025711 | 1.4246e-06 | 9.0961e-07 | 0.15276 | 0.15276 | 0.15276 | 0.99191 | -0.15483 | 0.99189 | -0.15512 | 41.9658
26 | -0.0084454 | -0.0021173 | 0.0084468 | 0.0021179 | 1.4627e-06 | 6.2934e-07 | 0.012741 | 0.01274 | 0.012741 | 0.98638 | -0.26178 | 0.98657 | -0.25815 | 3.5001
27 | 0.0084454 | 0.0021173 | -0.0084417 | -0.0021157 | 3.6175e-06 | 1.557e-06 | 0.012741 | 0.012741 | 0.012741 | 0.98638 | -0.26178 | 0.98592 | -0.27077 | 3.5002
28 | -0.015323 | -0.0038413 | 0.015325 | 0.0038424 | 1.8912e-06 | 1.0898e-06 | 0.023112 | 0.023112 | 0.023112 | 0.98657 | -0.25815 | 0.9867 | -0.25556 | 6.3494
29 | -0.015325 | -0.0038424 | 0.01533 | 0.003845 | 4.6178e-06 | 2.6608e-06 | 0.023112 | 0.023112 | 0.023112 | 0.9867 | -0.25556 | 0.98703 | -0.24923 | 6.3494
30 | -0.028232 | -0.0070786 | 0.028241 | 0.0070845 | 9.5327e-06 | 5.9215e-06 | 0.042563 | 0.042563 | 0.042563 | 0.98703 | -0.24923 | 0.98739 | -0.24215 | 11.693
31 | -0.01187 | -0.0029757 | 0.011872 | 0.0029771 | 2.5202e-06 | 1.3475e-06 | 0.017944 | 0.017944 | 0.017944 | 0.98431 | -0.30217 | 0.98454 | -0.29772 | 4.9297
32 | 0.01187 | 0.0029757 | -0.011867 | -0.002974 | 3.1552e-06 | 1.6873e-06 | 0.017944 | 0.017944 | 0.017944 | 0.98431 | -0.30217 | 0.98402 | -0.30775 | 4.9298
33 | -0.024297 | -0.0060909 | 0.024322 | 0.0061064 | 2.5253e-05 | 1.5526e-05 | 0.036722 | 0.036722 | 0.036722 | 0.98454 | -0.29772 | 0.98565 | -0.27593 | 10.0885
34 | 0.015665 | 0.0039306 | -0.015659 | -0.0039267 | 6.6464e-06 | 3.844e-06 | 0.023563 | 0.023563 | 0.023563 | 0.98935 | -0.20466 | 0.98889 | -0.21356 | 6.4733
35 | 0.015659 | 0.0039267 | -0.015652 | -0.0039227 | 7.0059e-06 | 4.0523e-06 | 0.023563 | 0.023563 | 0.023563 | 0.98889 | -0.21356 | 0.98841 | -0.22295 | 6.4733
36 | 0.0062587 | 0.0015686 | -0.0062585 | -0.0015685 | 2.4967e-07 | 6.3676e-08 | 0.0094223 | 0.0094223 | 0.0094223 | 0.98841 | -0.22295 | 0.98837 | -0.22379 | 2.5886
37 | 0.0062585 | 0.0015685 | -0.0062567 | -0.0015681 | 1.7832e-06 | 4.5505e-07 | 0.0094223 | 0.0094226 | 0.0094226 | 0.98837 | -0.22379 | 0.98806 | -0.22977 | 2.5886
38 | 0.038465 | 0.0096507 | -0.038446 | -0.0096388 | 1.886e-05 | 1.1878e-05 | 0.057887 | 0.057887 | 0.057887 | 0.98882 | -0.21482 | 0.98829 | -0.22511 | 15.903
39 | -0.07918 | -0.019901 | 0.07927 | 0.019958 | 9.0656e-05 | 5.7802e-05 | 0.11935 | 0.11935 | 0.11935 | 0.98739 | -0.24215 | 0.98863 | -0.2182 | 32.7872
40 | 0.050938 | 0.012816 | -0.050856 | -0.012764 | 8.2066e-05 | 5.2048e-05 | 0.076783 | 0.076783 | 0.076783 | 0.98739 | -0.24215 | 0.98565 | -0.27593 | 21.0942
41 | 0.026535 | 0.0066576 | -0.026515 | -0.0066452 | 1.9943e-05 | 1.2341e-05 | 0.040061 | 0.040061 | 0.040061 | 0.98565 | -0.27593 | 0.98485 | -0.2917 | 11.0058
42 | -0.015916 | -0.0039889 | 0.015922 | 0.0039923 | 5.7872e-06 | 3.3657e-06 | 0.024076 | 0.024076 | 0.024076 | 0.98368 | -0.31405 | 0.98407 | -0.30642 | 6.6142
43 | -0.013513 | -0.0033866 | 0.013513 | 0.0033867 | 2.0923e-07 | 1.1688e-07 | 0.020417 | 0.020417 | 0.020417 | 0.98483 | -0.29203 | 0.98485 | -0.2917 | 5.609
44 | -0.087395 | -0.021995 | 0.087398 | 0.021996 | 2.8555e-06 | 1.8219e-06 | 0.13157 | 0.13157 | 0.13157 | 0.98863 | -0.2182 | 0.98866 | -0.21752 | 36.1466
45 | -0.09521 | -0.023954 | 0.095495 | 0.024136 | 0.00028476 | 0.00018177 | 0.14333 | 0.14333 | 0.14333 | 0.98866 | -0.21752 | 0.99189 | -0.15512 | 39.3768
46 | 0.029678 | 0.0074414 | -0.029669 | -0.0074357 | 9.2131e-06 | 5.7388e-06 | 0.044686 | 0.044686 | 0.044686 | 0.98829 | -0.22511 | 0.98795 | -0.23163 | 12.2764

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38757 | 0.098258

## res_load
| p_mw | q_mvar
0 | 0.0076786 | 0.0019244
1 | 0.0048257 | 0.0012094
2 | 0.018617 | 0.0046658
3 | 0.0081133 | 0.0020334
4 | 0.022138 | 0.0055482
5 | 0.012109 | 0.0030349
6 | 0.015442 | 0.0038701
7 | 0.014933 | 0.0037426
8 | 0.0049844 | 0.0012492
9 | 0.013721 | 0.0034387
10 | 0.0068764 | 0.0017234
11 | 0.0084417 | 0.0021157
12 | 0.012902 | 0.0032336
13 | 0.012424 | 0.0031138
14 | 0.011867 | 0.002974
15 | 0.010098 | 0.0025307
16 | 0.0093928 | 0.0023541
17 | 0.042622 | 0.010682
18 | 0.0062567 | 0.0015681
19 | 0.0028445 | 0.0007129
20 | 0.017492 | 0.0043838
21 | 0.0091015 | 0.002281
22 | 0.015916 | 0.0039889
23 | 0.013513 | 0.0033866
24 | 0.013002 | 0.0032585
25 | 0.0081245 | 0.0020362
26 | 0.005965 | 0.001495
27 | 0.0078122 | 0.0019579
28 | 0.0062821 | 0.0015744
29 | 0.0087677 | 0.0021974
30 | 0.029669 | 0.0074357

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1