## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_195-14_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_195-14_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_195-14_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_195-14_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_195-14_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_195-14_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_195-14_0_8_node_59 | 0.4 | n |  | TRUE
7 | bus_LV_195-14_0_8_node_58 | 0.4 | n |  | TRUE
8 | bus_LV_195-14_0_8_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_195-14_0_8_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_195-14_0_8_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_195-14_0_8_node_53 | 0.4 | n |  | TRUE
12 | bus_LV_195-14_0_8_node_48 | 0.4 | n |  | TRUE
13 | bus_LV_195-14_0_8_node_62 | 0.4 | n |  | TRUE
14 | bus_LV_195-14_0_8_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_195-14_0_8_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_195-14_0_8_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_195-14_0_8_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_195-14_0_8_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_195-14_0_8_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_195-14_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_195-14_0_8_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_195-14_0_8_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_195-14_0_8_node_121 | 0.4 | n |  | TRUE
24 | bus_LV_195-14_0_8_node_93 | 0.4 | n |  | TRUE
25 | bus_LV_195-14_0_8_node_119 | 0.4 | n |  | TRUE
26 | bus_LV_195-14_0_8_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_195-14_0_8_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_195-14_0_8_node_138 | 0.4 | n |  | TRUE
29 | bus_LV_195-14_0_8_node_137 | 0.4 | n |  | TRUE
30 | bus_LV_195-14_0_8_node_143 | 0.4 | n |  | TRUE
31 | bus_LV_195-14_0_8_node_144 | 0.4 | n |  | TRUE
32 | bus_LV_195-14_0_8_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_195-14_0_8_node_136 | 0.4 | n |  | TRUE
34 | bus_LV_195-14_0_8_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_195-14_0_8_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_195-14_0_8_node_122 | 0.4 | n |  | TRUE
37 | bus_LV_195-14_0_8_node_94 | 0.4 | n |  | TRUE
38 | bus_LV_195-14_0_8_node_118 | 0.4 | n |  | TRUE
39 | bus_LV_195-14_0_8_node_116 | 0.4 | n |  | TRUE
40 | bus_LV_195-14_0_8_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_195-14_0_8_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_195-14_0_8_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_195-14_0_8_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_195-14_0_8_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_195-14_0_8_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_195-14_0_8_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_195-14_0_8_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_195-14_0_8_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_195-14_0_8_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_195-14_0_8_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_195-14_0_8_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_195-14_0_8_node_140 | 0.4 | n |  | TRUE
53 | bus_LV_195-14_0_8_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_195-14_0_8_node_30 | 0.4 | n |  | TRUE
55 | bus_LV_195-14_0_8_node_128 | 0.4 | n |  | TRUE
56 | bus_LV_195-14_0_8_node_104 | 0.4 | n |  | TRUE
57 | bus_LV_195-14_0_8_node_131 | 0.4 | n |  | TRUE
58 | bus_LV_195-14_0_8_node_102 | 0.4 | n |  | TRUE
59 | bus_LV_195-14_0_8_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_195-14_0_8_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_195-14_0_8_node_29 | 0.4 | n |  | TRUE
62 | bus_LV_195-14_0_8_node_31 | 0.4 | n |  | TRUE
63 | bus_LV_195-14_0_8_node_32 | 0.4 | n |  | TRUE
64 | bus_LV_195-14_0_8_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_195-14_0_8_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_195-14_0_8_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_195-14_0_8_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_195-14_0_8_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_195-14_0_8_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_195-14_0_8_node_41 | 0.4 | n |  | TRUE
71 | bus_LV_195-14_0_8_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_195-14_0_8_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_195-14_0_8_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_195-14_0_8_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_195-14_0_8_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_195-14_0_8_node_55 | 0.4 | n |  | TRUE
77 | bus_LV_195-14_0_8_node_130 | 0.4 | n |  | TRUE
78 | bus_LV_195-14_0_8_node_126 | 0.4 | n |  | TRUE
79 | bus_LV_195-14_0_8_node_132 | 0.4 | n |  | TRUE
80 | bus_LV_195-14_0_8_node_109 | 0.4 | n |  | TRUE
81 | bus_LV_195-14_0_8_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_195-14_0_8_node_110 | 0.4 | n |  | TRUE
83 | bus_LV_195-14_0_8_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_195-14_0_8_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_195-14_0_8_node_65 | 0.4 | n |  | TRUE
86 | bus_LV_195-14_0_8_node_66 | 0.4 | n |  | TRUE
87 | bus_LV_195-14_0_8_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_195-14_0_8_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_195-14_0_8_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_195-14_0_8_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_195-14_0_8_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_195-14_0_8_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_195-14_0_8_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_195-14_0_8_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_195-14_0_8_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_195-14_0_8_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_195-14_0_8_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_195-14_0_8_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_195-14_0_8_node_142 | 0.4 | n |  | TRUE
100 | bus_LV_195-14_0_8_node_125 | 0.4 | n |  | TRUE
101 | bus_LV_195-14_0_8_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_195-14_0_8_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_195-14_0_8_node_75 | 0.4 | n |  | TRUE
104 | bus_LV_195-14_0_8_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_195-14_0_8_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_195-14_0_8_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_195-14_0_8_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_195-14_0_8_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_195-14_0_8_node_113 | 0.4 | n |  | TRUE
110 | bus_LV_195-14_0_8_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_195-14_0_8_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_195-14_0_8_node_88 | 0.4 | n |  | TRUE
113 | bus_LV_195-14_0_8_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_195-14_0_8_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_195-14_0_8_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_195-14_0_8_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_195-14_0_8_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_195-14_0_8_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_195-14_0_8_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_195-14_0_8_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_195-14_0_8_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_195-14_0_8_node_98 | 0.4 | n |  | TRUE
123 | bus_LV_195-14_0_8_node_99 | 0.4 | n |  | TRUE
124 | bus_LV_195-14_0_8_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_195-14_0_8_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_195-14_0_8_node_135 | 0.4 | n |  | TRUE
127 | bus_LV_195-14_0_8_node_101 | 0.4 | n |  | TRUE
128 | bus_LV_195-14_0_8_node_106 | 0.4 | n |  | TRUE
129 | bus_LV_195-14_0_8_node_114 | 0.4 | n |  | TRUE
130 | bus_LV_195-14_0_8_node_112 | 0.4 | n |  | TRUE
131 | bus_LV_195-14_0_8_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_195-14_0_8_node_133 | 0.4 | n |  | TRUE
133 | bus_LV_195-14_0_8_node_124 | 0.4 | n |  | TRUE
134 | bus_LV_195-14_0_8_node_134 | 0.4 | n |  | TRUE
135 | bus_LV_195-14_0_8_node_129 | 0.4 | n |  | TRUE
136 | bus_MV_364_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_195-14_0_8_load_0 | 0 | 0.007593 | 0.001903 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_195-14_0_8_load_1 | 1 | 0.0020856 | 0.0005227 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_195-14_0_8_load_4 | 4 | 0.0019022 | 0.00047674 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_195-14_0_8_load_5 | 5 | 0.0021224 | 0.00053192 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_195-14_0_8_load_59 | 6 | 0.0019848 | 0.00049743 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_195-14_0_8_load_58 | 7 | 0.0021661 | 0.00054288 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_195-14_0_8_load_49 | 8 | 0.0018965 | 0.0004753 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_195-14_0_8_load_60 | 10 | 0.0021729 | 0.00054458 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_195-14_0_8_load_53 | 11 | 0.0077503 | 0.0019424 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_195-14_0_8_load_48 | 12 | 0.0018586 | 0.00046582 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_195-14_0_8_load_62 | 13 | 0.0021956 | 0.00055026 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_195-14_0_8_load_6 | 14 | 0.0019652 | 0.00049253 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_195-14_0_8_load_7 | 15 | 0.002221 | 0.00055663 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_195-14_0_8_load_8 | 16 | 0.0020426 | 0.00051192 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_195-14_0_8_load_10 | 18 | 0.0027915 | 0.00069961 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_195-14_0_8_load_12 | 19 | 0.0030906 | 0.00077457 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_195-14_0_8_load_121 | 23 | 0.0050736 | 0.0012716 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_195-14_0_8_load_93 | 24 | 0.0031448 | 0.00078816 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_195-14_0_8_load_119 | 25 | 0.0058157 | 0.0014576 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_195-14_0_8_load_138 | 28 | 0.0095278 | 0.0023879 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_195-14_0_8_load_137 | 29 | 0.0096679 | 0.002423 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_195-14_0_8_load_143 | 30 | 0.0078664 | 0.0019715 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_195-14_0_8_load_144 | 31 | 0.0095319 | 0.0023889 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_195-14_0_8_load_136 | 33 | 0.007926 | 0.0019864 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_195-14_0_8_load_50 | 35 | 0.0020275 | 0.00050815 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_195-14_0_8_load_122 | 36 | 0.0055604 | 0.0013936 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_195-14_0_8_load_94 | 37 | 0.0030983 | 0.0007765 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_195-14_0_8_load_116 | 39 | 0.0029993 | 0.00075171 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_195-14_0_8_load_18 | 41 | 0.0014117 | 0.00035379 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_195-14_0_8_load_19 | 42 | 0.0015407 | 0.00038614 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_195-14_0_8_load_20 | 43 | 0.0015199 | 0.00038093 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_195-14_0_8_load_21 | 44 | 0.0013803 | 0.00034595 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_195-14_0_8_load_22 | 45 | 0.0013258 | 0.00033227 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_195-14_0_8_load_23 | 46 | 0.0015353 | 0.00038479 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_195-14_0_8_load_35 | 47 | 0.0014999 | 0.0003759 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_195-14_0_8_load_36 | 49 | 0.0014657 | 0.00036734 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_195-14_0_8_load_140 | 52 | 0.012556 | 0.0031468 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_195-14_0_8_load_33 | 53 | 0.0015926 | 0.00039914 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_195-14_0_8_load_128 | 55 | 0.0079679 | 0.001997 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_195-14_0_8_load_102 | 58 | 0.0075572 | 0.001894 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_195-14_0_8_load_27 | 59 | 0.0015909 | 0.00039873 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_195-14_0_8_load_28 | 60 | 0.0055214 | 0.0013838 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_195-14_0_8_load_31 | 62 | 0.0013325 | 0.00033395 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_195-14_0_8_load_32 | 63 | 0.0013085 | 0.00032794 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_195-14_0_8_load_34 | 64 | 0.0014751 | 0.0003697 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_195-14_0_8_load_37 | 65 | 0.00142 | 0.00035589 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_195-14_0_8_load_56 | 66 | 0.0016302 | 0.00040856 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_195-14_0_8_load_39 | 67 | 0.006883 | 0.001725 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_195-14_0_8_load_40 | 69 | 0.0053251 | 0.0013346 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_195-14_0_8_load_41 | 70 | 0.0013735 | 0.00034422 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_195-14_0_8_load_52 | 74 | 0.0016374 | 0.00041038 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_195-14_0_8_load_57 | 75 | 0.0067892 | 0.0017015 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_195-14_0_8_load_130 | 77 | 0.0094383 | 0.0023655 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_195-14_0_8_load_126 | 78 | 0.0048346 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_195-14_0_8_load_109 | 80 | 0.004765 | 0.0011942 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_195-14_0_8_load_110 | 82 | 0.0053433 | 0.0013392 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_195-14_0_8_load_63 | 83 | 0.010955 | 0.0027457 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_195-14_0_8_load_66 | 86 | 0.01106 | 0.0027719 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_195-14_0_8_load_73 | 88 | 0.011409 | 0.0028593 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_195-14_0_8_load_86 | 94 | 0.009135 | 0.0022895 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_195-14_0_8_load_85 | 97 | 0.0072985 | 0.0018292 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_195-14_0_8_load_142 | 99 | 0.0028569 | 0.00071601 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_195-14_0_8_load_80 | 101 | 0.015749 | 0.0039471 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_195-14_0_8_load_79 | 102 | 0.010797 | 0.002706 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_195-14_0_8_load_75 | 103 | 0.010711 | 0.0026844 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_195-14_0_8_load_91 | 104 | 0.0026577 | 0.00066608 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_195-14_0_8_load_84 | 106 | 0.0026741 | 0.0006702 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_195-14_0_8_load_82 | 107 | 0.0048614 | 0.0012184 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_195-14_0_8_load_90 | 110 | 0.0047453 | 0.0011893 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_195-14_0_8_load_87 | 111 | 0.0044565 | 0.0011169 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_195-14_0_8_load_88 | 112 | 0.011953 | 0.0029958 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_195-14_0_8_load_105 | 114 | 0.014736 | 0.0036933 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_195-14_0_8_load_95 | 116 | 0.0031222 | 0.00078249 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_195-14_0_8_load_108 | 117 | 0.0030427 | 0.00076257 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_195-14_0_8_load_107 | 118 | 0.004573 | 0.0011461 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_195-14_0_8_load_111 | 120 | 0.013224 | 0.0033143 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_195-14_0_8_load_97 | 121 | 0.0041825 | 0.0010482 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_195-14_0_8_load_98 | 122 | 0.018312 | 0.0045894 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_195-14_0_8_load_99 | 123 | 0.0033139 | 0.00083054 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_195-14_0_8_load_135 | 126 | 0.0086401 | 0.0021654 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_195-14_0_8_load_101 | 127 | 0.013154 | 0.0032967 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_195-14_0_8_load_106 | 128 | 0.0095593 | 0.0023958 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_195-14_0_8_load_114 | 129 | 0.0049468 | 0.0012398 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_195-14_0_8_load_112 | 130 | 0.0041862 | 0.0010492 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_195-14_0_8_load_123 | 131 | 0.0028452 | 0.00071308 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_195-14_0_8_load_133 | 132 | 0.0046093 | 0.0011552 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_195-14_0_8_load_124 | 133 | 0.0026468 | 0.00066334 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_195-14_0_8_load_134 | 134 | 0.0053774 | 0.0013477 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_195-14_0_8_load_129 | 135 | 0.0057592 | 0.0014434 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_195-14_0_8_line_0 |  | 0 | 1 | 0.0044609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_195-14_0_8_line_1 |  | 0 | 2 | 0.0080395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_195-14_0_8_line_2 |  | 1 | 3 | 0.015097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_195-14_0_8_line_3 |  | 2 | 4 | 0.017318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_195-14_0_8_line_4 |  | 2 | 5 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_195-14_0_8_line_5 |  | 3 | 6 | 0.018248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_195-14_0_8_line_6 |  | 3 | 7 | 0.013028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_195-14_0_8_line_7 |  | 4 | 8 | 0.0069534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_195-14_0_8_line_8 |  | 5 | 9 | 0.012954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_195-14_0_8_line_9 |  | 6 | 10 | 0.0075699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_195-14_0_8_line_10 |  | 7 | 11 | 0.001246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_195-14_0_8_line_11 |  | 8 | 12 | 0.006895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_195-14_0_8_line_12 |  | 9 | 13 | 0.016057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_195-14_0_8_line_13 |  | 11 | 72 | 0.013817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_195-14_0_8_line_14 |  | 12 | 35 | 0.0069935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_195-14_0_8_line_15 |  | 13 | 18 | 0.0028903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_195-14_0_8_line_16 |  | 14 | 15 | 0.0075925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_195-14_0_8_line_17 |  | 14 | 16 | 0.0019972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_195-14_0_8_line_18 |  | 15 | 17 | 0.011552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_195-14_0_8_line_19 |  | 16 | 18 | 0.0048386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_195-14_0_8_line_20 |  | 17 | 19 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_195-14_0_8_line_21 |  | 17 | 20 | 0.0543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_195-14_0_8_line_22 |  | 19 | 24 | 0.0031826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_195-14_0_8_line_23 |  | 20 | 25 | 0.031339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_195-14_0_8_line_24 |  | 20 | 26 | 0.071426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_195-14_0_8_line_25 |  | 21 | 22 | 0.003628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_195-14_0_8_line_26 |  | 21 | 23 | 0.02544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_195-14_0_8_line_27 |  | 22 | 34 | 0.015653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_195-14_0_8_line_28 |  | 22 | 35 | 0.011187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_195-14_0_8_line_29 |  | 23 | 36 | 0.022606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_195-14_0_8_line_30 |  | 24 | 37 | 0.013769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_195-14_0_8_line_31 |  | 25 | 38 | 0.023182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_195-14_0_8_line_32 |  | 26 | 30 | 0.041194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_195-14_0_8_line_33 |  | 26 | 31 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_195-14_0_8_line_34 |  | 26 | 27 | 0.024867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_195-14_0_8_line_35 |  | 27 | 28 | 0.043931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_195-14_0_8_line_36 |  | 27 | 29 | 0.011531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_195-14_0_8_line_37 |  | 29 | 32 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_195-14_0_8_line_38 |  | 32 | 33 | 0.018196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_195-14_0_8_line_39 |  | 34 | 80 | 0.021778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_195-14_0_8_line_40 |  | 37 | 116 | 0.0048623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_195-14_0_8_line_41 |  | 38 | 132 | 0.012879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_195-14_0_8_line_42 |  | 39 | 40 | 0.0025256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_195-14_0_8_line_43 |  | 40 | 119 | 0.020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_195-14_0_8_line_44 |  | 41 | 42 | 0.005604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_195-14_0_8_line_45 |  | 41 | 43 | 0.0019885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_195-14_0_8_line_46 |  | 42 | 44 | 0.0012158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_195-14_0_8_line_47 |  | 43 | 45 | 0.0049622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_195-14_0_8_line_48 |  | 44 | 46 | 0.0072762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_195-14_0_8_line_49 |  | 45 | 47 | 0.0026282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_195-14_0_8_line_50 |  | 46 | 48 | 0.015396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_195-14_0_8_line_51 |  | 47 | 49 | 0.0043703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_195-14_0_8_line_52 |  | 48 | 50 | 0.030259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_195-14_0_8_line_53 |  | 49 | 65 | 0.0030574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_195-14_0_8_line_54 |  | 50 | 51 | 0.026258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_195-14_0_8_line_55 |  | 50 | 52 | 0.031202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_195-14_0_8_line_56 |  | 51 | 55 | 0.026769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_195-14_0_8_line_57 |  | 53 | 54 | 0.019089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_195-14_0_8_line_58 |  | 54 | 64 | 0.01375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_195-14_0_8_line_59 |  | 54 | 60 | 0.0096568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_195-14_0_8_line_60 |  | 55 | 79 | 0.016496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_195-14_0_8_line_61 |  | 56 | 57 | 0.002559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_195-14_0_8_line_62 |  | 56 | 58 | 0.01974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_195-14_0_8_line_63 |  | 57 | 79 | 0.027359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_195-14_0_8_line_64 |  | 57 | 129 | 0.026167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_195-14_0_8_line_65 |  | 58 | 127 | 0.0044792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_195-14_0_8_line_66 |  | 59 | 60 | 0.0034005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_195-14_0_8_line_67 |  | 59 | 61 | 0.014431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_195-14_0_8_line_68 |  | 61 | 62 | 0.015412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_195-14_0_8_line_69 |  | 61 | 63 | 0.010241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_195-14_0_8_line_70 |  | 62 | 65 | 0.0040617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_195-14_0_8_line_71 |  | 63 | 66 | 0.002661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_195-14_0_8_line_72 |  | 64 | 67 | 0.012926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_195-14_0_8_line_73 |  | 66 | 68 | 0.0061372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_195-14_0_8_line_74 |  | 68 | 75 | 0.0034688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_195-14_0_8_line_75 |  | 69 | 70 | 0.0075244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_195-14_0_8_line_76 |  | 69 | 71 | 0.01291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_195-14_0_8_line_77 |  | 70 | 72 | 0.012685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_195-14_0_8_line_78 |  | 71 | 73 | 0.012385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_195-14_0_8_line_79 |  | 72 | 74 | 0.018008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_195-14_0_8_line_80 |  | 73 | 75 | 0.039918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_195-14_0_8_line_81 |  | 76 | 77 | 0.0184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_195-14_0_8_line_82 |  | 76 | 78 | 0.012063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_195-14_0_8_line_83 |  | 77 | 79 | 0.025446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_195-14_0_8_line_84 |  | 78 | 81 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_195-14_0_8_line_85 |  | 80 | 82 | 0.022539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_195-14_0_8_line_86 |  | 81 | 135 | 0.003395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_195-14_0_8_line_87 |  | 83 | 84 | 0.033167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_195-14_0_8_line_88 |  | 83 | 85 | 0.011659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_195-14_0_8_line_89 |  | 84 | 86 | 0.022351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_195-14_0_8_line_90 |  | 84 | 87 | 0.030585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_195-14_0_8_line_91 |  | 85 | 88 | 0.013407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_195-14_0_8_line_92 |  | 86 | 89 | 0.011649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_195-14_0_8_line_93 |  | 87 | 91 | 0.022001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_195-14_0_8_line_94 |  | 89 | 90 | 0.051872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_195-14_0_8_line_95 |  | 90 | 99 | 0.043839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_195-14_0_8_line_96 |  | 90 | 100 | 0.054551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_195-14_0_8_line_97 |  | 91 | 102 | 0.0060653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_195-14_0_8_line_98 |  | 91 | 101 | 0.016368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_195-14_0_8_line_99 |  | 92 | 93 | 0.024946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_195-14_0_8_line_100 |  | 92 | 94 | 0.030225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_195-14_0_8_line_101 |  | 93 | 102 | 0.022893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_195-14_0_8_line_102 |  | 94 | 96 | 0.016767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_195-14_0_8_line_103 |  | 95 | 96 | 0.014288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_195-14_0_8_line_104 |  | 95 | 97 | 0.033894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_195-14_0_8_line_105 |  | 96 | 98 | 0.032243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_195-14_0_8_line_106 |  | 98 | 103 | 0.026563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_195-14_0_8_line_107 |  | 100 | 104 | 0.026783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_195-14_0_8_line_108 |  | 104 | 113 | 0.020888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_195-14_0_8_line_109 |  | 105 | 106 | 0.023428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_195-14_0_8_line_110 |  | 105 | 107 | 0.038912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_195-14_0_8_line_111 |  | 106 | 108 | 0.034561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_195-14_0_8_line_112 |  | 108 | 109 | 0.027419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_195-14_0_8_line_113 |  | 108 | 110 | 0.04053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_195-14_0_8_line_114 |  | 109 | 119 | 0.044177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_195-14_0_8_line_115 |  | 109 | 120 | 0.055005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_195-14_0_8_line_116 |  | 110 | 112 | 0.036126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_195-14_0_8_line_117 |  | 111 | 112 | 0.035705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_195-14_0_8_line_118 |  | 111 | 113 | 0.007359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_195-14_0_8_line_119 |  | 114 | 115 | 0.051293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_195-14_0_8_line_120 |  | 115 | 128 | 0.017385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_195-14_0_8_line_121 |  | 115 | 127 | 0.02381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_195-14_0_8_line_122 |  | 116 | 117 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_195-14_0_8_line_123 |  | 117 | 118 | 0.0054804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_195-14_0_8_line_124 |  | 119 | 131 | 0.031767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_195-14_0_8_line_125 |  | 120 | 130 | 0.013595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_195-14_0_8_line_126 |  | 121 | 122 | 0.0095807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_195-14_0_8_line_127 |  | 121 | 123 | 0.027608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_195-14_0_8_line_128 |  | 122 | 124 | 0.03353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_195-14_0_8_line_129 |  | 124 | 125 | 0.14657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_195-14_0_8_line_130 |  | 125 | 126 | 0.055354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_195-14_0_8_line_131 |  | 126 | 134 | 0.043171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_195-14_0_8_line_132 |  | 129 | 130 | 0.019366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_195-14_0_8_line_133 |  | 131 | 133 | 0.0016661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_195-14_0_8_line_134 |  | 132 | 134 | 0.029076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_195-14_0_8_trafo_111 | 0.63 MVA 20/0.4 kV | 136 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2689433.9801 | 1246054.1487 | 2689433.588 | 1246049.7051
1 | 2689434.6869 | 1246062.1571 | 2689433.9801 | 1246054.1487
2 | 2689432.2608 | 1246034.6666 | 2689433.588 | 1246049.7051
3 | 2689434.6869 | 1246062.1571 | 2689438.6913 | 1246060.6608 | 2689450.3573 | 1246054.8279
4 | 2689434.6869 | 1246062.1571 | 2689435.9569 | 1246077.4921
5 | 2689432.2608 | 1246034.6666 | 2689436.2343 | 1246033.2144 | 2689448.6707 | 1246026.7466
6 | 2689432.2608 | 1246034.6666 | 2689431.2092 | 1246021.6807
7 | 2689450.3573 | 1246054.8279 | 2689456.5765 | 1246051.7183
8 | 2689437.026 | 1246090.4024 | 2689435.9569 | 1246077.4921
9 | 2689448.6707 | 1246026.7466 | 2689455.3867 | 1246023.2539
10 | 2689431.1086 | 1246020.4388 | 2689431.2092 | 1246021.6807
11 | 2689462.7436 | 1246048.6348 | 2689456.5765 | 1246051.7183
12 | 2689437.026 | 1246090.4024 | 2689451.3799 | 1246083.2066
13 | 2689429.9934 | 1246006.6671 | 2689431.1086 | 1246020.4388
14 | 2689462.7436 | 1246048.6348 | 2689468.6333 | 1246045.69 | 2689468.9995 | 1246045.5086
15 | 2689451.3799 | 1246083.2066 | 2689453.9636 | 1246081.9113
16 | 2689460.0745 | 1246078.8478 | 2689466.8619 | 1246075.4452
17 | 2689460.0745 | 1246078.8478 | 2689458.2892 | 1246079.7428
18 | 2689477.2881 | 1246070.4725 | 2689469.1307 | 1246074.3078 | 2689466.8619 | 1246075.4452
19 | 2689458.2892 | 1246079.7428 | 2689453.9636 | 1246081.9113
20 | 2689477.2881 | 1246070.4725 | 2689490.0944 | 1246069.9986 | 2689495.0158 | 1246069.8172 | 2689496.2066 | 1246069.0691
21 | 2689477.2881 | 1246070.4725 | 2689481.069 | 1246088.7876 | 2689487.6012 | 1246108.0228 | 2689499.4833 | 1246102.1977 | 2689501.3181 | 1246101.2802
22 | 2689498.9015 | 1246067.376 | 2689496.2066 | 1246069.0691
23 | 2689501.3181 | 1246101.2802 | 2689506.3173 | 1246110.9518 | 2689508.1007 | 1246112.9357 | 2689515.9957 | 1246117.9698 | 2689524.1676 | 1246120.0017
24 | 2689461.8175 | 1246142.3484 | 2689460.5696 | 1246142.4296 | 2689461.2346 | 1246128.9073 | 2689461.3443 | 1246114.6317 | 2689487.6012 | 1246108.0228 | 2689499.4833 | 1246102.1977 | 2689501.3181 | 1246101.2802
25 | 2689478.811 | 1246044.1646 | 2689479.0244 | 1246040.5429
26 | 2689478.811 | 1246044.1646 | 2689494.0548 | 1246045.8959 | 2689502.6179 | 1246040.5432
27 | 2689479.0244 | 1246040.5429 | 2689477.4158 | 1246024.9737
28 | 2689479.0244 | 1246040.5429 | 2689468.9995 | 1246045.5086
29 | 2689502.6179 | 1246040.5432 | 2689521.7866 | 1246028.5611
30 | 2689498.9015 | 1246067.376 | 2689510.5606 | 1246060.0513
31 | 2689538.7592 | 1246133.0579 | 2689532.6074 | 1246129.1622 | 2689534.6562 | 1246126.0797 | 2689528.1534 | 1246121.9117 | 2689525.8037 | 1246120.4085 | 2689524.1676 | 1246120.0017
32 | 2689461.8175 | 1246142.3484 | 2689461.8092 | 1246153.9125 | 2689460.8257 | 1246154.9985 | 2689461.1192 | 1246173.0942 | 2689471.2145 | 1246173.0131
33 | 2689461.8175 | 1246142.3484 | 2689472.5473 | 1246142.2769
34 | 2689457.3539 | 1246163.2634 | 2689457.9193 | 1246152.3304 | 2689459.9153 | 1246152.2382 | 2689459.7006 | 1246142.4388 | 2689460.5696 | 1246142.4296 | 2689461.8175 | 1246142.3484
35 | 2689457.3539 | 1246163.2634 | 2689457.5748 | 1246173.6523 | 2689451.1975 | 1246195.2167 | 2689440.1521 | 1246195.5902
36 | 2689457.3539 | 1246163.2634 | 2689445.8271 | 1246163.5787
37 | 2689431.7599 | 1246165.5125 | 2689443.7092 | 1246165.2369 | 2689445.8271 | 1246163.5787
38 | 2689431.7599 | 1246165.5125 | 2689428.3574 | 1246173.6895 | 2689419.0188 | 1246173.7983
39 | 2689477.4158 | 1246024.9737 | 2689487.6853 | 1246023.383 | 2689497.2569 | 1246017.2165
40 | 2689514.6778 | 1246057.4647 | 2689510.5606 | 1246060.0513
41 | 2689538.7592 | 1246133.0579 | 2689531.6943 | 1246143.8261
42 | 2689557.6615 | 1246073.6544 | 2689555.1608 | 1246074.0086
43 | 2689577.3878 | 1246078.7339 | 2689568.3219 | 1246074.6828 | 2689557.6615 | 1246073.6544
44 | 2689474.1732 | 1245903.0332 | 2689479.1465 | 1245900.4503
45 | 2689472.4085 | 1245903.9497 | 2689474.1732 | 1245903.0332
46 | 2689480.2255 | 1245899.89 | 2689479.1465 | 1245900.4503
47 | 2689472.4085 | 1245903.9497 | 2689468.0048 | 1245906.2367
48 | 2689480.2255 | 1245899.89 | 2689486.6828 | 1245896.5365
49 | 2689468.0048 | 1245906.2367 | 2689465.6724 | 1245907.448
50 | 2689500.346 | 1245889.4406 | 2689486.6828 | 1245896.5365
51 | 2689461.7939 | 1245909.4623 | 2689465.6724 | 1245907.448
52 | 2689519.9073 | 1245912.4974 | 2689507.6417 | 1245896.656 | 2689500.346 | 1245889.4406
53 | 2689459.0806 | 1245910.8714 | 2689461.7939 | 1245909.4623
54 | 2689497.0731 | 1245925.5515 | 2689499.4124 | 1245924.2525 | 2689515.199 | 1245915.5731 | 2689519.9073 | 1245912.4974
55 | 2689519.9073 | 1245912.4974 | 2689530.0407 | 1245903.4213 | 2689538.8491 | 1245892.0235 | 2689540.4685 | 1245889.2705
56 | 2689511.0919 | 1245948.3801 | 2689497.0731 | 1245925.5515
57 | 2689439.5823 | 1245892.4485 | 2689456.6355 | 1245883.8716
58 | 2689439.5823 | 1245892.4485 | 2689438.3945 | 1245878.7496
59 | 2689439.5823 | 1245892.4485 | 2689440.3608 | 1245902.0739
60 | 2689511.0919 | 1245948.3801 | 2689520.2001 | 1245962.15
61 | 2689541.7964 | 1245945.0076 | 2689543.1615 | 1245947.1743
62 | 2689541.7964 | 1245945.0076 | 2689557.3182 | 1245932.8116
63 | 2689520.2001 | 1245962.15 | 2689543.1615 | 1245947.1743
64 | 2689543.1615 | 1245947.1743 | 2689557.1584 | 1245969.2828
65 | 2689560.8402 | 1245930.0442 | 2689557.3182 | 1245932.8116
66 | 2689440.6349 | 1245905.4633 | 2689440.3608 | 1245902.0739
67 | 2689441.7983 | 1245919.8469 | 2689440.6349 | 1245905.4633
68 | 2689441.7983 | 1245919.8469 | 2689455.476 | 1245912.7435
69 | 2689441.7983 | 1245919.8469 | 2689442.8272 | 1245930.0362
70 | 2689459.0806 | 1245910.8714 | 2689455.476 | 1245912.7435
71 | 2689443.0945 | 1245932.6837 | 2689442.8272 | 1245930.0362
72 | 2689438.3945 | 1245878.7496 | 2689437.278 | 1245865.8724
73 | 2689443.7112 | 1245938.7899 | 2689443.0945 | 1245932.6837
74 | 2689443.7112 | 1245938.7899 | 2689440.2425 | 1245938.8265
75 | 2689428.0885 | 1245986.5477 | 2689428.7978 | 1245994.0386
76 | 2689426.8717 | 1245973.6954 | 2689428.0885 | 1245986.5477
77 | 2689429.9934 | 1246006.6671 | 2689428.7978 | 1245994.0386
78 | 2689426.8717 | 1245973.6954 | 2689424.8167 | 1245972.1855 | 2689419.2803 | 1245964.0404
79 | 2689429.9934 | 1246006.6671 | 2689434.1472 | 1246005.2842 | 2689446.3174 | 1245999.1478
80 | 2689419.2803 | 1245964.0404 | 2689421.7491 | 1245962.1651 | 2689423.7915 | 1245957.0031 | 2689433.1436 | 1245956.6216 | 2689434.8936 | 1245953.8126 | 2689440.8805 | 1245950.6227 | 2689440.2425 | 1245938.8265
81 | 2689496.2087 | 1245987.3068 | 2689498.1655 | 1245987.8145 | 2689511.8884 | 1245978.8735
82 | 2689496.2087 | 1245987.3068 | 2689495.0914 | 1245986.7451 | 2689489.286 | 1245977.6229
83 | 2689520.2001 | 1245962.15 | 2689525.27 | 1245970.1548 | 2689511.8884 | 1245978.8735
84 | 2689482.5518 | 1245967.0412 | 2689489.286 | 1245977.6229
85 | 2689497.2569 | 1246017.2165 | 2689516.2041 | 1246005.0099
86 | 2689480.6067 | 1245964.2542 | 2689482.5518 | 1245967.0412
87 | 2689796.4603 | 1246002.9895 | 2689822.3828 | 1246023.6791
88 | 2689831.4952 | 1246030.952 | 2689822.3828 | 1246023.6791
89 | 2689796.4603 | 1246002.9895 | 2689797.3897 | 1245980.6579
90 | 2689772.9916 | 1246016.5111 | 2689779.5802 | 1246009.5278 | 2689796.2234 | 1246007.1557 | 2689796.4603 | 1246002.9895
91 | 2689831.4952 | 1246030.952 | 2689832.8092 | 1246031.9949 | 2689840.0295 | 1246022.7509
92 | 2689797.8741 | 1245969.0189 | 2689797.3897 | 1245980.6579
93 | 2689757.8794 | 1246032.5388 | 2689772.9916 | 1246016.5111
94 | 2689791.8113 | 1245918.8451 | 2689797.5271 | 1245928.083 | 2689798.6421 | 1245937.7738 | 2689797.8741 | 1245969.0189
95 | 2689791.8113 | 1245918.8451 | 2689760.726 | 1245949.8423
96 | 2689753.7443 | 1245918.9135 | 2689773.9953 | 1245899.3609 | 2689791.8113 | 1245918.8451
97 | 2689757.8794 | 1246032.5388 | 2689753.7187 | 1246036.952
98 | 2689757.8794 | 1246032.5388 | 2689752.2619 | 1246026.794 | 2689751.4733 | 1246018.4981
99 | 2689756.2515 | 1246070.6872 | 2689752.5191 | 1246067.1948 | 2689747.997 | 1246062.9565 | 2689738.014 | 1246053.6096
100 | 2689756.2515 | 1246070.6872 | 2689755.1466 | 1246071.8047 | 2689728.8863 | 1246083.269
101 | 2689738.014 | 1246053.6096 | 2689753.7187 | 1246036.952
102 | 2689713.5199 | 1246089.9774 | 2689728.8863 | 1246083.269
103 | 2689713.5199 | 1246089.9774 | 2689715.4729 | 1246091.7305 | 2689721.6225 | 1246097.261 | 2689718.4826 | 1246098.5478
104 | 2689718.4826 | 1246098.5478 | 2689687.1125 | 1246111.3816
105 | 2689689.0689 | 1246071.5828 | 2689710.3672 | 1246091.1084 | 2689713.5199 | 1246089.9774
106 | 2689689.0689 | 1246071.5828 | 2689706.9903 | 1246051.9769
107 | 2689753.7443 | 1245918.9135 | 2689734.3576 | 1245937.3929
108 | 2689719.238 | 1245951.805 | 2689734.3576 | 1245937.3929
109 | 2689634.4064 | 1246080.9413 | 2689629.6804 | 1246074.6986 | 2689625.7425 | 1246066.7998 | 2689623.9485 | 1246061.5243 | 2689623.7484 | 1246060.3412
110 | 2689634.4064 | 1246080.9413 | 2689660.9295 | 1246052.4693
111 | 2689625.1975 | 1246025.8943 | 2689623.1717 | 1246056.9314 | 2689623.7484 | 1246060.3412
112 | 2689625.1975 | 1246025.8943 | 2689604.2047 | 1246043.6015
113 | 2689625.1975 | 1246025.8943 | 2689657.0336 | 1246000.8123
114 | 2689577.3878 | 1246078.7339 | 2689591.1337 | 1246059.5827 | 2689604.2047 | 1246043.6015
115 | 2689604.2047 | 1246043.6015 | 2689601.5792 | 1246039.3476 | 2689584.8301 | 1246012.241 | 2689579.2244 | 1246003.7055 | 2689575.5725 | 1245998.3686 | 2689574.7896 | 1245997.1319
116 | 2689685.4111 | 1245978.4553 | 2689657.0336 | 1246000.8123
117 | 2689713.4575 | 1245956.3591 | 2689685.4111 | 1245978.4553
118 | 2689719.238 | 1245951.805 | 2689713.4575 | 1245956.3591
119 | 2689579.5626 | 1245915.3334 | 2689600.7965 | 1245936.1808 | 2689604.5055 | 1245935.7365 | 2689616.9536 | 1245923.013
120 | 2689572.4191 | 1245903.5501 | 2689582.3918 | 1245913.1078 | 2689579.5626 | 1245915.3334
121 | 2689579.5626 | 1245915.3334 | 2689560.8402 | 1245930.0442
122 | 2689528.2348 | 1246048.9476 | 2689514.6778 | 1246057.4647
123 | 2689532.8754 | 1246046.0322 | 2689528.2348 | 1246048.9476
124 | 2689577.3878 | 1246078.7339 | 2689596.4433 | 1246090.7084 | 2689591.4666 | 1246098.5194
125 | 2689574.7896 | 1245997.1319 | 2689567.5173 | 1245985.6451
126 | 2689604.5757 | 1246137.264 | 2689599.4754 | 1246145.3742
127 | 2689619.2731 | 1246113.8929 | 2689604.5757 | 1246137.264
128 | 2689581.6259 | 1246173.7578 | 2689599.4754 | 1246145.3742
129 | 2689466.2971 | 1246250.5191 | 2689495.9982 | 1246234.4329 | 2689497.1882 | 1246232.6829 | 2689515.2758 | 1246221.1694 | 2689533.2481 | 1246217.7937 | 2689576.9816 | 1246191.1007 | 2689575.3811 | 1246186.0172 | 2689575.7941 | 1246181.6868 | 2689577.6935 | 1246177.4901 | 2689581.6259 | 1246173.7578
130 | 2689466.2971 | 1246250.5191 | 2689466.9789 | 1246243.8911 | 2689485.3697 | 1246225.299 | 2689486.5827 | 1246222.026 | 2689497.336 | 1246210.8799 | 2689499.1479 | 1246207.8142
131 | 2689515.7443 | 1246168.1368 | 2689505.3997 | 1246197.2358 | 2689499.1479 | 1246207.8142
132 | 2689557.1584 | 1245969.2828 | 2689567.5173 | 1245985.6451
133 | 2689591.4666 | 1246098.5194 | 2689590.5714 | 1246099.9245
134 | 2689531.6943 | 1246143.8261 | 2689515.7443 | 1246168.1368 | 2689515.7443 | 1246168.1368

## bus_geodata
| x | y | coords
0 | 2689433.9801 | 1246054.1487
1 | 2689433.588 | 1246049.7051
2 | 2689434.6869 | 1246062.1571
3 | 2689432.2608 | 1246034.6666
4 | 2689450.3573 | 1246054.8279
5 | 2689435.9569 | 1246077.4921
6 | 2689448.6707 | 1246026.7466
7 | 2689431.2092 | 1246021.6807
8 | 2689456.5765 | 1246051.7183
9 | 2689437.026 | 1246090.4024
10 | 2689455.3867 | 1246023.2539
11 | 2689431.1086 | 1246020.4388
12 | 2689462.7436 | 1246048.6348
13 | 2689451.3799 | 1246083.2066
14 | 2689460.0745 | 1246078.8478
15 | 2689466.8619 | 1246075.4452
16 | 2689458.2892 | 1246079.7428
17 | 2689477.2881 | 1246070.4725
18 | 2689453.9636 | 1246081.9113
19 | 2689496.2066 | 1246069.0691
20 | 2689501.3181 | 1246101.2802
21 | 2689478.811 | 1246044.1646
22 | 2689479.0244 | 1246040.5429
23 | 2689502.6179 | 1246040.5432
24 | 2689498.9015 | 1246067.376
25 | 2689524.1676 | 1246120.0017
26 | 2689461.8175 | 1246142.3484
27 | 2689457.3539 | 1246163.2634
28 | 2689440.1521 | 1246195.5902
29 | 2689445.8271 | 1246163.5787
30 | 2689471.2145 | 1246173.0131
31 | 2689472.5473 | 1246142.2769
32 | 2689431.7599 | 1246165.5125
33 | 2689419.0188 | 1246173.7983
34 | 2689477.4158 | 1246024.9737
35 | 2689468.9995 | 1246045.5086
36 | 2689521.7866 | 1246028.5611
37 | 2689510.5606 | 1246060.0513
38 | 2689538.7592 | 1246133.0579
39 | 2689555.1608 | 1246074.0086
40 | 2689557.6615 | 1246073.6544
41 | 2689474.1732 | 1245903.0332
42 | 2689479.1465 | 1245900.4503
43 | 2689472.4085 | 1245903.9497
44 | 2689480.2255 | 1245899.89
45 | 2689468.0048 | 1245906.2367
46 | 2689486.6828 | 1245896.5365
47 | 2689465.6724 | 1245907.448
48 | 2689500.346 | 1245889.4406
49 | 2689461.7939 | 1245909.4623
50 | 2689519.9073 | 1245912.4974
51 | 2689497.0731 | 1245925.5515
52 | 2689540.4685 | 1245889.2705
53 | 2689456.6355 | 1245883.8716
54 | 2689439.5823 | 1245892.4485
55 | 2689511.0919 | 1245948.3801
56 | 2689541.7964 | 1245945.0076
57 | 2689543.1615 | 1245947.1743
58 | 2689557.3182 | 1245932.8116
59 | 2689440.6349 | 1245905.4633
60 | 2689440.3608 | 1245902.0739
61 | 2689441.7983 | 1245919.8469
62 | 2689455.476 | 1245912.7435
63 | 2689442.8272 | 1245930.0362
64 | 2689438.3945 | 1245878.7496
65 | 2689459.0806 | 1245910.8714
66 | 2689443.0945 | 1245932.6837
67 | 2689437.278 | 1245865.8724
68 | 2689443.7112 | 1245938.7899
69 | 2689428.0885 | 1245986.5477
70 | 2689428.7978 | 1245994.0386
71 | 2689426.8717 | 1245973.6954
72 | 2689429.9934 | 1246006.6671
73 | 2689419.2803 | 1245964.0404
74 | 2689446.3174 | 1245999.1478
75 | 2689440.2425 | 1245938.8265
76 | 2689496.2087 | 1245987.3068
77 | 2689511.8884 | 1245978.8735
78 | 2689489.286 | 1245977.6229
79 | 2689520.2001 | 1245962.15
80 | 2689497.2569 | 1246017.2165
81 | 2689482.5518 | 1245967.0412
82 | 2689516.2041 | 1246005.0099
83 | 2689822.3828 | 1246023.6791
84 | 2689796.4603 | 1246002.9895
85 | 2689831.4952 | 1246030.952
86 | 2689797.3897 | 1245980.6579
87 | 2689772.9916 | 1246016.5111
88 | 2689840.0295 | 1246022.7509
89 | 2689797.8741 | 1245969.0189
90 | 2689791.8113 | 1245918.8451
91 | 2689757.8794 | 1246032.5388
92 | 2689756.2515 | 1246070.6872
93 | 2689738.014 | 1246053.6096
94 | 2689728.8863 | 1246083.269
95 | 2689718.4826 | 1246098.5478
96 | 2689713.5199 | 1246089.9774
97 | 2689687.1125 | 1246111.3816
98 | 2689689.0689 | 1246071.5828
99 | 2689760.726 | 1245949.8423
100 | 2689753.7443 | 1245918.9135
101 | 2689751.4733 | 1246018.4981
102 | 2689753.7187 | 1246036.952
103 | 2689706.9903 | 1246051.9769
104 | 2689734.3576 | 1245937.3929
105 | 2689634.4064 | 1246080.9413
106 | 2689623.7484 | 1246060.3412
107 | 2689660.9295 | 1246052.4693
108 | 2689625.1975 | 1246025.8943
109 | 2689604.2047 | 1246043.6015
110 | 2689657.0336 | 1246000.8123
111 | 2689713.4575 | 1245956.3591
112 | 2689685.4111 | 1245978.4553
113 | 2689719.238 | 1245951.805
114 | 2689616.9536 | 1245923.013
115 | 2689579.5626 | 1245915.3334
116 | 2689514.6778 | 1246057.4647
117 | 2689528.2348 | 1246048.9476
118 | 2689532.8754 | 1246046.0322
119 | 2689577.3878 | 1246078.7339
120 | 2689574.7896 | 1245997.1319
121 | 2689604.5757 | 1246137.264
122 | 2689599.4754 | 1246145.3742
123 | 2689619.2731 | 1246113.8929
124 | 2689581.6259 | 1246173.7578
125 | 2689466.2971 | 1246250.5191
126 | 2689499.1479 | 1246207.8142
127 | 2689560.8402 | 1245930.0442
128 | 2689572.4191 | 1245903.5501
129 | 2689557.1584 | 1245969.2828
130 | 2689567.5173 | 1245985.6451
131 | 2689591.4666 | 1246098.5194
132 | 2689531.6943 | 1246143.8261
133 | 2689590.5714 | 1246099.9245
134 | 2689515.7443 | 1246168.1368
135 | 2689480.6067 | 1245964.2542
136 | 2689604.2047 | 1246043.6015

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97828 | -0.41673 | 0.007593 | 0.001903
1 | 0.97845 | -0.41339 | 0.0020856 | 0.0005227
2 | 0.97798 | -0.42246 | 0 | 0
3 | 0.97903 | -0.40197 | 0 | 0
4 | 0.97753 | -0.43144 | 0.0019022 | 0.00047674
5 | 0.97752 | -0.43146 | 0.0021224 | 0.00053192
6 | 0.97896 | -0.40335 | 0.0019848 | 0.00049743
7 | 0.97955 | -0.39187 | 0.0021661 | 0.00054288
8 | 0.97736 | -0.43481 | 0.0018965 | 0.0004753
9 | 0.97714 | -0.43891 | 0 | 0
10 | 0.97895 | -0.40365 | 0.0021729 | 0.00054458
11 | 0.9796 | -0.3909 | 0.0077503 | 0.0019424
12 | 0.9772 | -0.43791 | 0.0018586 | 0.00046582
13 | 0.97667 | -0.44816 | 0.0021956 | 0.00055026
14 | 0.9764 | -0.45356 | 0.0019652 | 0.00049253
15 | 0.97619 | -0.45762 | 0.002221 | 0.00055663
16 | 0.97645 | -0.45247 | 0.0020426 | 0.00051192
17 | 0.97588 | -0.4637 | 0 | 0
18 | 0.97659 | -0.44979 | 0.0027915 | 0.00069961
19 | 0.97552 | -0.47073 | 0.0030906 | 0.00077457
20 | 0.97468 | -0.48728 | 0 | 0
21 | 0.9768 | -0.44576 | 0 | 0
22 | 0.97684 | -0.44505 | 0 | 0
23 | 0.97655 | -0.4507 | 0.0050736 | 0.0012716
24 | 0.97547 | -0.47172 | 0.0031448 | 0.00078816
25 | 0.97431 | -0.49451 | 0.0058157 | 0.0014576
26 | 0.97171 | -0.54581 | 0 | 0
27 | 0.97108 | -0.55827 | 0 | 0
28 | 0.97069 | -0.56601 | 0.0095278 | 0.0023879
29 | 0.97089 | -0.56202 | 0.0096679 | 0.002423
30 | 0.97141 | -0.55179 | 0.0078664 | 0.0019715
31 | 0.97162 | -0.54769 | 0.0095319 | 0.0023889
32 | 0.97078 | -0.56417 | 0 | 0
33 | 0.97065 | -0.56683 | 0.007926 | 0.0019864
34 | 0.97669 | -0.44794 | 0 | 0
35 | 0.97705 | -0.44081 | 0.0020275 | 0.00050815
36 | 0.97643 | -0.453 | 0.0055604 | 0.0013936
37 | 0.9753 | -0.47521 | 0.0030983 | 0.0007765
38 | 0.97407 | -0.49925 | 0 | 0
39 | 0.99794 | -0.038951 | 0.0029993 | 0.00075171
40 | 0.99795 | -0.038818 | 0 | 0
41 | 0.98679 | -0.25163 | 0.0014117 | 0.00035379
42 | 0.98708 | -0.24598 | 0.0015407 | 0.00038614
43 | 0.98668 | -0.25363 | 0.0015199 | 0.00038093
44 | 0.98714 | -0.24474 | 0.0013803 | 0.00034595
45 | 0.98643 | -0.25857 | 0.0013258 | 0.00033227
46 | 0.98753 | -0.23731 | 0.0015353 | 0.00038479
47 | 0.98629 | -0.26118 | 0.0014999 | 0.0003759
48 | 0.98835 | -0.2215 | 0 | 0
49 | 0.98607 | -0.26548 | 0.0014657 | 0.00036734
50 | 0.98997 | -0.1905 | 0 | 0
51 | 0.99145 | -0.16223 | 0 | 0
52 | 0.98961 | -0.19747 | 0.012556 | 0.0031468
53 | 0.98454 | -0.29498 | 0.0015926 | 0.00039914
54 | 0.98457 | -0.29444 | 0 | 0
55 | 0.99296 | -0.13348 | 0.0079679 | 0.001997
56 | 0.99553 | -0.08466 | 0 | 0
57 | 0.99563 | -0.082635 | 0 | 0
58 | 0.99472 | -0.1003 | 0.0075572 | 0.001894
59 | 0.98471 | -0.29176 | 0.0015909 | 0.00039873
60 | 0.98466 | -0.29271 | 0.0055214 | 0.0013838
61 | 0.98493 | -0.28734 | 0 | 0
62 | 0.98571 | -0.27242 | 0.0013325 | 0.00033395
63 | 0.98446 | -0.29647 | 0.0013085 | 0.00032794
64 | 0.98447 | -0.2965 | 0.0014751 | 0.0003697
65 | 0.98591 | -0.26847 | 0.00142 | 0.00035589
66 | 0.98434 | -0.29883 | 0.0016302 | 0.00040856
67 | 0.98438 | -0.2981 | 0.006883 | 0.001725
68 | 0.98406 | -0.30423 | 0 | 0
69 | 0.98104 | -0.36286 | 0.0053251 | 0.0013346
70 | 0.98072 | -0.36911 | 0.0013735 | 0.00034422
71 | 0.98161 | -0.35183 | 0 | 0
72 | 0.98018 | -0.37958 | 0 | 0
73 | 0.98215 | -0.34127 | 0 | 0
74 | 0.98015 | -0.38012 | 0.0016374 | 0.00041038
75 | 0.9839 | -0.30729 | 0.0067892 | 0.0017015
76 | 0.99327 | -0.12768 | 0 | 0
77 | 0.99345 | -0.12423 | 0.0094383 | 0.0023655
78 | 0.99316 | -0.12993 | 0.0048346 | 0.0012117
79 | 0.99392 | -0.11523 | 0 | 0
80 | 0.97648 | -0.45197 | 0.004765 | 0.0011942
81 | 0.99309 | -0.13121 | 0 | 0
82 | 0.97637 | -0.45417 | 0.0053433 | 0.0013392
83 | 0.97529 | -0.47428 | 0.010955 | 0.0027457
84 | 0.97598 | -0.4607 | 0 | 0
85 | 0.97517 | -0.47672 | 0 | 0
86 | 0.97757 | -0.42964 | 0.01106 | 0.0027719
87 | 0.97445 | -0.4908 | 0 | 0
88 | 0.97503 | -0.47952 | 0.011409 | 0.0028593
89 | 0.97851 | -0.41115 | 0 | 0
90 | 0.98272 | -0.32923 | 0 | 0
91 | 0.97335 | -0.51251 | 0 | 0
92 | 0.97192 | -0.54068 | 0 | 0
93 | 0.97255 | -0.52819 | 0 | 0
94 | 0.97115 | -0.55583 | 0.009135 | 0.0022895
95 | 0.97077 | -0.56334 | 0 | 0
96 | 0.97087 | -0.56141 | 0 | 0
97 | 0.97054 | -0.56792 | 0.0072985 | 0.0018292
98 | 0.97055 | -0.5678 | 0 | 0
99 | 0.98261 | -0.33149 | 0.0028569 | 0.00071601
100 | 0.9873 | -0.24105 | 0 | 0
101 | 0.97311 | -0.51725 | 0.015749 | 0.0039471
102 | 0.97313 | -0.51674 | 0.010797 | 0.002706
103 | 0.97028 | -0.57307 | 0.010711 | 0.0026844
104 | 0.98955 | -0.19805 | 0.0026577 | 0.00066608
105 | 0.99723 | -0.052292 | 0 | 0
106 | 0.99734 | -0.050295 | 0.0026741 | 0.0006702
107 | 0.99706 | -0.055608 | 0.0048614 | 0.0012184
108 | 0.99757 | -0.045731 | 0 | 0
109 | 0.99835 | -0.031174 | 0 | 0
110 | 0.99543 | -0.086211 | 0.0047453 | 0.0011893
111 | 0.99199 | -0.15158 | 0.0044565 | 0.0011169
112 | 0.9936 | -0.12093 | 0.011953 | 0.0029958
113 | 0.99135 | -0.16367 | 0 | 0
114 | 0.99335 | -0.1268 | 0.014736 | 0.0036933
115 | 0.99404 | -0.11345 | 0 | 0
116 | 0.97525 | -0.47617 | 0.0031222 | 0.00078249
117 | 0.97513 | -0.4784 | 0.0030427 | 0.00076257
118 | 0.97511 | -0.47886 | 0.004573 | 0.0011461
119 | 0.998 | -0.037738 | 0 | 0
120 | 1 | 0 | -0.46413 | -0.11897
121 | 0.97094 | -0.56119 | 0.0041825 | 0.0010482
122 | 0.971 | -0.55986 | 0.018312 | 0.0045894
123 | 0.97085 | -0.56288 | 0.0033139 | 0.00083054
124 | 0.97181 | -0.54387 | 0 | 0
125 | 0.97299 | -0.52062 | 0 | 0
126 | 0.97332 | -0.51405 | 0.0086401 | 0.0021654
127 | 0.99456 | -0.10325 | 0.013154 | 0.0032967
128 | 0.99388 | -0.11639 | 0.0095593 | 0.0023958
129 | 0.99754 | -0.046402 | 0.0049468 | 0.0012398
130 | 0.99898 | -0.019258 | 0.0041862 | 0.0010492
131 | 0.99785 | -0.040791 | 0.0028452 | 0.00071308
132 | 0.97394 | -0.50188 | 0.0046093 | 0.0011552
133 | 0.99784 | -0.040869 | 0.0026468 | 0.00066334
134 | 0.97367 | -0.5072 | 0.0053774 | 0.0013477
135 | 0.99307 | -0.13156 | 0.0057592 | 0.0014434
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.16491 | -0.041575 | 0.16493 | 0.041592 | 2.6331e-05 | 1.6627e-05 | 0.25092 | 0.25092 | 0.25092 | 0.97828 | -0.41673 | 0.97845 | -0.41339 | 17.2335
1 | 0.15731 | 0.039672 | -0.15727 | -0.039645 | 4.3186e-05 | 2.7235e-05 | 0.23937 | 0.23937 | 0.23937 | 0.97828 | -0.41673 | 0.97798 | -0.42246 | 16.4402
2 | -0.16702 | -0.042114 | 0.16711 | 0.042172 | 9.1377e-05 | 5.7722e-05 | 0.25409 | 0.25409 | 0.25409 | 0.97845 | -0.41339 | 0.97903 | -0.40197 | 17.4513
3 | 0.028462 | 0.0071448 | -0.02845 | -0.0071372 | 1.2181e-05 | 7.5787e-06 | 0.043309 | 0.04331 | 0.04331 | 0.97798 | -0.42246 | 0.97753 | -0.43144 | 11.8982
4 | 0.12881 | 0.0325 | -0.12875 | -0.032465 | 5.5452e-05 | 3.4717e-05 | 0.19606 | 0.19606 | 0.19606 | 0.97798 | -0.42246 | 0.97752 | -0.43146 | 13.4657
5 | 0.004158 | 0.0010419 | -0.0041577 | -0.0010419 | 2.733e-07 | -5.4545e-08 | 0.0063196 | 0.0063196 | 0.0063196 | 0.97903 | -0.40197 | 0.97896 | -0.40335 | 1.7362
6 | -0.17127 | -0.043214 | 0.17135 | 0.043266 | 8.2828e-05 | 5.2354e-05 | 0.26041 | 0.26041 | 0.26041 | 0.97903 | -0.40197 | 0.97955 | -0.39187 | 17.8853
7 | 0.026548 | 0.0066605 | -0.026543 | -0.0066578 | 4.2588e-06 | 2.6385e-06 | 0.040414 | 0.040414 | 0.040414 | 0.97753 | -0.43144 | 0.97736 | -0.43481 | 11.1027
8 | 0.12663 | 0.031933 | -0.12658 | -0.031905 | 4.5159e-05 | 2.8252e-05 | 0.19283 | 0.19283 | 0.19283 | 0.97752 | -0.43146 | 0.97714 | -0.43891 | 13.2438
9 | 0.0021729 | 0.00054451 | -0.0021729 | -0.00054458 | 3.0967e-08 | -7.5357e-08 | 0.0033028 | 0.0033028 | 0.0033028 | 0.97896 | -0.40335 | 0.97895 | -0.40365 | 0.90738
10 | -0.17352 | -0.043809 | 0.17352 | 0.043814 | 8.1231e-06 | 5.136e-06 | 0.2637 | 0.2637 | 0.2637 | 0.97955 | -0.39187 | 0.9796 | -0.3909 | 18.1113
11 | 0.024647 | 0.0061825 | -0.024643 | -0.0061803 | 3.6412e-06 | 2.244e-06 | 0.037527 | 0.037527 | 0.037527 | 0.97736 | -0.43481 | 0.9772 | -0.43791 | 10.3095
12 | 0.12658 | 0.031905 | -0.12653 | -0.03187 | 5.5972e-05 | 3.5018e-05 | 0.19283 | 0.19283 | 0.19283 | 0.97714 | -0.43891 | 0.97667 | -0.44816 | 13.2439
13 | -0.18127 | -0.045757 | 0.18137 | 0.045819 | 9.8296e-05 | 6.2213e-05 | 0.27547 | 0.27547 | 0.27547 | 0.9796 | -0.3909 | 0.98018 | -0.37958 | 18.9198
14 | 0.022785 | 0.0057145 | -0.022781 | -0.0057125 | 3.1571e-06 | 1.933e-06 | 0.034696 | 0.034696 | 0.034696 | 0.9772 | -0.43791 | 0.97705 | -0.44081 | 9.532
15 | 0.12433 | 0.03132 | -0.12432 | -0.031314 | 9.7289e-06 | 6.0818e-06 | 0.18949 | 0.18949 | 0.18949 | 0.97667 | -0.44816 | 0.97659 | -0.44979 | 13.0141
16 | 0.1175 | 0.029596 | -0.11748 | -0.029582 | 2.2838e-05 | 1.4237e-05 | 0.17912 | 0.17912 | 0.17912 | 0.9764 | -0.45356 | 0.97619 | -0.45762 | 12.3025
17 | -0.11947 | -0.030089 | 0.11947 | 0.030093 | 6.2101e-06 | 3.8745e-06 | 0.18212 | 0.18212 | 0.18212 | 0.9764 | -0.45356 | 0.97645 | -0.45247 | 12.5082
18 | 0.11526 | 0.029025 | -0.11522 | -0.029004 | 3.3448e-05 | 2.0829e-05 | 0.17574 | 0.17574 | 0.17574 | 0.97619 | -0.45762 | 0.97588 | -0.4637 | 12.07
19 | -0.12152 | -0.030604 | 0.12153 | 0.030614 | 1.5564e-05 | 9.719e-06 | 0.18523 | 0.18523 | 0.18523 | 0.97645 | -0.45247 | 0.97659 | -0.44979 | 12.722
20 | 0.020083 | 0.0050368 | -0.020076 | -0.0050327 | 6.7331e-06 | 4.0701e-06 | 0.030623 | 0.030623 | 0.030623 | 0.97588 | -0.4637 | 0.97552 | -0.47073 | 8.413
21 | 0.095142 | 0.023968 | -0.095035 | -0.023902 | 0.0001072 | 6.5899e-05 | 0.14512 | 0.14512 | 0.14512 | 0.97588 | -0.4637 | 0.97468 | -0.48728 | 9.9668
22 | 0.016985 | 0.0042582 | -0.016985 | -0.0042577 | 8.0117e-07 | 4.7302e-07 | 0.025909 | 0.025909 | 0.025909 | 0.97552 | -0.47073 | 0.97547 | -0.47172 | 7.1179
23 | 0.050362 | 0.012649 | -0.050345 | -0.01264 | 1.7373e-05 | 9.5569e-06 | 0.076897 | 0.076897 | 0.076897 | 0.97468 | -0.48728 | 0.97431 | -0.49451 | 5.2814
24 | 0.044672 | 0.011252 | -0.044548 | -0.011173 | 0.00012466 | 7.8893e-05 | 0.06822 | 0.068221 | 0.068221 | 0.97468 | -0.48728 | 0.97171 | -0.54581 | 18.742
25 | -0.010637 | -0.0026665 | 0.010638 | 0.0026667 | 3.5725e-07 | 1.8322e-07 | 0.016204 | 0.016204 | 0.016204 | 0.9768 | -0.44576 | 0.97684 | -0.44505 | 4.4518
26 | 0.010637 | 0.0026665 | -0.010635 | -0.0026653 | 2.5051e-06 | 1.2849e-06 | 0.016204 | 0.016205 | 0.016205 | 0.9768 | -0.44576 | 0.97655 | -0.4507 | 4.4518
27 | 0.010112 | 0.0025351 | -0.010111 | -0.0025344 | 1.3929e-06 | 6.9551e-07 | 0.015404 | 0.015404 | 0.015404 | 0.97684 | -0.44505 | 0.97669 | -0.44794 | 4.2319
28 | -0.02075 | -0.0052018 | 0.020754 | 0.0052044 | 4.1915e-06 | 2.5425e-06 | 0.031609 | 0.031609 | 0.031609 | 0.97684 | -0.44505 | 0.97705 | -0.44081 | 8.6837
29 | 0.0055611 | 0.0013937 | -0.0055604 | -0.0013936 | 6.0868e-07 | 1.0677e-07 | 0.0084736 | 0.0084737 | 0.0084737 | 0.97655 | -0.4507 | 0.97643 | -0.453 | 2.328
30 | 0.01384 | 0.0034695 | -0.013838 | -0.0034682 | 2.3014e-06 | 1.301e-06 | 0.021112 | 0.021112 | 0.021112 | 0.97547 | -0.47172 | 0.9753 | -0.47521 | 5.8
31 | 0.044529 | 0.011182 | -0.044519 | -0.011177 | 1.0054e-05 | 5.28e-06 | 0.068015 | 0.068016 | 0.068016 | 0.97431 | -0.49451 | 0.97407 | -0.49925 | 4.6714
32 | 0.0078687 | 0.0019724 | -0.0078664 | -0.0019715 | 2.243e-06 | 9.2538e-07 | 0.01205 | 0.01205 | 0.01205 | 0.97171 | -0.54581 | 0.97141 | -0.55179 | 3.3104
33 | 0.0095328 | 0.0023893 | -0.0095319 | -0.0023889 | 8.5491e-07 | 4.1463e-07 | 0.014598 | 0.014598 | 0.014598 | 0.97171 | -0.54581 | 0.97162 | -0.54769 | 4.0104
34 | 0.027146 | 0.0068117 | -0.02713 | -0.0068017 | 1.6117e-05 | 1.0007e-05 | 0.041573 | 0.041573 | 0.041573 | 0.97171 | -0.54581 | 0.97108 | -0.55827 | 11.4212
35 | 0.0095313 | 0.0023896 | -0.0095278 | -0.0023879 | 3.5143e-06 | 1.7059e-06 | 0.014605 | 0.014606 | 0.014606 | 0.97108 | -0.55827 | 0.97069 | -0.56601 | 4.0125
36 | 0.017599 | 0.0044121 | -0.017596 | -0.0044102 | 3.1448e-06 | 1.87e-06 | 0.026968 | 0.026968 | 0.026968 | 0.97108 | -0.55827 | 0.97089 | -0.56202 | 7.4087
37 | 0.0079278 | 0.0019872 | -0.007927 | -0.0019869 | 8.1065e-07 | 3.3776e-07 | 0.012151 | 0.012151 | 0.012151 | 0.97089 | -0.56202 | 0.97078 | -0.56417 | 3.3381
38 | 0.007927 | 0.0019869 | -0.007926 | -0.0019864 | 1.0074e-06 | 4.1979e-07 | 0.012151 | 0.012151 | 0.012151 | 0.97078 | -0.56417 | 0.97065 | -0.56683 | 3.3381
39 | 0.010111 | 0.0025344 | -0.010109 | -0.0025335 | 1.9379e-06 | 9.6777e-07 | 0.015404 | 0.015404 | 0.015404 | 0.97669 | -0.44794 | 0.97648 | -0.45197 | 4.232
40 | 0.010739 | 0.0026917 | -0.010739 | -0.0026915 | 4.8951e-07 | 2.5261e-07 | 0.016385 | 0.016385 | 0.016385 | 0.9753 | -0.47521 | 0.97525 | -0.47617 | 4.5014
41 | 0.044519 | 0.011177 | -0.044514 | -0.011174 | 5.5856e-06 | 2.9336e-06 | 0.068016 | 0.068016 | 0.068016 | 0.97407 | -0.49925 | 0.97394 | -0.50188 | 4.6714
42 | -0.0029993 | -0.00075171 | 0.0029994 | 0.00075168 | 1.8943e-08 | -2.0874e-08 | 0.0044723 | 0.0044723 | 0.0044723 | 0.99794 | -0.038951 | 0.99795 | -0.038818 | 1.2286
43 | -0.0029994 | -0.00075168 | 0.0029995 | 0.00075151 | 1.5438e-07 | -1.7014e-07 | 0.0044723 | 0.0044722 | 0.0044723 | 0.99795 | -0.038818 | 0.998 | -0.037738 | 1.2286
44 | -0.22771 | -0.057902 | 0.22777 | 0.057941 | 6.205e-05 | 3.9425e-05 | 0.34367 | 0.34367 | 0.34367 | 0.98679 | -0.25163 | 0.98708 | -0.24598 | 23.6034
45 | 0.22629 | 0.057548 | -0.22627 | -0.057534 | 2.1746e-05 | 1.3816e-05 | 0.34154 | 0.34154 | 0.34154 | 0.98679 | -0.25163 | 0.98668 | -0.25363 | 23.4572
46 | -0.22931 | -0.058327 | 0.22932 | 0.058336 | 1.3644e-05 | 8.6703e-06 | 0.34599 | 0.34599 | 0.34599 | 0.98708 | -0.24598 | 0.98714 | -0.24474 | 23.7629
47 | 0.22475 | 0.057153 | -0.2247 | -0.057119 | 5.3539e-05 | 3.4011e-05 | 0.33924 | 0.33924 | 0.33924 | 0.98668 | -0.25363 | 0.98643 | -0.25857 | 23.2998
48 | -0.2307 | -0.058682 | 0.23078 | 0.058735 | 8.2642e-05 | 5.2519e-05 | 0.34807 | 0.34807 | 0.34807 | 0.98714 | -0.24474 | 0.98753 | -0.23731 | 23.9058
49 | 0.22337 | 0.056787 | -0.22334 | -0.056769 | 2.8023e-05 | 1.78e-05 | 0.33724 | 0.33724 | 0.33724 | 0.98643 | -0.25857 | 0.98629 | -0.26118 | 23.1624
50 | -0.23232 | -0.059119 | 0.2325 | 0.059232 | 0.0001772 | 0.00011262 | 0.35038 | 0.35038 | 0.35038 | 0.98753 | -0.23731 | 0.98835 | -0.2215 | 24.0647
51 | 0.22184 | 0.056393 | -0.2218 | -0.056364 | 4.5976e-05 | 2.9201e-05 | 0.33498 | 0.33498 | 0.33498 | 0.98629 | -0.26118 | 0.98607 | -0.26548 | 23.007
52 | -0.2325 | -0.059232 | 0.23285 | 0.059453 | 0.00034826 | 0.00022133 | 0.35038 | 0.35038 | 0.35038 | 0.98835 | -0.2215 | 0.98997 | -0.1905 | 24.0647
53 | 0.22033 | 0.055997 | -0.2203 | -0.055977 | 3.1741e-05 | 2.0158e-05 | 0.33277 | 0.33277 | 0.33277 | 0.98607 | -0.26548 | 0.98591 | -0.26847 | 22.8551
54 | -0.24541 | -0.062602 | 0.24574 | 0.062816 | 0.00033566 | 0.00021347 | 0.36926 | 0.36926 | 0.36926 | 0.98997 | -0.1905 | 0.99145 | -0.16223 | 25.3613
55 | 0.01256 | 0.003149 | -0.012556 | -0.0031468 | 4.1705e-06 | 2.2681e-06 | 0.018879 | 0.018879 | 0.018879 | 0.98997 | -0.1905 | 0.98961 | -0.19747 | 5.1866
56 | -0.24574 | -0.062816 | 0.24608 | 0.063033 | 0.00034219 | 0.00021762 | 0.36926 | 0.36926 | 0.36926 | 0.99145 | -0.16223 | 0.99296 | -0.13348 | 25.3612
57 | -0.0015926 | -0.00039914 | 0.0015926 | 0.00039892 | 4.147e-08 | -2.1621e-07 | 0.002407 | 0.0024069 | 0.002407 | 0.98454 | -0.29498 | 0.98457 | -0.29444 | 0.66126
58 | 0.0083595 | 0.0020953 | -0.0083587 | -0.0020949 | 8.2306e-07 | 3.5191e-07 | 0.012634 | 0.012634 | 0.012634 | 0.98457 | -0.29444 | 0.98447 | -0.2965 | 3.4709
59 | -0.0099521 | -0.0024942 | 0.0099529 | 0.0024946 | 8.1924e-07 | 4.0149e-07 | 0.015041 | 0.015041 | 0.015041 | 0.98457 | -0.29444 | 0.98466 | -0.29271 | 4.1321
60 | -0.25405 | -0.06503 | 0.25428 | 0.065173 | 0.00022473 | 0.00014297 | 0.3812 | 0.3812 | 0.3812 | 0.99296 | -0.13348 | 0.99392 | -0.11523 | 26.1813
61 | -0.045068 | -0.011318 | 0.045073 | 0.01132 | 4.3557e-06 | 2.7544e-06 | 0.067372 | 0.067372 | 0.067372 | 0.99553 | -0.08466 | 0.99563 | -0.082635 | 18.5087
62 | 0.045068 | 0.011318 | -0.045035 | -0.011296 | 3.36e-05 | 2.1247e-05 | 0.067372 | 0.067372 | 0.067372 | 0.99553 | -0.08466 | 0.99472 | -0.1003 | 18.5087
63 | 0.27475 | 0.070477 | -0.27432 | -0.070201 | 0.00043371 | 0.00027615 | 0.41121 | 0.41121 | 0.41121 | 0.99563 | -0.082635 | 0.99392 | -0.11523 | 28.2423
64 | -0.31983 | -0.081797 | 0.32039 | 0.082155 | 0.00056186 | 0.00035823 | 0.47858 | 0.47858 | 0.47858 | 0.99563 | -0.082635 | 0.99754 | -0.046402 | 32.8694
65 | 0.037478 | 0.0094023 | -0.037472 | -0.009399 | 5.2802e-06 | 3.3212e-06 | 0.056067 | 0.056067 | 0.056067 | 0.99472 | -0.1003 | 0.99456 | -0.10325 | 15.403
66 | 0.015475 | 0.0038788 | -0.015474 | -0.0038784 | 6.9733e-07 | 4.0304e-07 | 0.023385 | 0.023385 | 0.023385 | 0.98471 | -0.29176 | 0.98466 | -0.29271 | 6.4244
67 | -0.017066 | -0.0042775 | 0.01707 | 0.0042796 | 3.599e-06 | 2.1197e-06 | 0.025789 | 0.025789 | 0.025789 | 0.98471 | -0.29176 | 0.98493 | -0.28734 | 7.0849
68 | -0.21735 | -0.055161 | 0.21751 | 0.05526 | 0.00015603 | 9.9075e-05 | 0.32862 | 0.32862 | 0.32862 | 0.98493 | -0.28734 | 0.98571 | -0.27242 | 22.5698
69 | 0.20028 | 0.050882 | -0.20019 | -0.050826 | 8.8046e-05 | 5.5828e-05 | 0.30283 | 0.30283 | 0.30283 | 0.98493 | -0.28734 | 0.98446 | -0.29647 | 20.7986
70 | -0.21884 | -0.055594 | 0.21888 | 0.055621 | 4.1626e-05 | 2.6433e-05 | 0.33063 | 0.33063 | 0.33063 | 0.98571 | -0.27242 | 0.98591 | -0.26847 | 22.7079
71 | 0.19889 | 0.050498 | -0.19886 | -0.050484 | 2.258e-05 | 1.4316e-05 | 0.30085 | 0.30085 | 0.30085 | 0.98446 | -0.29647 | 0.98434 | -0.29883 | 20.6627
72 | 0.0068835 | 0.0017252 | -0.006883 | -0.001725 | 5.2471e-07 | 1.7148e-07 | 0.010404 | 0.010404 | 0.010404 | 0.98447 | -0.2965 | 0.98438 | -0.2981 | 2.8584
73 | 0.19723 | 0.050075 | -0.19718 | -0.050043 | 5.1227e-05 | 3.2473e-05 | 0.29839 | 0.29839 | 0.29839 | 0.98434 | -0.29883 | 0.98406 | -0.30423 | 20.4935
74 | 0.19718 | 0.050043 | -0.19715 | -0.050024 | 2.8954e-05 | 1.8354e-05 | 0.29839 | 0.29839 | 0.29839 | 0.98406 | -0.30423 | 0.9839 | -0.30729 | 20.4935
75 | 0.18453 | 0.046667 | -0.18448 | -0.046632 | 5.5321e-05 | 3.5026e-05 | 0.28004 | 0.28004 | 0.28004 | 0.98104 | -0.36286 | 0.98072 | -0.36911 | 19.2337
76 | -0.18986 | -0.048001 | 0.18996 | 0.048065 | 0.00010047 | 6.3648e-05 | 0.28812 | 0.28812 | 0.28812 | 0.98104 | -0.36286 | 0.98161 | -0.35183 | 19.7884
77 | 0.1831 | 0.046287 | -0.18301 | -0.046229 | 9.188e-05 | 5.8163e-05 | 0.27796 | 0.27796 | 0.27796 | 0.98072 | -0.36911 | 0.98018 | -0.37958 | 19.0906
78 | -0.18996 | -0.048065 | 0.19005 | 0.048126 | 9.6385e-05 | 6.106e-05 | 0.28812 | 0.28812 | 0.28812 | 0.98161 | -0.35183 | 0.98215 | -0.34127 | 19.7884
79 | 0.0016375 | 0.00041018 | -0.0016374 | -0.00041038 | 4.1728e-08 | -2.0026e-07 | 0.0024858 | 0.0024859 | 0.0024859 | 0.98018 | -0.37958 | 0.98015 | -0.38012 | 0.68293
80 | -0.19005 | -0.048126 | 0.19036 | 0.048323 | 0.00031066 | 0.0001968 | 0.28812 | 0.28812 | 0.28812 | 0.98215 | -0.34127 | 0.9839 | -0.30729 | 19.7884
81 | -0.010595 | -0.0026557 | 0.010597 | 0.0026566 | 1.7385e-06 | 8.7444e-07 | 0.015873 | 0.015873 | 0.015873 | 0.99327 | -0.12768 | 0.99345 | -0.12423 | 4.3607
82 | 0.010595 | 0.0026557 | -0.010594 | -0.0026552 | 1.1398e-06 | 5.7334e-07 | 0.015873 | 0.015873 | 0.015873 | 0.99327 | -0.12768 | 0.99316 | -0.12993 | 4.3607
83 | -0.020035 | -0.0050221 | 0.020044 | 0.0050272 | 8.5938e-06 | 5.1704e-06 | 0.03001 | 0.03001 | 0.03001 | 0.99345 | -0.12423 | 0.99392 | -0.11523 | 8.2445
84 | 0.0057597 | 0.0014435 | -0.0057593 | -0.0014434 | 3.5027e-07 | 6.1875e-08 | 0.0086295 | 0.0086296 | 0.0086296 | 0.99316 | -0.12993 | 0.99309 | -0.13121 | 2.3708
85 | 0.0053439 | 0.0013392 | -0.0053433 | -0.0013392 | 5.6048e-07 | 7.6791e-08 | 0.0081432 | 0.0081433 | 0.0081433 | 0.97648 | -0.45197 | 0.97637 | -0.45417 | 2.2372
86 | 0.0057593 | 0.0014434 | -0.0057592 | -0.0014434 | 9.4809e-08 | 1.6752e-08 | 0.0086296 | 0.0086296 | 0.0086296 | 0.99309 | -0.13121 | 0.99307 | -0.13156 | 2.3708
87 | -0.022367 | -0.0056065 | 0.022381 | 0.0056153 | 1.4484e-05 | 8.8557e-06 | 0.034126 | 0.034126 | 0.034126 | 0.97529 | -0.47428 | 0.97598 | -0.4607 | 9.3752
88 | 0.011411 | 0.0028608 | -0.01141 | -0.0028601 | 1.3254e-06 | 7.0277e-07 | 0.017411 | 0.017411 | 0.017411 | 0.97529 | -0.47428 | 0.97517 | -0.47672 | 4.7832
89 | -0.07628 | -0.019201 | 0.076394 | 0.019274 | 0.00011342 | 7.2312e-05 | 0.11633 | 0.11633 | 0.11633 | 0.97598 | -0.4607 | 0.97757 | -0.42964 | 31.9587
90 | 0.053899 | 0.013586 | -0.053821 | -0.013537 | 7.7505e-05 | 4.9221e-05 | 0.082204 | 0.082204 | 0.082204 | 0.97598 | -0.4607 | 0.97445 | -0.4908 | 22.5836
91 | 0.01141 | 0.0028601 | -0.011409 | -0.0028593 | 1.5241e-06 | 8.0819e-07 | 0.017411 | 0.017411 | 0.017411 | 0.97517 | -0.47672 | 0.97503 | -0.47952 | 4.7833
92 | -0.087453 | -0.022045 | 0.087531 | 0.022095 | 7.7464e-05 | 4.9431e-05 | 0.13316 | 0.13316 | 0.13316 | 0.97757 | -0.42964 | 0.97851 | -0.41115 | 36.5836
93 | 0.053821 | 0.013537 | -0.053766 | -0.013501 | 5.5752e-05 | 3.5408e-05 | 0.082204 | 0.082204 | 0.082204 | 0.97445 | -0.4908 | 0.97335 | -0.51251 | 22.5836
94 | -0.087531 | -0.022095 | 0.087876 | 0.022315 | 0.00034494 | 0.00022011 | 0.13316 | 0.13316 | 0.13316 | 0.97851 | -0.41115 | 0.98272 | -0.32923 | 36.5836
95 | 0.0028572 | 0.00071565 | -0.0028569 | -0.00071601 | 3.0769e-07 | -3.5845e-07 | 0.0043262 | 0.0043264 | 0.0043264 | 0.98272 | -0.32923 | 0.98261 | -0.33149 | 1.1886
96 | -0.090733 | -0.023031 | 0.09112 | 0.023277 | 0.0003867 | 0.0002468 | 0.13749 | 0.13749 | 0.13749 | 0.98272 | -0.32923 | 0.9873 | -0.24105 | 37.772
97 | 0.038013 | 0.0095521 | -0.038005 | -0.0095473 | 7.6835e-06 | 4.8421e-06 | 0.058122 | 0.058122 | 0.058122 | 0.97335 | -0.51251 | 0.97313 | -0.51674 | 15.9675
98 | 0.015753 | 0.0039492 | -0.015749 | -0.0039471 | 3.5599e-06 | 2.075e-06 | 0.024083 | 0.024083 | 0.024083 | 0.97335 | -0.51251 | 0.97311 | -0.51725 | 6.6161
99 | -0.027177 | -0.006822 | 0.027193 | 0.006832 | 1.6198e-05 | 1.0057e-05 | 0.041612 | 0.041612 | 0.041612 | 0.97192 | -0.54068 | 0.97255 | -0.52819 | 11.4319
100 | 0.027177 | 0.006822 | -0.027157 | -0.0068098 | 1.9626e-05 | 1.2187e-05 | 0.041612 | 0.041612 | 0.041612 | 0.97192 | -0.54068 | 0.97115 | -0.55583 | 11.4319
101 | -0.027193 | -0.006832 | 0.027208 | 0.0068413 | 1.4865e-05 | 9.2296e-06 | 0.041612 | 0.041612 | 0.041612 | 0.97255 | -0.52819 | 0.97313 | -0.51674 | 11.4318
102 | 0.018022 | 0.0045203 | -0.018017 | -0.0045175 | 4.7949e-06 | 2.8614e-06 | 0.027615 | 0.027615 | 0.027615 | 0.97115 | -0.55583 | 0.97087 | -0.56141 | 7.5866
103 | -0.0073 | -0.0018298 | 0.0073007 | 0.00183 | 6.7089e-07 | 2.5269e-07 | 0.01119 | 0.01119 | 0.01119 | 0.97077 | -0.56334 | 0.97087 | -0.56141 | 3.0741
104 | 0.0073 | 0.0018298 | -0.0072985 | -0.0018292 | 1.5915e-06 | 5.9958e-07 | 0.01119 | 0.01119 | 0.01119 | 0.97077 | -0.56334 | 0.97054 | -0.56792 | 3.0741
105 | 0.010717 | 0.0026875 | -0.010713 | -0.0026858 | 3.2623e-06 | 1.6893e-06 | 0.016426 | 0.016426 | 0.016426 | 0.97087 | -0.56141 | 0.97055 | -0.5678 | 4.5126
106 | 0.010713 | 0.0026858 | -0.010711 | -0.0026844 | 2.6876e-06 | 1.3919e-06 | 0.016426 | 0.016426 | 0.016426 | 0.97055 | -0.5678 | 0.97028 | -0.57307 | 4.5126
107 | -0.09112 | -0.023277 | 0.09131 | 0.023399 | 0.00018986 | 0.00012117 | 0.13749 | 0.13749 | 0.13749 | 0.9873 | -0.24105 | 0.98955 | -0.19805 | 37.772
108 | -0.093967 | -0.024065 | 0.094124 | 0.024165 | 0.0001568 | 0.00010009 | 0.14149 | 0.14149 | 0.14149 | 0.98955 | -0.19805 | 0.99135 | -0.16367 | 38.8698
109 | -0.0048621 | -0.0012184 | 0.0048626 | 0.0012183 | 4.6241e-07 | -9.752e-09 | 0.0072549 | 0.0072548 | 0.0072549 | 0.99723 | -0.052292 | 0.99734 | -0.050295 | 1.9931
110 | 0.0048621 | 0.0012184 | -0.0048614 | -0.0012184 | 7.6805e-07 | -1.6038e-08 | 0.0072549 | 0.0072551 | 0.0072551 | 0.99723 | -0.052292 | 0.99706 | -0.055608 | 1.9932
111 | -0.0075367 | -0.0018885 | 0.0075384 | 0.0018891 | 1.6387e-06 | 5.9766e-07 | 0.011245 | 0.011244 | 0.011245 | 0.99734 | -0.050295 | 0.99757 | -0.045731 | 3.0892
112 | -0.12343 | -0.031748 | 0.12352 | 0.031802 | 8.7414e-05 | 5.4512e-05 | 0.18441 | 0.18441 | 0.18441 | 0.99757 | -0.045731 | 0.99835 | -0.031174 | 12.6654
113 | 0.1159 | 0.029859 | -0.11567 | -0.029714 | 0.00022787 | 0.00014478 | 0.17316 | 0.17316 | 0.17316 | 0.99757 | -0.045731 | 0.99543 | -0.086211 | 23.7863
114 | 0.0084949 | 0.0021291 | -0.0084923 | -0.002128 | 2.6559e-06 | 1.1223e-06 | 0.012662 | 0.012662 | 0.012662 | 0.99835 | -0.031174 | 0.998 | -0.037738 | 3.4785
115 | -0.13202 | -0.033931 | 0.13222 | 0.034057 | 0.00020027 | 0.00012529 | 0.19707 | 0.19707 | 0.19707 | 0.99835 | -0.031174 | 1 | 0 | 13.535
116 | 0.11092 | 0.028524 | -0.11074 | -0.028406 | 0.00018682 | 0.00011862 | 0.16607 | 0.16607 | 0.16607 | 0.99543 | -0.086211 | 0.9936 | -0.12093 | 22.812
117 | -0.098636 | -0.025317 | 0.098783 | 0.02541 | 0.00014698 | 9.3143e-05 | 0.14817 | 0.14817 | 0.14817 | 0.99199 | -0.15158 | 0.9936 | -0.12093 | 20.3531
118 | 0.094179 | 0.0242 | -0.094124 | -0.024165 | 5.5243e-05 | 3.526e-05 | 0.14149 | 0.14149 | 0.14149 | 0.99199 | -0.15158 | 0.99135 | -0.16367 | 38.8698
119 | -0.014736 | -0.0036933 | 0.014746 | 0.0036986 | 9.3731e-06 | 5.3343e-06 | 0.022075 | 0.022075 | 0.022075 | 0.99335 | -0.1268 | 0.99404 | -0.11345 | 6.0645
120 | 0.0095607 | 0.0023964 | -0.0095593 | -0.0023958 | 1.3354e-06 | 6.2931e-07 | 0.014312 | 0.014312 | 0.014312 | 0.99404 | -0.11345 | 0.99388 | -0.11639 | 3.9319
121 | -0.024306 | -0.0060951 | 0.024318 | 0.0061023 | 1.1822e-05 | 7.257e-06 | 0.036387 | 0.036386 | 0.036387 | 0.99404 | -0.11345 | 0.99456 | -0.10325 | 9.9963
122 | 0.0076166 | 0.001909 | -0.0076157 | -0.0019087 | 8.1085e-07 | 3.1919e-07 | 0.011621 | 0.011621 | 0.011621 | 0.97525 | -0.47617 | 0.97513 | -0.4784 | 3.1927
123 | 0.0045731 | 0.0011461 | -0.004573 | -0.0011461 | 1.0008e-07 | -4.3154e-09 | 0.0069783 | 0.0069783 | 0.0069783 | 0.97513 | -0.4784 | 0.97511 | -0.47886 | 1.9171
124 | 0.0054928 | 0.0013765 | -0.005492 | -0.0013764 | 7.99e-07 | 9.6325e-08 | 0.0081896 | 0.0081898 | 0.0081898 | 0.998 | -0.037738 | 0.99785 | -0.040791 | 2.2499
125 | 0.33026 | 0.084915 | -0.32995 | -0.084718 | 0.00030877 | 0.0001969 | 0.49219 | 0.49219 | 0.49219 | 1 | 0 | 0.99898 | -0.019258 | 33.8044
126 | -0.0074967 | -0.0018786 | 0.0074971 | 0.0018788 | 4.7423e-07 | 1.8501e-07 | 0.011489 | 0.011489 | 0.011489 | 0.97094 | -0.56119 | 0.971 | -0.55986 | 3.1563
127 | 0.0033141 | 0.00083036 | -0.0033139 | -0.00083054 | 2.6708e-07 | -1.7049e-07 | 0.005079 | 0.0050792 | 0.0050792 | 0.97094 | -0.56119 | 0.97085 | -0.56288 | 1.3954
128 | -0.025809 | -0.0064682 | 0.025829 | 0.0064804 | 1.9669e-05 | 1.2173e-05 | 0.039551 | 0.039551 | 0.039551 | 0.971 | -0.55986 | 0.97181 | -0.54387 | 10.8657
129 | -0.025829 | -0.0064804 | 0.025857 | 0.0064932 | 2.8657e-05 | 1.2886e-05 | 0.039551 | 0.039549 | 0.039551 | 0.97181 | -0.54387 | 0.97299 | -0.52062 | 3.6219
130 | -0.025857 | -0.0064932 | 0.025865 | 0.0064957 | 8.1166e-06 | 2.4437e-06 | 0.039549 | 0.039548 | 0.039549 | 0.97299 | -0.52062 | 0.97332 | -0.51405 | 2.7163
131 | -0.034506 | -0.0086611 | 0.034517 | 0.0086662 | 1.1265e-05 | 5.0623e-06 | 0.052757 | 0.052756 | 0.052757 | 0.97332 | -0.51405 | 0.97367 | -0.5072 | 3.6234
132 | -0.32534 | -0.083395 | 0.32576 | 0.083668 | 0.00042875 | 0.00027338 | 0.48596 | 0.48596 | 0.48596 | 0.99754 | -0.046402 | 0.99898 | -0.019258 | 33.3762
133 | 0.0026468 | 0.00066333 | -0.0026468 | -0.00066334 | 9.7332e-09 | -1.5535e-08 | 0.0039469 | 0.0039469 | 0.0039469 | 0.99785 | -0.040791 | 0.99784 | -0.040869 | 1.0843
134 | 0.039904 | 0.010019 | -0.039894 | -0.010014 | 1.0134e-05 | 5.039e-06 | 0.060974 | 0.060974 | 0.060974 | 0.97394 | -0.50188 | 0.97367 | -0.5072 | 4.1878

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47735 | 0.12229

## res_load
| p_mw | q_mvar
0 | 0.007593 | 0.001903
1 | 0.0020856 | 0.0005227
2 | 0.0019022 | 0.00047674
3 | 0.0021224 | 0.00053192
4 | 0.0019848 | 0.00049743
5 | 0.0021661 | 0.00054288
6 | 0.0018965 | 0.0004753
7 | 0.0021729 | 0.00054458
8 | 0.0077503 | 0.0019424
9 | 0.0018586 | 0.00046582
10 | 0.0021956 | 0.00055026
11 | 0.0019652 | 0.00049253
12 | 0.002221 | 0.00055663
13 | 0.0020426 | 0.00051192
14 | 0.0027915 | 0.00069961
15 | 0.0030906 | 0.00077457
16 | 0.0050736 | 0.0012716
17 | 0.0031448 | 0.00078816
18 | 0.0058157 | 0.0014576
19 | 0.0095278 | 0.0023879
20 | 0.0096679 | 0.002423
21 | 0.0078664 | 0.0019715
22 | 0.0095319 | 0.0023889
23 | 0.007926 | 0.0019864
24 | 0.0020275 | 0.00050815
25 | 0.0055604 | 0.0013936
26 | 0.0030983 | 0.0007765
27 | 0.0029993 | 0.00075171
28 | 0.0014117 | 0.00035379
29 | 0.0015407 | 0.00038614
30 | 0.0015199 | 0.00038093
31 | 0.0013803 | 0.00034595
32 | 0.0013258 | 0.00033227
33 | 0.0015353 | 0.00038479
34 | 0.0014999 | 0.0003759
35 | 0.0014657 | 0.00036734
36 | 0.012556 | 0.0031468
37 | 0.0015926 | 0.00039914
38 | 0.0079679 | 0.001997
39 | 0.0075572 | 0.001894
40 | 0.0015909 | 0.00039873
41 | 0.0055214 | 0.0013838
42 | 0.0013325 | 0.00033395
43 | 0.0013085 | 0.00032794
44 | 0.0014751 | 0.0003697
45 | 0.00142 | 0.00035589
46 | 0.0016302 | 0.00040856
47 | 0.006883 | 0.001725
48 | 0.0053251 | 0.0013346
49 | 0.0013735 | 0.00034422
50 | 0.0016374 | 0.00041038
51 | 0.0067892 | 0.0017015
52 | 0.0094383 | 0.0023655
53 | 0.0048346 | 0.0012117
54 | 0.004765 | 0.0011942
55 | 0.0053433 | 0.0013392
56 | 0.010955 | 0.0027457
57 | 0.01106 | 0.0027719
58 | 0.011409 | 0.0028593
59 | 0.009135 | 0.0022895
60 | 0.0072985 | 0.0018292
61 | 0.0028569 | 0.00071601
62 | 0.015749 | 0.0039471
63 | 0.010797 | 0.002706
64 | 0.010711 | 0.0026844
65 | 0.0026577 | 0.00066608
66 | 0.0026741 | 0.0006702
67 | 0.0048614 | 0.0012184
68 | 0.0047453 | 0.0011893
69 | 0.0044565 | 0.0011169
70 | 0.011953 | 0.0029958
71 | 0.014736 | 0.0036933
72 | 0.0031222 | 0.00078249
73 | 0.0030427 | 0.00076257
74 | 0.004573 | 0.0011461
75 | 0.013224 | 0.0033143
76 | 0.0041825 | 0.0010482
77 | 0.018312 | 0.0045894
78 | 0.0033139 | 0.00083054
79 | 0.0086401 | 0.0021654
80 | 0.013154 | 0.0032967
81 | 0.0095593 | 0.0023958
82 | 0.0049468 | 0.0012398
83 | 0.0041862 | 0.0010492
84 | 0.0028452 | 0.00071308
85 | 0.0046093 | 0.0011552
86 | 0.0026468 | 0.00066334
87 | 0.0053774 | 0.0013477
88 | 0.0057592 | 0.0014434

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1