## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_195-3_3_2_node_268 | 0.4 | n |  | TRUE
1 | bus_LV_195-3_3_2_node_40 | 0.4 | n |  | TRUE
2 | bus_LV_195-3_3_2_node_269 | 0.4 | n |  | TRUE
3 | bus_LV_195-3_3_2_node_27 | 0.4 | n |  | TRUE
4 | bus_LV_195-3_3_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_195-3_3_2_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_195-3_3_2_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_195-3_3_2_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_195-3_3_2_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_195-3_3_2_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_195-3_3_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_195-3_3_2_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_195-3_3_2_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_195-3_3_2_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_195-3_3_2_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_195-3_3_2_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_195-3_3_2_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_195-3_3_2_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_195-3_3_2_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_195-3_3_2_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_195-3_3_2_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_195-3_3_2_node_47 | 0.4 | n |  | TRUE
22 | bus_LV_195-3_3_2_node_48 | 0.4 | n |  | TRUE
23 | bus_LV_195-3_3_2_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_195-3_3_2_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_195-3_3_2_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_195-3_3_2_node_72 | 0.4 | n |  | TRUE
27 | bus_LV_195-3_3_2_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_195-3_3_2_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_195-3_3_2_node_58 | 0.4 | n |  | TRUE
30 | bus_MV_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_195-3_3_2_load_268 | 0 | 0.00070862 | 0.0001776 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_195-3_3_2_load_269 | 2 | 0.00074843 | 0.00018757 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_195-3_3_2_load_27 | 3 | 0.0058299 | 0.0014611 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_195-3_3_2_load_28 | 4 | 0.00188 | 0.00047117 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_195-3_3_2_load_31 | 6 | 0.0058329 | 0.0014619 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_195-3_3_2_load_32 | 7 | 0.0037151 | 0.0009311 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_195-3_3_2_load_33 | 9 | 0.001933 | 0.00048446 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_195-3_3_2_load_35 | 10 | 0.0039126 | 0.00098059 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_195-3_3_2_load_36 | 11 | 0.0061329 | 0.0015371 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_195-3_3_2_load_38 | 14 | 0.0019552 | 0.00049002 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_195-3_3_2_load_45 | 15 | 0.0031495 | 0.00078934 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_195-3_3_2_load_55 | 18 | 0.0008057 | 0.00020193 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_195-3_3_2_load_50 | 19 | 0.0019788 | 0.00049594 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_195-3_3_2_load_46 | 20 | 0.0014144 | 0.00035447 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_195-3_3_2_load_47 | 21 | 0.00091696 | 0.00022981 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_195-3_3_2_load_48 | 22 | 0.0010997 | 0.00027562 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_195-3_3_2_load_49 | 23 | 0.0013977 | 0.00035029 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_195-3_3_2_load_72 | 26 | 0.0037291 | 0.0009346 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_195-3_3_2_load_54 | 27 | 0.001568 | 0.00039298 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_195-3_3_2_load_58 | 29 | 0.0012108 | 0.00030345 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_195-3_3_2_line_0 |  | 0 | 1 | 0.014273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_195-3_3_2_line_1 |  | 0 | 2 | 0.024879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_195-3_3_2_line_2 |  | 1 | 16 | 0.243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_195-3_3_2_line_3 |  | 3 | 4 | 0.0056893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_195-3_3_2_line_4 |  | 3 | 5 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_195-3_3_2_line_5 |  | 5 | 6 | 0.017922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_195-3_3_2_line_6 |  | 5 | 7 | 0.016152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_195-3_3_2_line_7 |  | 6 | 8 | 0.021272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_195-3_3_2_line_8 |  | 8 | 10 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_195-3_3_2_line_9 |  | 8 | 11 | 0.017541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_195-3_3_2_line_10 |  | 8 | 9 | 0.012805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_195-3_3_2_line_11 |  | 10 | 12 | 0.01312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_195-3_3_2_line_12 |  | 11 | 13 | 0.070024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_195-3_3_2_line_13 |  | 12 | 14 | 0.030916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_195-3_3_2_line_14 |  | 13 | 17 | 0.003752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_195-3_3_2_line_15 |  | 14 | 15 | 0.00048627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_195-3_3_2_line_16 |  | 15 | 20 | 0.021202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_195-3_3_2_line_17 |  | 16 | 17 | 0.21312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_195-3_3_2_line_18 |  | 16 | 18 | 0.074145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_195-3_3_2_line_19 |  | 17 | 19 | 0.012289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_195-3_3_2_line_20 |  | 18 | 27 | 0.060894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_195-3_3_2_line_21 |  | 20 | 21 | 0.017079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_195-3_3_2_line_22 |  | 21 | 22 | 0.024003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_195-3_3_2_line_23 |  | 22 | 23 | 0.0045058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_195-3_3_2_line_24 |  | 23 | 24 | 0.22432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_195-3_3_2_line_25 |  | 24 | 25 | 0.12569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_195-3_3_2_line_26 |  | 25 | 26 | 0.063029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_195-3_3_2_line_27 |  | 27 | 28 | 0.0251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_195-3_3_2_line_28 |  | 28 | 29 | 0.047902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_195-3_3_2_trafo_37 | 0.63 MVA 20/0.4 kV | 30 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2691459.8764 | 1245420.2215 | 2691457.2491 | 1245413.209 | 2691460.4882 | 1245407.2479
1 | 2691460.4882 | 1245407.2479 | 2691472.3666 | 1245385.3873
2 | 2691338.0187 | 1245627.7999 | 2691345.6232 | 1245623.1913 | 2691352.2297 | 1245616.1766 | 2691364.7315 | 1245599.2564 | 2691376.0276 | 1245581.6394 | 2691380.5566 | 1245572.1465 | 2691395.9833 | 1245541.4834 | 2691430.2472 | 1245465.3097 | 2691435.2194 | 1245456.4908 | 2691446.3309 | 1245442.5405 | 2691458.4673 | 1245423.8803 | 2691459.8764 | 1245420.2215
3 | 2691468.2241 | 1245877.2381 | 2691473.9012 | 1245876.8669
4 | 2691454.3538 | 1245867.7838 | 2691468.2241 | 1245877.2381 | 2691468.2241 | 1245877.2381
5 | 2691454.3538 | 1245867.7838 | 2691463.639 | 1245852.4549
6 | 2691454.3538 | 1245867.7838 | 2691446.2177 | 1245881.7371
7 | 2691474.66 | 1245834.2606 | 2691463.639 | 1245852.4549
8 | 2691474.66 | 1245834.2606 | 2691482.821 | 1245821.7729
9 | 2691474.66 | 1245834.2606 | 2691459.1321 | 1245826.1017
10 | 2691474.66 | 1245834.2606 | 2691485.5442 | 1245841.0064
11 | 2691489.9981 | 1245810.7906 | 2691482.821 | 1245821.7729
12 | 2691409.8127 | 1245781.4879 | 2691411.8896 | 1245783.5103 | 2691411.5557 | 1245791.9337 | 2691450.0009 | 1245821.3039 | 2691459.1321 | 1245826.1017
13 | 2691489.9981 | 1245810.7906 | 2691495.6507 | 1245803.8948 | 2691501.6368 | 1245797.4156 | 2691511.371 | 1245788.5316
14 | 2691409.8127 | 1245781.4879 | 2691410.3234 | 1245777.7707
15 | 2691511.7302 | 1245788.2038 | 2691511.371 | 1245788.5316
16 | 2691511.7302 | 1245788.2038 | 2691516.7808 | 1245783.5944 | 2691529.5374 | 1245776.9916
17 | 2691338.0187 | 1245627.7999 | 2691362.7094 | 1245633.8735 | 2691386.0136 | 1245639.2032 | 2691391.0484 | 1245637.0903 | 2691396.0316 | 1245637.345 | 2691399.3001 | 1245640.0085 | 2691404.9966 | 1245640.0629 | 2691410.4743 | 1245642.5492 | 2691412.5881 | 1245647.5745 | 2691412.5695 | 1245651.7217 | 2691412.2497 | 1245653.8406 | 2691409.5923 | 1245662.9954 | 2691405.2138 | 1245680.8636 | 2691403.7216 | 1245693.35 | 2691403.3384 | 1245707.9106 | 2691410.7748 | 1245748.9894 | 2691410.7779 | 1245764.957 | 2691411.1831 | 1245771.5126 | 2691410.3234 | 1245777.7707
18 | 2691338.0187 | 1245627.7999 | 2691335.697 | 1245630.3772 | 2691333.2042 | 1245635.2313 | 2691328.6514 | 1245646.2806 | 2691309.2276 | 1245695.882
19 | 2691410.3234 | 1245777.7707 | 2691407.3663 | 1245777.4583 | 2691398.0936 | 1245776.5703
20 | 2691309.2276 | 1245695.882 | 2691306.0536 | 1245703.9872 | 2691296.1719 | 1245724.4839 | 2691288.1581 | 1245734.5792 | 2691279.8831 | 1245742.013 | 2691276.1228 | 1245745.9197
21 | 2691529.5374 | 1245776.9916 | 2691544.7055 | 1245769.1406
22 | 2691544.7055 | 1245769.1406 | 2691557.417 | 1245762.5612 | 2691563.9938 | 1245755.4452
23 | 2691567.0521 | 1245752.1362 | 2691563.9938 | 1245755.4452
24 | 2691708.8041 | 1245598.8321 | 2691690.0388 | 1245600.9881 | 2691670.2213 | 1245605.7076 | 2691651.258 | 1245611.3855 | 2691642.3345 | 1245622.1112 | 2691620.0652 | 1245675.474 | 2691581.846 | 1245736.1295 | 2691567.0521 | 1245752.1362
25 | 2691708.8041 | 1245598.8321 | 2691727.8105 | 1245601.6058 | 2691759.8587 | 1245600.0002 | 2691785.9697 | 1245593.3881 | 2691809.383 | 1245594.1065 | 2691821.4228 | 1245614.9085
26 | 2691821.4228 | 1245614.9085 | 2691822.4124 | 1245633.46 | 2691821.5908 | 1245657.2318 | 2691827.6515 | 1245674.7499 | 2691829.146 | 1245676.2652
27 | 2691257.2288 | 1245761.2345 | 2691259.7645 | 1245761.4403 | 2691265.0984 | 1245756.5743 | 2691273.1333 | 1245749.0256 | 2691276.1228 | 1245745.9197
28 | 2691257.2288 | 1245761.2345 | 2691243.5017 | 1245804.289 | 2691243.0623 | 1245806.9649

## bus_geodata
| x | y | coords
0 | 2691460.4882 | 1245407.2479
1 | 2691459.8764 | 1245420.2215
2 | 2691472.3666 | 1245385.3873
3 | 2691468.2241 | 1245877.2381
4 | 2691473.9012 | 1245876.8669
5 | 2691454.3538 | 1245867.7838
6 | 2691463.639 | 1245852.4549
7 | 2691446.2177 | 1245881.7371
8 | 2691474.66 | 1245834.2605
9 | 2691485.5442 | 1245841.0064
10 | 2691482.821 | 1245821.7729
11 | 2691459.1321 | 1245826.1017
12 | 2691489.9981 | 1245810.7906
13 | 2691409.8127 | 1245781.4879
14 | 2691511.371 | 1245788.5316
15 | 2691511.7302 | 1245788.2038
16 | 2691338.0187 | 1245627.7999
17 | 2691410.3234 | 1245777.7708
18 | 2691309.2276 | 1245695.882
19 | 2691398.0936 | 1245776.5703
20 | 2691529.5374 | 1245776.9916
21 | 2691544.7055 | 1245769.1406
22 | 2691563.9938 | 1245755.4452
23 | 2691567.0521 | 1245752.1362
24 | 2691708.8041 | 1245598.8321
25 | 2691821.4228 | 1245614.9085
26 | 2691829.146 | 1245676.2652
27 | 2691276.1228 | 1245745.9197
28 | 2691257.2288 | 1245761.2345
29 | 2691243.0623 | 1245806.9649
30 | 2691489.9981 | 1245810.7906

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99713 | -0.055321 | 0.00070862 | 0.0001776
1 | 0.99715 | -0.054957 | 0 | 0
2 | 0.99712 | -0.055648 | 0.00074843 | 0.00018757
3 | 0.99849 | -0.028984 | 0.0058299 | 0.0014611
4 | 0.99848 | -0.029171 | 0.00188 | 0.00047117
5 | 0.99861 | -0.026721 | 0 | 0
6 | 0.9988 | -0.023143 | 0.0058329 | 0.0014619
7 | 0.99856 | -0.02777 | 0.0037151 | 0.0009311
8 | 0.99913 | -0.01673 | 0 | 0
9 | 0.99911 | -0.017162 | 0.001933 | 0.00048446
10 | 0.99957 | -0.0083013 | 0.0039126 | 0.00098059
11 | 0.99892 | -0.020767 | 0.0061329 | 0.0015371
12 | 1 | 0 | -0.051629 | -0.012531
13 | 0.99847 | -0.029389 | 0 | 0
14 | 0.99962 | -0.0073739 | 0.0019552 | 0.00049002
15 | 0.99961 | -0.0074733 | 0.0031495 | 0.00078934
16 | 0.99747 | -0.048729 | 0 | 0
17 | 0.99845 | -0.029851 | 0 | 0
18 | 0.99723 | -0.053393 | 0.0008057 | 0.00020193
19 | 0.99843 | -0.030276 | 0.0019788 | 0.00049594
20 | 0.99945 | -0.010645 | 0.0014144 | 0.00035447
21 | 0.99934 | -0.012778 | 0.00091696 | 0.00022981
22 | 0.9992 | -0.015393 | 0.0010997 | 0.00027562
23 | 0.99918 | -0.015797 | 0.0013977 | 0.00035029
24 | 0.99842 | -0.030452 | 0 | 0
25 | 0.99799 | -0.03866 | 0 | 0
26 | 0.99778 | -0.042775 | 0.0037291 | 0.0009346
27 | 0.99708 | -0.056363 | 0.001568 | 0.00039298
28 | 0.99705 | -0.056897 | 0 | 0
29 | 0.997 | -0.057915 | 0.0012108 | 0.00030345
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0014571 | -0.00036485 | 0.0014571 | 0.00036468 | 2.5301e-08 | -1.6999e-07 | 0.0021742 | 0.0021742 | 0.0021742 | 0.99713 | -0.055321 | 0.99715 | -0.054957 | 0.59732
1 | 0.00074844 | 0.00018726 | -0.00074843 | -0.00018757 | 1.1637e-08 | -3.1708e-07 | 0.0011168 | 0.0011169 | 0.0011169 | 0.99713 | -0.055321 | 0.99712 | -0.055648 | 0.30684
2 | -0.0014571 | -0.00036468 | 0.0014575 | 0.00036179 | 4.3053e-07 | -2.8953e-06 | 0.0021742 | 0.0021731 | 0.0021742 | 0.99715 | -0.054957 | 0.99747 | -0.048729 | 0.5973
3 | 0.00188 | 0.00047111 | -0.00188 | -0.00047117 | 1.6747e-08 | -6.3696e-08 | 0.0028017 | 0.0028017 | 0.0028017 | 0.99849 | -0.028984 | 0.99848 | -0.029171 | 0.7697
4 | -0.0077099 | -0.0019322 | 0.0077108 | 0.0019325 | 8.3099e-07 | 3.1225e-07 | 0.01149 | 0.01149 | 0.01149 | 0.99849 | -0.028984 | 0.99861 | -0.026721 | 3.1565
5 | -0.011426 | -0.0028635 | 0.011428 | 0.0028646 | 1.9482e-06 | 1.0123e-06 | 0.017026 | 0.017026 | 0.017026 | 0.99861 | -0.026721 | 0.9988 | -0.023143 | 4.6774
6 | 0.0037153 | 0.00093101 | -0.0037151 | -0.0009311 | 1.8564e-07 | -9.2494e-08 | 0.0055361 | 0.0055362 | 0.0055362 | 0.99861 | -0.026721 | 0.99856 | -0.02777 | 1.5209
7 | -0.017261 | -0.0043264 | 0.017266 | 0.0043295 | 5.2751e-06 | 3.0976e-06 | 0.025716 | 0.025716 | 0.025716 | 0.9988 | -0.023143 | 0.99913 | -0.01673 | 7.0647
8 | -0.032364 | -0.0081074 | 0.032377 | 0.0081155 | 1.2996e-05 | 8.1222e-06 | 0.048199 | 0.048199 | 0.048199 | 0.99913 | -0.01673 | 0.99957 | -0.0083013 | 13.2416
9 | 0.013165 | 0.0032936 | -0.013163 | -0.0032922 | 2.5282e-06 | 1.3884e-06 | 0.019605 | 0.019605 | 0.019605 | 0.99913 | -0.01673 | 0.99892 | -0.020767 | 5.386
10 | 0.0019331 | 0.00048432 | -0.001933 | -0.00048446 | 3.98e-08 | -1.4223e-07 | 0.0028789 | 0.002879 | 0.002879 | 0.99913 | -0.01673 | 0.99911 | -0.017162 | 0.79092
11 | -0.03629 | -0.0090961 | 0.036304 | 0.0091051 | 1.4359e-05 | 9.0176e-06 | 0.054024 | 0.054024 | 0.054024 | 0.99957 | -0.0083013 | 1 | 0 | 14.8417
12 | 0.0070297 | 0.0017551 | -0.0070268 | -0.0017542 | 2.8782e-06 | 9.2576e-07 | 0.010469 | 0.01047 | 0.01047 | 0.99892 | -0.020767 | 0.99847 | -0.029389 | 2.8762
13 | 0.013675 | 0.0034255 | -0.01367 | -0.0034228 | 4.8003e-06 | 2.6668e-06 | 0.020348 | 0.020348 | 0.020348 | 1 | 0 | 0.99962 | -0.0073739 | 5.5902
14 | 0.0070268 | 0.0017542 | -0.0070266 | -0.0017542 | 1.5422e-07 | 4.963e-08 | 0.01047 | 0.01047 | 0.01047 | 0.99847 | -0.029389 | 0.99845 | -0.029851 | 2.8762
15 | 0.011715 | 0.0029328 | -0.011715 | -0.0029328 | 5.5448e-08 | 2.9113e-08 | 0.017438 | 0.017438 | 0.017438 | 0.99962 | -0.0073739 | 0.99961 | -0.0074733 | 4.7906
16 | 0.0085655 | 0.0021434 | -0.0085642 | -0.0021429 | 1.2924e-06 | 5.4923e-07 | 0.012749 | 0.012749 | 0.012749 | 0.99961 | -0.0074733 | 0.99945 | -0.010645 | 3.5026
17 | -0.0050432 | -0.0012582 | 0.0050478 | 0.0012583 | 4.5207e-06 | 1.0861e-07 | 0.0075214 | 0.0075205 | 0.0075214 | 0.99747 | -0.048729 | 0.99845 | -0.029851 | 2.0663
18 | 0.0035857 | 0.00089645 | -0.0035849 | -0.00089691 | 7.9539e-07 | -4.5854e-07 | 0.0053484 | 0.0053487 | 0.0053487 | 0.99747 | -0.048729 | 0.99723 | -0.053393 | 1.4694
19 | 0.0019789 | 0.0004958 | -0.0019788 | -0.00049594 | 4.0079e-08 | -1.3506e-07 | 0.0029491 | 0.0029491 | 0.0029491 | 0.99845 | -0.029851 | 0.99843 | -0.030276 | 0.8102
20 | 0.0027792 | 0.00069498 | -0.0027788 | -0.00069553 | 3.9264e-07 | -5.4306e-07 | 0.0041465 | 0.0041468 | 0.0041468 | 0.99723 | -0.053393 | 0.99708 | -0.056363 | 1.1392
21 | 0.0071498 | 0.0017884 | -0.0071491 | -0.0017882 | 7.256e-07 | 2.4059e-07 | 0.010644 | 0.010644 | 0.010644 | 0.99945 | -0.010645 | 0.99934 | -0.012778 | 2.9241
22 | 0.0062322 | 0.0015584 | -0.0062314 | -0.0015582 | 7.7492e-07 | 1.815e-07 | 0.0092785 | 0.0092786 | 0.0092786 | 0.99934 | -0.012778 | 0.9992 | -0.015393 | 2.5491
23 | 0.0051317 | 0.0012826 | -0.0051316 | -0.0012826 | 9.8649e-08 | 4.1178e-09 | 0.0076409 | 0.0076409 | 0.0076409 | 0.9992 | -0.015393 | 0.99918 | -0.015797 | 2.0991
24 | 0.0037339 | 0.00093227 | -0.0037313 | -0.00093354 | 2.6004e-06 | -1.2716e-06 | 0.0055594 | 0.0055605 | 0.0055605 | 0.99918 | -0.015797 | 0.99842 | -0.030452 | 1.5276
25 | 0.0037313 | 0.00093354 | -0.0037298 | -0.00093425 | 1.4575e-06 | -7.1028e-07 | 0.0055605 | 0.005561 | 0.005561 | 0.99842 | -0.030452 | 0.99799 | -0.03866 | 1.5278
26 | 0.0037298 | 0.00093425 | -0.0037291 | -0.0009346 | 7.3098e-07 | -3.5558e-07 | 0.005561 | 0.0055613 | 0.0055613 | 0.99799 | -0.03866 | 0.99778 | -0.042775 | 1.5278
27 | 0.0012109 | 0.00030255 | -0.0012108 | -0.00030286 | 3.0726e-08 | -3.0769e-07 | 0.0018067 | 0.0018068 | 0.0018068 | 0.99708 | -0.056363 | 0.99705 | -0.056897 | 0.49639
28 | 0.0012108 | 0.00030286 | -0.0012108 | -0.00030345 | 5.8651e-08 | -5.8716e-07 | 0.0018068 | 0.0018071 | 0.0018071 | 0.99705 | -0.056897 | 0.997 | -0.057915 | 0.49645

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.051629 | 0.012531

## res_load
| p_mw | q_mvar
0 | 0.00070862 | 0.0001776
1 | 0.00074843 | 0.00018757
2 | 0.0058299 | 0.0014611
3 | 0.00188 | 0.00047117
4 | 0.0058329 | 0.0014619
5 | 0.0037151 | 0.0009311
6 | 0.001933 | 0.00048446
7 | 0.0039126 | 0.00098059
8 | 0.0061329 | 0.0015371
9 | 0.0019552 | 0.00049002
10 | 0.0031495 | 0.00078934
11 | 0.0008057 | 0.00020193
12 | 0.0019788 | 0.00049594
13 | 0.0014144 | 0.00035447
14 | 0.00091696 | 0.00022981
15 | 0.0010997 | 0.00027562
16 | 0.0013977 | 0.00035029
17 | 0.0037291 | 0.0009346
18 | 0.001568 | 0.00039298
19 | 0.0012108 | 0.00030345

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1