## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_195-4_1_5_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_195-4_1_5_node_17 | 0.4 | n |  | TRUE
2 | bus_LV_195-4_1_5_node_241 | 0.4 | n |  | TRUE
3 | bus_LV_195-4_1_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_195-4_1_5_node_242 | 0.4 | n |  | TRUE
5 | bus_LV_195-4_1_5_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_195-4_1_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_195-4_1_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_195-4_1_5_node_113 | 0.4 | n |  | TRUE
9 | bus_LV_195-4_1_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_195-4_1_5_node_122 | 0.4 | n |  | TRUE
11 | bus_LV_195-4_1_5_node_144 | 0.4 | n |  | TRUE
12 | bus_LV_195-4_1_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_195-4_1_5_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_195-4_1_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_195-4_1_5_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_195-4_1_5_node_215 | 0.4 | n |  | TRUE
17 | bus_LV_195-4_1_5_node_216 | 0.4 | n |  | TRUE
18 | bus_LV_195-4_1_5_node_196 | 0.4 | n |  | TRUE
19 | bus_LV_195-4_1_5_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_195-4_1_5_node_213 | 0.4 | n |  | TRUE
21 | bus_LV_195-4_1_5_node_210 | 0.4 | n |  | TRUE
22 | bus_LV_195-4_1_5_node_212 | 0.4 | n |  | TRUE
23 | bus_LV_195-4_1_5_node_114 | 0.4 | n |  | TRUE
24 | bus_LV_195-4_1_5_node_204 | 0.4 | n |  | TRUE
25 | bus_LV_195-4_1_5_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_195-4_1_5_node_111 | 0.4 | n |  | TRUE
27 | bus_LV_195-4_1_5_node_112 | 0.4 | n |  | TRUE
28 | bus_LV_195-4_1_5_node_115 | 0.4 | n |  | TRUE
29 | bus_LV_195-4_1_5_node_130 | 0.4 | n |  | TRUE
30 | bus_LV_195-4_1_5_node_126 | 0.4 | n |  | TRUE
31 | bus_LV_195-4_1_5_node_117 | 0.4 | n |  | TRUE
32 | bus_LV_195-4_1_5_node_131 | 0.4 | n |  | TRUE
33 | bus_LV_195-4_1_5_node_118 | 0.4 | n |  | TRUE
34 | bus_LV_195-4_1_5_node_121 | 0.4 | n |  | TRUE
35 | bus_LV_195-4_1_5_node_119 | 0.4 | n |  | TRUE
36 | bus_LV_195-4_1_5_node_214 | 0.4 | n |  | TRUE
37 | bus_LV_195-4_1_5_node_240 | 0.4 | n |  | TRUE
38 | bus_LV_195-4_1_5_node_123 | 0.4 | n |  | TRUE
39 | bus_LV_195-4_1_5_node_211 | 0.4 | n |  | TRUE
40 | bus_LV_195-4_1_5_node_120 | 0.4 | n |  | TRUE
41 | bus_LV_195-4_1_5_node_207 | 0.4 | n |  | TRUE
42 | bus_LV_195-4_1_5_node_206 | 0.4 | n |  | TRUE
43 | bus_LV_195-4_1_5_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_195-4_1_5_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_195-4_1_5_node_97 | 0.4 | n |  | TRUE
46 | bus_LV_195-4_1_5_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_195-4_1_5_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_195-4_1_5_node_109 | 0.4 | n |  | TRUE
49 | bus_LV_195-4_1_5_node_110 | 0.4 | n |  | TRUE
50 | bus_LV_195-4_1_5_node_108 | 0.4 | n |  | TRUE
51 | bus_LV_195-4_1_5_node_208 | 0.4 | n |  | TRUE
52 | bus_LV_195-4_1_5_node_202 | 0.4 | n |  | TRUE
53 | bus_LV_195-4_1_5_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_195-4_1_5_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_195-4_1_5_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_195-4_1_5_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_195-4_1_5_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_195-4_1_5_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_195-4_1_5_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_195-4_1_5_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_195-4_1_5_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_195-4_1_5_node_66 | 0.4 | n |  | TRUE
63 | bus_LV_195-4_1_5_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_195-4_1_5_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_195-4_1_5_node_69 | 0.4 | n |  | TRUE
66 | bus_LV_195-4_1_5_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_195-4_1_5_node_73 | 0.4 | n |  | TRUE
68 | bus_LV_195-4_1_5_node_232 | 0.4 | n |  | TRUE
69 | bus_LV_195-4_1_5_node_239 | 0.4 | n |  | TRUE
70 | bus_LV_195-4_1_5_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_195-4_1_5_node_93 | 0.4 | n |  | TRUE
72 | bus_LV_195-4_1_5_node_75 | 0.4 | n |  | TRUE
73 | bus_LV_195-4_1_5_node_96 | 0.4 | n |  | TRUE
74 | bus_LV_195-4_1_5_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_195-4_1_5_node_79 | 0.4 | n |  | TRUE
76 | bus_LV_195-4_1_5_node_80 | 0.4 | n |  | TRUE
77 | bus_LV_195-4_1_5_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_195-4_1_5_node_103 | 0.4 | n |  | TRUE
79 | bus_LV_195-4_1_5_node_88 | 0.4 | n |  | TRUE
80 | bus_LV_195-4_1_5_node_230 | 0.4 | n |  | TRUE
81 | bus_LV_195-4_1_5_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_195-4_1_5_node_90 | 0.4 | n |  | TRUE
83 | bus_LV_195-4_1_5_node_107 | 0.4 | n |  | TRUE
84 | bus_LV_195-4_1_5_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_195-4_1_5_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_195-4_1_5_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_195-4_1_5_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_195-4_1_5_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_195-4_1_5_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_195-4_1_5_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_195-4_1_5_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_195-4_1_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_195-4_1_5_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_195-4_1_5_node_102 | 0.4 | n |  | TRUE
95 | bus_LV_195-4_1_5_node_98 | 0.4 | n |  | TRUE
96 | bus_LV_195-4_1_5_node_100 | 0.4 | n |  | TRUE
97 | bus_LV_195-4_1_5_node_236 | 0.4 | n |  | TRUE
98 | bus_LV_195-4_1_5_node_235 | 0.4 | n |  | TRUE
99 | bus_LV_195-4_1_5_node_227 | 0.4 | n |  | TRUE
100 | bus_LV_195-4_1_5_node_222 | 0.4 | n |  | TRUE
101 | bus_LV_195-4_1_5_node_209 | 0.4 | n |  | TRUE
102 | bus_LV_195-4_1_5_node_205 | 0.4 | n |  | TRUE
103 | bus_LV_195-4_1_5_node_203 | 0.4 | n |  | TRUE
104 | bus_LV_195-4_1_5_node_124 | 0.4 | n |  | TRUE
105 | bus_LV_195-4_1_5_node_129 | 0.4 | n |  | TRUE
106 | bus_LV_195-4_1_5_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_195-4_1_5_node_127 | 0.4 | n |  | TRUE
108 | bus_LV_195-4_1_5_node_128 | 0.4 | n |  | TRUE
109 | bus_LV_195-4_1_5_node_217 | 0.4 | n |  | TRUE
110 | bus_LV_195-4_1_5_node_218 | 0.4 | n |  | TRUE
111 | bus_LV_195-4_1_5_node_219 | 0.4 | n |  | TRUE
112 | bus_LV_195-4_1_5_node_220 | 0.4 | n |  | TRUE
113 | bus_LV_195-4_1_5_node_221 | 0.4 | n |  | TRUE
114 | bus_LV_195-4_1_5_node_223 | 0.4 | n |  | TRUE
115 | bus_LV_195-4_1_5_node_224 | 0.4 | n |  | TRUE
116 | bus_LV_195-4_1_5_node_225 | 0.4 | n |  | TRUE
117 | bus_LV_195-4_1_5_node_226 | 0.4 | n |  | TRUE
118 | bus_LV_195-4_1_5_node_233 | 0.4 | n |  | TRUE
119 | bus_LV_195-4_1_5_node_231 | 0.4 | n |  | TRUE
120 | bus_LV_195-4_1_5_node_228 | 0.4 | n |  | TRUE
121 | bus_LV_195-4_1_5_node_234 | 0.4 | n |  | TRUE
122 | bus_LV_195-4_1_5_node_238 | 0.4 | n |  | TRUE
123 | bus_LV_195-4_1_5_node_229 | 0.4 | n |  | TRUE
124 | bus_LV_195-4_1_5_node_237 | 0.4 | n |  | TRUE
125 | bus_MV_364_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_195-4_1_5_load_241 | 2 | 0.00073062 | 0.00018311 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_195-4_1_5_load_242 | 4 | 0.0027892 | 0.00069905 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_195-4_1_5_load_113 | 8 | 0.0033226 | 0.00083272 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_195-4_1_5_load_122 | 10 | 0.00099174 | 0.00024855 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_195-4_1_5_load_144 | 11 | 0.0041064 | 0.0010292 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_195-4_1_5_load_216 | 17 | 0.0010401 | 0.00026068 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_195-4_1_5_load_196 | 18 | 0.0030525 | 0.00076503 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_195-4_1_5_load_213 | 20 | 0.0021091 | 0.0005286 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_195-4_1_5_load_210 | 21 | 0.0031255 | 0.00078333 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_195-4_1_5_load_212 | 22 | 0.0065165 | 0.0016332 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_195-4_1_5_load_204 | 24 | 0.0045107 | 0.0011305 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_195-4_1_5_load_130 | 29 | 0.0053945 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_195-4_1_5_load_131 | 32 | 0.0022638 | 0.00056737 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_195-4_1_5_load_121 | 34 | 0.0030519 | 0.00076487 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_195-4_1_5_load_214 | 36 | 0.00056314 | 0.00014114 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_195-4_1_5_load_240 | 37 | 0.001014 | 0.00025413 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_195-4_1_5_load_123 | 38 | 0.0015399 | 0.00038593 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_195-4_1_5_load_211 | 39 | 0.0025867 | 0.00064829 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_195-4_1_5_load_120 | 40 | 0.00075441 | 0.00018907 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_195-4_1_5_load_207 | 41 | 0.008764 | 0.0021965 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_195-4_1_5_load_104 | 44 | 0.0029049 | 0.00072803 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_195-4_1_5_load_108 | 50 | 0.011407 | 0.0028589 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_195-4_1_5_load_208 | 51 | 0.0068256 | 0.0017107 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_195-4_1_5_load_202 | 52 | 0.0078381 | 0.0019644 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_195-4_1_5_load_56 | 53 | 0.0039713 | 0.0009953 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_195-4_1_5_load_57 | 55 | 0.0077229 | 0.0019355 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_195-4_1_5_load_61 | 58 | 0.0033031 | 0.00082785 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_195-4_1_5_load_64 | 61 | 0.0095998 | 0.0024059 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_195-4_1_5_load_66 | 62 | 0.005915 | 0.0014824 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_195-4_1_5_load_67 | 63 | 0.0094819 | 0.0023764 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_195-4_1_5_load_68 | 64 | 0.003355 | 0.00084085 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_195-4_1_5_load_232 | 68 | 0.0033545 | 0.00084071 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_195-4_1_5_load_239 | 69 | 0.0072028 | 0.0018052 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_195-4_1_5_load_93 | 71 | 0.010334 | 0.00259 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_195-4_1_5_load_75 | 72 | 0.0059395 | 0.0014886 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_195-4_1_5_load_79 | 75 | 0.0057348 | 0.0014373 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_195-4_1_5_load_74 | 77 | 0.0055386 | 0.0013881 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_195-4_1_5_load_103 | 78 | 0.0094812 | 0.0023762 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_195-4_1_5_load_230 | 80 | 0.0032547 | 0.0008157 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_195-4_1_5_load_90 | 82 | 0.0087594 | 0.0021953 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_195-4_1_5_load_107 | 83 | 0.0078921 | 0.0019779 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_195-4_1_5_load_81 | 84 | 0.0057316 | 0.0014365 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_195-4_1_5_load_84 | 86 | 0.0055228 | 0.0013841 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_195-4_1_5_load_91 | 87 | 0.0013823 | 0.00034642 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_195-4_1_5_load_83 | 89 | 0.0057714 | 0.0014464 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_195-4_1_5_load_89 | 90 | 0.0057746 | 0.0014472 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_195-4_1_5_load_94 | 92 | 0.002843 | 0.00071252 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_195-4_1_5_load_92 | 93 | 0.0060185 | 0.0015084 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_195-4_1_5_load_102 | 94 | 0.0094843 | 0.002377 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_195-4_1_5_load_98 | 95 | 0.0028342 | 0.00071032 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_195-4_1_5_load_100 | 96 | 0.0042663 | 0.0010692 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_195-4_1_5_load_236 | 97 | 0.0045154 | 0.0011317 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_195-4_1_5_load_235 | 98 | 0.0049203 | 0.0012332 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_195-4_1_5_load_227 | 99 | 0.0052415 | 0.0013137 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_195-4_1_5_load_209 | 101 | 0.0068246 | 0.0017104 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_195-4_1_5_load_205 | 102 | 0.0087552 | 0.0021943 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_195-4_1_5_load_203 | 103 | 0.0013696 | 0.00034325 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_195-4_1_5_load_124 | 104 | 0.0058855 | 0.0014751 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_195-4_1_5_load_129 | 105 | 0.0012785 | 0.00032042 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_195-4_1_5_load_125 | 106 | 0.00070289 | 0.00017616 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_195-4_1_5_load_128 | 108 | 0.0016839 | 0.00042201 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_195-4_1_5_load_217 | 109 | 0.0039464 | 0.00098905 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_195-4_1_5_load_218 | 110 | 0.0038525 | 0.00096553 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_195-4_1_5_load_220 | 112 | 0.0055426 | 0.0013891 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_195-4_1_5_load_223 | 114 | 0.0049764 | 0.0012472 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_195-4_1_5_load_224 | 115 | 0.0027122 | 0.00067973 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_195-4_1_5_load_225 | 116 | 0.0065318 | 0.001637 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_195-4_1_5_load_226 | 117 | 0.0078179 | 0.0019593 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_195-4_1_5_load_233 | 118 | 0.0031351 | 0.00078573 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_195-4_1_5_load_231 | 119 | 0.0036687 | 0.00091946 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_195-4_1_5_load_228 | 120 | 0.0027592 | 0.00069153 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_195-4_1_5_load_234 | 121 | 0.0041929 | 0.0010508 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_195-4_1_5_load_238 | 122 | 0.0047343 | 0.0011865 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_195-4_1_5_load_229 | 123 | 0.0029463 | 0.00073841 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_195-4_1_5_load_237 | 124 | 0.0041517 | 0.0010405 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_195-4_1_5_line_0 |  | 0 | 1 | 0.38911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_195-4_1_5_line_1 |  | 0 | 2 | 0.01742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_195-4_1_5_line_2 |  | 1 | 11 | 0.07418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_195-4_1_5_line_3 |  | 2 | 12 | 0.0313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_195-4_1_5_line_4 |  | 3 | 4 | 0.029232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_195-4_1_5_line_5 |  | 3 | 5 | 0.040658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_195-4_1_5_line_6 |  | 5 | 23 | 0.013898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_195-4_1_5_line_7 |  | 5 | 8 | 0.011822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_195-4_1_5_line_8 |  | 6 | 7 | 0.58858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_195-4_1_5_line_9 |  | 6 | 8 | 0.035082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_195-4_1_5_line_10 |  | 7 | 18 | 0.014717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_195-4_1_5_line_11 |  | 9 | 10 | 0.099296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_195-4_1_5_line_12 |  | 9 | 11 | 0.012944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_195-4_1_5_line_13 |  | 10 | 35 | 0.09761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_195-4_1_5_line_14 |  | 12 | 13 | 1.3998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_195-4_1_5_line_15 |  | 13 | 22 | 0.15776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_195-4_1_5_line_16 |  | 14 | 15 | 0.066091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_195-4_1_5_line_17 |  | 14 | 16 | 0.003352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_195-4_1_5_line_18 |  | 14 | 17 | 0.03009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_195-4_1_5_line_19 |  | 15 | 24 | 0.03323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_195-4_1_5_line_20 |  | 16 | 36 | 0.04112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_195-4_1_5_line_21 |  | 17 | 25 | 0.065681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_195-4_1_5_line_22 |  | 19 | 20 | 0.019514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_195-4_1_5_line_23 |  | 19 | 21 | 0.039892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_195-4_1_5_line_24 |  | 20 | 36 | 0.013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_195-4_1_5_line_25 |  | 21 | 39 | 0.0048338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_195-4_1_5_line_26 |  | 22 | 39 | 0.031051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_195-4_1_5_line_27 |  | 23 | 35 | 0.15587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_195-4_1_5_line_28 |  | 23 | 40 | 0.035556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_195-4_1_5_line_29 |  | 25 | 26 | 0.0796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_195-4_1_5_line_30 |  | 25 | 27 | 0.038898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_195-4_1_5_line_31 |  | 26 | 51 | 0.015981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_195-4_1_5_line_32 |  | 26 | 42 | 0.022475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_195-4_1_5_line_33 |  | 27 | 52 | 0.0017864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_195-4_1_5_line_34 |  | 27 | 49 | 0.029202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_195-4_1_5_line_35 |  | 28 | 29 | 0.0092558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_195-4_1_5_line_36 |  | 28 | 30 | 0.036179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_195-4_1_5_line_37 |  | 30 | 104 | 0.022448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_195-4_1_5_line_38 |  | 31 | 32 | 0.02184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_195-4_1_5_line_39 |  | 31 | 33 | 0.030883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_195-4_1_5_line_40 |  | 32 | 105 | 0.024819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_195-4_1_5_line_41 |  | 33 | 34 | 0.023374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_195-4_1_5_line_42 |  | 34 | 40 | 0.0042488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_195-4_1_5_line_43 |  | 35 | 38 | 0.066478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_195-4_1_5_line_44 |  | 37 | 38 | 0.080886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_195-4_1_5_line_45 |  | 41 | 42 | 0.013611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_195-4_1_5_line_46 |  | 42 | 102 | 0.020272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_195-4_1_5_line_47 |  | 43 | 44 | 0.012163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_195-4_1_5_line_48 |  | 43 | 45 | 0.023494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_195-4_1_5_line_49 |  | 44 | 46 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_195-4_1_5_line_50 |  | 45 | 96 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_195-4_1_5_line_51 |  | 46 | 47 | 0.025478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_195-4_1_5_line_52 |  | 47 | 85 | 0.022781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_195-4_1_5_line_53 |  | 48 | 49 | 0.014531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_195-4_1_5_line_54 |  | 48 | 50 | 0.03003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_195-4_1_5_line_55 |  | 49 | 83 | 0.01326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_195-4_1_5_line_56 |  | 51 | 101 | 0.016282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_195-4_1_5_line_57 |  | 52 | 103 | 0.025718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_195-4_1_5_line_58 |  | 53 | 54 | 0.019001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_195-4_1_5_line_59 |  | 54 | 57 | 0.034171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_195-4_1_5_line_60 |  | 54 | 58 | 0.029291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_195-4_1_5_line_61 |  | 54 | 59 | 0.004927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_195-4_1_5_line_62 |  | 55 | 56 | 0.018223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_195-4_1_5_line_63 |  | 56 | 60 | 0.030254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_195-4_1_5_line_64 |  | 56 | 61 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_195-4_1_5_line_65 |  | 57 | 62 | 0.018894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_195-4_1_5_line_66 |  | 58 | 63 | 0.047518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_195-4_1_5_line_67 |  | 59 | 64 | 0.019379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_195-4_1_5_line_68 |  | 59 | 65 | 0.11612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_195-4_1_5_line_69 |  | 60 | 62 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_195-4_1_5_line_70 |  | 60 | 66 | 0.033917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_195-4_1_5_line_71 |  | 61 | 67 | 0.0095622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_195-4_1_5_line_72 |  | 64 | 68 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_195-4_1_5_line_73 |  | 65 | 69 | 0.074929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_195-4_1_5_line_74 |  | 66 | 72 | 0.010193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_195-4_1_5_line_75 |  | 67 | 73 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_195-4_1_5_line_76 |  | 67 | 70 | 0.005196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_195-4_1_5_line_77 |  | 68 | 80 | 0.021207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_195-4_1_5_line_78 |  | 70 | 71 | 0.017521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_195-4_1_5_line_79 |  | 71 | 81 | 0.020298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_195-4_1_5_line_80 |  | 72 | 77 | 0.00021685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_195-4_1_5_line_81 |  | 73 | 83 | 0.0036199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_195-4_1_5_line_82 |  | 74 | 75 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_195-4_1_5_line_83 |  | 74 | 76 | 0.033556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_195-4_1_5_line_84 |  | 75 | 84 | 9.6671e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_195-4_1_5_line_85 |  | 76 | 85 | 0.017777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_195-4_1_5_line_86 |  | 76 | 86 | 0.017681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_195-4_1_5_line_87 |  | 78 | 79 | 0.021251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_195-4_1_5_line_88 |  | 79 | 94 | 0.035659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_195-4_1_5_line_89 |  | 79 | 85 | 0.00687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_195-4_1_5_line_90 |  | 80 | 123 | 0.026738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_195-4_1_5_line_91 |  | 81 | 82 | 0.01498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_195-4_1_5_line_92 |  | 82 | 87 | 0.0054033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_195-4_1_5_line_93 |  | 85 | 90 | 0.023122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_195-4_1_5_line_94 |  | 86 | 88 | 0.011465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_195-4_1_5_line_95 |  | 87 | 93 | 0.016436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_195-4_1_5_line_96 |  | 88 | 89 | 0.0023247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_195-4_1_5_line_97 |  | 89 | 91 | 0.013336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_195-4_1_5_line_98 |  | 90 | 95 | 0.014254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_195-4_1_5_line_99 |  | 91 | 92 | 0.00044989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_195-4_1_5_line_100 |  | 91 | 93 | 0.022103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_195-4_1_5_line_101 |  | 97 | 98 | 0.028662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_195-4_1_5_line_102 |  | 98 | 121 | 0.029254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_195-4_1_5_line_103 |  | 99 | 100 | 0.062625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_195-4_1_5_line_104 |  | 100 | 117 | 0.034596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_195-4_1_5_line_105 |  | 100 | 111 | 0.00859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_195-4_1_5_line_106 |  | 104 | 106 | 0.0055581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_195-4_1_5_line_107 |  | 105 | 107 | 0.01231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_195-4_1_5_line_108 |  | 106 | 107 | 0.012046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_195-4_1_5_line_109 |  | 107 | 108 | 0.030248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_195-4_1_5_line_110 |  | 109 | 110 | 0.010591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_195-4_1_5_line_111 |  | 109 | 111 | 0.019362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_195-4_1_5_line_112 |  | 110 | 112 | 0.001693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_195-4_1_5_line_113 |  | 111 | 113 | 0.031786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_195-4_1_5_line_114 |  | 112 | 114 | 0.012257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_195-4_1_5_line_115 |  | 113 | 115 | 0.027118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_195-4_1_5_line_116 |  | 113 | 116 | 0.0197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_195-4_1_5_line_117 |  | 114 | 118 | 0.023672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_195-4_1_5_line_118 |  | 115 | 119 | 0.039216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_195-4_1_5_line_119 |  | 116 | 120 | 0.034783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_195-4_1_5_line_120 |  | 118 | 121 | 0.0013883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_195-4_1_5_line_121 |  | 119 | 122 | 0.0324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_195-4_1_5_line_122 |  | 120 | 123 | 0.00017585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_195-4_1_5_line_123 |  | 122 | 124 | 0.041572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_195-4_1_5_trafo_204 | 0.63 MVA 20/0.4 kV | 125 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56
0 | 2692205.9168 | 1244917.1252 | 2692279.0208 | 1244940.6684 | 2692376.4132 | 1244959.8207 | 2692370.8735 | 1244971.9658 | 2692449.0308 | 1245024.178 | 2692456.6005 | 1245028.2101 | 2692497.6333 | 1244940.1724
1 | 2692205.9168 | 1244917.1252 | 2692189.1424 | 1244921.8236
2 | 2692497.6333 | 1244940.1724 | 2692506.2382 | 1244944.6988 | 2692510.9166 | 1244953.8676 | 2692514.9131 | 1244970.409 | 2692518.7804 | 1244975.373 | 2692548.7045 | 1244982.8901
3 | 2692165.376 | 1244942.1919 | 2692189.1424 | 1244921.8236
4 | 2692330.3352 | 1245200.1508 | 2692348.0063 | 1245208.6656 | 2692350.5513 | 1245217.99
5 | 2692350.5513 | 1245217.99 | 2692354.6188 | 1245232.8979 | 2692360.3234 | 1245236.3449 | 2692354.8728 | 1245248.1244 | 2692352.6623 | 1245253.2272
6 | 2692361.8203 | 1245262.4879 | 2692359.4037 | 1245256.568 | 2692352.6623 | 1245253.2272
7 | 2692352.6623 | 1245253.2272 | 2692347.6616 | 1245263.9392
8 | 2691934.5243 | 1245521.868 | 2691950.0856 | 1245502.2055 | 2691964.1227 | 1245487.2785 | 2691981.0003 | 1245480.6797 | 2691999.3472 | 1245477.2727 | 2692011.6326 | 1245474.9282 | 2692024.5139 | 1245470.2133 | 2692032.617 | 1245462.2553 | 2692044.5535 | 1245439.5567 | 2692121.1853 | 1245257.5871 | 2692137.8993 | 1245226.0785 | 2692170.915 | 1245238.2116 | 2692178.4763 | 1245243.2662 | 2692203.8666 | 1245260.2847 | 2692220.9028 | 1245265.8982 | 2692257.674 | 1245268.305 | 2692296.4034 | 1245278.8932 | 2692332.8214 | 1245295.7281
9 | 2692332.8214 | 1245295.7281 | 2692347.6616 | 1245263.9392
10 | 2691934.5243 | 1245521.868 | 2691944.5748 | 1245532.6193
11 | 2692561.2584 | 1244986.0437 | 2692557.1821 | 1245005.1166 | 2692555.7119 | 1245027.644 | 2692551.9592 | 1245044.3869 | 2692547.5834 | 1245057.9622 | 2692541.8324 | 1245070.0705 | 2692534.8718 | 1245080.3221
12 | 2692561.2584 | 1244986.0437 | 2692548.7045 | 1244982.8901
13 | 2692464.0289 | 1245145.9478 | 2692481.9125 | 1245135.5187 | 2692490.7506 | 1245129.4408 | 2692497.4135 | 1245123.7738 | 2692508.9531 | 1245111.6557 | 2692526.1515 | 1245091.8757 | 2692531.3286 | 1245085.5406 | 2692534.8718 | 1245080.3221
14 | 2691522.4327 | 1245069.523 | 2691535.3847 | 1245029.9153 | 2691547.9762 | 1245013.6641 | 2691557.4838 | 1244992.5617 | 2691565.3198 | 1244956.8892 | 2691569.9623 | 1244934.2216 | 2691582.4252 | 1244896.9638 | 2691586.4104 | 1244863.5336 | 2691586.894 | 1244827.8254 | 2691597.0015 | 1244852.5444 | 2691606.579 | 1244886.1286 | 2691607.7046 | 1244902.7807 | 2691618.8079 | 1244914.3942 | 2691647.0203 | 1244970.0161 | 2691676.3565 | 1245035.5185 | 2691684.1149 | 1245021.5168 | 2691689.2264 | 1245014.9686 | 2691696.2105 | 1245016.8335 | 2691701.182 | 1245021.7807 | 2691705.2099 | 1245033.0181 | 2691715.5087 | 1245089.7643 | 2691722.7459 | 1245110.9143 | 2691719.9633 | 1245134.956 | 2691714.1413 | 1245161.0523 | 2691704.1629 | 1245181.3021 | 2691694.2317 | 1245202.8982 | 2691681.7475 | 1245238.1094 | 2691681.0679 | 1245253.2214 | 2691694.0107 | 1245243.5697 | 2691716.0833 | 1245220.16 | 2691731.7189 | 1245207.9037 | 2691741.7909 | 1245205.5354 | 2691755.5041 | 1245206.6594 | 2691769.4196 | 1245213.7578 | 2691779.8353 | 1245216.521 | 2691791.3555 | 1245214.8202 | 2691803.8782 | 1245204.4951 | 2691814.2866 | 1245191.6354 | 2691820.4945 | 1245184.5595 | 2691829.0659 | 1245182.4795 | 2691842.0177 | 1245174.2182 | 2691848.9351 | 1245169.6441 | 2691854.0627 | 1245164.4974 | 2691864.6629 | 1245120.7398 | 2691870.2349 | 1245111.3079 | 2691878.743 | 1245101.6212 | 2691890.5127 | 1245097 | 2691910.2063 | 1245096.0044 | 2691943.4219 | 1245098.243 | 2691964.331 | 1245109.987 | 2691974.926 | 1245108.9949 | 2691986.6627 | 1245106.9976 | 2691999.3529 | 1245093.7066 | 2692051.7012 | 1245042.9916 | 2692121.1141 | 1244991.308 | 2692129.7661 | 1244982.6025 | 2692165.376 | 1244942.1919
15 | 2691522.4327 | 1245069.523 | 2691481.6382 | 1245052.0362 | 2691388.1113 | 1245039.9302 | 2691369.127 | 1245041.7451
16 | 2691183.3301 | 1245037.1772 | 2691178.4093 | 1245054.4589 | 2691220.4139 | 1245052.2808 | 2691222.7689 | 1245057.8656
17 | 2691224.074 | 1245060.9547 | 2691222.7689 | 1245057.8656
18 | 2691222.7689 | 1245057.8656 | 2691214.3865 | 1245058.9598 | 2691193.0492 | 1245062.5485
19 | 2691183.3301 | 1245037.1772 | 2691188.2593 | 1245019.8511 | 2691203.2145 | 1245017.0459
20 | 2691224.074 | 1245060.9547 | 2691232.7809 | 1245062.8344 | 2691250.5891 | 1245057.1707 | 2691263.0423 | 1245051.8935
21 | 2691130.7146 | 1245068.9036 | 2691134.9256 | 1245073.7052 | 2691149.4995 | 1245070.4822 | 2691170.1117 | 1245068.2195 | 2691191.7934 | 1245062.7597 | 2691193.0492 | 1245062.5485
22 | 2691293.7064 | 1245040.1546 | 2691279.6309 | 1245044.8638 | 2691275.3292 | 1245046.6867
23 | 2691293.7064 | 1245040.1546 | 2691333.4063 | 1245044.0678
24 | 2691275.3292 | 1245046.6867 | 2691263.0423 | 1245051.8935
25 | 2691333.4063 | 1245044.0678 | 2691338.2167 | 1245044.5419
26 | 2691369.127 | 1245041.7451 | 2691339.0322 | 1245044.6223 | 2691338.2167 | 1245044.5419
27 | 2692361.8203 | 1245262.4879 | 2692392.4761 | 1245217.9984 | 2692448.9938 | 1245155.9321 | 2692456.3499 | 1245150.3871 | 2692464.0289 | 1245145.9478
28 | 2692361.8203 | 1245262.4879 | 2692365.6965 | 1245291.6146 | 2692365.4748 | 1245297.7827
29 | 2691130.7146 | 1245068.9036 | 2691114.3714 | 1245076.1246 | 2691109.2516 | 1245078.3366 | 2691115.8251 | 1245092.1701 | 2691121.3604 | 1245094.8794 | 2691132.2129 | 1245094.3345 | 2691137.0394 | 1245096.944 | 2691148.4719 | 1245111.2637
30 | 2691095.4853 | 1245066.8721 | 2691114.3714 | 1245076.1246 | 2691130.7146 | 1245068.9036
31 | 2691148.4719 | 1245111.2637 | 2691162.6862 | 1245103.9602
32 | 2691129.8462 | 1245123.9204 | 2691148.4719 | 1245111.2637
33 | 2691095.4853 | 1245066.8721 | 2691096.9253 | 1245065.8149
34 | 2691070.2834 | 1245081.6074 | 2691082.3101 | 1245074.9759 | 2691095.4853 | 1245066.8721
35 | 2692342.4419 | 1245418.8817 | 2692347.6221 | 1245425.901 | 2692347.5236 | 1245426.4238
36 | 2692352.1133 | 1245384.0171 | 2692342.4419 | 1245418.8817
37 | 2692352.1133 | 1245384.0171 | 2692373.9327 | 1245389.2906
38 | 2692355.8184 | 1245355.2532 | 2692367.3798 | 1245358.1687 | 2692375.7576 | 1245363.4747
39 | 2692355.8184 | 1245355.2532 | 2692360.0499 | 1245332.4685 | 2692362.4912 | 1245325.1566
40 | 2692390.5081 | 1245382.5694 | 2692382.4276 | 1245367.6991 | 2692375.7576 | 1245363.4747
41 | 2692362.4912 | 1245325.1566 | 2692364.9362 | 1245312.7631 | 2692365.3221 | 1245302.0287
42 | 2692365.3221 | 1245302.0287 | 2692365.4748 | 1245297.7827
43 | 2692464.0289 | 1245145.9478 | 2692467.8571 | 1245150.5109 | 2692493.5208 | 1245165.9671 | 2692518.9822 | 1245174.5261 | 2692522.4786 | 1245175.7405
44 | 2692522.4786 | 1245175.7405 | 2692571.8803 | 1245192.8985 | 2692578.0945 | 1245193.7072 | 2692586.3355 | 1245192.9574 | 2692599.3986 | 1245187.7916
45 | 2691129.8462 | 1245123.9204 | 2691120.0758 | 1245133.397
46 | 2691129.8462 | 1245123.9204 | 2691144.1852 | 1245138.2498
47 | 2691133.5916 | 1244912.7197 | 2691127.3218 | 1244911.0777 | 2691121.8279 | 1244909.6302
48 | 2691128.305 | 1244935.6112 | 2691133.5916 | 1244912.7197
49 | 2691100.8808 | 1244904.1109 | 2691121.8279 | 1244909.6302
50 | 2691128.305 | 1244935.6112 | 2691120.1075 | 1244934.0063 | 2691113.5657 | 1244932.3946
51 | 2691087.953 | 1244926.0844 | 2691100.8808 | 1244904.1109
52 | 2691075.3733 | 1244945.0833 | 2691084.7018 | 1244931.6053 | 2691087.953 | 1244926.0844
53 | 2691070.2834 | 1245081.6074 | 2691079.2742 | 1245093.0428
54 | 2691079.2742 | 1245093.0428 | 2691051.5334 | 1245104.5425
55 | 2691070.2834 | 1245081.6074 | 2691065.639 | 1245075.9985 | 2691062.0648 | 1245071.2064
56 | 2691162.6862 | 1245103.9602 | 2691177.1679 | 1245096.5193
57 | 2691109.9038 | 1245044.7548 | 2691107.2201 | 1245055.1435 | 2691103.802 | 1245060.2171 | 2691098.749 | 1245064.476 | 2691096.9253 | 1245065.8149
58 | 2690972.4974 | 1245059.446 | 2690977.228 | 1245063.8775 | 2690986.3702 | 1245072.4307
59 | 2690972.4974 | 1245059.446 | 2690995.3399 | 1245033.9773
60 | 2690972.4974 | 1245059.446 | 2690972.8579 | 1245048.2654 | 2690985.0924 | 1245034.9204
61 | 2690972.4974 | 1245059.446 | 2690969.2066 | 1245063.1206
62 | 2691032.9293 | 1245074.2508 | 2691021.8858 | 1245085.2674 | 2691019.7189 | 1245086.7466
63 | 2691016.6958 | 1245053.6641 | 2691013.725 | 1245056.6763 | 2691014.2565 | 1245057.4962 | 2691017.8167 | 1245060.3974 | 2691032.9293 | 1245074.2508
64 | 2691032.9293 | 1245074.2508 | 2691042.7356 | 1245064.4243
65 | 2690995.3399 | 1245033.9773 | 2691009.2315 | 1245046.7832
66 | 2691017.204 | 1244999.8945 | 2690985.0924 | 1245034.9204
67 | 2690969.2066 | 1245063.1206 | 2690954.2902 | 1245050.7493
68 | 2690885.5357 | 1245098.1755 | 2690896.0039 | 1245099.5258 | 2690917.487 | 1245119.3031 | 2690947.0644 | 1245087.2881 | 2690961.5499 | 1245071.5984 | 2690969.2066 | 1245063.1206
69 | 2691016.6958 | 1245053.6641 | 2691009.2315 | 1245046.7832
70 | 2691016.6958 | 1245053.6641 | 2691033.8409 | 1245035.558 | 2691040.0168 | 1245029.0368
71 | 2691050.6365 | 1245059.4003 | 2691045.8694 | 1245061.2841 | 2691042.7356 | 1245064.4243
72 | 2690949.1517 | 1245030.0439 | 2690954.2902 | 1245050.7493 | 2690954.2902 | 1245050.7493
73 | 2690885.5357 | 1245098.1755 | 2690885.5967 | 1245089.2698 | 2690894.1098 | 1245089 | 2690893.7358 | 1245067.0668 | 2690906.4182 | 1245066.4495 | 2690905.7461 | 1245054.0966 | 2690907.508 | 1245054.0236 | 2690906.9466 | 1245045.3041
74 | 2691040.0168 | 1245029.0368 | 2691032.5836 | 1245022.0618
75 | 2691059.9005 | 1245068.3047 | 2691054.9606 | 1245067.6617 | 2691050.6365 | 1245059.4003
76 | 2691050.6365 | 1245059.4003 | 2691055.4433 | 1245057.3948
77 | 2690951.0573 | 1245008.9867 | 2690949.5341 | 1245016.9399 | 2690949.1517 | 1245030.0439 | 2690949.1517 | 1245030.0439
78 | 2691055.4433 | 1245057.3948 | 2691056.9264 | 1245056.2834 | 2691066.4016 | 1245043.8056
79 | 2691078.677 | 1245027.6402 | 2691066.4016 | 1245043.8056
80 | 2691032.5836 | 1245022.0618 | 2691032.4255 | 1245021.9135
81 | 2691059.9005 | 1245068.3047 | 2691062.0648 | 1245071.2064
82 | 2691041.3275 | 1244983.5451 | 2691055.8152 | 1244996.8128
83 | 2691041.3275 | 1244983.5451 | 2691063.9643 | 1244958.7183
84 | 2691055.8152 | 1244996.8128 | 2691055.8865 | 1244996.8781
85 | 2691063.9643 | 1244958.7183 | 2691070.0981 | 1244951.9964 | 2691075.3733 | 1244945.0833
86 | 2691063.9643 | 1244958.7183 | 2691077.3013 | 1244970.3267
87 | 2691070.1522 | 1244940.5998 | 2691059.1605 | 1244954.1301 | 2691056.58 | 1244956.9448
88 | 2691070.1522 | 1244940.5998 | 2691076.3958 | 1244932.1448 | 2691089.6079 | 1244910.7461
89 | 2691070.1522 | 1244940.5998 | 2691075.3733 | 1244945.0833
90 | 2690956.7864 | 1244982.8716 | 2690951.9165 | 1245004.5005 | 2690951.0573 | 1245008.9867
91 | 2691078.677 | 1245027.6402 | 2691087.2022 | 1245015.3222
92 | 2691090.2772 | 1245010.8792 | 2691087.2022 | 1245015.3222
93 | 2691075.3733 | 1244945.0833 | 2691080.651 | 1244948.8338 | 2691096.8205 | 1244952.7946
94 | 2691087.1192 | 1244975.4308 | 2691082.093 | 1244974.4973 | 2691077.3013 | 1244970.3267
95 | 2691090.2772 | 1245010.8792 | 2691099.6307 | 1244997.3644
96 | 2691087.1192 | 1244975.4308 | 2691089.3827 | 1244975.9607
97 | 2691102.3673 | 1244979.0009 | 2691089.3827 | 1244975.9607
98 | 2691096.8205 | 1244952.7946 | 2691110.6652 | 1244956.1859
99 | 2691102.802 | 1244979.1168 | 2691102.3673 | 1244979.0009
100 | 2691102.3673 | 1244979.0009 | 2691100.6481 | 1244985.1458 | 2691105.0391 | 1244989.5498 | 2691099.6307 | 1244997.3644
101 | 2691047.4995 | 1244850.6818 | 2691062.7003 | 1244826.3824
102 | 2691047.4995 | 1244850.6818 | 2691031.9849 | 1244875.4829
103 | 2690980.4796 | 1244890.8979 | 2690993.1132 | 1244847.6926 | 2690998.5401 | 1244830.9391
104 | 2690980.4796 | 1244890.8979 | 2690968.7268 | 1244884.5907 | 2690962.2935 | 1244881.2896 | 2690957.4184 | 1244881.8264 | 2690951.4319 | 1244888.8065
105 | 2690980.4796 | 1244890.8979 | 2690977.8452 | 1244899.0747
106 | 2692379.3353 | 1245390.5963 | 2692373.9327 | 1245389.2906
107 | 2692390.558 | 1245394.8795 | 2692390.5081 | 1245382.5694
108 | 2692390.558 | 1245394.8795 | 2692382.3089 | 1245391.315 | 2692379.3353 | 1245390.5963
109 | 2692390.558 | 1245394.8795 | 2692413.3247 | 1245414.7954
110 | 2690996.3005 | 1244904.9288 | 2691003.846 | 1244904.6999 | 2691006.752 | 1244903.7999
111 | 2690977.8452 | 1244899.0747 | 2690996.3005 | 1244904.9288
112 | 2691008.3692 | 1244903.2991 | 2691006.752 | 1244903.7999
113 | 2690977.8452 | 1244899.0747 | 2690968.7927 | 1244929.5476
114 | 2691018.265 | 1244896.4253 | 2691016.5835 | 1244898.5462 | 2691010.2091 | 1244902.7294 | 2691008.3692 | 1244903.2991
115 | 2690968.7927 | 1244929.5476 | 2690960.3352 | 1244927.1606 | 2690945.7667 | 1244927.0594 | 2690942.0377 | 1244927.5524
116 | 2690968.7927 | 1244929.5476 | 2690964.4654 | 1244948.7664
117 | 2691018.265 | 1244896.4253 | 2691021.1996 | 1244892.7238 | 2691031.2486 | 1244876.6599
118 | 2690942.0377 | 1244927.5524 | 2690928.5091 | 1244929.341 | 2690914.9226 | 1244935.1816 | 2690905.9512 | 1244941.1595
119 | 2690964.4654 | 1244948.7664 | 2690956.825 | 1244982.7
120 | 2691031.9849 | 1244875.4829 | 2691031.2486 | 1244876.6599
121 | 2690882.8469 | 1244963.6521 | 2690899.9808 | 1244945.1379 | 2690905.9512 | 1244941.1595
122 | 2690956.825 | 1244982.7 | 2690956.7864 | 1244982.8716
123 | 2690854.2886 | 1244993.8621 | 2690878.795 | 1244968.0304 | 2690882.8469 | 1244963.6521

## bus_geodata
| x | y | coords
0 | 2692205.9168 | 1244917.1252
1 | 2692497.6333 | 1244940.1724
2 | 2692189.1424 | 1244921.8236
3 | 2692350.5513 | 1245217.99
4 | 2692330.3352 | 1245200.1508
5 | 2692352.6623 | 1245253.2272
6 | 2692332.8214 | 1245295.7281
7 | 2691934.5243 | 1245521.868
8 | 2692347.6616 | 1245263.9392
9 | 2692561.2584 | 1244986.0437
10 | 2692534.8718 | 1245080.3221
11 | 2692548.7045 | 1244982.8901
12 | 2692165.376 | 1244942.1919
13 | 2691522.4327 | 1245069.523
14 | 2691222.7689 | 1245057.8656
15 | 2691183.3301 | 1245037.1772
16 | 2691224.074 | 1245060.9547
17 | 2691193.0492 | 1245062.5485
18 | 2691944.5748 | 1245532.6193
19 | 2691293.7064 | 1245040.1546
20 | 2691275.3292 | 1245046.6867
21 | 2691333.4063 | 1245044.0678
22 | 2691369.127 | 1245041.7451
23 | 2692361.8203 | 1245262.4879
24 | 2691203.2145 | 1245017.0459
25 | 2691130.7146 | 1245068.9036
26 | 2691148.4719 | 1245111.2637
27 | 2691095.4853 | 1245066.8721
28 | 2692342.4419 | 1245418.8817
29 | 2692347.5236 | 1245426.4238
30 | 2692352.1133 | 1245384.0171
31 | 2692355.8184 | 1245355.2532
32 | 2692375.7576 | 1245363.4747
33 | 2692362.4912 | 1245325.1566
34 | 2692365.3221 | 1245302.0287
35 | 2692464.0289 | 1245145.9478
36 | 2691263.0423 | 1245051.8935
37 | 2692599.3986 | 1245187.7916
38 | 2692522.4786 | 1245175.7405
39 | 2691338.2167 | 1245044.5419
40 | 2692365.4748 | 1245297.7827
41 | 2691120.0758 | 1245133.397
42 | 2691129.8462 | 1245123.9204
43 | 2691133.5916 | 1244912.7197
44 | 2691121.8279 | 1244909.6302
45 | 2691128.305 | 1244935.6112
46 | 2691100.8808 | 1244904.1109
47 | 2691087.953 | 1244926.0844
48 | 2691079.2742 | 1245093.0428
49 | 2691070.2834 | 1245081.6074
50 | 2691051.5334 | 1245104.5425
51 | 2691162.6862 | 1245103.9602
52 | 2691096.9253 | 1245065.8149
53 | 2690986.3702 | 1245072.4307
54 | 2690972.4974 | 1245059.4461
55 | 2691019.7189 | 1245086.7466
56 | 2691032.9293 | 1245074.2508
57 | 2690995.3399 | 1245033.9773
58 | 2690985.0924 | 1245034.9204
59 | 2690969.2066 | 1245063.1206
60 | 2691016.6958 | 1245053.6641
61 | 2691042.7356 | 1245064.4243
62 | 2691009.2315 | 1245046.7832
63 | 2691017.204 | 1244999.8945
64 | 2690954.2902 | 1245050.7493
65 | 2690885.5357 | 1245098.1755
66 | 2691040.0168 | 1245029.0368
67 | 2691050.6365 | 1245059.4003
68 | 2690949.1517 | 1245030.0439
69 | 2690906.9466 | 1245045.3041
70 | 2691055.4433 | 1245057.3948
71 | 2691066.4016 | 1245043.8056
72 | 2691032.5836 | 1245022.0618
73 | 2691059.9005 | 1245068.3047
74 | 2691041.3275 | 1244983.5451
75 | 2691055.8152 | 1244996.8128
76 | 2691063.9643 | 1244958.7183
77 | 2691032.4255 | 1245021.9135
78 | 2691056.58 | 1244956.9448
79 | 2691070.1522 | 1244940.5998
80 | 2690951.0573 | 1245008.9867
81 | 2691078.677 | 1245027.6402
82 | 2691087.2022 | 1245015.3222
83 | 2691062.0648 | 1245071.2064
84 | 2691055.8865 | 1244996.8781
85 | 2691075.3733 | 1244945.0833
86 | 2691077.3013 | 1244970.3267
87 | 2691090.2772 | 1245010.8792
88 | 2691087.1192 | 1244975.4308
89 | 2691089.3827 | 1244975.9607
90 | 2691096.8205 | 1244952.7946
91 | 2691102.3673 | 1244979.0009
92 | 2691102.802 | 1244979.1168
93 | 2691099.6307 | 1244997.3644
94 | 2691089.6079 | 1244910.7461
95 | 2691110.6652 | 1244956.1859
96 | 2691113.5657 | 1244932.3946
97 | 2691062.7003 | 1244826.3824
98 | 2691047.4995 | 1244850.6818
99 | 2690998.5401 | 1244830.9391
100 | 2690980.4796 | 1244890.8979
101 | 2691177.1679 | 1245096.5193
102 | 2691144.1852 | 1245138.2498
103 | 2691109.9038 | 1245044.7548
104 | 2692373.9327 | 1245389.2906
105 | 2692390.5081 | 1245382.5694
106 | 2692379.3353 | 1245390.5963
107 | 2692390.558 | 1245394.8795
108 | 2692413.3247 | 1245414.7954
109 | 2690996.3005 | 1244904.9288
110 | 2691006.752 | 1244903.7999
111 | 2690977.8452 | 1244899.0747
112 | 2691008.3692 | 1244903.2991
113 | 2690968.7927 | 1244929.5476
114 | 2691018.265 | 1244896.4253
115 | 2690942.0377 | 1244927.5524
116 | 2690964.4654 | 1244948.7664
117 | 2690951.4319 | 1244888.8065
118 | 2691031.2486 | 1244876.6599
119 | 2690905.9512 | 1244941.1595
120 | 2690956.825 | 1244982.7
121 | 2691031.9849 | 1244875.4829
122 | 2690882.8469 | 1244963.6521
123 | 2690956.7864 | 1244982.8716
124 | 2690854.2886 | 1244993.8621
125 | 2691207.1609 | 1245016.3056

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98072 | -0.372 | 0 | 0
1 | 0.97799 | -0.42577 | 0 | 0
2 | 0.98084 | -0.3696 | 0.00073062 | 0.00018311
3 | 0.97516 | -0.48146 | 0 | 0
4 | 0.97509 | -0.48295 | 0.0027892 | 0.00069905
5 | 0.97527 | -0.47938 | 0 | 0
6 | 0.97523 | -0.48006 | 0 | 0
7 | 0.9744 | -0.49664 | 0 | 0
8 | 0.97525 | -0.47966 | 0.0033226 | 0.00083272
9 | 0.97738 | -0.43764 | 0 | 0
10 | 0.97676 | -0.44991 | 0.00099174 | 0.00024855
11 | 0.97746 | -0.43604 | 0.0041064 | 0.0010292
12 | 0.98107 | -0.36521 | 0 | 0
13 | 0.9911 | -0.17 | 0 | 0
14 | 0.99366 | -0.12057 | 0 | 0
15 | 0.99788 | -0.04017 | 0 | 0
16 | 0.99362 | -0.12121 | 0 | 0
17 | 0.99203 | -0.15165 | 0.0010401 | 0.00026068
18 | 0.97436 | -0.49746 | 0.0030525 | 0.00076503
19 | 0.9929 | -0.13511 | 0 | 0
20 | 0.99309 | -0.13157 | 0.0021091 | 0.0005286
21 | 0.99253 | -0.14234 | 0.0031255 | 0.00078333
22 | 0.99223 | -0.14817 | 0.0065165 | 0.0016332
23 | 0.97529 | -0.47891 | 0 | 0
24 | 1 | 0 | -0.35284 | -0.090017
25 | 0.98851 | -0.2196 | 0 | 0
26 | 0.98622 | -0.26396 | 0 | 0
27 | 0.98664 | -0.25572 | 0 | 0
28 | 0.97426 | -0.49929 | 0 | 0
29 | 0.97421 | -0.5002 | 0.0053945 | 0.001352
30 | 0.97444 | -0.4957 | 0 | 0
31 | 0.97496 | -0.4854 | 0 | 0
32 | 0.97489 | -0.48677 | 0.0022638 | 0.00056737
33 | 0.97506 | -0.48344 | 0 | 0
34 | 0.97514 | -0.48197 | 0.0030519 | 0.00076487
35 | 0.97617 | -0.46164 | 0 | 0
36 | 0.99322 | -0.12905 | 0.00056314 | 0.00014114
37 | 0.97593 | -0.46625 | 0.001014 | 0.00025413
38 | 0.97601 | -0.46475 | 0.0015399 | 0.00038593
39 | 0.99249 | -0.14316 | 0.0025867 | 0.00064829
40 | 0.97515 | -0.48165 | 0.00075441 | 0.00018907
41 | 0.98575 | -0.27316 | 0.008764 | 0.0021965
42 | 0.98586 | -0.27102 | 0 | 0
43 | 0.98192 | -0.34774 | 0 | 0
44 | 0.98193 | -0.34755 | 0.0029049 | 0.00072803
45 | 0.9819 | -0.3481 | 0 | 0
46 | 0.98196 | -0.34699 | 0 | 0
47 | 0.98199 | -0.34632 | 0 | 0
48 | 0.98513 | -0.28494 | 0 | 0
49 | 0.98529 | -0.28197 | 0 | 0
50 | 0.98482 | -0.2911 | 0.011407 | 0.0028589
51 | 0.98602 | -0.26787 | 0.0068256 | 0.0017107
52 | 0.98662 | -0.25602 | 0.0078381 | 0.0019644
53 | 0.98126 | -0.3605 | 0.0039713 | 0.0009953
54 | 0.98133 | -0.35913 | 0 | 0
55 | 0.98321 | -0.32252 | 0.0077229 | 0.0019355
56 | 0.98334 | -0.31998 | 0 | 0
57 | 0.98202 | -0.34558 | 0 | 0
58 | 0.98126 | -0.36049 | 0.0033031 | 0.00082785
59 | 0.98125 | -0.36079 | 0 | 0
60 | 0.98262 | -0.33385 | 0 | 0
61 | 0.98368 | -0.31324 | 0.0095998 | 0.0024059
62 | 0.98241 | -0.33809 | 0.005915 | 0.0014824
63 | 0.98118 | -0.36212 | 0.0094819 | 0.0023764
64 | 0.98094 | -0.3668 | 0.003355 | 0.00084085
65 | 0.98109 | -0.36383 | 0 | 0
66 | 0.98253 | -0.33561 | 0 | 0
67 | 0.98394 | -0.30826 | 0 | 0
68 | 0.98061 | -0.37317 | 0.0033545 | 0.00084071
69 | 0.98099 | -0.36578 | 0.0072028 | 0.0018052
70 | 0.98385 | -0.30989 | 0 | 0
71 | 0.98357 | -0.31538 | 0.010334 | 0.00259
72 | 0.98243 | -0.33772 | 0.0059395 | 0.0014886
73 | 0.98455 | -0.29637 | 0 | 0
74 | 0.98206 | -0.34489 | 0 | 0
75 | 0.98201 | -0.34591 | 0.0057348 | 0.0014373
76 | 0.98213 | -0.3435 | 0 | 0
77 | 0.98243 | -0.33774 | 0.0055386 | 0.0013881
78 | 0.98179 | -0.35016 | 0.0094812 | 0.0023762
79 | 0.98198 | -0.34652 | 0 | 0
80 | 0.9803 | -0.37924 | 0.0032547 | 0.0008157
81 | 0.98329 | -0.32098 | 0 | 0
82 | 0.98307 | -0.32511 | 0.0087594 | 0.0021953
83 | 0.9847 | -0.29336 | 0.0078921 | 0.0019779
84 | 0.98201 | -0.34592 | 0.0057316 | 0.0014365
85 | 0.98202 | -0.34573 | 0 | 0
86 | 0.98229 | -0.34054 | 0.0055228 | 0.0013841
87 | 0.98301 | -0.32643 | 0.0013823 | 0.00034642
88 | 0.9824 | -0.3384 | 0 | 0
89 | 0.98242 | -0.33796 | 0.0057714 | 0.0014464
90 | 0.98198 | -0.34645 | 0.0057746 | 0.0014472
91 | 0.98256 | -0.33519 | 0 | 0
92 | 0.98256 | -0.33522 | 0.002843 | 0.00071252
93 | 0.98281 | -0.33037 | 0.0060185 | 0.0015084
94 | 0.98167 | -0.35263 | 0.0094843 | 0.002377
95 | 0.98197 | -0.3467 | 0.0028342 | 0.00071032
96 | 0.98188 | -0.34849 | 0.0042663 | 0.0010692
97 | 0.97856 | -0.41338 | 0.0045154 | 0.0011317
98 | 0.97859 | -0.41291 | 0.0049203 | 0.0012332
99 | 0.97855 | -0.41359 | 0.0052415 | 0.0013137
100 | 0.97886 | -0.40762 | 0 | 0
101 | 0.98592 | -0.26986 | 0.0068246 | 0.0017104
102 | 0.9857 | -0.2742 | 0.0087552 | 0.0021943
103 | 0.98659 | -0.25665 | 0.0013696 | 0.00034325
104 | 0.97455 | -0.49348 | 0.0058855 | 0.0014751
105 | 0.97482 | -0.48814 | 0.0012785 | 0.00032042
106 | 0.97461 | -0.49233 | 0.00070289 | 0.00017616
107 | 0.97475 | -0.48968 | 0 | 0
108 | 0.9747 | -0.49061 | 0.0016839 | 0.00042201
109 | 0.97884 | -0.40805 | 0.0039464 | 0.00098905
110 | 0.97877 | -0.40925 | 0.0038525 | 0.00096553
111 | 0.97896 | -0.40558 | 0 | 0
112 | 0.97877 | -0.40942 | 0.0055426 | 0.0013891
113 | 0.97924 | -0.40001 | 0 | 0
114 | 0.97872 | -0.41039 | 0.0049764 | 0.0012472
115 | 0.97886 | -0.40754 | 0.0027122 | 0.00067973
116 | 0.97948 | -0.39547 | 0.0065318 | 0.001637
117 | 0.97861 | -0.41254 | 0.0078179 | 0.0019593
118 | 0.97864 | -0.41183 | 0.0031351 | 0.00078573
119 | 0.9784 | -0.4165 | 0.0036687 | 0.00091946
120 | 0.97993 | -0.38663 | 0.0027592 | 0.00069153
121 | 0.97864 | -0.4119 | 0.0041929 | 0.0010508
122 | 0.97814 | -0.42175 | 0.0047343 | 0.0011865
123 | 0.97993 | -0.38658 | 0.0029463 | 0.00073841
124 | 0.97798 | -0.42489 | 0.0041517 | 0.0010405
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.038029 | 0.0095242 | -0.037932 | -0.0094865 | 9.7168e-05 | 3.7707e-05 | 0.057698 | 0.057707 | 0.057707 | 0.98072 | -0.372 | 0.97799 | -0.42577 | 3.1707
1 | -0.038029 | -0.0095242 | 0.038034 | 0.0095259 | 4.3494e-06 | 1.6844e-06 | 0.057698 | 0.057698 | 0.057698 | 0.98072 | -0.372 | 0.98084 | -0.3696 | 3.1702
2 | 0.037932 | 0.0094865 | -0.037914 | -0.0094793 | 1.8528e-05 | 7.2061e-06 | 0.057707 | 0.057709 | 0.057709 | 0.97799 | -0.42577 | 0.97746 | -0.43604 | 3.1708
3 | -0.038764 | -0.009709 | 0.038773 | 0.0097122 | 8.1181e-06 | 3.2198e-06 | 0.058806 | 0.058806 | 0.058806 | 0.98084 | -0.3696 | 0.98107 | -0.36521 | 3.2311
4 | 0.0027894 | 0.00069881 | -0.0027892 | -0.00069905 | 1.986e-07 | -2.3756e-07 | 0.0042563 | 0.0042564 | 0.0042564 | 0.97516 | -0.48146 | 0.97509 | -0.48295 | 1.1694
5 | -0.0027894 | -0.00069881 | 0.0027897 | 0.00069848 | 2.762e-07 | -3.3053e-07 | 0.0042563 | 0.0042561 | 0.0042563 | 0.97516 | -0.48146 | 0.97527 | -0.47938 | 1.1693
6 | -0.0091675 | -0.0022801 | 0.0091677 | 0.0022794 | 2.0374e-07 | -7.3675e-07 | 0.013981 | 0.013981 | 0.013981 | 0.97527 | -0.47938 | 0.97529 | -0.47891 | 0.76819
7 | 0.0063778 | 0.0015817 | -0.0063777 | -0.0015824 | 8.3854e-08 | -6.8391e-07 | 0.0097249 | 0.0097251 | 0.0097251 | 0.97527 | -0.47938 | 0.97525 | -0.47966 | 0.53435
8 | 0.003055 | 0.00075178 | -0.0030526 | -0.00076492 | 2.3955e-06 | -1.3142e-05 | 0.0046564 | 0.0046616 | 0.0046616 | 0.97523 | -0.48006 | 0.9744 | -0.49664 | 0.64033
9 | -0.003055 | -0.00075178 | 0.0030551 | 0.00074963 | 5.704e-08 | -2.1522e-06 | 0.0046564 | 0.0046556 | 0.0046564 | 0.97523 | -0.48006 | 0.97525 | -0.47966 | 0.25585
10 | 0.0030526 | 0.00076492 | -0.0030525 | -0.00076503 | 1.1994e-07 | -1.0656e-07 | 0.0046616 | 0.0046617 | 0.0046617 | 0.9744 | -0.49664 | 0.97436 | -0.49746 | 1.2807
11 | 0.033805 | 0.0084493 | -0.033785 | -0.0084429 | 1.972e-05 | 6.4028e-06 | 0.051458 | 0.05146 | 0.05146 | 0.97738 | -0.43764 | 0.97676 | -0.44991 | 2.8275
12 | -0.033805 | -0.0084493 | 0.033807 | 0.0084501 | 2.5706e-06 | 8.3399e-07 | 0.051458 | 0.051458 | 0.051458 | 0.97738 | -0.43764 | 0.97746 | -0.43604 | 2.8274
13 | 0.032793 | 0.0081943 | -0.032775 | -0.0081887 | 1.8265e-05 | 5.5849e-06 | 0.049949 | 0.049951 | 0.049951 | 0.97676 | -0.44991 | 0.97617 | -0.46164 | 2.7446
14 | -0.038773 | -0.0097122 | 0.039135 | 0.0098551 | 0.00036285 | 0.00014294 | 0.058806 | 0.058774 | 0.058806 | 0.98107 | -0.36521 | 0.9911 | -0.17 | 3.2311
15 | -0.039135 | -0.0098551 | 0.039176 | 0.0098711 | 4.087e-05 | 1.598e-05 | 0.058774 | 0.05877 | 0.058774 | 0.9911 | -0.17 | 0.99223 | -0.14817 | 3.2293
16 | -0.34915 | -0.088718 | 0.35051 | 0.089582 | 0.0013573 | 0.0008644 | 0.52329 | 0.52329 | 0.52329 | 0.99366 | -0.12057 | 0.99788 | -0.04017 | 28.7522
17 | 0.054145 | 0.013639 | -0.054143 | -0.013638 | 1.6538e-06 | 8.4135e-07 | 0.081107 | 0.081107 | 0.081107 | 0.99366 | -0.12057 | 0.99362 | -0.12121 | 4.4564
18 | 0.29501 | 0.075079 | -0.29457 | -0.074798 | 0.00044126 | 0.00028046 | 0.44218 | 0.44218 | 0.44218 | 0.99366 | -0.12057 | 0.99203 | -0.15165 | 24.2958
19 | -0.35051 | -0.089582 | 0.35119 | 0.090017 | 0.00068245 | 0.00043459 | 0.52329 | 0.52329 | 0.52329 | 0.99788 | -0.04017 | 1 | 0 | 28.7521
20 | 0.054143 | 0.013638 | -0.054123 | -0.013628 | 2.0288e-05 | 1.0322e-05 | 0.081107 | 0.081108 | 0.081108 | 0.99362 | -0.12121 | 0.99322 | -0.12905 | 4.4565
21 | 0.29353 | 0.074538 | -0.29257 | -0.07393 | 0.00095639 | 0.00060787 | 0.44062 | 0.44063 | 0.44063 | 0.99203 | -0.15165 | 0.98851 | -0.2196 | 24.2102
22 | -0.051436 | -0.012951 | 0.051444 | 0.012955 | 8.7012e-06 | 4.3066e-06 | 0.077105 | 0.077105 | 0.077105 | 0.9929 | -0.13511 | 0.99309 | -0.13157 | 4.2365
23 | 0.051436 | 0.012951 | -0.051418 | -0.012942 | 1.7788e-05 | 8.8053e-06 | 0.077105 | 0.077106 | 0.077106 | 0.9929 | -0.13511 | 0.99253 | -0.14234 | 4.2366
24 | -0.053553 | -0.013484 | 0.05356 | 0.013487 | 6.4479e-06 | 3.2632e-06 | 0.080265 | 0.080265 | 0.080265 | 0.99309 | -0.13157 | 0.99322 | -0.12905 | 4.4102
25 | 0.048292 | 0.012158 | -0.04829 | -0.012158 | 1.9014e-06 | 9.0453e-07 | 0.07242 | 0.07242 | 0.07242 | 0.99253 | -0.14234 | 0.99249 | -0.14316 | 3.9791
26 | -0.045693 | -0.011504 | 0.045704 | 0.011509 | 1.0941e-05 | 4.9965e-06 | 0.068543 | 0.068542 | 0.068543 | 0.99223 | -0.14817 | 0.99249 | -0.14316 | 3.7661
27 | -0.030196 | -0.0075441 | 0.030221 | 0.0075502 | 2.4801e-05 | 6.1385e-06 | 0.046062 | 0.046058 | 0.046062 | 0.97529 | -0.47891 | 0.97617 | -0.46164 | 2.5309
28 | 0.021028 | 0.0052647 | -0.021025 | -0.0052651 | 2.7446e-06 | -4.6164e-07 | 0.032081 | 0.032082 | 0.032082 | 0.97529 | -0.47891 | 0.97515 | -0.48165 | 1.7627
29 | 0.031247 | 0.0078592 | -0.031181 | -0.0078179 | 6.6069e-05 | 4.1266e-05 | 0.047046 | 0.047047 | 0.047047 | 0.98851 | -0.2196 | 0.98622 | -0.26396 | 12.9249
30 | 0.26132 | 0.066071 | -0.26087 | -0.065784 | 0.00045191 | 0.00028674 | 0.39358 | 0.39358 | 0.39358 | 0.98851 | -0.2196 | 0.98664 | -0.25572 | 21.6253
31 | 0.013653 | 0.0034227 | -0.013651 | -0.0034213 | 2.5432e-06 | 1.4238e-06 | 0.020601 | 0.020601 | 0.020601 | 0.98622 | -0.26396 | 0.98602 | -0.26787 | 5.6595
32 | 0.017527 | 0.0043952 | -0.017521 | -0.0043917 | 5.8946e-06 | 3.4859e-06 | 0.026446 | 0.026446 | 0.026446 | 0.98622 | -0.26396 | 0.98586 | -0.27102 | 7.2654
33 | 0.0092079 | 0.0023074 | -0.0092078 | -0.0023074 | 1.2919e-07 | 5.9867e-08 | 0.013887 | 0.013887 | 0.013887 | 0.98664 | -0.25572 | 0.98662 | -0.25602 | 3.8151
34 | 0.25166 | 0.063477 | -0.25135 | -0.063276 | 0.00031575 | 0.00020021 | 0.37969 | 0.37969 | 0.37969 | 0.98664 | -0.25572 | 0.98529 | -0.28197 | 20.8623
35 | 0.0053947 | 0.001352 | -0.0053945 | -0.001352 | 2.3564e-07 | 3.5556e-08 | 0.0082395 | 0.0082395 | 0.0082395 | 0.97426 | -0.49929 | 0.97421 | -0.5002 | 2.2636
36 | -0.0053947 | -0.001352 | 0.0053956 | 0.0013522 | 9.2104e-07 | 1.3886e-07 | 0.0082395 | 0.0082393 | 0.0082395 | 0.97426 | -0.49929 | 0.97444 | -0.4957 | 2.2636
37 | -0.0053956 | -0.0013522 | 0.0053962 | 0.0013522 | 5.7145e-07 | 8.606e-08 | 0.0082393 | 0.0082392 | 0.0082393 | 0.97444 | -0.4957 | 0.97455 | -0.49348 | 2.2635
38 | 0.017216 | 0.0043128 | -0.017215 | -0.0043135 | 1.1309e-06 | -6.3795e-07 | 0.026275 | 0.026276 | 0.026276 | 0.97496 | -0.4854 | 0.97489 | -0.48677 | 1.4437
39 | -0.017216 | -0.0043128 | 0.017218 | 0.0043119 | 1.599e-06 | -9.0247e-07 | 0.026275 | 0.026274 | 0.026275 | 0.97496 | -0.4854 | 0.97506 | -0.48344 | 1.4437
40 | 0.014951 | 0.0037461 | -0.01495 | -0.003747 | 9.6938e-07 | -9.2682e-07 | 0.02282 | 0.022821 | 0.022821 | 0.97489 | -0.48677 | 0.97482 | -0.48814 | 1.2539
41 | -0.017218 | -0.0043119 | 0.017219 | 0.0043113 | 1.2102e-06 | -6.8332e-07 | 0.026274 | 0.026274 | 0.026274 | 0.97506 | -0.48344 | 0.97514 | -0.48197 | 1.4436
42 | -0.020271 | -0.0050761 | 0.020271 | 0.0050761 | 3.0486e-07 | -6.991e-08 | 0.030931 | 0.030931 | 0.030931 | 0.97514 | -0.48197 | 0.97515 | -0.48165 | 1.6995
43 | 0.0025544 | 0.00063852 | -0.002554 | -0.0006391 | 3.7786e-07 | -5.891e-07 | 0.0038931 | 0.0038934 | 0.0038934 | 0.97617 | -0.46164 | 0.97601 | -0.46475 | 1.0696
44 | -0.001014 | -0.00025413 | 0.0010141 | 0.00025317 | 7.2487e-08 | -9.6439e-07 | 0.0015461 | 0.0015457 | 0.0015461 | 0.97593 | -0.46625 | 0.97601 | -0.46475 | 0.42474
45 | -0.008764 | -0.0021965 | 0.0087649 | 0.0021969 | 8.9333e-07 | 3.9819e-07 | 0.013229 | 0.013229 | 0.013229 | 0.98575 | -0.27316 | 0.98586 | -0.27102 | 3.6345
46 | 0.0087566 | 0.0021949 | -0.0087552 | -0.0021943 | 1.3279e-06 | 5.9145e-07 | 0.013217 | 0.013217 | 0.013217 | 0.98586 | -0.27102 | 0.9857 | -0.2742 | 3.631
47 | -0.0042664 | -0.0010673 | 0.0042665 | 0.0010665 | 3.8121e-08 | -7.4485e-07 | 0.0064647 | 0.0064644 | 0.0064647 | 0.98192 | -0.34774 | 0.98193 | -0.34755 | 0.3552
48 | 0.0042664 | 0.0010673 | -0.0042664 | -0.0010687 | 7.3647e-08 | -1.4387e-06 | 0.0064647 | 0.0064652 | 0.0064652 | 0.98192 | -0.34774 | 0.9819 | -0.3481 | 0.35523
49 | -0.0071713 | -0.0017946 | 0.0071715 | 0.0017933 | 1.9183e-07 | -1.2473e-06 | 0.010866 | 0.010866 | 0.010866 | 0.98193 | -0.34755 | 0.98196 | -0.34699 | 0.59706
50 | 0.0042664 | 0.0010687 | -0.0042663 | -0.0010692 | 7.885e-08 | -5.2215e-07 | 0.0064652 | 0.0064655 | 0.0064655 | 0.9819 | -0.3481 | 0.98188 | -0.34849 | 0.59207
51 | -0.0071715 | -0.0017933 | 0.0071718 | 0.0017918 | 2.256e-07 | -1.4672e-06 | 0.010866 | 0.010865 | 0.010866 | 0.98196 | -0.34699 | 0.98199 | -0.34632 | 0.59703
52 | -0.0071718 | -0.0017918 | 0.007172 | 0.0017905 | 2.017e-07 | -1.312e-06 | 0.010865 | 0.010865 | 0.010865 | 0.98199 | -0.34632 | 0.98202 | -0.34573 | 0.597
53 | -0.01141 | -0.0028606 | 0.011412 | 0.0028615 | 1.6187e-06 | 8.5091e-07 | 0.017235 | 0.017235 | 0.017235 | 0.98513 | -0.28494 | 0.98529 | -0.28197 | 4.735
54 | 0.01141 | 0.0028606 | -0.011407 | -0.0028589 | 3.3452e-06 | 1.7587e-06 | 0.017235 | 0.017235 | 0.017235 | 0.98513 | -0.28494 | 0.98482 | -0.2911 | 4.735
55 | 0.23993 | 0.060415 | -0.2398 | -0.060332 | 0.00013066 | 8.2777e-05 | 0.36246 | 0.36246 | 0.36246 | 0.98529 | -0.28197 | 0.9847 | -0.29336 | 19.9153
56 | 0.0068252 | 0.0017106 | -0.0068246 | -0.0017104 | 6.4775e-07 | 2.0691e-07 | 0.0103 | 0.0103 | 0.0103 | 0.98602 | -0.26787 | 0.98592 | -0.26986 | 2.8297
57 | 0.0013696 | 0.00034295 | -0.0013696 | -0.00034325 | 4.1149e-08 | -3.0209e-07 | 0.0020655 | 0.0020657 | 0.0020657 | 0.98662 | -0.25602 | 0.98659 | -0.25665 | 0.56749
58 | -0.0039713 | -0.0009953 | 0.0039716 | 0.00099523 | 2.5842e-07 | -7.4659e-08 | 0.0060222 | 0.0060221 | 0.0060222 | 0.98126 | -0.3605 | 0.98133 | -0.35913 | 1.6545
59 | -0.10976 | -0.027545 | 0.10983 | 0.027588 | 7.1002e-05 | 4.3281e-05 | 0.16645 | 0.16645 | 0.16645 | 0.98133 | -0.35913 | 0.98202 | -0.34558 | 9.1454
60 | 0.012787 | 0.0032004 | -0.012786 | -0.0032017 | 8.2573e-07 | -1.3217e-06 | 0.019387 | 0.019388 | 0.019388 | 0.98133 | -0.35913 | 0.98126 | -0.36049 | 1.0653
61 | 0.093003 | 0.023349 | -0.092996 | -0.023345 | 7.3505e-06 | 4.3931e-06 | 0.14104 | 0.14104 | 0.14104 | 0.98133 | -0.35913 | 0.98125 | -0.36079 | 7.7493
62 | -0.0077229 | -0.0019355 | 0.0077238 | 0.0019359 | 9.3351e-07 | 3.6631e-07 | 0.011688 | 0.011688 | 0.011688 | 0.98321 | -0.32252 | 0.98334 | -0.31998 | 3.211
63 | 0.12737 | 0.032037 | -0.12729 | -0.031985 | 8.4335e-05 | 5.2057e-05 | 0.19279 | 0.19279 | 0.19279 | 0.98334 | -0.31998 | 0.98262 | -0.33385 | 10.5928
64 | -0.1351 | -0.033973 | 0.13514 | 0.034 | 4.3533e-05 | 2.698e-05 | 0.20448 | 0.20448 | 0.20448 | 0.98334 | -0.31998 | 0.98368 | -0.31324 | 11.235
65 | -0.10983 | -0.027588 | 0.10987 | 0.027612 | 3.9258e-05 | 2.3929e-05 | 0.16645 | 0.16645 | 0.16645 | 0.98202 | -0.34558 | 0.98241 | -0.33809 | 9.1454
66 | 0.0094826 | 0.0023739 | -0.0094819 | -0.0023764 | 7.3688e-07 | -2.5294e-06 | 0.014379 | 0.01438 | 0.01438 | 0.98126 | -0.36049 | 0.98118 | -0.36212 | 0.7901
67 | 0.085792 | 0.02155 | -0.085767 | -0.021536 | 2.4607e-05 | 1.4525e-05 | 0.13012 | 0.13012 | 0.13012 | 0.98125 | -0.36079 | 0.98094 | -0.3668 | 7.1493
68 | 0.0072045 | 0.0017942 | -0.0072035 | -0.0018009 | 1.039e-06 | -6.6679e-06 | 0.010921 | 0.010924 | 0.010924 | 0.98125 | -0.36079 | 0.98109 | -0.36383 | 0.60021
69 | 0.11581 | 0.029109 | -0.11579 | -0.029094 | 2.3426e-05 | 1.435e-05 | 0.1754 | 0.1754 | 0.1754 | 0.98262 | -0.33385 | 0.98241 | -0.33809 | 9.6376
70 | 0.01148 | 0.0028762 | -0.011479 | -0.0028773 | 9.61e-07 | -1.1034e-06 | 0.017384 | 0.017385 | 0.017385 | 0.98262 | -0.33385 | 0.98253 | -0.33561 | 1.194
71 | -0.14474 | -0.036406 | 0.14478 | 0.036427 | 3.4395e-05 | 2.1406e-05 | 0.219 | 0.219 | 0.219 | 0.98368 | -0.31324 | 0.98394 | -0.30826 | 12.0328
72 | 0.082412 | 0.020695 | -0.082387 | -0.02068 | 2.5011e-05 | 1.4661e-05 | 0.12503 | 0.12503 | 0.12503 | 0.98094 | -0.3668 | 0.98061 | -0.37317 | 6.8697
73 | 0.0072035 | 0.0018009 | -0.0072028 | -0.0018052 | 6.7071e-07 | -4.3012e-06 | 0.010924 | 0.010926 | 0.010926 | 0.98109 | -0.36383 | 0.98099 | -0.36578 | 0.6003
74 | 0.011479 | 0.0028773 | -0.011478 | -0.0028767 | 1.1553e-06 | 6.1031e-07 | 0.017385 | 0.017385 | 0.017385 | 0.98253 | -0.33561 | 0.98243 | -0.33772 | 4.7761
75 | -0.23175 | -0.05825 | 0.23188 | 0.058333 | 0.00013165 | 8.335e-05 | 0.35053 | 0.35053 | 0.35053 | 0.98394 | -0.30826 | 0.98455 | -0.29637 | 19.2601
76 | 0.086971 | 0.021823 | -0.086964 | -0.021819 | 6.7425e-06 | 3.9852e-06 | 0.13154 | 0.13154 | 0.13154 | 0.98394 | -0.30826 | 0.98385 | -0.30989 | 7.2272
77 | 0.079032 | 0.01984 | -0.07901 | -0.019826 | 2.288e-05 | 1.3306e-05 | 0.11994 | 0.11994 | 0.11994 | 0.98061 | -0.37317 | 0.9803 | -0.37924 | 6.59
78 | 0.086964 | 0.021819 | -0.086941 | -0.021805 | 2.2736e-05 | 1.3439e-05 | 0.13154 | 0.13154 | 0.13154 | 0.98385 | -0.30989 | 0.98357 | -0.31538 | 7.2273
79 | 0.076607 | 0.019215 | -0.076587 | -0.019204 | 2.045e-05 | 1.18e-05 | 0.1159 | 0.1159 | 0.1159 | 0.98357 | -0.31538 | 0.98329 | -0.32098 | 6.3683
80 | 0.0055386 | 0.0013881 | -0.0055386 | -0.0013881 | 5.7228e-09 | 9.1684e-10 | 0.008389 | 0.008389 | 0.008389 | 0.98243 | -0.33772 | 0.98243 | -0.33774 | 2.3047
81 | -0.23188 | -0.058333 | 0.23191 | 0.058354 | 3.3359e-05 | 2.112e-05 | 0.35053 | 0.35053 | 0.35053 | 0.98455 | -0.29637 | 0.9847 | -0.29336 | 19.2601
82 | 0.011467 | 0.0028731 | -0.011466 | -0.0028738 | 5.5597e-07 | -6.3839e-07 | 0.017374 | 0.017375 | 0.017375 | 0.98206 | -0.34489 | 0.98201 | -0.34591 | 1.1933
83 | -0.011467 | -0.0028731 | 0.011468 | 0.0028715 | 7.5968e-07 | -1.6369e-06 | 0.017374 | 0.017374 | 0.017374 | 0.98206 | -0.34489 | 0.98213 | -0.3435 | 0.95464
84 | 0.0057316 | 0.0014365 | -0.0057316 | -0.0014365 | 2.7342e-09 | 5.273e-10 | 0.008685 | 0.008685 | 0.008685 | 0.98201 | -0.34591 | 0.98201 | -0.34592 | 2.386
85 | 0.034755 | 0.008703 | -0.034752 | -0.0087018 | 3.6965e-06 | 1.2411e-06 | 0.052655 | 0.052655 | 0.052655 | 0.98213 | -0.3435 | 0.98202 | -0.34573 | 2.8931
86 | -0.046223 | -0.011575 | 0.04623 | 0.011578 | 6.5031e-06 | 3.0431e-06 | 0.070028 | 0.070028 | 0.070028 | 0.98213 | -0.3435 | 0.98229 | -0.34054 | 3.8477
87 | -0.0094812 | -0.0023762 | 0.0094828 | 0.002377 | 1.6455e-06 | 7.8434e-07 | 0.01437 | 0.01437 | 0.01437 | 0.98179 | -0.35016 | 0.98198 | -0.34652 | 3.9477
88 | 0.0094871 | 0.0023783 | -0.0094843 | -0.002377 | 2.7637e-06 | 1.3178e-06 | 0.014376 | 0.014376 | 0.014376 | 0.98198 | -0.34652 | 0.98167 | -0.35263 | 3.9496
89 | -0.01897 | -0.0047553 | 0.018971 | 0.0047555 | 7.096e-07 | 1.934e-07 | 0.028746 | 0.028746 | 0.028746 | 0.98198 | -0.34652 | 0.98202 | -0.34573 | 2.6324
90 | 0.075755 | 0.019011 | -0.075728 | -0.018995 | 2.652e-05 | 1.5288e-05 | 0.115 | 0.115 | 0.115 | 0.9803 | -0.37924 | 0.97993 | -0.38658 | 6.3186
91 | 0.076587 | 0.019204 | -0.076572 | -0.019195 | 1.5093e-05 | 8.7096e-06 | 0.1159 | 0.1159 | 0.1159 | 0.98329 | -0.32098 | 0.98307 | -0.32511 | 6.3683
92 | 0.067812 | 0.016999 | -0.067808 | -0.016997 | 4.2696e-06 | 2.39e-06 | 0.10264 | 0.10264 | 0.10264 | 0.98307 | -0.32511 | 0.98301 | -0.32643 | 5.6398
93 | 0.0086091 | 0.0021558 | -0.0086088 | -0.002157 | 2.9509e-07 | -1.2738e-06 | 0.013044 | 0.013045 | 0.013045 | 0.98202 | -0.34573 | 0.98198 | -0.34645 | 0.71675
94 | -0.051752 | -0.012962 | 0.051758 | 0.012964 | 5.2843e-06 | 2.6562e-06 | 0.078394 | 0.078394 | 0.078394 | 0.98229 | -0.34054 | 0.9824 | -0.3384 | 4.3074
95 | 0.066426 | 0.016651 | -0.066413 | -0.016644 | 1.2463e-05 | 6.935e-06 | 0.10055 | 0.10055 | 0.10055 | 0.98301 | -0.32643 | 0.98281 | -0.33037 | 5.5249
96 | -0.051758 | -0.012964 | 0.051759 | 0.012965 | 1.0715e-06 | 5.3858e-07 | 0.078394 | 0.078394 | 0.078394 | 0.9824 | -0.3384 | 0.98242 | -0.33796 | 4.3074
97 | -0.05753 | -0.014411 | 0.057538 | 0.014415 | 7.594e-06 | 4.0157e-06 | 0.087135 | 0.087135 | 0.087135 | 0.98242 | -0.33796 | 0.98256 | -0.33519 | 4.7877
98 | 0.0028342 | 0.0007098 | -0.0028342 | -0.00071032 | 3.2863e-08 | -5.1993e-07 | 0.0042946 | 0.0042948 | 0.0042948 | 0.98198 | -0.34645 | 0.98197 | -0.3467 | 0.39329
99 | 0.002843 | 0.00071251 | -0.002843 | -0.00071252 | 3.1275e-09 | -3.6968e-09 | 0.0043055 | 0.0043055 | 0.0043055 | 0.98256 | -0.33519 | 0.98256 | -0.33522 | 1.1828
100 | -0.060381 | -0.015128 | 0.060395 | 0.015135 | 1.3861e-05 | 7.471e-06 | 0.091441 | 0.09144 | 0.091441 | 0.98256 | -0.33519 | 0.98281 | -0.33037 | 5.0242
101 | -0.0045154 | -0.0011317 | 0.0045155 | 0.0011299 | 1.0133e-07 | -1.7356e-06 | 0.0068661 | 0.0068655 | 0.0068661 | 0.97856 | -0.41338 | 0.97859 | -0.41291 | 0.37726
102 | -0.0094358 | -0.0023631 | 0.0094363 | 0.0023615 | 4.5161e-07 | -1.5487e-06 | 0.014347 | 0.014347 | 0.014347 | 0.97859 | -0.41291 | 0.97864 | -0.4119 | 0.78831
103 | -0.0052415 | -0.0013137 | 0.005243 | 0.0013138 | 1.4919e-06 | 1.6781e-07 | 0.0079704 | 0.0079701 | 0.0079704 | 0.97855 | -0.41359 | 0.97886 | -0.40762 | 2.1897
104 | 0.0078197 | 0.0019601 | -0.0078179 | -0.0019593 | 1.8333e-06 | 7.3853e-07 | 0.011887 | 0.011887 | 0.011887 | 0.97886 | -0.40762 | 0.97861 | -0.41254 | 3.2658
105 | -0.013063 | -0.0032739 | 0.013064 | 0.0032746 | 1.2702e-06 | 7.0493e-07 | 0.019857 | 0.019857 | 0.019857 | 0.97886 | -0.40762 | 0.97896 | -0.40558 | 5.4553
106 | -0.011282 | -0.0028273 | 0.011282 | 0.0028276 | 6.1846e-07 | 3.2656e-07 | 0.017226 | 0.017226 | 0.017226 | 0.97455 | -0.49348 | 0.97461 | -0.49233 | 4.7323
107 | 0.013672 | 0.0034266 | -0.013671 | -0.0034263 | 1.0053e-06 | 3.3645e-07 | 0.020869 | 0.020869 | 0.020869 | 0.97482 | -0.48814 | 0.97475 | -0.48968 | 2.8667
108 | -0.011985 | -0.0030038 | 0.011987 | 0.0030046 | 1.5125e-06 | 8.1789e-07 | 0.018299 | 0.018299 | 0.018299 | 0.97461 | -0.49233 | 0.97475 | -0.48968 | 5.0271
109 | 0.0016839 | 0.00042169 | -0.0016839 | -0.00042201 | 7.4954e-08 | -3.2906e-07 | 0.0025705 | 0.0025706 | 0.0025706 | 0.97475 | -0.48968 | 0.9747 | -0.49061 | 0.70622
110 | 0.03114 | 0.0077995 | -0.031138 | -0.007799 | 1.7799e-06 | 4.7355e-07 | 0.047337 | 0.047337 | 0.047337 | 0.97884 | -0.40805 | 0.97877 | -0.40925 | 2.6009
111 | -0.035086 | -0.0087885 | 0.03509 | 0.00879 | 4.1308e-06 | 1.4267e-06 | 0.053336 | 0.053336 | 0.053336 | 0.97884 | -0.40805 | 0.97896 | -0.40558 | 2.9305
112 | 0.027286 | 0.0068335 | -0.027285 | -0.0068334 | 2.1847e-07 | 3.3433e-08 | 0.04148 | 0.04148 | 0.04148 | 0.97877 | -0.40925 | 0.97877 | -0.40942 | 2.2791
113 | -0.048154 | -0.012065 | 0.048167 | 0.012071 | 1.2771e-05 | 6.1747e-06 | 0.073193 | 0.073192 | 0.073193 | 0.97896 | -0.40558 | 0.97924 | -0.40001 | 4.0216
114 | 0.021743 | 0.0054443 | -0.021742 | -0.0054445 | 1.0044e-06 | -1.274e-07 | 0.033054 | 0.033054 | 0.033054 | 0.97877 | -0.40942 | 0.97872 | -0.41039 | 1.8162
115 | 0.015281 | 0.0038332 | -0.015275 | -0.0038301 | 5.4834e-06 | 3.1684e-06 | 0.023221 | 0.023221 | 0.023221 | 0.97924 | -0.40001 | 0.97886 | -0.40754 | 6.3794
116 | -0.063448 | -0.015904 | 0.063461 | 0.015912 | 1.3734e-05 | 7.5503e-06 | 0.096413 | 0.096413 | 0.096413 | 0.97924 | -0.40001 | 0.97948 | -0.39547 | 5.2974
117 | 0.016765 | 0.0041973 | -0.016764 | -0.004198 | 1.1534e-06 | -7.4911e-07 | 0.025488 | 0.025489 | 0.025489 | 0.97872 | -0.41039 | 0.97864 | -0.41183 | 1.4005
118 | 0.012563 | 0.0031503 | -0.012558 | -0.0031474 | 5.3638e-06 | 2.9401e-06 | 0.019098 | 0.019098 | 0.019098 | 0.97886 | -0.40754 | 0.9784 | -0.4165 | 5.2468
119 | -0.069993 | -0.017549 | 0.070023 | 0.017565 | 2.9498e-05 | 1.6688e-05 | 0.10634 | 0.10633 | 0.10634 | 0.97948 | -0.39547 | 0.97993 | -0.38663 | 5.8426
120 | 0.013629 | 0.0034123 | -0.013629 | -0.0034124 | 4.4711e-08 | -5.8607e-08 | 0.020722 | 0.020722 | 0.020722 | 0.97864 | -0.41183 | 0.97864 | -0.4119 | 1.1386
121 | 0.0088888 | 0.0022279 | -0.0088866 | -0.0022269 | 2.2205e-06 | 1.0143e-06 | 0.013519 | 0.013519 | 0.013519 | 0.9784 | -0.4165 | 0.97814 | -0.42175 | 3.714
122 | -0.072782 | -0.018257 | 0.072782 | 0.018257 | 1.6111e-07 | 9.2032e-08 | 0.11052 | 0.11052 | 0.11052 | 0.97993 | -0.38663 | 0.97993 | -0.38658 | 6.0728
123 | 0.0041523 | 0.0010404 | -0.0041517 | -0.0010405 | 6.2205e-07 | -1.2361e-07 | 0.0063167 | 0.0063169 | 0.0063169 | 0.97814 | -0.42175 | 0.97798 | -0.42489 | 1.7354

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35735 | 0.091148

## res_load
| p_mw | q_mvar
0 | 0.00073062 | 0.00018311
1 | 0.0027892 | 0.00069905
2 | 0.0033226 | 0.00083272
3 | 0.00099174 | 0.00024855
4 | 0.0041064 | 0.0010292
5 | 0.0010401 | 0.00026068
6 | 0.0030525 | 0.00076503
7 | 0.0021091 | 0.0005286
8 | 0.0031255 | 0.00078333
9 | 0.0065165 | 0.0016332
10 | 0.0045107 | 0.0011305
11 | 0.0053945 | 0.001352
12 | 0.0022638 | 0.00056737
13 | 0.0030519 | 0.00076487
14 | 0.00056314 | 0.00014114
15 | 0.001014 | 0.00025413
16 | 0.0015399 | 0.00038593
17 | 0.0025867 | 0.00064829
18 | 0.00075441 | 0.00018907
19 | 0.008764 | 0.0021965
20 | 0.0029049 | 0.00072803
21 | 0.011407 | 0.0028589
22 | 0.0068256 | 0.0017107
23 | 0.0078381 | 0.0019644
24 | 0.0039713 | 0.0009953
25 | 0.0077229 | 0.0019355
26 | 0.0033031 | 0.00082785
27 | 0.0095998 | 0.0024059
28 | 0.005915 | 0.0014824
29 | 0.0094819 | 0.0023764
30 | 0.003355 | 0.00084085
31 | 0.0033545 | 0.00084071
32 | 0.0072028 | 0.0018052
33 | 0.010334 | 0.00259
34 | 0.0059395 | 0.0014886
35 | 0.0057348 | 0.0014373
36 | 0.0055386 | 0.0013881
37 | 0.0094812 | 0.0023762
38 | 0.0032547 | 0.0008157
39 | 0.0087594 | 0.0021953
40 | 0.0078921 | 0.0019779
41 | 0.0057316 | 0.0014365
42 | 0.0055228 | 0.0013841
43 | 0.0013823 | 0.00034642
44 | 0.0057714 | 0.0014464
45 | 0.0057746 | 0.0014472
46 | 0.002843 | 0.00071252
47 | 0.0060185 | 0.0015084
48 | 0.0094843 | 0.002377
49 | 0.0028342 | 0.00071032
50 | 0.0042663 | 0.0010692
51 | 0.0045154 | 0.0011317
52 | 0.0049203 | 0.0012332
53 | 0.0052415 | 0.0013137
54 | 0.0068246 | 0.0017104
55 | 0.0087552 | 0.0021943
56 | 0.0013696 | 0.00034325
57 | 0.0058855 | 0.0014751
58 | 0.0012785 | 0.00032042
59 | 0.00070289 | 0.00017616
60 | 0.0016839 | 0.00042201
61 | 0.0039464 | 0.00098905
62 | 0.0038525 | 0.00096553
63 | 0.0055426 | 0.0013891
64 | 0.0049764 | 0.0012472
65 | 0.0027122 | 0.00067973
66 | 0.0065318 | 0.001637
67 | 0.0078179 | 0.0019593
68 | 0.0031351 | 0.00078573
69 | 0.0036687 | 0.00091946
70 | 0.0027592 | 0.00069153
71 | 0.0041929 | 0.0010508
72 | 0.0047343 | 0.0011865
73 | 0.0029463 | 0.00073841
74 | 0.0041517 | 0.0010405

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1